## Sheet1
Miller Power & Communications
PO Box 50 Santa Margarita CA 93453-0050 805-438-5600
ENGINEERING WORKSHEET
Point of Connection Worksheet
Buss Overcurrent rating | 200
Buss Rating | 200
Max Output amps per inverter | 20.8
Number of inverters | 2
Continuous rating | 1.25
Coninuous rated output | 52
Buss OC rating | 200
Buss Rating | 200
Buss Rating X 1.2 | 240
Total feeds (must be less than above) | 252
OK? | Not Ok
Instructions:
Enter buss over current protection rating and buss rating in shaded cells above.
If the design meets the criteria outlined in Section 690.64 B 2, you will see an "OK" in the last row.
Notes:
This spread sheet evaluates compliance with NEC section 690.64 B 2.
The spreadsheet is protected but not with a password. Feel free to tweak for your own use.
This spread sheet is provided as a courtesy and MP&C assumes no liability in it's use.
Microsoft Excel is not the spreadsheet of choice for the author. He has created
this tool in Excel as a courtesy to his colleagues. Any input is appreciated.
William Miller
wrmiller@mpandc.com