## String Sizing
|  |  | Solar PV String Sizing Tool | [16 empty] | 2021-11-03 |  | V4.0.0 | [7 empty] | -0.27%
Project Name | [14 empty] | Design Date
|  |  | PVR Repower | [17 empty] | 2022-04-28
Design Location and Temperatures | [14 empty] | Module Specifications
[18 empty] | MPPT 1 | MPPT 2 | MPPT 3 |  |  |  | 1
[15 empty] | MODULE NAME |  |  | Conergy S-175MU | Conergy S-175MU | Conergy S-175MU
Choose your region |  |  | North_America | [21 empty] | 33 | 33 | 33 | Location Selection |  |  | bi facial module?
Temperature Data Source |  |  | ASHRAE 2% High Temp | [24 empty] | State |  |  | Conergy S-175MU
Country |  |  | United_States | [11 empty] | Rated Power (STC) |  |  | 175 | 175 | 175 |  |  |  | 2 |  |  |  | California
State/Province |  |  | California | [11 empty] | Rated Power (t) [Regional Simulation Estimate] |  |  | 159.1609 | 159.1609 | 159.1609 |  |  |  | 0.90949 | 0.90949 | 0.90949
ASHRAE Weather Station |  |  | FRESNO YOSEMITE INTL AP | [9 empty] | W2 |  | Max System Voltage (Vdc) |  |  | 600 | 600 | 600 |  |  |  | 4
[15 empty] | Module Voc (STC) |  |  | 44.2 | 44.2 | 44.2 |  |  |  | 7 | [6 empty] | bi facial
|  |  | ASHRAE |  | SELECTED |  |  |  |  | MANUAL ENTRY |  | ↓Select |  |  | Module Vmp (STC) |  |  | 35.2 | 35.2 | 35.2 |  |  |  | 5
Extreme Low Temp |  |  | -1.9 |  | -1.9 |  |  |  |  | -21 |  | °C | -21 |  | Module Imp (STC) |  |  | 4.95 | 4.95 | 4.95 |  |  |  | 6 |  |  |  | Name Replacement
ASHRAE 2% High Temp |  |  | 41 |  | 41 |  |  |  |  | 46 |  | °C | 46 |  | Module Isc (STC) |  |  | 5.2 | 5.2 | 5.2 |  | Isc(t) Method |  | 8 |  |  |  | Module Lookup Name Replace |  | Module Manufacturer Name Replace |  |  |  |  | #REF!
Max Cell Temp. ASHRAE 2% |  |  | 66 | °C | [8 empty] | 0 |  | Module Isc(t) | (3hr Avg) |  | 5.4648 | 5.4648 | 5.4648 |  | Y | 3-Hr | 1.0509 | 1.0509 | 1.0509
Equipment Selection | [14 empty] | Module Isc (?) |  |  | 8.5251 | 8.5251 | 8.5251 |  |  |  | 1.0509 | 1.0509 | 1.0509 |  | Modules!B4:AH4000 |  | Custom_Module |  |  |  |  | #REF!
[15 empty] | Manufacturer's Fuse Rating (Max) |  |  | 15 | 15 | 15 |  |  |  | 12
Roof, Fixed, or Single Axis? |  |  | Single-Axis | [9 empty] | S |  | Voc Correction (%/°C) |  |  | -0.27% | -0.27% | -0.27% |  |  |  | 10 |  |  |  | Module List Range
|  |  | Custom_Module | [11 empty] | Vmp Correction (%/°C) |  |  | -0.35% | -0.35% | -0.35% |  |  |  | 9 |  |  |  | Q71:Q165
| MPPT 1 Module |  | Conergy S-175MU | [7 empty] | MonoFacial |  |  |  | Type- MonoFacial (MF) / BiFacial (BF) / ThinFilm (TF) |  |  | MF | MF | MF |  |  |  | 11
| MPPT 2 Module |  | Conergy S-175MU | [7 empty] | MonoFacial |  |  |  | Adjusted Module Voc @ Low Temp |  |  | 47.4102 | 47.4102 | 47.4102
| MPPT 3 Module |  | Conergy S-175MU | [7 empty] | MonoFacial |  |  |  | Adjusted Module Vmp @ High Temp |  |  | 30.1488 | 30.1488 | 30.1488 | [15 empty] | #REF!
| Total Modules | 336 | [12 empty] | Adjusted Module Vmp @ Low Temp |  |  | 38.5141 | 38.5141 | 38.5141 | [15 empty] | #REF!
Chint Inverter Model Number |  |  | SCA60KTL-DO/US-480-UL
[15 empty] | Inverter Specifications | [18 empty] | #REF! |  | #REF!
[15 empty] | Inverter Model Number |  | SCA60KTL-DO/US-480-UL | [18 empty] | #REF!
System Design Parameters | [14 empty] | Output (AC) | [18 empty] | #REF! |  | #REF!
Inverter Options | [14 empty] | Max Rated Output Power (W) ¦ (VA) |  | 60000 |  | ¦ | 60000 |  | 66000 | [5 empty] | Error Highlighting | [5 empty] | #REF! |  | #REF!
| Total Operate Range |  | Inverter Voltage Range |  |  |  | APPROVED |  |  |  | 2022-04-28 |  |  |  | Rated Output Voltage |  |  | 480 | [9 empty] | Is this a 50/60 inverter? | No |  |  |  |  | #REF! |  | #REF!
| No |  | Use KVA Overhead if available. |  |  |  | CPS APPLICATION ENGINEERING | [7 empty] | Neutral Required |  |  | NO | [9 empty] | Is total wattage too much? | #REF! | Hi-Lite Operating Max? | #REF! |  |  | #REF! |  | #REF!
[15 empty] | Max. Rated Output Current (IMAX) |  | 72.2543 |  | ¦ | 90.3179 | (IMAX x 1.25) | [6 empty] | Highlight MPPT 1 Wattage? | #REF! | Max parallel met mppt 1? | #REF! |  |  | #REF!
Y | Yes |  | Parallel MPPTs?? | [11 empty] | Manufacturer Specified Maximum OCPD |  |  | 100 | [9 empty] | Highlight MPPT 2 Wattage? | #REF! | Max parallel met mppt 2? | #REF! |  |  | #REF! |  | #REF!
| CPS Technican Must Parallel - Do Not Parallel in Wire box - Service Fee to Parallel Inverters | [13 empty] | Input (DC) | [12 empty] | Highlight MPPT 3 Wattage? | #REF! | Max parallel met mppt 3? | #REF! |  |  | #REF! |  | #REF!
[15 empty] | MPPTs ¦ Strings per MPPT |  | 3 |  | ¦ | 5 | [7 empty] | Single MPPT? | #REF! | Hi-Light Dual MPPT parallel? | #REF! |  |  |  |  | #REF!
| INVERTER DESIGN COMPATIBILITY STATUS | [13 empty] | Maximum Input Voltage |  |  | 1000 | [9 empty] | Dual MPPT? | #REF! | Hi-Light Single MPPT parallel? | #REF! |  |  | #REF! |  | #REF!
| High Voc | Status | Prompt |  | Isc | Status | Prompt |  | DC/AC Ratio |  | Status | Prompt |  |  | Max WdcSTC Input (TOTAL ¦ MPPT) |  | 90000 |  | ¦ | 33000 | [7 empty] | Triple MPPT? | #REF! | Current Input per MPPT | #REF! |  |  | #REF! |  | #REF!
#NAME? |  |  |  |  | 3hr-AVG | [9 empty] | Max IscSTC Input (TOTAL ¦ MPPT) |  | 163.2 |  | ¦ | 59.84 | [7 empty] | Highlight MPPT 1? | #REF! | Module voltage flag? | #REF! |  |  | #REF! |  | #REF!
|  | 0 |  |  |  | 0 |  |  |  | 0 | 0 | 0 |  |  | MPPT Voltage Range |  | 540 |  | ¦ | 850
Array Design Options | [14 empty] | DC Operation Range |  | 200 |  | ¦ | 950
Module Type |  | MPPT 1 |  | MPPT 2 |  | MPPT 3 | [8 empty] | DC/AC Ratio (LIMIT ¦ Actual) |  | 1.5 |  | ¦ | 0.8913 |  | 59.42% | [5 empty] | Highlight MPPT 2? | #REF! | Module Voltage Rating | 600 |  |  |  |  | #REF!
String Length |  | 12 |  | 12 |  | 12 |  | 0
String Length (Max ¦¦ Min) |  | 21 | 7 | 21 | 7 | 21 | 7 | 1 | [6 empty] | Terms and Conditions | [12 empty] | Highlight MPPT 3? | #REF! | Module Voltage Rating to display | 600 |  |  |  |  | #REF!
Number of Strings |  | 14 |  | 14 |  | 0 |  | 1 | External combiner required | [5 empty] | THE USER OF THIS SIZING TOOL HAS ACKNOWLEDGED: The Solar PV String Sizing Tool is being offered free of charge as a guide only. Chint Power Systems, make no representation or warranty regarding the output of the Solar PV String Sizing Tool or any claim to the actual performance of your system. It is the responsibility of the system design engineer to ensure that the PV module selection and array configuration are appropriate for the system being considered. The user agrees to use this Solar PV String Sizing Tool spreadsheet at their own risk and with the knowledge that Chint Power Systems will not be liable to the user for any damages, injury or death as a result of use of the Solar PV String Sizing Tool. | [12 empty] | Error Change MPPT Setup? | #REF! | Is minimum string greater than max? | #REF! |  |  |  |  | #REF!
Combined Parallel Strings |  | 1 |  | 1 |  | 0 |  |  |  |  | Limits | [16 empty] | MPPT 1 Minimum String met? | #REF! | DC Combiner required Single MPPT? | #REF! |  |  |  |  | #REF!
` |  | MPPT 1 |  | MPPT 2 |  | MPPT 3 |  | TOTALS |  |  | MPPT | Total | [15 empty] | MPPT 2 Minimum String met? | #REF! | DC Combiner required MPPT 1? | #REF! |  |  |  |  | #REF!
Connected Wdc(DYNAMIC) |  | 17826.0224 |  | 17826.0224 |  | 0 |  | 53478.0673 |  |  | 33000 | 90000 | [15 empty] | MPPT 3 Minimum String met? | #REF! | DC Combiner required MPPT 2? | #REF! |  |  |  |  | #REF!
Connected Isc(DYNAMIC) |  | 51.005 |  | 51.005 |  | 51.005 |  | 153.0151 |  |  | 59.84 | 163.2 | [15 empty] | Hi-Lite Operating Range Min? | #REF! | DC Combiner required MPPT 3? | #REF!
Connected Voc @TMIN |  | 568.923 |  | 568.923 |  | 0 |  |  |  |  | 1000 | 1000 | [15 empty] | Hi-Lite MPPT Range Min? | #REF! | DC Combiner required? | #REF!
Connected Vmp @ TMAX |  | 362 |  | 362 |  | 362 |  | #NAME? |  |  | 540 | 540 | [15 empty] | MPPT 1 Maximum String met? | #REF!
String Fuse Max (Manuf. Spec) |  | 15 |  | 15 |  | 15 |  | #NAME?
String Fuse (NEC Alternate) |  | 6.831 |  | 6.831 |  | 6.831 | [21 empty] | MPPT 2 Maximum String met? | #REF!
Connected Vmp @ TMAX |  | 362 |  | 362 |  | 362 | [21 empty] | MPPT 3 Maximum String met? | #REF!
Connected Vmp @ TMIN |  | 462.169 |  | 462.169 |  | 462.169
Pmp @ TMAX |  | 19600 |  | 19600 |  | 19600 |  | 58800
Imp @ TMAX |  | 54.1436 |  | 54.1436 |  | 54.1436 |  | 162.4309 | [24 empty] | IF($E$29="CPS SCA25KTL-DO/US-480",DUAL MPPT,IF($R$30=2,$AJ$81:$AJ$82,IF($R$30=3,$AK$81:$AK$82,IF($R$30=1,SINGLE MPPT)))
IMAX Inverter |  | 37.7929 |  | 37.7929 |  | 37.7929 |  | 113.3787 |  |  | 1.4326 | 1.4326
| Select | 1 |  | 1 |  | 1
| Wdc | 26739.0336 |  | 26739.0336 |  | 0
| Combined Strings | 1 |  | 1 |  | 0
| Isc | 76.5075 |  | 76.5075 |  | 0
| String Length | 12 |  | 12 |  | 12
336 | No Strings | 14 |  | 14 |  | 0
|  | 26739.0336 |  | 26739.0336 |  | 0
THE USER OF THIS SIZING TOOL HAS ACKNOWLEDGED: The Solar PV String Sizing Tool is being offered free of charge as a guide only. Chint Power Systems, Mayfield Renewables LLC, and Envect Inc. make no representation or warranty regarding the output of the Solar PV String Sizing Tool or any claim to the actual performance of your system. It is the responsibility of the system design engineer to ensure that the PV module selection and array configuration are appropriate for the system being considered. The user agrees to use this Solar PV String Sizing Tool spreadsheet at their own risk and with the knowledge that Chint Power Systems, Mayfield Renewables LLC, and Envect Inc. will not be liable to the user for any damages, injury or death as a result of use of the Solar PV String Sizing Tool.
0
Minimum is greater then the maximum check
| Module List | [5 empty] | Inverter List | [6 empty] | Updated Module List | [22 empty] | Calculated Minimum? | #REF! | Calculated Minimum | #REF!
| Custom_Module | [5 empty] | Custom_Inverter | [6 empty] | X | Custom_Module | Q71 | [12 empty] | Calculated Maximum? | #REF! | Calculated Maximum | #REF! | Temp Data Selection Method |  |  | Roof, Rack, or Pole
| Abound_Solar | [5 empty] | Advanced_Energy | [6 empty] | X | Abound_Solar | Q71 | [12 empty] | #REF! | Minimum Larger than maximum? | #REF! |  | ASHRAE 2% High Temp |  |  | Roof
| Advanced_Solar_Photonics | [5 empty] | Altenergy_Power_Systems | [6 empty] | X | Advanced_Solar_Photonics | Q71:Q72 | [16 empty] | ASHRAE .4% High Temp |  |  | Fixed
| Advent | [5 empty] | Alpha_Technologies | [6 empty] | X | Advent | Q71:Q73 | [16 empty] | Manual Entry |  |  | Single-Axis
| aleo_solar | [5 empty] | Ballard | [6 empty] | X | Aleo_Solar | Q71:Q74
| American_Solar_Wholesale | [5 empty] | Chint_Power | [6 empty] | X | American_Solar_Wholesale | Q71:Q75 | [16 empty] | Countries |  |  | Voltage Range
| Amerisolar | [5 empty] | Delta_Energy | [6 empty] | X | Amerisolar | Q71:Q76 | [14 empty] | Region |  | Canada |  |  | Operating DC Input Voltage Range
| Astronergy | [5 empty] | Eaton_Corp | [6 empty] | X | Astronergy | Q71:Q77 | [16 empty] | Mexico |  |  | MPPT Voltage Range
Latin_America
| AUO_Solar | [5 empty] | Enphase | [6 empty] | X | AUO_Solar | Q71:Q78 | [16 empty] | United_States
| Auxin_Solar | [5 empty] | Exeltech | [6 empty] | X | Auxin_Solar | Q71:Q79 | [19 empty] | MPPT Setup
| Bosch_Solar_Energy | [5 empty] | Fronius_USA | [6 empty] | X | Bosch_Solar_Energy | Q71:Q80 | [14 empty] | Region |  |  |  |  | Single MPPT | Triple MPPT
| BP_Solar | [5 empty] | Ingeteam | [6 empty] | X | Boviet_Solar | Q71:Q81 | [14 empty] | North_America |  |  |  |  | Dual MPPT | Single MPPT
| BYD | [5 empty] | KACO_new_energy | [6 empty] | X | BP_Solar | Q71:Q82 | [14 empty] | Europe
| Canadian_Solar | [5 empty] | Motech | [6 empty] | X | BYD | Q71:Q83
| Centrosolar | [5 empty] | Nextronex_Energy_Systems | [6 empty] | X | Canadian_Solar | Q71:Q84 | [18 empty] | NO=FALSE YES=TRUE
| Chaori_Solar | [5 empty] | OPTI_Solar | [6 empty] | X | Centrosolar | Q71:Q85 | [13 empty] | Inverters |  |  |  | MPPT1 | MPPT2 | MPPT3
| China_Sunergy | [5 empty] | Power_One | [6 empty] | X | Certainteed | Q71:Q86 | [15 empty] | #REF! |  | #REF! | #REF! | #REF! | String size too Large
| Conergy | [5 empty] | REFUsol | [6 empty] | X | Chaori_Solar | Q71:Q87 | [15 empty] | #REF! |  | #REF! | #REF! | #REF! | String size too small
| CSG_PVTech | [5 empty] | Satcon | [6 empty] | X | China_Sunergy | Q71:Q88 | [15 empty] | PV array input exceeds the maximum allowed input current or wattage per MPPT! |  | #REF! | #REF! | #REF!
| Dahai | [5 empty] | Schneider_Electric | [6 empty] | X | Conergy | Q71:Q89 | [15 empty] | PV array input power exceeds the inverter's input ability! |  | #REF!
| Day4_Energy | [5 empty] | Siemens_USA | [6 empty] | X | CSG_PVTech | Q71:Q90 | [14 empty] | #REF! | Module max. voltage is less than inverter max. voltage. |  | #REF!
| DelSolar | [5 empty] | Silicon_Energy_LLC | [6 empty] | X | Dahai | Q71:Q91 | [15 empty] | PV array voltage and input current exceeds the inverter's input ability! |  | #REF!
| ecoSolargy | [5 empty] | SMA_America | [6 empty] | X | Day4_Energy | Q71:Q92 | [15 empty] | PV array voltage and input power out of inverters operating range! |  | #REF!
| EGING_PV | [5 empty] | SolarEdge | [6 empty] | X | DelSolar | Q71:Q93 | [15 empty] | PV array current and input power exceeds the inverters input ability! |  | #REF!
| Eoplly | [5 empty] | Solectria_Renewables | [6 empty] | X | ecoSolargy | Q71:Q94 | [15 empty] | PV array current, voltage and input power out of the inverters input ability! |  | #REF!
[14 empty] | X | EGING_PV | Q71:Q95 | [15 empty] | Missing or Incomplete weather data. |  | No
[14 empty] | X | Eoplly | Q71:Q96 | [15 empty] | External DC combiner panel required.
| ET_Solar | [5 empty] | Soleil_Sonetek | [6 empty] | X | ET_Solar | Q71:Q97 | [14 empty] | #REF!
| Evergreen_Solar | [5 empty] | Sungrow_Power_Supply | [6 empty] | X | Evergreen_Solar | Q71:Q98
| First_Solar | [12 empty] | X | First_Solar | Q71:Q99
| GE | [12 empty] | X | GE | Q71:Q100
| Gloria_Solar | [12 empty] | X | Global_Solar | Q71:Q101
| Grape_Solar | [12 empty] | X | Gloria_Solar | Q71:Q102
| Global_Solar | [12 empty] | X | Grape_Solar | Q71:Q103
| Hanwha_SolarOne | [12 empty] | X | Hanwha_SolarOne | Q71:Q104
| Helios_Solar_Works | [12 empty] | X | Helios_Solar_Works | Q71:Q105
| Hyundai_Heavy_Industries | [12 empty] | X | Hyundai_Heavy_Industries | Q71:Q106
| Instalaciones_Pevafersa | [12 empty] | X | Instalaciones_Pevafersa | Q71:Q107
| itek_energy | [12 empty] | X | itek_energy | Q71:Q108
| JA_Solar | [12 empty] | X | JA_Solar | Q71:Q109
| Jinko_Solar | [12 empty] | X | Jinko_Solar | Q71:Q110
| Kaneka | [12 empty] | X | Kaneka | Q71:Q111
| Kyocera_Solar | [12 empty] | X | Kyocera_Solar | Q71:Q112
| LDK | [12 empty] | X | LDK | Q71:Q113
| LG_Electronics | [12 empty] | X | LG_Electronics | Q71:Q114
| Lightway | [12 empty] | X | Lightway_Solar | Q71:Q115
| Lumos | [12 empty] | X | Lumos | Q71:Q116
| MAGE_Solar | [12 empty] | X | MAGE_Solar | Q71:Q117
| MEMC | [12 empty] | X | MEMC | Q71:Q118
| Mitsubishi_Electric | [12 empty] | X | Mitsubishi_Electric | Q71:Q119
| Motech_Americas | [12 empty] | X | Motech_North_America | Q71:Q120
| Nexus_Energy_Solutions | [12 empty] | X | Nexus_Energy_Solutions | Q71:Q121
| Perlight_Solar | [12 empty] | X | Panasonic_Sanyo | Q71:Q122
| REC | [12 empty] | X | Peimar | Q71:Q123
| ReneSola | [12 empty] | X | Perlight_Solar | Q71:Q124
| Renogy | [12 empty] | X | REC | Q71:Q125
| Ritek | [12 empty] | X | ReneSola | Q71:Q126
| Samsung_Electronics | [12 empty] | X | Renogy | Q71:Q127
| Panasonic_Sanyo | [12 empty] | X | Ritek | Q71:Q128
| Sainty_Solar | [12 empty] | X | Samsung_Electronics | Q71:Q129
| Scheuten_Solar | [12 empty] | X | Sainty_Solar | Q71:Q130
| SCHOTT_Solar | [12 empty] | X | Scheuten_Solar | Q71:Q131
| Schüco | [12 empty] | X | SCHOTT_Solar | Q71:Q132
| SET_Solar | [12 empty] | X | Schüco | Q71:Q133
| Sharp | [12 empty] | X | SET_Solar | Q71:Q134
| Silfab_Solar | [12 empty] | X | Sharp | Q71:Q135
| Silicon_Energy | [12 empty] | X | Silfab_Solar | Q71:Q136
| Siliken | [12 empty] | X | Silicon_Energy | Q71:Q137
| Solar_Frontier | [12 empty] | X | Siliken | Q71:Q138
| Solaria | [12 empty] | X | SolarCity | Q71:Q139
| Solar_Power_Inc | [12 empty] | X | Solar_Frontier | Q71:Q140
| Solartech | [12 empty] | X | Solaria | Q71:Q141
| SolarWorld | [12 empty] | X | Solar_Power_Inc | Q71:Q142
| Solon | [12 empty] | X | Solartech | Q71:Q143
| Solopower | [12 empty] | X | SolarWorld | Q71:Q144
| SolTech | [12 empty] | X | Solon | Q71:Q145
| Stion | [12 empty] | X | Solopower | Q71:Q146
| Sun_Earth_Solar_Power | [12 empty] | X | SolTech | Q71:Q147
| Sunpreme | [12 empty] | X | Stion | Q71:Q148
| SunPower | [12 empty] | X | Sun_Earth_Solar_Power | Q71:Q149
| Suntech | [12 empty] | X | SunPower | Q71:Q150
| Sunwize | [12 empty] | X | Sunpreme | Q71:Q151
| Talesun | [12 empty] | X | Suntech | Q71:Q152
| Tianwei_New_Energy | [12 empty] | X | Sunwize | Q71:Q153
| Trina_Solar | [12 empty] | X | Talesun | Q71:Q154
| UniSolar | [12 empty] | X | Tianwei_New_Energy | Q71:Q155
| Upsolar | [12 empty] | X | Trina_Solar | Q71:Q156
| Westinghouse | [12 empty] | X | UniSolar | Q71:Q157
| XC3_International | [12 empty] | X | Upsolar | Q71:Q158
| Yingli_Green_Energy | [12 empty] | X | Westinghouse | Q71:Q159
| Xunlight | [12 empty] | X | XC3_International | Q71:Q160
| Zhejiang_Wanxiang_Solar | [12 empty] | X | Yingli_Green_Energy | Q71:Q161
| ZNSHINESOLAR | [12 empty] | X | Xunlight | Q71:Q162
[14 empty] | X | Zhejiang_Wanxiang_Solar | Q71:Q163
[14 empty] | X | ZNSHINE_SOLAR | Q71:Q164
[14 empty] | L |  | Q71:Q165
[14 empty] | N |  | Q71:Q166
[14 empty] | N |  | Q71:Q167
[14 empty] | N |  | Q71:Q168
[14 empty] | N |  | Q71:Q169
[14 empty] | N |  | Q71:Q170
[14 empty] | N |  | Q71:Q171
[14 empty] | N |  | Q71:Q172
[14 empty] | N |  | Q71:Q173
[14 empty] | N |  | Q71:Q174
[14 empty] | N |  | Q71:Q175
[14 empty] | N |  | Q71:Q176
[14 empty] | N |  | Q71:Q177
[14 empty] | N |  | Q71:Q178
[14 empty] | N |  | Q71:Q179
[14 empty] | N |  | Q71:Q180
[14 empty] | N |  | Q71:Q181
[14 empty] | N |  | Q71:Q182
[14 empty] | N |  | Q71:Q183
[14 empty] | N |  | Q71:Q184
[14 empty] | N |  | Q71:Q185
[14 empty] | N |  | Q71:Q186
[14 empty] | N |  | Q71:Q187
[14 empty] | N |  | Q71:Q188
[14 empty] | N |  | Q71:Q189
[14 empty] | N |  | Q71:Q190
[14 empty] | N |  | Q71:Q191
[14 empty] | N |  | Q71:Q192
[14 empty] | N |  | Q71:Q193
[14 empty] | N |  | Q71:Q194
[14 empty] | N |  | Q71:Q195
[14 empty] | N |  | Q71:Q196
[14 empty] | N |  | Q71:Q197
[14 empty] | N |  | Q71:Q198
Peru
Philippines
Poland
Portugal
Puerto_Rico
Qatar
Réunion
Romania
Russia
Saint_Helena
Saint_Lucia
Saudi_Arabia
Senegal
Serbia
Seychelles
Singapore
Slovakia
Slovenia
Solomon_Islands
South_Africa
Spain
Svalbard_and_Jan_Mayen
Sweden
Switzerland
Syrian_Arab_Republic
Taiwan
Tajikistan
Thailand
Trinidad_and_Tobago
Tunisia
Turkey
Turkmenistan
Tuvalu
Ukraine
United_Arab_Emirates
United_Kingdom
Uruguay
Uzbekistan
Vanuatu
Venezuela
Vietnam
Wallis_and_Futuna
Zimbabwe
States
Alabama
Alaska
Arizona
Arkansas
California
Colorado
Connecticut
Delaware
Florida
Georgia
Hawaii
Idaho
Illinois
Indiana
Iowa
Kansas
Kentucky
Louisiana
Maine
Maryland
Massachusetts
Michigan
Minnesota
Mississippi
Missouri
Montana
Nebraska
Nevada
New_Hampshire
New_Jersey
New_Mexico
New_York
North_Carolina
North_Dakota
Ohio
Oklahoma
Oregon
Pennsylvania
Rhode_Island
South_Carolina
South_Dakota
Tennessee
Territory_or_Island
Texas
Utah
Vermont
Virginia
Washington
West_Virginia
Wisconsin
Wyoming
Providence
Alberta
British_Columbia
Manitoba
New_Brunswick
Newfoundland_and_Labrador
Northwest_Territories
Nova_Scotia
Nunavut
Ontario
Prince_Edward_Island
Quebec
Saskatchewan
Yukon
Latin_States
Colombia
Honduras
Guatemala
Panama
Peru
Dominican_Republic
Puerto_Rico
Mexican_States
BCN_Baja_California_N
GRO_Guerrero
GUA_Guanajuato
JAL_Jalisco
MEX_México
NLE_Nuevo_León
ROO_Quintana_Roo
SIN_Sinaloa
SLP_San_Luis_Potosí
TAM_Tamaulipas
VER_Veracruz
YUC_Yucatán
ZAC_Zacatecas
Contact Chint Power
US 855-584-7168
Update Modules
Update Online

## P-Custom Module
|  | Solar PV String Sizing Tool | [9 empty] | V4.0.0
Fill out the blanks below to add your own equipment.
| 1 | 2 | 3 |  | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 17
Modules
| Manufacturer and Model | Rated power @ STC (W) | Rated power tolerance (%) | Max. System Voltage Rating | Max. power voltage (Vmp) | Max. power current (Imp) | Open-circuit voltage (Voc) | Short-circuit current (Isc) | Pmp/Vmp temp. coefficien (%/°C) | Voc temp. coefficient (%/°C) | Module Type (MonoFacial/BiFacial/Thin Flim) (MF/BF/TF) | Series fuse rating (A)
| Module Example | 250 | +3/3 | 1000 | 30.34 | 8.24 | 37.47 | 8.76 | -0.44 | -0.34 | MF | 20
Use the Custom Module sheet tab
1 | Proto type 600V array | 280 | +3/3 | 600 | 31.9 | 7.83 | 37.2 | 8.44 | -0.48 | -0.34 | MF | 20
2 | FS FS6420 Test-Thin Film | 420 | +5/-0 | 1500 | 180.4 | 2.33 | 218.5 | 2.54 | -0.32 | -0.28 | TF | 5
3 | Astronergy | 320 | +5/-0 | 1500 | 37.02 | 8.65 | 45.45 | 9.25 | -0.408 | -0.311 | MF | 15
4 | SunPower E20-435 | 435 |  | 1500 | 72.9 | 5.97 | 85.6 | 6.43 | -0.35 | -0.275 | MF | 15
5 | TSM-410DEG15MC.20(II) | 410 | +5/-0 | 1500 | 41.4 | 9.91 | 49.3 | 10.41 | -0.35 | -0.25 | MF | 20
7 | Astronergy CHSM6612P/HV 325 | 325 | +5/-0 | 1500 | 37.11 | 8.77 | 45.67 | 9.48 | -0.406 | -0.311 | MF | 15
8 | Trina TSM-545DE19 | 545 | +5/-0 | 1500 | 31.4 | 17.37 | 37.7 | 18.47 | -0.34 | -0.24934 | MF | 30
9 | Vertex 530 | 530 |  | 1500 | 31 | 17.11 | 37.3 | 18.19 | -0.35 | -0.27 | BF | 35
10 | Vertex 550 | 550 |  | 1500 | 31.8 | 17.29 | 38.1 | 18.39 | -0.35 | -0.27 | BF | 35
11 | Astronergy 525 | 525 |  | 1500 | 41.26 | 12.72 | 49.1 | 13.43 | -0.35 | -0.27 | MF | 25
12 | Astronergy 545 | 545 |  | 1500 | 41.93 | 13 | 49.9 | 13.81 | -0.35 | -0.27 | MF | 25
13 | BF465 | 465 |  | 1500 | 35.8 | 12.99 | 43 | 13.58 | -0.34 | -0.25 | BF | 25
14 | BF485 | 485 |  | 1500 | 36.2 | 13.39 | 43.4 | 13.97 | -0.34 | -0.25 | BF | 25
15 | CS7L-570 | 570 |  | 1500 | 33.7 | 16.93 | 40.1 | 18.17 | -0.34 | -0.26 | BF | 35
16 | CS7L-595 | 595 |  | 1500 | 34.7 | 17.15 | 41.1 | 18.42 | -0.34 | -0.26 | BF | 35
17 | CS7L-635 | 635 |  | 1500 | 37.3 | 17.03 | 44.4 | 18.27 | -0.34 | -0.26 | BF | 35
18 | CS7L-655 | 655 |  | 1500 | 38.1 | 17.2 | 45.2 | 18.43 | -0.34 | -0.26 | BF | 35
19 | RSM110-535 | 535 |  | 1500 | 31.36 | 17.07 | 37.66 | 18.07 | -0.34 | -0.25 | BF | 35
20 | RSM110-555 | 555 |  | 1500 | 32.16 | 17.27 | 38.54 | 18.28 | -0.34 | -0.25 | BF | 35
21 | RSM120-580 | 580 |  | 1500 | 34.25 | 16.94 | 40.8 | 18.22 | -0.35 | -0.27 | BF | 40
22 | RSM120-600 | 600 |  | 1500 | 34.85 | 17.22 | 41.4 | 18.5 | -0.35 | -0.27 | BF | 40
23 | Conergy S-175MU | 175 |  | 600 | 35.2 | 4.95 | 44.2 | 5.2 | -0.35 | -0.27 | MF | 15
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
Contact Chint Power
US 855-584-7168
Note on D9: For display purposes only.
Note on M9: For display purposes only.

## P-Inverters (hidden)
Manufacturer (Important) | V4.0.0 | Input Data (dc) | [14 empty] | Output Data (ac) | [21 empty] | Mechanical |  |  | Transportation |  | Termin/ation Specifications | [9 empty] | Integrated Disconnects and Combiners |  |  |  |  | Listing | Data | Warranty |  | Date |  | Notes
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 12 | 13 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 30 | 30 | 32 | 32 | 34 | 34 | 35 | 36 | 37 | 37 | 38 | 39 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59
| Model (Important) | Number of MPPT's | Strings/MPPT | MPPT Parallel (Y) | Maximum PV power at STC (W) TOTAL | Maximum PV power at STC (W) (per MPPT) | Maximum open-circuit voltage | PV start voltage | Minimum MPPT voltage | Maximum MPPT voltage | Minimum Operating DC Input voltage | Maximum Operating DC Input voltage | Maximum usable input current (Not Used) | Min. dc power throughput (W) | Maximum short-circuit INPUT current (TOTAL Module IscSTC x 1.25) | Maximum short-circuit INPUT current (per MPPT Module IscSTC x 1.25) | Max output power (W) | Max output power (VA) | Max DC Input Ratio | Nomin/al output voltage | Maximum output current | Maximum OutputCurrent 80% derate | 15-45A (Do not edit) | 50-110A (Do not edit) | 125-300A (Do not edit) | 350-800A (Do not edit) | 800-4000A (Do not edit) | 4000-6000A (Do not edit) | NEC Minimum AC OCPD Rating (Calculated from Column N) (Do not edit) | Manufacturers Maximum AC OCPD rating | OCPD interrupt capacity (kAic) | Neutral sizing requirements | Peak efficiency (%) | weighted efficiency (%) | CEC night tare loss (W) | Ambient temperature range (ºF) | Elevation (ft.) | Noise level @ 1 m (dB) | Enclosure NEMA rating | Dimensions H x W x D (inches) | Cooling method | Lifting provisions | Weight (lbs) | Number of dc string inputs | dc termin/al size range (AWG) | Max. dc termin/al size range (AWG) | dc termin/al type 2 | Number ac termin/als (per phase) | Min. ac termin/al size range (AWG) | Max. ac termin/al size range (AWG) | Number GEC termin/als | GEC termin/al size range (AWG) | Max GEC termin/al size range (AWG) | dc disconnect standard | ac disconnect standard | Disconnect amperage rating (dc/ac) | Fused combiner standard | Integrated fused subcombiner | Listing agency | Data | Warranty standard/extended (years) | Extended (yr.) | Date Updated | Spec Sheet Date | Notes
Chint Power
European Inverters
Chint Power | CPS SCE1.5KTL | 1 | 1 |  | 1700 |  | 550 |  | 175 | 500 | 100 | 550 | 9.1 |  |  |  | 1650 |  | 1.0303 | 230 | 7.2 | 9 | 15 | [5 empty] | 15 |  |  |  |  | 95.2% | [30 empty] | updated 6-18-13
Chint Power | CPS SCE2KTL | 1 | 1 |  | 2300 |  | 550 |  | 200 | 500 | 100 | 550 | 11 |  |  |  | 2200 |  | 1.0455 | 230 | 9.6 | 12 | 15 | [5 empty] | 15 |  |  |  |  | 95.8% | [30 empty] | updated 6-18-13
Chint Power | CPS SCE3KTL-O | 1 | 2 |  | 3450 |  | 600 |  | 200 | 500 | 100 | 500 | 17.5 |  |  |  | 3300 |  | 1.0455 | 230 | 14.4 | 18 | 20 | [5 empty] | 20 |  |  |  |  | 96.5% | [30 empty] | updated 6-18-13
Chint Power | CPS SCE4KTL-O | 1 | 2 |  | 4600 |  | 600 |  | 225 | 500 | 100 | 500 | 20 |  |  |  | 4400 |  | 1.0455 | 230 | 19.2 | 24 | 25 | [5 empty] | 25 |  |  |  |  | 97% | [30 empty] | updated 6-18-13
Chint Power | CPS SCE4.6KTL-O | 2 | 2 |  | 6800 |  | 600 |  | 225 | 500 | 100 | 500 | 17 |  |  |  | 4600 |  | 1.4783 | 230 | 22.1 | 27.625 | 30 | [5 empty] | 30 |  |  |  |  | 97% | [30 empty] | updated 6-18-13
Chint Power | CPS SC1.5KTL | 1 | 1 |  | 1740 |  | 450 |  | 200 | 405 | 100 | 450 | 8.9 |  |  |  | 1650 |  | 1.0545 | 230 | 7.9 | 9.875 | 15 | [5 empty] | 15 |  |  |  |  | 94% | [30 empty] | updated 6-18-13
Chint Power | CPS SC2KTL | 1 | 1 |  | 2290 |  | 500 |  | 250 | 450 | 100 | 500 | 10 |  |  |  | 2200 |  | 1.0409 | 230 | 10.5 | 13.125 | 15 | [5 empty] | 15 |  |  |  |  | 95% | [30 empty] | updated 6-18-13
Chint Power | CPS SC2.8KTL | 1 | 1 |  | 3120 |  | 500 |  | 250 | 450 | 100 | 500 | 13 |  |  |  | 3000 |  | 1.04 | 230 | 14.3 | 17.875 | 20 | [5 empty] | 20 |  |  |  |  | 95% | [30 empty] | updated 6-18-13
Chint Power | CPS SC4KTL | 1 | 2 |  | 4580 |  | 500 |  | 250 | 450 | 100 | 500 | 20 |  |  |  | 4400 |  | 1.0409 | 230 | 20 | 25 | 25 | [5 empty] | 25 |  |  |  |  | 95% | [30 empty] | updated 6-18-13
Chint Power | CPS SC4KTL-O | 1 | 3 |  | 4580 |  | 500 |  | 250 | 450 | 100 | 500 | 20 |  |  |  | 4400 |  | 1.0409 | 230 | 20 | 25 | 25 | [5 empty] | 25 |  |  |  |  | 95% | [30 empty] | updated 6-18-13
Chint Power | CPS SC4.6KTL (as Single MPPT) | 1 | 3 |  | 11850 |  | 750 |  | 450 | 750 | 100 | 750 | 25.5 |  |  |  | 5000 |  | 2.37 | 230 | 25.5 | 31.875 | 35 | [5 empty] | 35 |  |  |  |  | 94% | [30 empty] | updated 7-22-13
Chint Power | CPS SCA5KTL-DO | 2 | 2 |  | 6000 |  | 1000 |  | 250 | 800 | 250 | 950 | 12 |  |  |  | 5000 |  | 1.2 | 400 | 7.3 | 9.125 | 15 | [5 empty] | 15 |  |  |  |  | 97.7% | [30 empty] | updated 6-18-13
Chint Power | CPS SCA6KTL-DO | 2 | 2 |  | 8000 |  | 1000 |  | 275 | 800 | 250 | 950 | 12 |  |  |  | 6000 |  | 1.3333 | 400 | 8.7 | 10.875 | 15 | [5 empty] | 15 |  |  |  |  | 97.7% | [30 empty] | updated 6-18-13
Chint Power | CPS SCA7KTL-DO | 2 | 2 |  | 8000 |  | 1000 |  | 320 | 800 | 250 | 950 | 12 |  |  |  | 7000 |  | 1.1429 | 400 | 10.2 | 12.75 | 15 | [5 empty] | 15 |  |  |  |  | 97.7% | [30 empty] | updated 6-18-13
Chint Power | CPS SCA8KTL-DO | 2 | 2 |  | 10000 |  | 1000 |  | 320 | 800 | 250 | 950 | 17 |  |  |  | 8000 |  | 1.25 | 400 | 12.5 | 15.625 | 20 | [5 empty] | 20 |  |  |  |  | 97.9% | [30 empty] | updated 6-18-13
Chint Power | CPS SCA8KTL-DOHE | 2 | 2 |  | 10000 |  | 1000 |  | 320 | 800 | 250 | 950 | 17 |  |  |  | 8000 |  | 1.25 | 400 | 12.5 | 15.625 | 20 | [5 empty] | 20 |  |  |  |  | 98.2% | [30 empty] | updated 6-18-13
Chint Power | CPS SCA10KTL-DO | 2 | 2 |  | 12000 |  | 1000 |  | 320 | 800 | 250 | 950 | 17 |  |  |  | 10000 |  | 1.2 | 400 | 15.2 | 19 | 20 | [5 empty] | 20 |  |  |  |  | 97.9% | [30 empty] | updated 6-18-13
Chint Power | CPS SCA10KTL-DOHE | 2 | 2 |  | 12000 |  | 1000 |  | 320 | 800 | 250 | 950 | 17 |  |  |  | 10000 |  | 1.2 | 400 | 15.2 | 19 | 20 | [5 empty] | 20 |  |  |  |  | 98.2% | [30 empty] | updated 6-18-13
Chint Power | CPS SCA12KTL-DO | 2 | 2 |  | 14200 |  | 1000 |  | 380 | 800 | 250 | 950 | 17 |  |  |  | 12000 |  | 1.1833 | 400 | 18.2 | 22.75 | 25 | [5 empty] | 25 |  |  |  |  | 97.9% | [30 empty] | updated 6-18-13
Chint Power | CPS SCA12KTL-DOHE | 2 | 2 |  | 14200 |  | 1000 |  | 380 | 800 | 250 | 950 | 17 |  |  |  | 12000 |  | 1.1833 | 400 | 18.2 | 22.75 | 25 | [5 empty] | 25 |  |  |  |  | 98.2% | [30 empty] | updated 6-18-13
Chint Power | CPS SC20KTL-O/CN | 1 | 5 |  | 22000 |  | 850 |  | 500 | 800 | 430 | 800 | 42 |  |  |  | 20000 |  | 1.1 | 380 | 30 | 37.5 | 40 | [5 empty] | 40 |  |  |  |  | 97.5% | [30 empty] | updated 6-18-13
Chint Power | CPS SC20KTL-DO | 2 | 3 |  | 22000 |  | 850 |  | 500 | 800 | 430 | 800 | 21 |  |  |  | 20000 |  | 1.1 | 400 | 30 | 37.5 | 40 | [5 empty] | 40 |  |  |  |  | 97.5% | [30 empty] | updated 6-18-13
Chint Power | CPS SCA20KTL-DO | 2 | 4 |  | 24000 |  | 1000 |  | 400 | 800 | 300 | 900 | 54 |  |  |  | 20000 |  | 1.2 | 400 | 32 | 40 | 40 | [5 empty] | 40 |  |  |  |  | 97.8% | [30 empty] | updated 6-19-13
Chint Power | CPS SCA25KTL-DO | 2 | 4 |  | 28000 |  | 1000 |  | 400 | 800 | 300 | 900 | 64 |  |  |  | 25000 |  | 1.12 | 400 | 40 | 50 |  | 50 |  |  |  |  | 50 |  |  |  |  | 97.8% | [30 empty] | updated 6-19-13
Chint Power | CPS SC100KT | 1 | 4 |  | 110000 |  | 880 |  | 450 | 820 | 430 | 820 | 250 |  |  |  | 100000 |  | 1.1 | 400 | 152 | 190 |  |  | 200 |  |  |  | 200 |  |  |  |  | 97% | [30 empty] | updated 6-18-13
Chint Power | CPS SC250KTL-H | 1 | 4 |  | 275000 |  | 1000 |  | 450 | 820 | 450 | 820 | 600 |  |  |  | 275000 |  | 1 | 270 | 588 | 735 |  |  |  | 800 |  |  | 800 |  |  |  |  | 98% | [30 empty] | updated 6-18-13
Chint Power | CPS SC250KT-H | 1 | 8 |  | 275000 |  | 1000 |  | 450 | 820 | 450 | 940 | 600 |  |  |  | 275000 |  | 1 | 400 | 397 | 496.25 |  |  |  | 500 |  |  | 500 |  |  |  |  | 97% | [30 empty] | updated 7-19-13
Chint Power | CPS SC500KTL-H | 1 | 8 |  | 550000 |  | 1000 |  | 450 | 820 | 450 | 820 | 1200 |  |  |  | 550000 |  | 1 | 270 | 1176 | 1470 |  |  |  |  | 1600 |  | 1600 |  |  |  |  | 98.3% | [30 empty] | updated 6-18-13
Chint Power | CPS SCA500KTL-H | 1 | 8 |  | 565000 |  | 1000 |  | 450 | 820 | 450 | 940 | 1200 |  |  |  | 500000 |  | 1.13 | 315 | 1070 | 1337.5 |  |  |  |  | 1600 |  | 1600 |  |  |  |  | 98% | [30 empty] | updated 6-18-13
Chint Power | CPS PSW1M-O | 2 | 9 |  | 1100000 |  | 1000 |  | 450 | 820 | 450 | 820 | 1200 |  |  |  | 1100000 |  | 1 | 315 | 2352 | 2940 |  |  |  |  | 3000 |  | 3000 |  |  |  |  | 98.3% | [30 empty] | updated 6-18-13
North American Inverters
| SCA25KTL-DO/US-480-UL | 2 | 3 | N | 37500 | 22000 | 1000 | 330 | 560 | 850 | 200 | 950 | 23 |  | 90 | 49.5 | 25000 | 25000 | 1.5 | 480 | 30.5 | 38.125 | 40 | [5 empty] | 40 |  |  | NO |  | 98% | [33 empty] | 0
| SCA25KTL-DO/US-208-UL | 3 | 2 | N | 45000 | 16500 | 1000 | 330 | 480 | 850 | 200 | 950 |  |  | 135 | 52.2 | 25000 | 25000 | 1.8 | 208 | 69.5 | 86.875 | [9 empty] | NO |  | 96.5% | [31 empty] | 45000 | 16500 | 0
| SCA36KTL-DO/US-480-UL | 2 | 5 | Y | 54000 | 27000 | 1000 | 320 | 540 | 800 | 240 | 950 | 35 |  | 125 | 62.5 | 36000 | 36000 | 1.5 | 480 | 43.5 | 54.375 |  | 60 |  |  |  |  | 60 |  |  | NO |  | 98% | [33 empty] | 0
| SCA50KTL-DO/US-480-UL | 3 | 5 | Y | 90000 | 33000 | 1000 | 330 | 480 | 850 | 200 | 950 | 36 |  | 204 | 74.8 | 50000 | 55000 | 1.8 | 480 | 60.2 | 75.25 |  | 80 |  |  |  |  | 80 | 100 |  | NO |  | 98.5% | [33 empty] | 0 | 214.9425
| SCA60KTL-DO/US-480-UL | 3 | 5 | Y | 90000 | 33000 | 1000 | 330 | 540 | 850 | 200 | 950 | 38 |  | 204 | 74.8 | 60000 | 66000 | 1.5 | 480 | 72.2 | 90.25 |  | 100 |  |  |  |  | 100 | 100 |  | NO |  | 98.5% | [33 empty] | 0 | 236.4368
| SCA100KTL-DO/US-480-UL -C/S | 1 | 20 | N | 150000 | 150000 | 1500 | 900 | 870 | 1300 | 860 | 1450 | 176 |  | 275 | 275 | 100000 | 111000 | 1.5 | 480 | 133.6705 | 167.0882 | [9 empty] | NO |  | 98.5% | [33 empty] | 0 | 295.546
| SCH100KTL-DO/US-600-UL | 1 | 20 | N | 187500 | 187500 | 1500 | 900 | 870 | 1300 | 860 | 1450 | 176 |  | 275 | 275 | 100000 | 111000 | 1.875 | 600 | 106.9 | 133.625 | 150 | [5 empty] | 150 |  |  | NO |  | 98.5% | [33 empty] | 0
| SCH125KTL-DO/US-600-UL | 1 | 20 | N | 187500 | 187500 | 1500 | 900 | 870 | 1300 | 860 | 1450 | 220 |  | 275 | 275 | 125000 | 132000 | 1.5 | 600 | 127.2 | 159 | 175 | [5 empty] | 175 |  |  | NO |  | 98.5% | [33 empty] | 0
| SCH275KTL/36In | 12 | 3 | N | 440000 | 36666.6667 | 1500 | 600 | 880 | 1300 | 880 | 1500 |  |  | 750 | 62.5 | 275000 | 275000 | 1.6 | 800 | 198.5 | 248.125 | [7 empty] | 250 |  | NO |  | 98.5%
| SCH275KTL/24In | 12 | 2 | N | 440000 | 36666.6667 | 1500 | 600 | 880 | 1300 | 880 | 1500 |  |  | 750 | 62.5 | 275000 | 275000 | 1.6 | 800 | 198.5 | 248.125 | [7 empty] | 250 |  | NO |  | 98.5%
| SC14KTL-DO/US-208-UL N/A | 2 | 4 | Y | 19000 | 9500 | 600 |  | 300 | 540 | 180 | 580 | 25 |  | 90 | 45 | 14000 | 14000 | 1.3571 | 208 | 39 | 48.75 |  | 50 |  |  |  |  | 50 |  |  | YES |  | 96% | [33 empty] | 1
| SC20KTL-DO/US-480-UL N/A | 2 | 4 | Y | 27000 | 13500 | 600 |  | 300 | 550 | 260 | 580 | 35 |  | 91 | 45.5 | 20000 | 20000 | 1.35 | 480 | 24 | 30 | 30 | [5 empty] | 30 |  |  | YES |  | 96.5% | [33 empty] | 1
| SCA23KTL-DO/US-480-UL N/A | 2 | 4 | Y | 31000 | 15500 | 1000 | 330 | 480 | 800 | 300 | 950 | 25 |  | 82 | 41 | 23000 | 23000 | 1.3478 | 480 | 27.7 | 34.625 | 35 | [5 empty] | 35 |  |  | YES |  | 98% | [33 empty] | 1
| SCA28KTL-DO/US-480-UL N/A | 2 | 4 | Y | 38000 | 19000 | 1000 | 330 | 500 | 800 | 300 | 950 | 29 |  | 96 | 48 | 28000 | 28000 | 1.3571 | 480 | 33.7 | 42.125 | 45 | [5 empty] | 45 |  |  | YES |  | 98% | [33 empty] | 1
| SC100KT-O/US-480-UL - N/A | 1 | 4 | N | 135000 | 135000 | 600 | 200 | 330 | 500 | 300 | 600 | 350 |  | 410 | 410 | 100000 | 100000 | 1.35 | 480 | 120 | 150 |  |  | 150 |  |  |  | 150 |  |  | NO |  | 96% | [33 empty] | 1
Chint Power | SCA3KTL-O/US -208-IEC | 1 | 4 |  | 4000 |  | 550 |  | 200 | 470 | 150 | 550 | 8 |  | 12.8 |  | 2850 |  | 1.4035 | 208 | 15 | 18.75 | 20 | [5 empty] | 20 |  |  |  |  | 97%
Chint Power | SCA3KTL-O/US -240-IEC | 1 | 4 |  | 4000 |  | 550 |  | 200 | 470 | 150 | 550 | 8 |  | 12.8 |  | 3000 |  | 1.3333 | 240 | 15 | 18.75 | 20 | [5 empty] | 20 |  |  |  |  | 97%
Chint Power | SCA4KTL-O/US -208-IEC | 1 | 2 |  | 5200 |  | 550 |  | 200 | 470 | 150 | 550 | 10.5 |  | 16.8 |  | 3800 |  | 1.3684 | 208 | 19 | 23.75 | 25 | [5 empty] | 25 |  |  |  |  | 97%
Chint Power | SCA4KTL-O/US -240-IEC | 1 | 2 |  | 5200 |  | 550 |  | 200 | 470 | 150 | 550 | 10.5 |  | 16.8 |  | 4000 |  | 1.3 | 240 | 19 | 23.75 | 25 | [5 empty] | 25 |  |  |  |  | 97%
Chint Power | SCA5KTL-O/US -208-IEC | 2 | 2 |  | 6500 |  | 550 |  | 200 | 470 | 150 | 550 | 13 |  | 20.8 |  | 4600 |  | 1.413 | 208 | 22 | 27.5 | 30 | [5 empty] | 30 |  |  |  |  | 97%
Chint Power | SCA5KTL-O/US -240-IEC | 2 | 2 |  | 6500 |  | 550 |  | 200 | 470 | 150 | 550 | 13 |  | 20.8 |  | 5000 |  | 1.3 | 240 | 22 | 27.5 | 30 | [5 empty] | 30 |  |  |  |  | 97%
Chint Power | SCE4KTL-O/US -208-IEC | 1 | 4 |  | 4800 |  | 600 | 150 | 225 | 500 | 100 | 515 | 19 |  | 19 |  | 3800 |  | 1.2632 | 208 | 18.5 | 23.125 | 25 | [5 empty] | 25 |  |  |  |  | 97% | < 0.2 | -25 - 113 | 6500 | <= 50dB | 3R
Chint Power | SCE4KTL-O/US -240-IEC | 1 | 4 |  | 4800 |  | 600 | 150 | 225 | 500 | 100 | 515 | 19 |  | 19 |  | 4000 |  | 1.2 | 240 | 18.5 | 23.125 | 25 | [5 empty] | 25 |  |  |  |  | 97% | < 0.2 | -25 - 113 | 6500 | <= 50dB | 3R
Chint Power | SCE4KTL-O/US -277-IEC | 1 | 4 |  | 4800 |  | 600 | 150 | 225 | 500 | 100 | 515 | 19 |  | 19 |  | 4000 |  | 1.2 | 277 | 16.4 | 20.5 | 25 | [5 empty] | 25 |  |  |  |  | 97% | < 0.2 | -25 - 113 | 6500 | <= 50dB | 3R
Chint Power | SCE5KTL-O/US -208-IEC | 1 | 4 |  | 6000 |  | 600 | 150 | 200 | 500 | 100 | 515 | 26 |  | 26 |  | 4600 |  | 1.3043 | 208 | 22.5 | 28.125 | 30 | [5 empty] | 30 |  |  |  |  | 97% | < 0.2 | -25 - 113 | 6500 | <= 50dB | 3R
Chint Power | SCE5KTL-O/US -240-IEC | 1 | 4 |  | 6000 |  | 600 | 150 | 200 | 500 | 100 | 515 | 26 |  | 26 |  | 5000 |  | 1.2 | 240 | 22.5 | 28.125 | 30 | [5 empty] | 30 |  |  |  |  | 97% | < 0.2 | -25 - 113 | 6500 | <= 50dB | 3R
Chint Power | SCE5KTL-O/US -277-IEC | 1 | 4 |  | 6000 |  | 600 | 150 | 200 | 500 | 100 | 515 | 26 |  | 26 |  | 5000 |  | 1.2 | 277 | 20.5 | 25.625 | 30 | [5 empty] | 30 |  |  |  |  | 97% | < 0.2 | -25 - 113 | 6500 | <= 50dB | 3R
Chint Power | SCE6KTL-O/US -208-IEC | 1 | 4 |  | 7200 |  | 600 | 150 | 200 | 500 | 100 | 515 | 32 |  | 32 |  | 6000 |  | 1.2 | 208 | 30 | 37.5 | 40 | [5 empty] | 40 |  |  |  |  | 97% | < 0.2 | -25 - 113 | 6500 | <= 50dB | 3R
Chint Power | SCE6KTL-O/US -240-IEC | 1 | 4 |  | 7200 |  | 600 | 150 | 200 | 500 | 100 | 515 | 32 |  | 32 |  | 6000 |  | 1.2 | 240 | 28.5 | 35.625 | 40 | [5 empty] | 40 |  |  |  |  | 97% | < 0.2 | -25 - 113 | 6500 | <= 50dB | 3R
Chint Power | SCE6KTL-O/US -277-IEC | 1 | 4 |  | 7200 |  | 600 | 150 | 200 | 500 | 100 | 515 | 32 |  | 32 |  | 6000 |  | 1.2 | 277 | 24.6 | 30.75 | 35 | [5 empty] | 35 |  |  |  |  | 97% | < 0.2 | -25 - 113 | 6500 | <= 50dB | 3R
Chint Power | SCE7KTL-O/US -208-IEC | 1 | 4 |  | 8400 |  | 600 | 150 | 200 | 500 | 100 | 515 | 37 |  | 37 |  | 7000 |  | 1.2 | 208 | 35 | 43.75 | 45 | [5 empty] | 45 |  |  |  |  | 97% | < 0.2 | -25 - 113 | 6500 | <= 50dB | 3R
Chint Power | SCE7KTL-O/US -240-IEC | 1 | 4 |  | 8400 |  | 600 | 150 | 200 | 500 | 100 | 515 | 37 |  | 37 |  | 7000 |  | 1.2 | 240 | 33.2 | 41.5 | 45 | [5 empty] | 45 |  |  |  |  | 97% | < 0.2 | -25 - 113 | 6500 | <= 50dB | 3R
Chint Power | SCE7KTL-O/US -277-IEC | 1 | 4 |  | 8400 |  | 600 | 150 | 200 | 500 | 100 | 515 | 37 |  | 37 |  | 7000 |  | 1.2 | 277 | 28.7 | 35.875 | 40 | [5 empty] | 40 |  |  |  |  | 97% | < 0.2 | -25 - 113 | 6500 | <= 50dB | 3R
Chint Power
Chint Power
Chint Power | [64 empty] | updated 2-07-17
Chint Power | [34 empty] | <1W | -22 - 140 | 13123 | <50dba | [26 empty] | added 1/10/20 RM
Chint Power | [64 empty] | updated 2-07-17
Chint Power | [64 empty] | 2017-02-07
Chint Power | [35 empty] | -22-140 |  |  | 4X | [25 empty] | 2017-02-07
Chint Power | [35 empty] | -22-140 |  |  | 4X | [25 empty] | 2017-02-07
Chint Power | [38 empty] | 4x
Chint Power | [38 empty] | 4x | [25 empty] | 2018-02-21
Chint Power | [64 empty] | 2018-02-21
VLOOKUP($E$27,Inverters!B4:BH122,13,FALSE)
68
Chint Power | CPS SCA6KTL-O/US @ 208 | 2 | 2 |  | 7800 |  | 550 |  | 200 | 470 | 150 | 550 | 16 |  |  |  | 5700 |  | 1.3684 | 208 | 27.5 | 34.375 | 35 | [5 empty] | 35 |  |  |  |  | 97%
Chint Power | CPS SCA6KTL-O/US @ 240 | 2 | 2 |  | 7800 |  | 550 |  | 200 | 470 | 150 | 550 | 16 |  |  |  | 6200 |  | 1.2581 | 240 | 27.5 | 34.375 | 35 | [5 empty] | 35 |  |  |  |  | 97%
Chint Power | CPS SC10KTL-O | 3 |  |  | 11000 |  | 800 |  | 320 | 720 | 245 | 720 | 13 |  |  |  | 10000 |  | 1.1 | 400 | 17.5 | 21.875 | 25 | [5 empty] | 25 |  |  |  |  | 95% | [30 empty] | updated 6-18-13
Note on G37: Stephen: was 18750
Note on Q37: Stephen: was 45
Note on F40: Stephen: Was 75000
Note on G40: Stephen: was 30000 should be 33000?
Note on Q40: Stephen: was 68
Note on Q41: Stephen: was 68
Note on F42: Stephen: Was 150000
Note on F43: Stephen: Was 150000

## Modules (hidden)
Manufacturer | Model | Cell Type | Rated power @ STC (W) | Rated power @ PTC (W) | Rated power tolerance (%) | Rated power tolerance positive (%) | Rated power tolerance negative (%) | Rated power per sq. ft. (W)(col8) | Module efficiency (%)(col9) (Important) | Max. power voltage (Vmp) | Max. power current (Imp) | Open-circuit voltage (Voc) | Short-circuit current (Isc) | Pmp temp. coefficient (%/°C) | Voc temp. coefficient (%/°C) | Isc temp. coefficient (%/°C)(col16) | Nominal operating cell temp. (°C)(col17) | Series fuse rating (A) | PV Wire output cables | Connector type | Frame color | Backsheet color | Length (in.) | Width (in.) | Depth (in.) | Square footage | Weight (lbs.) | Materials warranty (yrs.) | Power warranty (yrs.) 90%/80% | Max System Voltage | Date Updated | Manufacturer | Bifacial (Y/N) | AC Module? (Leave Blank if not) | Peak AC Output Power | Continuous AC Output Power | Nominal AC Voltage | Nominal AC Output Current | CEC Weighted Efficiency | Max Number of AC modules per Branch Circuit | OCPD Rating | Output Voltage | Output Phase | NOCT
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43
Abound Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1 | [12 empty] | Password to prove this was provided by REA.
Abound Solar | AB1-62 |  | 62.5 |  | +2.5/-0 | 2.5 | 0 |  |  | 34.3 | 1.83 | 45.7 | 2.24 | -0.0031 | -0.0037 | [10 empty] | 0 |  |  |  | Check |  | Abound_Solar | Y | [11 empty] | Baertlein123!
Abound Solar | AB1-65 |  | 65 |  | +2.5/-0 | 2.5 | 0 |  |  | 35 | 1.88 | 46.1 | 2.26 | -0.0031 | -0.0037 | [10 empty] | 0 |  |  |  | Check |  | Abound_Solar
Abound Solar | AB1-67 |  | 67.5 |  | +2.5/-0 | 2.5 | 0 |  |  | 35.6 | 1.9 | 46.4 | 2.27 | -0.0031 | -0.0037 | [10 empty] | 0 |  |  |  | Check |  | Abound_Solar
Abound Solar | AB1-70 |  | 70 |  | +2.5/-0 | 2.5 | 0 |  |  | 35.9 | 1.95 | 46.6 | 2.3 | -0.0031 | -0.0037 | [10 empty] | 0 |  |  |  | Check |  | Abound_Solar
Abound Solar | AB1-72 |  | 72.5 |  | +2.5/-0 | 2.5 | 0 |  |  | 36.4 | 2 | 46.9 | 2.33 | -0.0031 | -0.0037 | [10 empty] | 0 |  |  |  | Check |  | Abound_Solar
Advanced Solar Photonics |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | AF9 | Abound_Solar
Advanced Solar Photonics | ASP-250-A | mono | 242 |  | +5/-5 | 5 | -5 | 13.6418 | 14.7 | 30.29 | 7.99 | 37.68 | 8.57 | -0.0051 | -0.00335 |  |  | 20 |  | MC |  |  | 65.5 | 39 | 1.68 | 17.7396 | 42 | 10 |  | Check |  | Advanced_Solar_Photonics
Advanced Solar Photonics | ASP-250-B | mono | 235 |  | +5/-5 | 5 | -5 | 13.2472 | 14.3 | 29.93 | 7.93 | 37.5 | 8.52 | -0.0051 | -0.00335 |  |  | 15 |  | MC |  |  | 65.5 | 39 | 1.68 | 17.7396 | 42 | 10 |  | Check |  | Advanced_Solar_Photonics
Advanced Solar Photonics | ASP-250-C | mono | 240 |  | +5/-5 | 5 | -5 | 13.5291 | 14.6 | 29.8 | 8.06 | 36.5 | 8.6 | -0.005 | -0.0036 |  |  | 15 |  | MC |  |  | 65.5 | 39 | 1.68 | 17.7396 | 53 | 10 |  | Check |  | Advanced_Solar_Photonics
Advanced Solar Photonics | ASP-300 | mono | 288 |  | +5/-5 | 5 | -5 | 13.7891 | 14.8 | 36 | 7.99 | 45 | 8.57 | -0.0047 | -0.004 |  |  | 20 |  | MC |  |  | 77.165 | 38.976 | 1.654 | 20.886 | 55 | 10 |  | Check |  | Advanced_Solar_Photonics
Advent | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | Advanced_Solar_Photonics
Advent | Advent 200 | poly | 200 |  | +3/-3 | 3 | -3 | 11.1709 | 12 | 28.11 | 7.14 | 34.92 | 7.98 | -0.0052 | -0.0036 |  |  | 15 |  | MC |  |  | 66.14 | 38.98 | 1.97 | 17.9037 | 50 | NA |  | Check |  | Advent
Advent | Advent 205 | poly | 205 |  | +3/-3 | 3 | -3 | 11.4501 | 12.3 | 28.431 | 7.23 | 35.1 | 8.08 | -0.0052 | -0.0036 |  |  | 15 |  | MC |  |  | 66.14 | 38.98 | 1.97 | 17.9037 | 50 | NA |  | Check |  | Advent
Advent | Advent 210 | poly | 210 |  | +3/-3 | 3 | -3 | 11.7294 | 12.6 | 28.43 | 7.39 | 35.1 | 8.23 | -0.0052 | -0.0036 |  |  | 15 |  | MC |  |  | 66.14 | 38.98 | 1.97 | 17.9037 | 50 | NA |  | Check |  | Advent
Advent | Advent 215 | poly | 215 |  | +3/-3 | 3 | -3 | 12.0087 | 12.9 | 28.74 | 7.49 | 35.4 | 8.27 | -0.0052 | -0.0036 |  |  | 15 |  | MC |  |  | 66.14 | 38.98 | 1.97 | 17.9037 | 50 | NA |  | Check |  | Advent
Advent | Advent 220 | poly | 220 |  | +3/-3 | 3 | -3 | 12.2879 | 13.2 | 29.06 | 7.62 | 35.7 | 8.4 | -0.0052 | -0.0036 |  |  | 15 |  | MC |  |  | 66.14 | 38.98 | 1.97 | 17.9037 | 50 | NA |  | Check |  | Advent
Advent | Advent 225 | poly | 225 |  | +3/-3 | 3 | -3 | 12.5672 | 13.5 | 29.34 | 7.75 | 36 | 8.52 | -0.0052 | -0.0036 |  |  | 15 |  | MC |  |  | 66.14 | 38.98 | 1.97 | 17.9037 | 50 | NA |  | Check |  | Advent
Advent | Advent 230 | poly | 230 |  | +3/-3 | 3 | -3 | 12.8465 | 13.8 | 29.66 | 7.83 | 36.3 | 8.57 | -0.0052 | -0.0036 |  |  | 15 |  | MC |  |  | 66.14 | 38.98 | 1.97 | 17.9037 | 50 | NA |  | Check |  | Advent
Advent | Advent 235 | poly | 235 |  | +3/-3 | 3 | -3 | 13.1258 | 14.1 | 29.69 | 7.93 | 36.3 | 8.64 | -0.0052 | -0.0036 |  |  | 15 |  | MC |  |  | 66.14 | 38.98 | 1.97 | 17.9037 | 50 | NA |  | Check |  | Advent
Advent | Advent 240 | poly | 240 |  | +3/-3 | 3 | -3 | 13.405 | 14.4 | 30.01 | 7.99 | 36.6 | 8.69 | -0.0052 | -0.0036 |  |  | 15 |  | MC |  |  | 66.14 | 38.98 | 1.97 | 17.9037 | 50 | NA |  | Check |  | Advent
aleo solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | Advent
aleo solar | A_18 225 | poly | 225 | 199.5679 | +/-3 | 3 | -3 | 12.7191 | 13.7 | 29.3 | 7.68 | 36.5 | 8.13 | -0.46% | -0.34% | 0.04 | 47.9 | 15 | yes | MC4 | silver | white | 65.35 | 38.98 | 1.97 | 17.6899 | 46.3 | 5 |  | Check |  | Aleo_Solar
aleo solar | A_18 230 | poly | 230 | 204.1275 | +/-3 | 3 | -3 | 13.0018 | 14 | 29.5 | 7.8 | 36.7 | 8.26 | -0.46% | -0.34% | 0.04 | 47.9 | 15 | yes | MC4 | silver | white | 65.35 | 38.98 | 1.97 | 17.6899 | 46.3 | 5 |  | Check |  | Aleo_Solar
aleo solar | A_79 235 | mono | 235 | 205.5324 | +/-3 | 3 | -3 | 13.2844 | 14.3 | 29.4 | 8 | 36.4 | 8.3 | -0.48% | -0.34% | 0.03 | 49.6 | 15 | yes | MC4 | black | black | 65.35 | 38.98 | 1.97 | 17.6899 | 46.3 | 5 |  | Check |  | Aleo_Solar
aleo solar | A_79 240 | mono | 240 | 210.0495 | +/-3 | 3 | -3 | 13.5671 | 14.6 | 29.8 | 8.05 | 36.8 | 8.56 | -0.48% | -0.34% | 0.03 | 49.6 | 15 | yes | MC4 | black | black | 65.35 | 38.98 | 1.97 | 17.6899 | 46.3 | 5 |  | Check |  | Aleo_Solar
aleo solar | A_79 245 | mono | 245 | 214.5727 | +/-3 | 3 | -3 | 13.8497 | 14.9 | 30.2 | 8.1 | 37.2 | 8.6 | -0.48% | -0.34% | 0.03 | 49.6 | 15 | yes | MC4 | black | black | 65.35 | 38.98 | 1.97 | 17.6899 | 46.3 | 5 |  | Check |  | Aleo_Solar
aleo solar | S_16 175 | poly | 175 | 155.2 | +/-3 | 3 | -3 | 11.7998 | 12.7 | 23.6 | 7.41 | 30 | 7.95 | -0.46% | -0.34% | 0.04 | 48 | 15 | yes | MC4 | silver | white | 65.35 | 32.68 | 1.97 | 14.8308 | 37.5 | 10 |  | Check |  | Aleo_Solar
aleo solar | S_16 180 | poly | 180 | 159.7 | +/-3 | 3 | -3 | 12.1369 | 13.1 | 23.8 | 7.55 | 30.2 | 8.07 | -0.46% | -0.34% | 0.04 | 48 | 15 | yes | MC4 | silver | white | 65.35 | 32.68 | 1.97 | 14.8308 | 37.5 | 10 |  | Check |  | Aleo_Solar
aleo solar | S_16 185 | poly | 185 | 164.3 | +/-3 | 3 | -3 | 12.474 | 13.4 | 24 | 7.7 | 30.4 | 8.2 | -0.46% | -0.34% | 0.04 | 48 | 15 | yes | MC4 | silver | white | 65.35 | 32.68 | 1.97 | 14.8308 | 37.5 | 10 |  | Check |  | Aleo_Solar
aleo solar | S_18 225 | poly | 225 | 199.5679 | +/-3 | 3 | -3 | 12.7191 | 13.7 | 29.3 | 7.68 | 36.5 | 8.13 | -0.46% | -0.34% | 0.04 | 47.9 | 15 | yes | MC4 | silver | white | 65.35 | 38.98 | 1.97 | 17.6899 | 46.3 | 10 |  | Check |  | Aleo_Solar
aleo solar | S_18 230 | poly | 230 | 204.1275 | +/-3 | 3 | -3 | 13.0018 | 14 | 29.5 | 7.8 | 36.7 | 8.26 | -0.46% | -0.34% | 0.04 | 47.9 | 15 | yes | MC4 | silver | white | 65.35 | 38.98 | 1.97 | 17.6899 | 46.3 | 10 |  | Check |  | Aleo_Solar
aleo solar | S_18j245 | poly | 245 |  | +/-3 | 3 | -3 |  |  | 30.2 | 8.11 | 37.5 | 8.63 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Aleo_Solar
aleo solar | S_18j250 | poly | 250 |  | +/-3 | 3 | -3 |  |  | 30.3 | 8.24 | 37.5 | 8.76 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Aleo_Solar
aleo solar | S_18j255 | poly | 255 |  | +/-3 | 3 | -3 |  |  | 30.4 | 8.38 | 37.6 | 8.88 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Aleo_Solar
aleo solar | S_18j260 | poly | 260 |  | +/-3 | 3 | -3 |  |  | 30.5 | 8.51 | 37.7 | 9.01 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Aleo_Solar
aleo solar | S_18j265 | poly | 265 |  | +/-3 | 3 | -3 |  |  | 30.7 | 8.64 | 37.7 | 9.14 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Aleo_Solar
aleo solar | S18_250 | poly | 250 |  | +/-3 | 3 | -3 |  |  | 30.3 | 8.24 | 37.5 | 8.76 | -0.42% | -0.31% |  |  | 20 | [11 empty] | Check | 2017-02-13 | Aleo_Solar
aleo solar | S18_255 | poly | 255 |  | +/-3 | 3 | -3 |  |  | 30.4 | 8.38 | 37.6 | 8.88 | -0.42% | -0.31% |  |  | 20 | [11 empty] | Check | 2017-02-13 | Aleo_Solar
aleo solar | S18_260 | poly | 260 |  | +/-3 | 3 | -3 |  |  | 30.5 | 8.51 | 37.7 | 9.01 | -0.42% | -0.31% |  |  | 20 | [11 empty] | Check | 2017-02-13 | Aleo_Solar
aleo solar | S18_265 | poly | 265 |  | +/-3 | 3 | -3 |  |  | 30.7 | 8.64 | 37.7 | 9.14 | -0.42% | -0.31% |  |  | 20 | [11 empty] | Check | 2017-02-13 | Aleo_Solar
aleo solar | P18_250 | poly | 250 |  | +/-3 | 3 | -3 |  |  | 30.3 | 8.24 | 37.5 | 8.76 | -0.42% | -0.31% |  |  | 20 | [11 empty] | Check | 2017-02-13 | Aleo_Solar
aleo solar | P18_255 | poly | 255 |  | +/-3 | 3 | -3 |  |  | 30.4 | 8.38 | 37.6 | 8.88 | -0.42% | -0.31% |  |  | 20 | [11 empty] | Check | 2017-02-13 | Aleo_Solar
aleo solar | P18_260 | poly | 260 |  | +/-3 | 3 | -3 |  |  | 30.5 | 8.51 | 37.7 | 9.01 | -0.42% | -0.31% |  |  | 20 | [11 empty] | Check | 2017-02-13 | Aleo_Solar
aleo solar | S19L280 | mono | 280 |  | +/-3 | 3 | -3 |  |  | 31.2 | 8.97 | 39.2 | 9.67 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Aleo_Solar
aleo solar | S19L285 | mono | 285 |  | +/-3 | 3 | -3 |  |  | 31.3 | 9.1 | 39.2 | 9.73 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Aleo_Solar
aleo solar | S19L290 | mono | 290 |  | +/-3 | 3 | -3 |  |  | 31.3 | 9.25 | 39.3 | 9.8 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Aleo_Solar
aleo solar | S19_300 | mono | 300 |  | +/-3 | 3 | -3 |  |  | 31.2 | 9.63 | 39.4 | 9.97 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-02-13 | Aleo_Solar
aleo solar | S19_305 | mono | 305 |  | +/-3 | 3 | -3 |  |  | 31.4 | 9.72 | 39.6 | 10.06 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-02-13 | Aleo_Solar
aleo solar | S19_310 | mono | 310 |  | +/-3 | 3 | -3 |  |  | 31.7 | 9.8 | 39.7 | 10.12 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-02-13 | Aleo_Solar
aleo solar | S25_235 | mono | 235 |  | +/-3 | 3 | -3 |  |  | 25.2 | 9.37 | 31.5 | 9.83 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Aleo_Solar
aleo solar | S25_240 | mono | 240 |  | +/-3 | 3 | -3 |  |  | 25.3 | 9.51 | 31.5 | 9.9 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Aleo_Solar
aleo solar | S25_245 | mono | 245 |  | +/-3 | 3 | -3 |  |  | 25.4 | 9.66 | 31.6 | 9.97 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Aleo_Solar
aleo solar | S59_300 | mono | 300 |  | +/-3 | 3 | -3 |  |  | 31.2 | 9.63 | 39.4 | 9.97 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-02-13 | Aleo_Solar
aleo solar | S59_305 | mono | 305 |  | +/-3 | 3 | -3 |  |  | 31.4 | 9.72 | 39.6 | 10.06 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-02-13 | Aleo_Solar
aleo solar | S59_310 | mono | 310 |  | +/-3 | 3 | -3 |  |  | 31.7 | 9.8 | 39.7 | 10.12 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-02-13 | Aleo_Solar
aleo solar | S75_230 | mono | 230 |  | +/-3 | 3 | -3 |  |  | 25.1 | 9.18 | 31.4 | 9.76 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Aleo_Solar
aleo solar | S75_235 | mono | 235 |  | +/-3 | 3 | -3 |  |  | 25.2 | 9.37 | 31.5 | 9.83 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Aleo_Solar
aleo solar | S75_240 | mono | 240 |  | +/-3 | 3 | -3 |  |  | 25.3 | 9.51 | 31.5 | 9.9 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Aleo_Solar
aleo solar | S_79 235 | mono | 235 | 205.5324 | +/-3 | 3 | -3 | 13.2844 | 14.3 | 29.4 | 8 | 36.4 | 8.3 | -0.48% | -0.34% | 0.03 | 49.6 | 15 | yes | MC4 | black | black | 65.35 | 38.98 | 1.97 | 17.6899 | 46.3 | 10 |  | Check |  | Aleo_Solar
aleo solar | S_79 240 | mono | 240 | 210.0495 | +/-3 | 3 | -3 | 13.5671 | 14.6 | 29.8 | 8.05 | 36.8 | 8.56 | -0.48% | -0.34% | 0.03 | 49.6 | 15 | yes | MC4 | black | black | 65.35 | 38.98 | 1.97 | 17.6899 | 46.3 | 10 |  | Check |  | Aleo_Solar
aleo solar | S_79 245 | mono | 245 | 214.5727 | +/-3 | 3 | -3 | 13.8497 | 14.9 | 30.2 | 8.1 | 37.2 | 8.6 | -0.48% | -0.34% | 0.03 | 49.6 | 15 | yes | MC4 | black | black | 65.35 | 38.98 | 1.97 | 17.6899 | 46.3 | 10 |  | Check |  | Aleo_Solar
aleo solar | S79L275 | mono | 275 |  | +/-3 | 3 | -3 |  |  | 31.1 | 8.83 | 39.1 | 9.62 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Aleo_Solar
aleo solar | S79L280 | mono | 280 |  | +/-3 | 3 | -3 |  |  | 31.2 | 8.97 | 39.2 | 9.67 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Aleo_Solar
aleo solar | S79L285 | mono | 285 |  | +/-3 | 3 | -3 |  |  | 31.3 | 9.1 | 39.2 | 9.73 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Aleo_Solar
aleo solar | S79L290 | mono | 290 |  | +/-3 | 3 | -3 |  |  | 31.3 | 9.25 | 39.3 | 9.8 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Aleo_Solar
aleo solar | S79_295 | mono | 295 |  | +/-3 | 3 | -3 |  |  | 31.3 | 9.42 | 39.3 | 9.87 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-11-22 | Aleo_Solar
aleo solar | S79_300 | mono | 300 |  | +/-3 | 3 | -3 |  |  | 31.2 | 9.63 | 39.4 | 9.97 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-11-22 | Aleo_Solar
aleo solar | S79_305 | mono | 305 |  | +/-3 | 3 | -3 |  |  | 31.4 | 9.72 | 39.6 | 10.06 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-11-22 | Aleo_Solar
aleo solar | P19_285 | mono | 285 |  | +/-3 | 3 | -3 |  |  | 31.3 | 9.1 | 39.2 | 9.73 | -0.4% | -0.29% |  |  | 20 | [11 empty] | Check | 2017-02-13 | Aleo_Solar
aleo solar | P19_290 | mono | 290 |  | +/-3 | 3 | -3 |  |  | 31.3 | 9.25 | 39.3 | 9.8 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-02-13 | Aleo_Solar
aleo solar | P19_295 | mono | 295 |  | +/-3 | 3 | -3 |  |  | 31.3 | 9.42 | 39.3 | 9.87 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-02-13 | Aleo_Solar
aleo solar | P19_300 | mono | 300 |  | +/-3 | 3 | -3 |  |  | 31.2 | 9.63 | 39.4 | 9.97 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Aleo_Solar
aleo solar | S79 SOL_290 | mono | 290 |  | +/-3 | 3 | -3 |  |  | 31.3 | 9.25 | 39.3 | 9.8 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-02-13 | Aleo_Solar
aleo solar | S79 SOL_295 | mono | 295 |  | +/-3 | 3 | -3 |  |  | 31.3 | 9.42 | 39.3 | 9.87 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-02-13 | Aleo_Solar
aleo solar | S79 SOL_300 | mono | 300 |  | +/-3 | 3 | -3 |  |  | 31.2 | 9.63 | 39.4 | 9.97 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-02-13 | Aleo_Solar
aleo solar | G40_190 | mono | 190 |  | +/-3 | 3 | -3 |  |  | 20.9 | 9.25 | 26.2 | 12.5 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-02-13 | Aleo_Solar
American Solar Wholesale | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | Aleo_Solar
American Solar Wholesale | ASW-230P | poly | 230 | 206.9 | +3/-0 | 3 | 0 | 13.0731 | 14.08 | 29.6 | 7.77 | 36.8 | 8.63 | -0.46% | -0.33% | 0.06 | 45 | 15 | yes | MC4 | silver | white | 64.96 | 39 | 2 | 17.5933 | 42 | 10 |  | Check |  | American_Solar_Wholesale
American Solar Wholesale | ASW-240M | mono | 240 | 213 | +3/-0 | 3 | 0 | 13.6415 | 14.7 | 30.81 | 7.82 | 37.36 | 8.45 | -0.47% | -0.35% | 0.06 | 45 | 10 | yes | MC4 | silver | white | 64.96 | 39 | 2 | 17.5933 | 42 | 10 |  | Check |  | American_Solar_Wholesale
American Solar Wholesale | ASW-240P | poly | 240 |  | +3/-0 | 3 | 0 |  |  | 29.8 | 8.05 | 37 | 8.69 | -0.44% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | American_Solar_Wholesale
American Solar Wholesale | ASW-245M | mono | 245 |  | +3/-0 | 3 | 0 |  |  | 30 | 8.19 | 37.4 | 8.79 | -0.44% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | American_Solar_Wholesale
American Solar Wholesale | ASW-245P | poly | 245 |  | +3/-0 | 3 | 0 |  |  | 29.9 | 8.19 | 37.1 | 8.74 | -0.44% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | American_Solar_Wholesale
American Solar Wholesale | ASW-250M | mono | 250 |  | +3/-0 | 3 | 0 |  |  | 30.1 | 8.32 | 37.5 | 8.87 | -0.44% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | American_Solar_Wholesale
American Solar Wholesale | ASW-255M | mono | 255 |  | +3/-0 | 3 | 0 |  |  | 30.2 | 8.44 | 37.6 | 8.99 | -0.44% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-11-30 | American_Solar_Wholesale
American Solar Wholesale | ASW-260M | mono | 260 | 230.1 | +3/-0 | 3 | 0 | 12.6084 | 13.47 | 30.4 | 8.55 | 37.7 | 9.1 | -0.44% | -0.3% | DNR | 45 | 15 | yes | MC4 | silver | white | 76.14 | 39 | 2 | 20.6212 | 51 | 10 |  | 1000 | 2015-11-30 | American_Solar_Wholesale
American Solar Wholesale | ASW-250P | poly | 250 |  | +3/-0 | 3 | 0 |  |  | 30.2 | 8.29 | 37.3 | 8.84 | -0.44% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-11-30 | American_Solar_Wholesale
American Solar Wholesale | ASW-255P | poly | 255 |  | +3/-0 | 3 | 0 |  |  | 30.3 | 8.43 | 37.4 | 8.98 | -0.44% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-11-30 | American_Solar_Wholesale
American Solar Wholesale | ASW-260P | poly | 260 | 237.1 | +3/-0 | 3 | 0 | 12.6084 | 13.47 | 30.4 | 8.56 | 37.6 | 9.09 | -0.44% | -3% | 0.06 | 45 | 15 | yes | MC4 | silver | white | 76.14 | 39 | 2 | 20.6212 | 51 | 10 |  | 1000 | 2015-11-30 | American_Solar_Wholesale
American Solar Wholesale | ASW-265M | mono | 265 |  | +3/-0 | 3 | 0 |  |  | 30.6 | 8.66 | 37.8 | 9.16 | -0.44% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-11-30 | American_Solar_Wholesale
American Solar Wholesale | ASW-270M | mono | 270 | 239.2 | +3/-0 | 3 | 0 | 13.0933 | 13.99 | 36.58 | 7.38 | 43.63 | 8.08 | -0.47% | -0.35% | DNR | 45 | 10 | yes | MC4 | silver | white | 76.14 | 39 | 2 | 20.6212 | 51 | 10 |  | Check |  | American_Solar_Wholesale
American Solar Wholesale | ASW-270P | poly | 270 | 246.4 | +3/-0 | 3 | 0 | 13.0933 | 13.99 | 36.29 | 7.44 | 43.63 | 7.86 | -0.44% | -0.3% | 0.06 | 45 | 15 | yes | MC4 | silver | white | 76.14 | 39 | 2 | 20.6212 | 51 | 10 |  | 1000 | 2015-11-30 | American_Solar_Wholesale
American Solar Wholesale | ASW-275P | poly | 275 |  | +3/-0 | 3 | 0 |  |  | 36.42 | 7.55 | 43.74 | 7.91 | -0.44% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-11-30 | American_Solar_Wholesale
American Solar Wholesale | ASW-280P | poly | 280 |  | +3/-0 | 3 | 0 |  |  | 36.58 | 7.65 | 43.78 | 7.93 | -0.44% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-11-30 | American_Solar_Wholesale
American Solar Wholesale | ASW-280M | mono | 280 | 248.4 | +3/-0 | 3 | 0 | 13.5782 | 14.5 | 37.01 | 7.57 | 43.99 | 8.14 | -0.47% | -0.35% | DNR | 45 | 10 | yes | MC4 | silver | white | 76.14 | 39 | 2 | 20.6212 | 51 | 10 |  | Check |  | American_Solar_Wholesale
American Solar Wholesale | ASW-290P | poly | 290 |  | +3/-0 | 3 | 0 |  |  | 37.23 | 7.79 | 44.72 | 8.45 | -0.44% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-11-30 | American_Solar_Wholesale
American Solar Wholesale | ASW-295P | poly | 295 |  | +3/-0 | 3 | 0 |  |  | 37.25 | 7.92 | 45.62 | 8.51 | -0.44% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-11-30 | American_Solar_Wholesale
American Solar Wholesale | ASW-300P | poly | 300 |  | +3/-0 | 3 | 0 |  |  | 37.46 | 8.01 | 46.12 | 8.56 | -0.44% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-11-30 | American_Solar_Wholesale
American Solar Wholesale | ASW-305P | poly | 305 |  | +3/-0 | 3 | 0 |  |  | 37.63 | 8.1 | 46.33 | 8.62 | -0.44% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-11-30 | American_Solar_Wholesale
American Solar Wholesale | ASW-310P | poly | 310 |  | +3/-0 | 3 | 0 |  |  | 37.7 | 8.2 | 46.46 | 8.7 | -0.44% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-11-30 | American_Solar_Wholesale
Amerisolar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | American_Solar_Wholesale
Amerisolar | AS-6P-295W | poly | 295 |  | +3/-0 | 3 | 0 |  |  | 36.6 | 8.07 | 45.2 | 8.6 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.97 |  |  |  |  | 1000 | 2017-12-18 | Amerisolar
Amerisolar | AS-6P-300W | poly | 300 |  | +3/-0 | 3 | 0 |  |  | 36.7 | 8.18 | 45.3 | 8.68 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.97 |  |  |  |  | 1000 | 2017-12-18 | Amerisolar
Amerisolar | AS-6P-305W | poly | 305 |  | +3/-0 | 3 | 0 |  |  | 36.8 | 8.29 | 45.4 | 8.76 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.97 |  |  |  |  | 1000 | 2017-12-18 | Amerisolar
Amerisolar | AS-6P-310W | poly | 310 |  | +3/-0 | 3 | 0 |  |  | 36.9 | 8.41 | 45.5 | 8.85 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.97 |  |  |  |  | 1000 | 2017-12-18 | Amerisolar
Amerisolar | AS-6P-3150W | poly | 315 |  | +3/-0 | 3 | 0 |  |  | 37 | 8.52 | 45.6 | 8.93 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.97 |  |  |  |  | 1000 | 2017-12-18 | Amerisolar
Amerisolar | AS-6P-320W | poly | 320 |  | +3/-0 | 3 | 0 |  |  | 37.1 | 8.63 | 45.7 | 9 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.97 |  |  |  |  | 1000 | 2017-12-18 | Amerisolar
Amerisolar | AS-6P-325W | poly | 325 |  | +3/-0 | 3 | 0 |  |  | 37.2 | 8.74 | 45.8 | 9.08 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.97 |  |  |  |  | 1000 | 2017-12-18 | Amerisolar
Amerisolar | AS-6P-330W | poly | 330 |  | +3/-0 | 3 | 0 |  |  | 37.3 | 8.85 | 45.9 | 9.16 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.97 |  |  |  |  | 1000 | 2017-12-18 | Amerisolar
Amerisolar | AS-6P30-235W | poly | 235 |  | +3/-0 | 3 | 0 |  |  | 29.7 | 7.92 | 37.5 | 8.48 | -0.43% | -0.33% |  |  | 15 | [11 empty] | Check | 2016-07-12 | Amerisolar
Amerisolar | AS-6P30-240W | poly | 240 |  | +3/-0 | 3 | 0 |  |  | 29.9 | 8.03 | 37.7 | 8.57 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  |  |  |  | 1000 | 2016-07-12 | Amerisolar
Amerisolar | AS-6P30-245W | poly | 245 |  | +3/-0 | 3 | 0 |  |  | 30.1 | 8.14 | 37.9 | 8.66 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  |  |  |  | 1000 | 2016-07-12 | Amerisolar
Amerisolar | AS-6P30-250W | poly | 250 |  | +3/-0 | 3 | 0 |  |  | 30.3 | 8.26 | 38 | 8.75 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  |  |  |  | 1000 | 2016-07-12 | Amerisolar
Amerisolar | AS-6P30-255W | poly | 255 |  | +3/-0 | 3 | 0 |  |  | 30.5 | 8.37 | 38.1 | 8.83 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  |  |  |  | 1000 | 2016-07-12 | Amerisolar
Amerisolar | AS-6P30-260W | poly | 260 |  | +3/-0 | 3 | 0 |  |  | 30.7 | 8.47 | 38.2 | 8.9 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  |  |  |  | 1000 | 2016-07-12 | Amerisolar
Amerisolar | AS-6P30-265W | poly | 265 |  | +3/-0 | 3 | 0 |  |  | 30.9 | 8.58 | 38.3 | 8.98 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  |  |  |  | 1000 | 2016-07-12 | Amerisolar
Amerisolar | AS-6P30-270W | poly | 270 |  | +3/-0 | 3 | 0 |  |  | 31.1 | 8.69 | 38.4 | 9.06 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  |  |  |  | 1000 | 2017-12-18 | Amerisolar
Amerisolar | AS-6P30-275W | poly | 275 |  | +3/-0 | 3 | 0 |  |  | 31.3 | 8.79 | 38.5 | 9.15 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  |  |  |  | 1000 | 2017-12-18 | Amerisolar
Astronergy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | Amerisolar
Astronergy | ASM6610P-240 | poly | 240 | 155.2 | +/-3 | 3 | -3 | 12.7364 | 13.7 | 29.86 | 8.1 | 36.45 | 8.59 | -0.42% | -0.32% | 0.062 | 48 | 15 | no | MC4 | silver/black | white/black | 62.2 | 31.81 | 1.77 | 13.7402 | 34.2 | 10 |  | 1000 | 7/14/15 RM | Astronergy
Astronergy | ASM6610P-245 | poly | 245 | 159.7 | +/-3 | 3 | -3 | 13.1003 | 14.1 | 30.12 | 8.2 | 36.78 | 8.68 | -0.42% | -0.32% | 0.062 | 48 | 15 | no | MC4 | silver/black | white/black | 62.2 | 31.81 | 1.77 | 13.7402 | 34.2 | 10 |  | 1000 | 7/14/15 RM | Astronergy
Astronergy | ASM6610P-250 | poly | 250 | 164.3 | +/-3 | 3 | -3 |  |  | 30.38 | 8.29 | 37.12 | 8.76 | -0.42% | -0.32% | 0.062 | 48 | 15 | no | MC4 | silver/black | white/black | 62.2 | 31.81 | 1.77 | 13.7402 | 34.2 | 10 |  | 1000 | 7/14/15 RM | Astronergy
Astronergy | ASM6610P-255 | poly | 255 | 168.9 | +/-3 | 3 | -3 |  |  | 30.64 | 8.39 | 37.45 | 8.85 | -0.42% | -0.32% | 0.062 | 48 | 15 | no | MC4 | silver/black | white/black | 62.2 | 31.81 | 1.77 | 13.7402 | 34.2 | 10 |  | 1000 | 7/14/15 RM | Astronergy
Astronergy | ASM6610P-260 | poly | 260 |  | +/-3 | 3 | -3 |  |  | 30.9 | 8.48 | 37.78 | 8.93 | -0.42% | -0.32% | 0.062 | 48 | 15 | [11 empty] | 1000 | 7/14/15 RM | Astronergy
Astronergy | ASM6610P-265 | poly | 265 |  | +/-3 | 3 | -3 |  |  | 31.16 | 8.57 | 38.12 | 9.01 | -0.42% | -0.32% | 0.062 | 48 | 15 | [11 empty] | 1000 | 7/14/15 RM | Astronergy
Astronergy | ASM6610P(BL)-250 | poly | 250 |  | +3/-0 | 3 | -0 |  |  | 30.29 | 8.33 | 36.91 | 8.8 | -0.42% | -0.32% |  |  | 15 | [11 empty] | 1000 | 2017-02-13 | Astronergy
Astronergy | ASM6610P(BL)-255 | poly | 255 |  | +3/-0 | 3 | --0 |  |  | 30.54 | 8.42 | 37.18 | 8.89 | -0.42% | -0.32% |  |  | 15 | [11 empty] | 1000 | 2017-02-13 | Astronergy
Astronergy | ASM6610P(BL)-260 | poly | 260 |  | +3/-0 | 3 | -0 |  |  | 30.79 | 8.52 | 37.45 | 8.98 | -0.42% | -0.32% |  |  | 15 | [11 empty] | 1000 | 2017-02-13 | Astronergy
Astronergy | ASM6610P(BL)-265 | poly | 265 |  | +3/-0 | 3 | -0 |  |  | 31.04 | 8.61 | 37.72 | 9.06 | -0.42% | -0.32% |  |  | 15 | [11 empty] | 1000 | 2017-02-13 | Astronergy
Astronergy | ASM6610P(BL)-270 | poly | 270 |  | +3/-0 | 3 | -0 |  |  | 31.29 | 8.7 | 37.99 | 9.15 | -0.42% | -0.32% |  |  | 15 | [11 empty] | 1000 | 2017-02-13 | Astronergy
Astronergy | ASM6610P(BL)-275 | poly | 275 |  | +3/-0 | 3 | -0 |  |  | 31.54 | 8.8 | 38.26 | 9.23 | -0.42% | -0.32% |  |  | 15 | [11 empty] | 1000 | 2017-02-13 | Astronergy
Astronergy | ASM6610P(BF)-250 | poly | 250 |  | +5/-0 | 5 | -0 |  |  | 30.38 | 8.29 | 37.12 | 8.76 | -0.42% | -0.32% |  |  | 15 | [11 empty] | 1000 | 2017-02-13 | Astronergy
Astronergy | ASM6610P(BF)-255 | poly | 255 |  | +5/-0 | 5 | -0 |  |  | 30.64 | 8.39 | 37.45 | 8.85 | -0.42% | -0.32% |  |  | 15 | [11 empty] | 1000 | 2017-02-13 | Astronergy
Astronergy | ASM6610P(BF)-260 | poly | 260 |  | +5/-0 | 5 | -0 |  |  | 30.9 | 8.48 | 37.78 | 8.93 | -0.42% | -0.32% |  |  | 15 | [11 empty] | 1000 | 2017-02-13 | Astronergy
Astronergy | ASM6610P(BF)-265 | poly | 265 |  | +5/-0 | 5 | -0 |  |  | 31.16 | 8.57 | 38.12 | 9.01 | -0.42% | -0.32% |  |  | 15 | [11 empty] | 1000 |  | Astronergy
Astronergy | CHSM5612M-175 | mono | 175 | 155.2 | +/-3 | 3 | -3 | 12.7364 | 13.7 | 35.65 | 4.92 | 44.63 | 5.23 | -0.48% | -0.355% | 0.062 | 48 | 10 | no | MC4 | silver/black | white/black | 62.2 | 31.81 | 1.77 | 13.7402 | 34.2 | 10 |  | Check |  | Astronergy
Astronergy | CHSM5612M-180 | mono | 180 | 159.7 | +/-3 | 3 | -3 | 13.1003 | 14.1 | 36.02 | 5 | 44.88 | 5.31 | -0.48% | -0.355% | 0.062 | 48 | 10 | no | MC4 | silver/black | white/black | 62.2 | 31.81 | 1.77 | 13.7402 | 34.2 | 10 |  | Check |  | Astronergy
Astronergy | CHSM5612M-185 | mono | 185 | 164.3 | +5/-0 | 5 | -0 |  |  | 36.38 | 5.09 | 45.12 | 5.39 | -0.48% | -0.355% |  |  | 10 | no | MC4 | silver/black | white/black | 62.2 | 31.81 | 1.77 | 13.7402 | 34.2 | 10 |  | Check |  | Astronergy
Astronergy | CHSM5612M-190 | mono | 190 | 168.9 | +5/-0 | 5 | -0 |  |  | 36.74 | 5.17 | 45.37 | 5.47 | -0.48% | -0.355% |  |  | 10 | no | MC4 | silver/black | white/black | 62.2 | 31.81 | 1.77 | 13.7402 | 34.2 | 10 |  | Check |  | Astronergy
Astronergy | CHSM5612M-195 | mono | 195 |  | +5/-0 | 5 | -0 |  |  | 37.1 | 5.25 | 45.62 | 5.55 | -0.48% | -0.355% |  |  | 10 | [11 empty] | Check |  | Astronergy
Astronergy | CHSM5612M-200 | mono | 200 |  | +5/-0 | 5 | -0 |  |  | 37.46 | 5.34 | 45.87 | 5.63 | -0.48% | -0.355% |  |  | 10 | [11 empty] | Check |  | Astronergy
Astronergy | CHSM5612M-205 | mono | 205 |  | +5/-0 | 5 | -0 |  |  | 37.83 | 5.42 | 46.11 | 5.71 | -0.48% | -0.355% |  |  | 10 | [11 empty] | Check |  | Astronergy
Astronergy | CHSM6610M-220 | mono | 220 | 195.5 | +/-3 | 3 | -3 | 12.4479 | 13.4 | 28.3 | 7.78 | 37.18 | 8.45 | -0.469% | -0.328% | 0.035 | 47 | 15 | no | MC4 | silver/black | white/black | 65.04 | 39.13 | 1.77 | 17.6737 | 44 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6610M-225 | mono | 225 | 200.1 | +/-3 | 3 | -3 | 12.7308 | 13.7 | 28.66 | 7.86 | 37.33 | 8.48 | -0.469% | -0.328% | 0.035 | 47 | 15 | no | MC4 | silver/black | white/black | 65.04 | 39.13 | 1.77 | 17.6737 | 44 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6610M-230 | mono | 230 | 204.7 | +/-3 | 3 | -3 | 13.0137 | 14 | 29.03 | 7.93 | 37.48 | 8.52 | -0.469% | -0.328% | 0.035 | 47 | 15 | no | MC4 | silver/black | white/black | 65.04 | 39.13 | 1.77 | 17.6737 | 44 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6610M-235 | mono | 235 | 209.2 | +/-3 | 3 | -3 | 13.2966 | 14.3 | 29.39 | 8.01 | 37.63 | 8.55 | -0.469% | -0.328% | 0.035 | 47 | 15 | no | MC4 | silver/black | white/black | 65.04 | 39.13 | 1.77 | 17.6737 | 44 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6610M-240 | mono | 240 | 213.8 | +/-3 | 3 | -3 | 13.5795 | 14.6 | 29.75 | 8.08 | 37.78 | 8.58 | -0.469% | -0.328% | 0.035 | 47 | 15 | no | MC4 | silver/black | white/black | 65.04 | 39.13 | 1.77 | 17.6737 | 44 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6610M-245 | mono | 245 | 218.4 | +/-3 | 3 | -3 | 13.8624 | 14.9 | 30.12 | 8.16 | 37.94 | 8.61 | -0.469% | -0.328% | 0.035 | 47 | 15 | no | MC4 | silver/black | white/black | 65.04 | 39.13 | 1.77 | 17.6737 | 44 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6610M-250 | mono | 250 | 223 | +/-3 | 3 | -3 | 14.1453 | 15.2 | 30.48 | 8.23 | 38.09 | 8.64 | -0.469% | -0.328% | 0.035 | 47 | 15 | no | MC4 | silver/black | white/black | 65.04 | 39.13 | 1.77 | 17.6737 | 44 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6610M-255 | mono | 255 |  | +5/-0 | 5 | 0 |  |  | 30.84 | 8.31 | 38.24 | 8.67 | -0.47% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Astronergy
Astronergy | CHSM6610M-260 | mono | 260 |  | +5/-0 | 5 | 0 |  |  | 31.19 | 8.38 | 38.39 | 8.7 | -0.47% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Astronergy
Astronergy | CHSM6610M-265 | mono | 265 |  | +5/-0 | 5 | 0 |  |  | 31.49 | 8.44 | 38.55 | 8.74 | -0.47% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Astronergy
Astronergy | CHSM6610M-270 | mono | 270 |  | +5/-0 | 5 | 0 |  |  | 31.82 | 8.51 | 38.7 | 8.77 | -0.47% | -0.33% |  |  | 15 | [11 empty] | 1000 | 2015-12-02 | Astronergy
Astronergy | CHSM6610M-275 | mono | 275 |  | +5/-0 | 5 | 0 |  |  | 32.09 | 8.57 | 38.85 | 8.79 | -0.47% | -0.33% |  |  | 15 | [11 empty] | 1000 | 2015-12-02 | Astronergy
Astronergy | CHSM6610M-280 | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 32.56 | 8.6 | 39.16 | 8.85 | -0.47% | -0.33% |  |  | 15 | [11 empty] | 1000 | 2015-12-02 | Astronergy
Astronergy | CHSM6610M-285 | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 32.99 | 8.64 | 39.34 | 8.91 | -0.47% | -0.33% |  |  | 15 | [11 empty] | 1000 | 2015-12-02 | Astronergy
Astronergy | CHSM6610M-290 | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 32.15 | 9.03 | 39.45 | 9.54 | -0.38% | -0.284% |  |  | 15 | [11 empty] | 1000 | 2017-12-18 | Astronergy
Astronergy | CHSM6610M-295 | mono | 295 |  | +5/-0 | 5 | 0 |  |  | 32.38 | 9.12 | 39.81 | 9.59 | -0.38% | -0.284% |  |  | 15 | [11 empty] | 1000 | 2017-12-18 | Astronergy
Astronergy | CHSM6610M-300 | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 32.59 | 9.21 | 39.9 | 9.68 | -0.38% | -0.284% |  |  | 15 | [11 empty] | 1000 | 2017-12-18 | Astronergy
Astronergy | CHSM6610M-305 | mono | 305 |  | +5/-0 | 5 | 0 |  |  | 32.8 | 9.3 | 40.05 | 9.72 | -0.38% | -0.284% |  |  | 15 | [11 empty] | 1000 | 2017-12-18 | Astronergy
Astronergy | CHSM6610M/HV-290 | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 32.15 | 9.03 | 39.45 | 9.54 | -0.38% | -0.284% |  |  | 15 | [11 empty] | 1500 | 2017-12-18 | Astronergy
Astronergy | CHSM6610M/HV-295 | mono | 295 |  | +5/-0 | 5 | 0 |  |  | 32.38 | 9.12 | 39.81 | 9.59 | -0.38% | -0.284% |  |  | 15 | [11 empty] | 1500 | 2017-12-18 | Astronergy
Astronergy | CHSM6610M/HV-300 | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 32.59 | 9.21 | 39.9 | 9.68 | -0.38% | -0.284% |  |  | 15 | [11 empty] | 1500 | 2017-12-18 | Astronergy
Astronergy | CHSM6610M/HV-305 | mono | 305 |  | +5/-0 | 5 | 0 |  |  | 32.8 | 9.3 | 40.05 | 9.72 | -0.38% | -0.284% |  |  | 15 | [11 empty] | 1500 | 2017-12-18 | Astronergy
Astronergy | CHSM6610M/HV-270 | mono | 270 |  | +5/-0 | 5 | 0 |  |  | 31.82 | 8.51 | 38.7 | 8.77 | -0.47% | -0.33% |  |  | 15 | [11 empty] | 1500 | 2015-12-02 | Astronergy
Astronergy | CHSM6610M/HV-275 | mono | 275 |  | +5/-0 | 5 | 0 |  |  | 32.09 | 8.57 | 38.85 | 8.79 | -0.47% | -0.33% |  |  | 15 | [11 empty] | 1500 | 2015-12-02 | Astronergy
Astronergy | CHSM6610M/HV-280 | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 32.56 | 8.6 | 39.16 | 8.85 | -0.47% | -0.33% |  |  | 15 | [11 empty] | 1500 | 2015-12-02 | Astronergy
Astronergy | CHSM6610M/HV-285 | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 32.99 | 8.64 | 39.34 | 8.91 | -0.47% | -0.33% |  |  | 15 | [11 empty] | 1500 | 2015-12-02 | Astronergy
Astronergy | CHSM6610P-220 | poly | 220 | 199.9 | +/-3 | 3 | -3 | 12.4479 | 13.4 | 28.02 | 7.86 | 36.92 | 8.46 | -0.469% | -0.344% | 0.052 | 43 | 15 | yes | MC4 | silver | white | 65.04 | 39.13 | 1.77 | 17.6737 | 44 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6610P-225 | poly | 225 | 204.6 | +/-3 | 3 | -3 | 12.7308 | 13.7 | 28.4 | 7.92 | 37.14 | 8.49 | -0.469% | -0.344% | 0.052 | 43 | 15 | yes | MC4 | silver | white | 65.04 | 39.13 | 1.77 | 17.6737 | 44 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6610P-230 | poly | 230 | 209.2 | +/-3 | 3 | -3 | 13.0137 | 14 | 28.78 | 7.99 | 37.35 | 8.53 | -0.469% | -0.344% | 0.052 | 43 | 15 | yes | MC4 | silver | white | 65.04 | 39.13 | 1.77 | 17.6737 | 44 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6610P-235 | poly | 235 | 213.9 | +/-3 | 3 | -3 | 13.2966 | 14.3 | 29.16 | 8.06 | 37.56 | 8.56 | -0.469% | -0.344% | 0.052 | 43 | 15 | yes | MC4 | silver | white | 65.04 | 39.13 | 1.77 | 17.6737 | 44 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6610P-240 | poly | 240 | 218.5 | +/-3 | 3 | -3 | 13.5795 | 14.6 | 29.54 | 8.13 | 37.77 | 8.59 | -0.469% | -0.344% | 0.052 | 43 | 15 | yes | MC4 | silver | white | 65.04 | 39.13 | 1.77 | 17.6737 | 44 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6610P-245 | poly | 245 |  | +5/-0 | 5 | 0 |  |  | 29.9 | 8.2 | 37.98 | 8.62 | -0.469% | -0.344% |  |  | 15 | [11 empty] | Check |  | Astronergy
Astronergy | CHSM6610P-250 | poly | 250 |  | +5/-0 | 5 | 0 |  |  | 30.3 | 8.27 | 38.19 | 8.65 | -0.469% | -0.344% |  |  | 15 | [11 empty] | Check |  | Astronergy
Astronergy | CHSM6610P-255 | poly | 255 |  | +5/-0 | 5 | 0 |  |  | 30.68 | 8.33 | 38.4 | 8.69 | -0.469% | -0.344% |  |  | 15 | [11 empty] | Check |  | Astronergy
Astronergy | CHSM6610P-260 | poly | 260 |  | +5/-0 | 5 | 0 |  |  | 31.05 | 8.39 | 38.53 | 8.72 | -0.469% | -0.344% |  |  | 15 | [11 empty] | Check |  | Astronergy
Astronergy | CHSM6610P-265 | poly | 265 |  | +5/-0 | 5 | 0 |  |  | 31.43 | 8.46 | 38.72 | 8.75 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Astronergy
Astronergy | CHSM6610P-270 | poly | 270 |  | +5/-0 | 5 | 0 |  |  | 31.78 | 8.52 | 38.91 | 8.79 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Astronergy
Astronergy | CHSM6610P-275 | poly | 275 |  | +5/-0 | 5 | 0 |  |  | 32.09 | 8.57 | 39.13 | 8.96 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Astronergy
Astronergy | CHSM6610P-280 | poly | 280 |  | +5/-0 | 5 | 0 |  |  | 32.44 | 8.63 | 39.32 | 9.06 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Astronergy
Astronergy | CHSM6612P-265 | poly | 265 | 237 | +/-3 | 3 | -3 | 12.6634 | 13.6 | 35.54 | 7.48 | 44.24 | 8.27 | -0.451% | -0.332% | 0.087 | 43 | 15 | yes | MC4 | silver | white | 77.01 | 39.13 | 1.97 | 20.9264 | 51.7 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6612P-270 | poly | 270 | 241.6 | +/-3 | 3 | -3 | 12.9024 | 13.9 | 35.57 | 7.62 | 44.38 | 8.42 | -0.451% | -0.332% | 0.087 | 43 | 15 | yes | MC4 | silver | white | 77.01 | 39.13 | 1.97 | 20.9264 | 51.7 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6612P-275 | poly | 275 | 246.2 | +/-3 | 3 | -3 | 13.1413 | 14.1 | 35.6 | 7.76 | 44.51 | 8.56 | -0.451% | -0.332% | 0.087 | 43 | 15 | yes | MC4 | silver | white | 77.01 | 39.13 | 1.97 | 20.9264 | 51.7 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6612P-280 | poly | 280 | 250.8 | +/-3 | 3 | -3 | 13.3802 | 14.4 | 35.63 | 7.9 | 44.64 | 8.71 | -0.451% | -0.332% | 0.087 | 43 | 15 | yes | MC4 | silver | white | 77.01 | 39.13 | 1.97 | 20.9264 | 51.7 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6612P-285 | poly | 285 | 257.2 | +/-3 | 3 | -3 | 13.6192 | 14.7 | 35.66 | 8.04 | 44.77 | 8.86 | -0.451% | -0.332% | 0.087 | 43 | 15 | yes | MC4 | silver | white | 77.01 | 39.13 | 1.97 | 20.9264 | 51.7 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6612P-290 | poly | 290 | 261.8 | +/-3 | 3 | -3 | 13.8581 | 14.9 | 35.68 | 8.15 | 44.9 | 8.94 | -0.451% | -0.332% | 0.087 | 43 | 15 | yes | MC4 | silver | white | 77.01 | 39.13 | 1.97 | 20.9264 | 51.7 | 10 |  | Check |  | Astronergy
Astronergy | CHSM6612P-295 | poly | 295 | 266.4 | +5/-0 | 5 | -0 |  |  | 35.72 | 8.3 | 45.03 | 9.16 | -0.451% | -0.332% |  |  | 15 | [11 empty] | Check |  | Astronergy
Astronergy | CHSM6612P-300 | poly | 300 | 271.1 | +5/-0 | 5 | -0 |  |  | 35.74 | 8.4 | 45.16 | 9.27 | -0.408% | -0.311% |  |  | 15 | [11 empty] | Check | 2017-02-13 | Astronergy
Astronergy | CHSM6612P(/HV)-305 | poly | 305 | 275.5 | +5/-0 | 5 | -0 |  |  | 35.77 | 8.53 | 45.29 | 8.95 | -0.408% | -0.311% |  |  | 15 | [11 empty] | Check | 2017-02-13 | Astronergy
Astronergy | CHSM6612P(/HV)-310 | poly | 310 | 280.3 | +5/-0 | 5 | -0 |  |  | 35.8 | 8.68 | 45.42 | 8.99 | -0.408% | -0.311% |  |  | 15 | [11 empty] | Check | 2017-02-13 | Astronergy
Astronergy | CHSM6612P(/HV)-315 | poly | 315 | 286.2 | +5/-0 | 5 | -0 |  |  | 35.83 | 8.8 | 45.55 | 9.02 | -0.408% | -0.311% |  |  | 15 | [11 empty] | Check | 2017-02-13 | Astronergy
Astronergy | CHSM6612P(/HV)-320 | poly | 320 | 290.9 | +5/-0 | 5 | -0 |  |  | 35.86 | 8.92 | 45.68 | 9.06 | -0.408% | -0.311% |  |  | 15 | [11 empty] | Check | 2017-02-13 | Astronergy
Astronergy | CHSM6612P(/HV)-325 | poly | 325 | 295.5 | +5/-0 | 5 | -0 |  |  | 36.31 | 8.95 | 45.82 | 9.1 | -0.408% | -0.311% |  |  | 15 | [11 empty] | Check | 2017-02-13 | Astronergy
Astronergy | CHSM6612P-330 | poly | 330 | 300.2 | +5/-0 | 5 | -0 |  |  | 37.15 | 8.89 | 45.86 | 9.52 | -0.41% | -0.31% |  |  | 15 | [11 empty] | 1000 | 2017-12-18 | Astronergy
Astronergy | CHSM6612P-335 | poly | 335 | 304.9 | +5/-0 | 5 | -0 |  |  | 37.26 | 9 | 45.98 | 9.57 | -0.41% | -0.31% |  |  | 15 | [11 empty] | 1000 | 2017-12-18 | Astronergy
Astronergy | CHSM6612P-340 | poly | 340 | 309.6 | +5/-0 | 5 | -0 |  |  | 37.33 | 9.11 | 46.16 | 9.62 | -0.41% | -0.31% |  |  | 15 | [11 empty] | 1000 | 2017-12-18 | Astronergy
Astronergy | CHSM6612P-345 | poly | 345 | 314.3 | +5/-0 | 5 | -0 |  |  | 37.38 | 9.23 | 46.37 | 9.67 | -0.41% | -0.31% |  |  | 15 | [11 empty] | 1000 | 2017-12-18 | Astronergy
Astronergy | CHSM6612P/HV-330 | poly | 330 | 298 | +5/-0 | 5 | -0 |  |  | 37.15 | 8.89 | 45.86 | 9.52 | -0.41% | -0.31% |  |  | 15 | [11 empty] | 1500 | 2017-12-18 | Astronergy
Astronergy | CHSM6612P/HV-335 | poly | 335 | 302.7 | +5/-0 | 5 | -0 |  |  | 37.26 | 9 | 45.98 | 9.57 | -0.41% | -0.31% |  |  | 15 | [11 empty] | 1500 | 2017-12-18 | Astronergy
Astronergy | CHSM6612P/HV-340 | poly | 340 | 307.3 | +5/-0 | 5 | -0 |  |  | 37.33 | 9.11 | 46.16 | 9.62 | -0.41% | -0.31% |  |  | 15 | [11 empty] | 1500 | 2017-12-18 | Astronergy
Astronergy | CHSM6612P/HV-345 | poly | 345 | 312 | +5/-0 | 5 | -0 |  |  | 37.38 | 9.23 | 46.37 | 9.67 | -0.41% | -0.31% |  |  | 15 | [11 empty] | 1500 | 2017-12-18 | Astronergy
Astronergy | CHSM6612M-315 | mono | 315 | 284.3 | +5/-0 | 5 | -0 |  |  | 37.74 | 8.35 | 45.58 | 8.56 | -0.43% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Astronergy
Astronergy | CHSM6612M-320 | mono | 320 | 288.9 | +5/-0 | 5 | -0 |  |  | 38.11 | 8.41 | 45.69 | 8.59 | -0.43% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Astronergy
Astronergy | CHSM6612M-325 | mono | 325 | 293.6 | +5/-0 | 5 | -0 |  |  | 38.43 | 8.47 | 45.74 | 8.6 | -0.43% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Astronergy
Astronergy | CHSM6612M-330 | mono | 330 | 300 | +5/-0 | 5 | -0 |  |  | 38.73 | 8.52 | 45.89 | 8.62 | -0.43% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Astronergy
Astronergy | CHSM6612M-335 | mono | 335 | 304.7 | +5/-0 | 5 | -0 |  |  | 39.04 | 8.58 | 46.01 | 8.63 | -0.43% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Astronergy
Astronergy | CHSM6612M-350 | mono | 350 | 318.8 | 3/-3 | 3 | -3 |  | 18.1 | 38.58 | 9.08 | 47.01 | 9.53 | -0.376% | -0.282% |  |  | 15 |  |  |  |  | 76.93 | 38.98 | 1.57 |  | 48.06 |  |  | 1000 | 2018-11-12 | Astronergy
Astronergy | CHSM6612M-355 | mono | 355 | 323.5 | 3/-3 | 3 | -3 |  | 18.4 | 38.82 | 9.15 | 47.31 | 9.6 | -0.376% | -0.282% |  |  | 15 |  |  |  |  | 76.93 | 38.98 | 1.57 |  | 48.06 |  |  | 1000 | 2018-11-12 | Astronergy
Astronergy | CHSM6612M-360 | mono | 360 | 328.2 | 3/-3 | 3 | -3 |  | 18.6 | 39.14 | 9.2 | 47.62 | 9.66 | -0.38% | -0.282% |  |  | 15 |  |  |  |  | 76.93 | 38.98 | 1.57 |  | 48.06 |  |  | 1000 | 2018-11-12 | Astronergy | [11 empty] | 46.1
Astronergy | CHSM6612M-365 | mono | 365 | 332.6 | 3/-3 | 3 | -3 |  | 18.9 | 39.38 | 9.27 | 47.82 | 9.75 | -0.376% | -0.282% |  |  | 15 |  |  |  |  | 76.93 | 38.98 | 1.57 |  | 48.06 |  |  | 1000 | 2018-11-12 | Astronergy | [11 empty] | 46.1
Astronergy | CHSM6612M-370 | mono | 370 | 337.3 | 3/-3 | 3 | -3 |  | 19.1 | 39.66 | 9.34 | 48.13 | 9.82 | -0.376% | -0.282% |  |  | 15 |  |  |  |  | 76.93 | 38.98 | 1.57 |  | 48.06 |  |  | 1000 | 2018-11-12 | Astronergy | [11 empty] | 46.1
Astronergy | CHSM6612M/HV-350 | mono | 350 | 318.8 | 3/-3 | 3 | -3 |  | 18.1 | 38.58 | 9.08 | 47.01 | 9.53 | -0.376% | -0.282% |  |  | 15 |  |  |  |  | 76.93 | 38.98 | 1.57 |  | 48.06 |  |  | 1500 | 2018-11-12 | Astronergy
Astronergy | CHSM6612M/HV-355 | mono | 355 | 323.5 | 3/-3 | 3 | -3 |  | 18.4 | 38.82 | 9.15 | 47.31 | 9.6 | -0.376% | -0.282% |  |  | 15 |  |  |  |  | 76.93 | 38.98 | 1.57 |  | 48.06 |  |  | 1500 | 2018-11-12 | Astronergy
Astronergy | CHSM6612M/HV-360 | mono | 360 | 328.2 | 3/-3 | 3 | -3 |  | 18.6 | 39.14 | 9.2 | 47.62 | 9.66 | -0.376% | -0.282% |  |  | 15 |  |  |  |  | 76.93 | 38.98 | 1.57 |  | 48.06 |  |  | 1500 | 2018-11-12 | Astronergy
Astronergy | CHSM6612M/HV-365 | mono | 365 | 332.6 | 3/-3 | 3 | -3 |  | 18.9 | 39.38 | 9.27 | 47.82 | 9.75 | -0.376% | -0.282% |  |  | 15 |  |  |  |  | 76.93 | 38.98 | 1.57 |  | 48.06 |  |  | 1500 | 2018-11-12 | Astronergy
Astronergy | CHSM6612M/HV-370 | mono | 370 | 337.3 | 3/-3 | 3 | -3 |  | 19.1 | 39.66 | 9.34 | 48.13 | 9.82 | -0.376% | -0.282% |  |  | 15 |  |  |  |  | 76.93 | 38.98 | 1.57 |  | 48.06 |  |  | 1500 | 2018-11-12 | Astronergy
Astronergy | ASM6612P-305 | poly | 305 | 275.5 | +5/-0 | 5 | -0 |  |  | 35.77 | 8.53 | 45.29 | 8.95 | -0.408% | -0.311% |  |  | 15 | [11 empty] | Check | 2017-02-13 | Astronergy
Astronergy | ASM6612P-310 | poly | 310 | 280.3 | +5/-0 | 5 | -0 |  |  | 35.8 | 8.68 | 45.42 | 8.99 | -0.408% | -0.311% |  |  | 15 | [11 empty] | Check | 2017-02-13 | Astronergy
Astronergy | ASM6612P-315 | poly | 315 | 286.2 | +5/-0 | 5 | -0 |  |  | 35.83 | 8.8 | 45.55 | 9.02 | -0.408% | -0.311% |  |  | 15 | [11 empty] | Check | 2017-02-13 | Astronergy
Astronergy | ASM6612P-320 | poly | 320 | 290.9 | +5/-0 | 5 | -0 |  |  | 35.86 | 8.92 | 45.68 | 9.06 | -0.408% | -0.311% |  |  | 15 | [11 empty] | Check | 2017-02-13 | Astronergy
Astronergy | ASM66129-325 | Poly | 325 | 295.5 | +5/-0 | 5 | -0 |  |  | 36.31 | 8.95 | 45.82 | 9.1 | -0.408% | -0.311% |  |  | 15 | [11 empty] | Check | 2017-02-13 | Astronergy
AUO Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | AUO_Solar
AUO Solar | PM220P00_220 | poly | 220 | 197.3 | +/-2.5 | 2.5 | -2.5 | 12.2533 | 13.39 | 28.73 | 7.78 | 36.37 | 8.36 | -0.44% | -0.32% | 0.04 | 46 | 15 | DNR | tyco/MC4 | silver | white | 65.67 | 39.37 | 1.57 | 17.9544 | 44.1 | 5 |  | Check |  | AUO_Solar
AUO Solar | PM220P00_225 | poly | 225 | 201.9 | +/-2.5 | 2.5 | -2.5 | 12.5318 | 13.71 | 28.91 | 7.91 | 36.79 | 8.46 | -0.44% | -0.32% | 0.04 | 46 | 15 | DNR | tyco/MC4 | silver | white | 65.67 | 39.37 | 1.57 | 17.9544 | 44.1 | 5 |  | Check |  | AUO_Solar
AUO Solar | PM220P00_230 | poly | 230 | 206.5 | +/-2.5 | 2.5 | -2.5 | 12.8103 | 13.8 | 29.23 | 7.94 | 37.01 | 8.49 | -0.44% | -0.32% | 0.04 | 46 | 15 | DNR | tyco/MC4 | silver | white | 65.67 | 39.37 | 1.57 | 17.9544 | 44.1 | 5 |  | Check |  | AUO_Solar
AUO Solar | PM220P00_235 | poly | 235 | 211.1 | +/-2.5 | 2.5 | -2.5 | 13.0887 | 14.1 | 29.44 | 8.02 | 37.21 | 8.55 | -0.44% | -0.32% | 0.04 | 46 | 15 | DNR | tyco/MC4 | silver | white | 65.67 | 39.37 | 1.57 | 17.9544 | 44.1 | 5 |  | Check |  | AUO_Solar
AUO Solar | PM220P00_240 | poly | 240 | 215.7 | +/-2.5 | 2.5 | -2.5 | 13.3672 | 14.39 | 29.65 | 8.1 | 37.42 | 8.62 | -0.44% | -0.32% | 0.04 | 46 | 15 | DNR | tyco/MC4 | silver | white | 65.67 | 39.37 | 1.57 | 17.9544 | 44.1 | 5 |  | Check |  | AUO_Solar
AUO Solar | PM220P00_245 | poly | 245 | 220.3 | +/-2.5 | 2.5 | -2.5 | 13.6457 | 14.69 | 29.87 | 8.18 | 37.63 | 8.68 | -0.44% | -0.32% | 0.04 | 46 | 15 | DNR | tyco/MC4 | silver | white | 65.67 | 39.37 | 1.57 | 17.9544 | 44.1 | 5 |  | Check |  | AUO_Solar
AUO Solar | PM240P00_220 | poly | 220 | 197.3 | +3/-0 | 3 | 0 | 12.2533 | 13.39 | 28.73 | 7.78 | 36.37 | 8.36 | -0.44% | -0.32% | 0.04 | 46 | 15 | DNR | tyco/MC4 | silver | white | 65.67 | 39.37 | 1.57 | 17.9544 | 44.1 | 5 |  | Check |  | AUO_Solar
AUO Solar | PM240P00_225 | poly | 225 | 201.9 | +3/-0 | 3 | 0 | 12.5318 | 13.71 | 28.91 | 7.91 | 36.79 | 8.46 | -0.44% | -0.32% | 0.04 | 46 | 15 | DNR | tyco/MC4 | silver | white | 65.67 | 39.37 | 1.57 | 17.9544 | 44.1 | 5 |  | Check |  | AUO_Solar
AUO Solar | PM240P00_230 | poly | 230 | 206.5 | +3/-0 | 3 | 0 | 12.8103 | 13.8 | 29.23 | 7.94 | 37.01 | 8.49 | -0.44% | -0.32% | 0.04 | 46 | 15 | DNR | tyco/MC4 | silver | white | 65.67 | 39.37 | 1.57 | 17.9544 | 44.1 | 5 |  | Check |  | AUO_Solar
AUO Solar | PM240P00_235 | poly | 235 | 211.1 | +3/-0 | 3 | 0 | 13.0887 | 14.1 | 29.44 | 8.02 | 37.21 | 8.55 | -0.44% | -0.32% | 0.04 | 46 | 15 | DNR | tyco/MC4 | silver | white | 65.67 | 39.37 | 1.57 | 17.9544 | 44.1 | 5 |  | Check |  | AUO_Solar
AUO Solar | PM240P00_240 | poly | 240 | 215.7 | +3/-0 | 3 | 0 | 13.3672 | 14.39 | 29.65 | 8.1 | 37.42 | 8.62 | -0.44% | -0.32% | 0.04 | 46 | 15 | DNR | tyco/MC4 | silver | white | 65.67 | 39.37 | 1.57 | 17.9544 | 44.1 | 5 |  | Check |  | AUO_Solar
AUO Solar | PM240P00_245 | poly | 245 | 220.3 | +3/-0 | 3 | 0 | 13.6457 | 14.69 | 29.87 | 8.18 | 37.63 | 8.68 | -0.44% | -0.32% | 0.04 | 46 | 15 | DNR | tyco/MC4 | silver | white | 65.67 | 39.37 | 1.57 | 17.9544 | 44.1 | 5 |  | Check |  | AUO_Solar
AUO Solar | PM240P00_250 | poly | 250 |  | +3/-0 | 3 | 0 |  |  | 30.08 | 8.26 | 37.83 | 8.75 | -0.44% | -0.32% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | AUO_Solar
AUO Solar | PM250AC0_245 | mono | 245 | 219.5 | +3/-0 | 3 | 0 | 13.8936 | DNR | 30.78 | 8.09 | 37.8 | 8.6 | -0.48% | -0.36% | 0.03 | 46 | 15 | DNR | tyco | black | black | 65.01 | 39.06 | 2.44 | 17.634 | 48.4 | 10 |  | Check |  | AUO_Solar
AUO Solar | PM250AC0_250 | mono | 250 | 224.1 | +3/-0 | 3 | 0 | 14.1772 | DNR | 30.82 | 8.22 | 37.86 | 8.66 | -0.48% | -0.36% | 0.03 | 46 | 15 | DNR | tyco | black | black | 65.01 | 39.06 | 2.44 | 17.634 | 48.4 | 10 |  | Check |  | AUO_Solar
AUO Solar | PM250AC0_255 | mono | 255 | 228.8 | +3/-0 | 3 | 0 | 14.4607 | DNR | 30.86 | 8.34 | 37.92 | 8.72 | -0.48% | -0.36% | 0.03 | 46 | 15 | DNR | tyco | black | black | 65.01 | 39.06 | 2.44 | 17.634 | 48.4 | 10 |  | Check |  | AUO_Solar
AUO Solar | PM250AC0_260 | mono | 260 | 233.4 | +3/-0 | 3 | 0 | 14.7443 | DNR | 30.9 | 8.46 | 37.98 | 8.78 | -0.48% | -0.36% | 0.03 | 46 | 15 | DNR | tyco | black | black | 65.01 | 39.06 | 2.44 | 17.634 | 48.4 | 10 |  | Check |  | AUO_Solar
AUO Solar | PM250M00_245 | mono | 245 | 219.5 | +3/-0 | 3 | 0 | 13.8936 | 14.7 | 30.78 | 8.09 | 37.8 | 8.6 | -0.48% | -0.36% | 0.03 | 46 | 15 | DNR | tyco | black | white/black | 65.01 | 39.06 | 1.57 | 17.634 | 42.5 | 5 |  | Check |  | AUO_Solar
AUO Solar | PM250M00_250 | mono | 250 | 224.1 | +3/-0 | 3 | 0 | 14.1772 | 15.3 | 30.82 | 8.22 | 37.86 | 8.66 | -0.48% | -0.36% | 0.03 | 46 | 15 | DNR | tyco | black | white/black | 65.01 | 39.06 | 1.57 | 17.634 | 42.5 | 5 |  | Check |  | AUO_Solar
AUO Solar | PM250M00_255 | mono | 255 | 228.8 | +3/-0 | 3 | 0 | 14.4607 | 15.6 | 30.86 | 8.34 | 37.92 | 8.72 | -0.48% | -0.36% | 0.03 | 46 | 15 | DNR | tyco | black | white/black | 65.01 | 39.06 | 1.57 | 17.634 | 42.5 | 5 |  | Check |  | AUO_Solar
AUO Solar | PM250M00_260 | mono | 260 | 233.4 | +3/-0 | 3 | 0 | 14.7443 | 15.9 | 30.9 | 8.46 | 37.98 | 8.78 | -0.48% | -0.36% | 0.03 | 46 | 15 | DNR | tyco | black | white/black | 65.01 | 39.06 | 1.57 | 17.634 | 42.5 | 5 |  | Check |  | AUO_Solar
AUO Solar | PM060PW(B)0_250 | multi | 250 |  | +3/-0 | 3 | 0 |  |  | 30.6 | 8.17 | 37.4 | 8.69 | -0.39% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060PW(B)0_255 | multi | 255 |  | +3/-0 | 3 | 0 |  |  | 30.8 | 8.28 | 37.6 | 8.76 | -0.39% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060PW(B)0_260 | multi | 260 |  | +3/-0 | 3 | 0 |  |  | 31.2 | 8.34 | 37.7 | 8.83 | -0.39% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060PW0_265 | multi | 265 |  | +3/-0 | 3 | 0 |  |  | 31.6 | 8.36 | 37.9 | 8.89 | -0.39% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060MW(B)0_270 | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 31.8 | 8.5 | 38.5 | 9.01 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060MW(B)0_275 | mono | 275 |  | +3/-0 | 3 | 0 |  |  | 32.3 | 8.52 | 38.7 | 9.03 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060MW(B)0_280 | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 32.7 | 8.57 | 38.9 | 9.06 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060MW(B)2_275 | mono | 275 |  | +3/-0 | 3 | 0 |  |  | 31.05 | 8.86 | 37.9 | 9.43 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060MW(B)2_280 | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 31.21 | 9 | 38.6 | 9.58 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060MW(B)2_285 | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 31.42 | 9.07 | 38.9 | 9.65 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060MW(B)1_280 | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 32.7 | 8.57 | 38.9 | 9.06 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060MW(B)1_285 | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 31 | 9.2 | 40 | 9.8 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060MW(B)1_290 | mono | 290 |  | +3/-0 | 3 | 0 |  |  | 31.3 | 9.27 | 40.4 | 9.82 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060MW5_280 | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 30.7 | 9.13 | 39.6 | 9.78 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060MW5_283 | mono | 283 |  | +3/-0 | 3 | 0 |  |  | 30.9 | 9.17 | 39.8 | 9.79 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060MW5_285 | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 31 | 9.2 | 40 | 9.8 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060MW3_285 | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 32.2 | 8.84 | 39 | 9.4 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060MW3_290 | mono | 290 |  | +3/-0 | 3 | 0 |  |  | 32.3 | 8.99 | 39.7 | 9.57 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM060MW3_295 | mono | 295 |  | +3/-0 | 3 | 0 |  |  | 32.6 | 9.05 | 39.8 | 9.63 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | AUO_Solar
AUO Solar | PM072PW0_300 | multi | 300 |  | +3/-0 | 3 | 0 |  |  | 36.62 | 8.19 | 45.43 | 8.8 | -0.43% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-11-30 | AUO_Solar
AUO Solar | PM072PW0_305 | multi | 305 |  | +3/-0 | 3 | 0 |  |  | 36.97 | 8.25 | 45.72 | 8.89 | -0.43% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-11-30 | AUO_Solar
AUO Solar | PM072PW0_310 | multi | 310 |  | +3/-0 | 3 | 0 |  |  | 37.33 | 8.3 | 46.01 | 8.98 | -0.43% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-11-30 | AUO_Solar
AUO Solar | PM072PW0_315 | multi | 315 |  | +3/-0 | 3 | 0 |  |  | 37.6 | 8.38 | 46.23 | 9.09 | -0.43% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-11-30 | AUO_Solar
AUO Solar | PM096B00_325 | mono | 325 |  | +3/-0 | 3 | 0 |  |  | 54.7 | 5.94 | 64.9 | 6.39 | -0.33% | -0.26% |  |  | 20 | [11 empty] | Check | 2015-11-30 | AUO_Solar
AUO Solar | PM096B00_327 | mono | 327 |  | +3/-0 | 3 | 0 |  |  | 54.7 | 5.98 | 64.9 | 6.46 | -0.33% | -0.26% |  |  | 20 | [11 empty] | Check | 2015-11-30 | AUO_Solar
AUO Solar | PM096B00_330 | mono | 330 |  | +3/-0 | 3 | 0 |  |  | 54.7 | 6.04 | 64.9 | 6.52 | -0.33% | -0.26% |  |  | 20 | [11 empty] | Check | 2015-11-30 | AUO_Solar
AUO Solar | PM096B00_333 | mono | 333 |  | +3/-0 | 3 | 0 |  |  | 54.7 | 6.09 | 64.9 | 6.58 | -0.33% | -0.26% |  |  | 20 | [11 empty] | Check | 2015-11-30 | AUO_Solar
AUO Solar | PM096B00_335 | mono | 335 |  | +3/-0 | 3 | 0 |  |  | 54.7 | 6.13 | 64.9 | 6.62 | -0.33% | -0.26% |  |  | 20 | [11 empty] | Check | 2015-11-30 | AUO_Solar
Auxin Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Auxin_Solar
Auxin Solar | AXN-M5T175 | mono | 175 | 153.7 | +/-3 | 3 | -3 | 12.5038 | 13.46 | 36.72 | 4.77 | 43.99 | 5.17 | -0.4% | -0.33% | 0.05 | 48 | 12 | yes | tyco | silver | white | 62.05 | 32.48 | 1.97 | 13.9957 | 35.3 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-M5T180 | mono | 180 | 158.3 | +/-3 | 3 | -3 | 12.8611 | 13.8435 | 36.72 | 4.9 | 44.06 | 5.31 | -0.4% | -0.33% | 0.05 | 48 | 12 | yes | tyco | silver | white | 62.05 | 32.48 | 1.97 | 13.9957 | 35.3 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T175 | poly | 175 | 151 | +/-3 | 3 | -3 | 12.4175 | 13.37 | 24.1 | 7.26 | 28.85 | 7.95 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 51.81 | 39.17 | 1.97 | 14.093 | 35.3 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T180 | poly | 180 | 155.4 | +/-3 | 3 | -3 | 12.7723 | 13.7479 | 24.29 | 7.41 | 29.14 | 8.1 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 51.81 | 39.17 | 1.97 | 14.093 | 35.3 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T190 | poly | 190 | 164.2 | +/-3 | 3 | -3 | 11.9626 | 12.8764 | 26.78 | 7.09 | 32.4 | 7.72 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 58.39 | 39.17 | 1.97 | 15.8829 | 40.8 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T195 | poly | 195 | 168.6 | +/-3 | 3 | -3 | 12.2774 | 13.2152 | 26.95 | 7.24 | 32.4 | 7.83 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 58.39 | 39.17 | 1.97 | 15.8829 | 40.8 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T200 | poly | 200 | 173.1 | +/-3 | 3 | -3 | 12.5922 | 13.5541 | 27.22 | 7.35 | 32.62 | 8.04 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 58.39 | 39.17 | 1.97 | 15.8829 | 40.8 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T205 | poly | 205 | 178.6 | +/-3 | 3 | -3 | 12.907 | 13.8929 | 27.32 | 7.5 | 32.78 | 8.1 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 58.39 | 39.17 | 1.97 | 15.8829 | 40.8 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T210 | poly | 210 | 182.5 | +/-3 | 3 | -3 | 11.9139 | 12.824 | 29.64 | 7.09 | 35.94 | 7.6 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 64.8 | 39.17 | 1.97 | 17.6265 | 44.1 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T215 | poly | 215 | 185.6 | +/-3 | 3 | -3 | 12.1975 | 13.1293 | 29.94 | 7.18 | 36 | 7.83 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 64.8 | 39.17 | 1.97 | 17.6265 | 44.1 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T220 | poly | 220 | 190.1 | +/-3 | 3 | -3 | 12.4812 | 13.4347 | 30.12 | 7.3 | 36.06 | 7.95 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 64.8 | 39.17 | 1.97 | 17.6265 | 44.1 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T225 | poly | 225 | 194.5 | +/-3 | 3 | -3 | 12.7649 | 13.74 | 30.36 | 7.41 | 36.42 | 8.1 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 64.8 | 39.17 | 1.97 | 17.6265 | 44.1 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T230 | poly | 230 | 199 | +/-3 | 3 | -3 | 13.0485 | 14.0453 | 30.48 | 7.55 | 36.6 | 8.17 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 64.8 | 39.17 | 1.97 | 17.6265 | 44.1 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T235 | poly | 235 | 203.4 | +/-3 | 3 | -3 | 13.3322 | 14.3507 | 30.6 | 7.68 | 36.72 | 8.23 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 64.8 | 39.17 | 1.97 | 17.6265 | 44.1 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T240 | poly | 240 | 207.2 | +/-3 | 3 | -3 | 12.4304 | 13.3799 | 33.13 | 7.24 | 39.67 | 7.95 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 70.98 | 39.17 | 1.97 | 19.3075 | 48.5 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T245 | poly | 245 | 211.6 | +/-3 | 3 | -3 | 12.6893 | 13.6587 | 33.26 | 7.37 | 39.86 | 8.04 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 70.98 | 39.17 | 1.97 | 19.3075 | 48.5 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T250 | poly | 250 | 216.1 | +/-3 | 3 | -3 | 12.9483 | 13.9374 | 33.4 | 7.49 | 40.06 | 8.1 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 70.98 | 39.17 | 1.97 | 19.3075 | 48.5 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T255 | poly | 255 | 217.3 | +/-3 | 3 | -3 | 12.1432 | 13.0708 | 35.71 | 7.14 | 43.2 | 7.72 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 77.2 | 39.17 | 1.97 | 20.9995 | 52.9 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T260 | poly | 260 | 221.7 | +/-3 | 3 | -3 | 12.3813 | 13.3271 | 35.93 | 7.24 | 43.2 | 7.83 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 77.2 | 39.17 | 1.97 | 20.9995 | 52.9 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T265 | poly | 265 | 226.1 | +/-3 | 3 | -3 | 12.6194 | 13.5834 | 36.14 | 7.33 | 43.27 | 7.95 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 77.2 | 39.17 | 1.97 | 20.9995 | 52.9 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T270 | poly | 270 | 230.6 | +/-3 | 3 | -3 | 12.8575 | 13.8397 | 36.43 | 7.41 | 43.7 | 8.1 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 77.2 | 39.17 | 1.97 | 20.9995 | 52.9 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T275 | poly | 275 | 235 | +/-3 | 3 | -3 | 13.0956 | 14.096 | 36.58 | 7.52 | 43.92 | 8.17 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 77.2 | 39.17 | 1.97 | 20.9995 | 52.9 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T280 | poly | 280 | 239.4 | +/-3 | 3 | -3 | 13.3337 | 14.3522 | 36.72 | 7.63 | 44.06 | 8.23 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 77.2 | 39.17 | 1.97 | 20.9995 | 52.9 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-P6T285 | poly | 285 | 243.9 | +/-3 | 3 | -3 | 13.5718 | 14.6085 | 36.79 | 7.75 | 44.21 | 8.32 | -0.45% | -0.15% | 0.06 | 44.9 | 15 | yes | tyco | silver | white | 77.2 | 39.17 | 1.97 | 20.9995 | 52.9 | 5 |  | Check |  | Auxin_Solar
Auxin Solar | AXN-M6T250 | mono | 250 |  | +/-3 | 3 | -3 |  |  | 33.26 | 7.52 | 40.92 | 8.14 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Auxin_Solar
Auxin Solar | AXN-M6T255 | mono | 255 |  | +/-3 | 3 | -3 |  |  | 33.79 | 7.55 | 41.12 | 8.21 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Auxin_Solar
Auxin Solar | AXN-M6T260 | mono | 260 |  | +/-3 | 3 | -3 |  |  | 34.32 | 7.58 | 41.32 | 8.29 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Auxin_Solar
Auxin Solar | AXN-M6T265 | mono | 265 |  | +/-3 | 3 | -3 |  |  | 36 | 7.36 | 44.42 | 8.11 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Auxin_Solar
Auxin Solar | AXN-M6T270 | mono | 270 |  | +/-3 | 3 | -3 |  |  | 36.21 | 7.44 | 44.64 | 8.14 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Auxin_Solar
Auxin Solar | AXN-M6T275 | mono | 275 |  | +/-3 | 3 | -3 |  |  | 36.58 | 7.52 | 44.78 | 8.18 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Auxin_Solar
Auxin Solar | AXN-M6T280 | mono | 280 |  | +/-3 | 3 | -3 |  |  | 36.86 | 7.6 | 44.86 | 8.21 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Auxin_Solar
Auxin Solar | AXN-M6T285 | mono | 285 |  | +/-3 | 3 | -3 |  |  | 36.72 | 7.77 | 44.21 | 8.39 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Auxin_Solar
Auxin Solar | AXN-M6T290 | mono | 290 |  | +/-3 | 3 | -3 |  |  | 36.72 | 7.9 | 44.43 | 8.48 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Auxin_Solar
Auxin Solar | AXN-M6T295 | mono | 295 |  | +/-3 | 3 | -3 |  |  | 36.72 | 8.04 | 44.57 | 8.52 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Auxin_Solar
Auxin Solar | AXN-M6T300 | mono | 300 |  | +/-3 | 3 | -3 |  |  | 36.72 | 8.17 | 44.71 | 8.58 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Auxin_Solar
Auxin Solar | AXN-M6T305 | mono | 305 |  | +/-3 | 3 | -3 |  |  | 36.72 | 8.31 | 44.86 | 8.72 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Auxin_Solar
Auxin Solar | AXN-M6T310 | mono | 310 |  | +/-3 | 3 | -3 |  |  | 36.72 | 8.45 | 45 | 8.79 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Auxin_Solar
Auxin Solar | AXN-M6T315 | mono | 315 |  | +/-3 | 3 | -3 |  |  | 36.72 | 8.58 | 45.22 | 8.89 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Auxin_Solar
Auxin Solar | AXN-6P610T240 | Poly | 240 |  | +/-3 | 3 | -3 |  |  | 30.54 | 7.9 | 36.72 | 8.42 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 39.8 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P610T245 | Poly | 245 |  | +/-3 | 3 | -3 |  |  | 30.84 | 8 | 36.9 | 8.46 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 39.8 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P610T250 | Poly | 250 |  | +/-3 | 3 | -3 |  |  | 31.2 | 8.03 | 37.2 | 8.52 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 39.8 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P610T255 | Poly | 255 |  | +/-3 | 3 | -3 |  |  | 31.56 | 8.08 | 37.5 | 8.56 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 39.8 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P610T260 | Poly | 260 |  | +/-3 | 3 | -3 |  |  | 31.86 | 8.19 | 37.86 | 8.64 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 39.8 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P610T265 | Poly | 265 |  | +/-3 | 3 | -3 |  |  | 32.16 | 8.26 | 38.04 | 8.68 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 39.8 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P610T270 | Poly | 270 |  | +/-3 | 3 | -3 |  |  | 32.16 | 8.44 | 38.58 | 8.97 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 39.8 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P610T275 | Poly | 275 |  | +/-3 | 3 | -3 |  |  | 32.4 | 8.49 | 38.91 | 9.1 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 39.8 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P610T280 | Poly | 280 |  | +/-3 | 3 | -3 |  |  | 32.64 | 8.58 | 39.24 | 9.24 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 39.8 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P610T285 | Poly | 285 |  | +/-3 | 3 | -3 |  |  | 32.89 | 8.67 | 39.57 | 9.38 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 39.8 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P610T290 | Poly | 290 |  | +/-3 | 3 | -3 |  |  | 33.14 | 8.75 | 39.91 | 9.52 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 39.8 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P612T285 | Poly | 285 |  | +/-3 | 3 | -3 |  |  | 36.79 | 7.75 | 44.21 | 8.32 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 47.2 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P612T290 | Poly | 290 |  | +/-3 | 3 | -3 |  |  | 36.79 | 7.96 | 44.28 | 8.46 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 47.2 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P612T295 | Poly | 295 |  | +/-3 | 3 | -3 |  |  | 37.01 | 8 | 44.42 | 8.49 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 47.2 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P612T300 | Poly | 300 |  | +/-3 | 3 | -3 |  |  | 37.66 | 8.05 | 44.86 | 8.54 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 47.2 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P612T305 | Poly | 305 |  | +/-3 | 3 | -3 |  |  | 37.87 | 8.08 | 45 | 8.56 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 47.2 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P612T310 | Poly | 310 |  | +/-3 | 3 | -3 |  |  | 38.02 | 8.16 | 45.22 | 8.62 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 47.2 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P612T315 | Poly | 315 |  | +/-3 | 3 | -3 |  |  | 36.29 | 8.68 | 45.23 | 9.31 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 47.2 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P612T320 | Poly | 320 |  | +/-3 | 3 | -3 |  |  | 36.59 | 8.75 | 45.51 | 9.38 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 47.2 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P612T325 | Poly | 325 |  | +/-3 | 3 | -3 |  |  | 36.88 | 8.81 | 45.79 | 9.44 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 47.2 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P612T330 | Poly | 330 |  | +/-3 | 3 | -3 |  |  | 37.22 | 8.87 | 46.08 | 9.5 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 47.2 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6P612T335 | Poly | 335 |  | +/-3 | 3 | -3 |  |  | 37.55 | 8.94 | 46.37 | 9.56 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 47.2 |  |  | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M610T265 | mono | 265 |  | +/-3 | 3 | -3 |  |  | 30.83 | 8.6 | 38.12 | 8.93 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M610T270 | mono | 270 |  | +/-3 | 3 | -3 |  |  | 31.06 | 8.69 | 38.45 | 9.07 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M610T275 | mono | 275 |  | +/-3 | 3 | -3 |  |  | 31.29 | 8.79 | 38.77 | 9.2 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M610T280 | mono | 280 |  | +/-3 | 3 | -3 |  |  | 31.53 | 8.88 | 39.1 | 9.34 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M610T285 | mono | 285 |  | +/-3 | 3 | -3 |  |  | 31.76 | 8.97 | 39.43 | 9.48 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M610T290 | mono | 290 |  | +/-3 | 3 | -3 |  |  | 32 | 9.06 | 39.77 | 9.62 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M610T295 | mono | 295 |  | +/-3 | 3 | -3 |  |  | 32.24 | 9.15 | 40.11 | 9.77 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M610T300 | mono | 300 |  | +/-3 | 3 | -3 |  |  | 32.48 | 9.24 | 40.45 | 9.91 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M610T305 | mono | 305 |  | +/-3 | 3 | -3 |  |  | 32.73 | 9.32 | 40.79 | 10.06 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M612T330 | mono | 330 |  | +/-3 | 3 | -3 |  |  | 37.71 | 8.75 | 46.76 | 9.57 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M612T335 | mono | 335 |  | +/-3 | 3 | -3 |  |  | 37.98 | 8.82 | 47.04 | 9.61 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M612T340 | mono | 340 |  | +/-3 | 3 | -3 |  |  | 38.32 | 8.96 | 47.18 | 9.64 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M612T345 | mono | 345 |  | +/-3 | 3 | -3 |  |  | 38.4 | 8.98 | 47.28 | 9.72 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M612T350 | mono | 350 |  | +/-3 | 3 | -3 |  |  | 38.48 | 9.1 | 47.37 | 9.81 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M612T355 | mono | 355 |  | +/-3 | 3 | -3 |  |  | 38.55 | 9.21 | 47.47 | 9.9 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M612T360 | mono | 360 |  | +/-3 | 3 | -3 |  |  | 38.63 | 9.32 | 47.56 | 9.99 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Auxin Solar | AXN-6M612T365 | mono | 365 |  | +/-3 | 3 | -3 |  |  | 38.71 | 9.43 | 47.66 | 10.08 | -0.38% | -0.28% |  |  | 15 | [11 empty] | 1000 | 2017-11-22 | Auxin_Solar
Bosch Solar Energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Bosch_Solar_Energy
Bosch Solar Energy | c-Si M 60-225-16 | mono | 225 | 201 | +/-2.5 | 2.5 | -2.5 | 12.7453 | 13.7195 | 29 | 7.76 | 35.96 | 8.29 | -0.478% | -0.374% | 0.071 | 46.2 | 17 | yes | tyco | silver | white | 64.57 | 39.37 | 1.65 | 17.6536 | 51.81 | 10 |  | Check |  | Bosch_Solar_Energy
Bosch Solar Energy | c-Si M 60-230-16 | mono | 230 | 205.6 | +/-2.5 | 2.5 | -2.5 | 13.0285 | 14.0244 | 29.2 | 7.88 | 36.22 | 8.38 | -0.478% | -0.374% | 0.071 | 46.2 | 17 | yes | tyco | silver | white | 64.57 | 39.37 | 1.65 | 17.6536 | 51.81 | 10 |  | Check |  | Bosch_Solar_Energy
Bosch Solar Energy | c-Si M 60-235-16 | mono | 235 | 210.2 | +/-2.5 | 2.5 | -2.5 | 13.3117 | 14.3293 | 29.41 | 7.99 | 36.48 | 8.47 | -0.478% | -0.374% | 0.071 | 46.2 | 17 | yes | tyco | silver | white | 64.57 | 39.37 | 1.65 | 17.6536 | 51.81 | 10 |  | Check |  | Bosch_Solar_Energy
Bosch Solar Energy | c-Si M 60-240-16 | mono | 240 | 214.8 | +/-2.5 | 2.5 | -2.5 | 13.5949 | 14.6341 | 29.62 | 8.11 | 36.75 | 8.56 | -0.478% | -0.374% | 0.071 | 46.2 | 17 | yes | tyco | silver | white | 64.57 | 39.37 | 1.65 | 17.6536 | 51.81 | 10 |  | Check |  | Bosch_Solar_Energy
Bosch Solar Energy | M220 3BB |  | 220 |  | +4.99/-0 | 4.99 | 0 |  |  | 29.4 | 7.55 | 36 | 8.1 | -0.5% | -0.36% | [10 empty] | 0 |  |  |  | Check |  | Bosch_Solar_Energy
Bosch Solar Energy | M225 3BB |  | 225 |  | +4.99/-0 | 4.99 | 0 |  |  | 29.6 | 7.65 | 36.2 | 8.2 | -0.5% | -0.36% | [10 empty] | 0 |  |  |  | Check |  | Bosch_Solar_Energy
Bosch Solar Energy | M230 3BB |  | 230 |  | +4.99/-0 | 4.99 | 0 |  |  | 29.8 | 7.75 | 36.4 | 8.3 | -0.5% | -0.36% | [10 empty] | 0 |  |  |  | Check |  | Bosch_Solar_Energy
Bosch Solar Energy | M235 3BB |  | 235 |  | +4.99/-0 | 4.99 | 0 |  |  | 30 | 7.85 | 36.6 | 8.4 | -0.5% | -0.36% | [10 empty] | 0 |  |  |  | Check |  | Bosch_Solar_Energy
Bosch Solar Energy | M240 3BB |  | 240 |  | +4.99/-0 | 4.99 | 0 |  |  | 30.2 | 7.95 | 36.8 | 8.5 | -0.5% | -0.36% | [10 empty] | 0 |  |  |  | Check |  | Bosch_Solar_Energy
Boviet Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Bosch_Solar_Energy
Boviet Solar | BVM6610P-250 | poly | 250 | 225.6 | +5/-0 | 5 | 0 |  |  | 30.2 | 8.28 | 37.5 | 8.79 | -0.43% | -0.33% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 40.79 |  |  | 1000 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6610P-255 | poly | 255 | 231 | +5/-0 | 5 | 0 |  |  | 30.4 | 8.39 | 37.7 | 8.88 | -0.43% | -0.33% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 40.79 |  |  | 1000 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6610P-260 | poly | 260 | 235.7 | +5/-0 | 5 | 0 |  |  | 30.6 | 8.5 | 37.9 | 8.98 | -0.43% | -0.33% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 40.79 |  |  | 1000 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6610P-265 | poly | 265 | 240.3 | +5/-0 | 5 | 0 |  |  | 30.8 | 8.61 | 38.1 | 9.07 | -0.43% | -0.33% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 40.79 |  |  | 1000 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6610P-270 | poly | 270 | 247.8 | +5/-0 | 5 | 0 |  |  | 31 | 8.71 | 38.3 | 9.16 | -0.43% | -0.33% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 40.79 |  |  | 1000 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6612P-310 | poly | 310 | 280 | +5/-0 | 5 | 0 |  |  | 36.6 | 8.47 | 45.1 | 9.02 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 58.42 |  |  | 1500 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6612P-315 | poly | 315 | 285.2 | +5/-0 | 5 | 0 |  |  | 36.8 | 8.56 | 45.3 | 9.09 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 58.42 |  |  | 1500 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6612P-320 | poly | 320 | 293.7 | +5/-0 | 5 | 0 |  |  | 37 | 8.65 | 45.5 | 9.17 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 58.42 |  |  | 1500 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6612P-325 | poly | 325 | 298.4 | +5/-0 | 5 | 0 |  |  | 37.2 | 8.74 | 45.7 | 9.25 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 58.42 |  |  | 1500 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6612P-330 | poly | 330 | 303.1 | +5/-0 | 5 | 0 |  |  | 37.4 | 8.83 | 45.8 | 9.33 | -0.41% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 58.42 |  |  | 1500 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6610M-265 | mono | 265 | 242.7 | +5/-0 | 5 | 0 |  |  | 30.9 | 8.58 | 38.1 | 9.09 | -0.4% | -0.32% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 40.79 |  |  | 1500 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6610M-270 | mono | 270 | 247.4 | +5/-0 | 5 | 0 |  |  | 31.1 | 8.69 | 38.2 | 9.2 | -0.4% | -0.32% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 40.79 |  |  | 1500 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6610M-275 | mono | 275 | 252.3 | +5/-0 | 5 | 0 |  |  | 31.4 | 8.76 | 38.4 | 9.28 | -0.4% | -0.32% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 40.79 |  |  | 1500 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6610M-280 | mono | 280 | 257 | +5/-0 | 5 | 0 |  |  | 31.7 | 8.84 | 38.7 | 9.39 | -0.4% | -0.32% |  |  | 15 |  |  |  |  | 64.57 | 39.06 | 1.57 |  | 40.79 |  |  | 1500 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6612M-340 | mono | 340 | 312 | +5/-0 | 5 | 0 |  |  | 38.1 | 8.93 | 46.6 | 9.45 | -0.4% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 58.42 |  |  | 1500 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6612M-345 | mono | 345 | 316.7 | +5/-0 | 5 | 0 |  |  | 38.4 | 8.99 | 47 | 9.5 | -0.4% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 58.42 |  |  | 1500 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6612M-350 | mono | 350 | 321.4 | +5/-0 | 5 | 0 |  |  | 38.5 | 9.1 | 47.2 | 9.59 | -0.4% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 58.42 |  |  | 1500 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6612M-355 | mono | 355 | 326.1 | +5/-0 | 5 | 0 |  |  | 38.6 | 9.2 | 47.4 | 9.67 | -0.4% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 58.42 |  |  | 1500 | 2018-06-12 | Boviet_Solar
Boviet Solar | BVM6612M-360 | mono | 360 | 330.8 | +5/-0 | 5 | 0 |  |  | 38.8 | 9.29 | 47.5 | 9.83 | -0.4% | -0.31% |  |  | 15 |  |  |  |  | 77.01 | 39.06 | 1.57 |  | 58.42 |  |  | 1500 | 2018-06-12 | Boviet_Solar
BP Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | BP_Solar
BP Solar | BP 170B | poly | 170 |  | +5/-5 | 5 | -5 | 12.5507 | 13.5 | 35.4 | 4.8 | 43.6 | 5.27 | -0.47% | -0.367% |  |  | 15 |  | MC |  |  | 62.7165 | 31.1 | 1.9685 | 13.545 | 33.88 | 5 |  | Check |  | BP_Solar
BP Solar | BP 170I | poly | 170 |  | +5/-5 | 5 | -5 | 12.3933 | 13.1 | 35.4 | 4.8 | 43.6 | 5.27 | -0.47% | -0.367% |  |  | 15 |  | MC |  |  | 62.4803 | 32.6142 | 1.9685 | 14.151 | 33.88 | 5 |  | Check |  | BP_Solar
BP Solar | BP 175B | poly | 175 |  | +5/-5 | 5 | -5 | 12.9199 | 13.9 | 36.1 | 4.9 | 43.6 | 5.3 | -0.47% | -0.367% |  |  | 15 |  | MC |  |  | 62.7165 | 31.1 | 1.9685 | 13.545 | 33.88 | 5 |  | Check |  | BP_Solar
BP Solar | BP 175I | poly | 175 |  | +5/-5 | 5 | -5 | 12.7578 | 13.9 | 36.1 | 4.9 | 43.6 | 5.3 | -0.47% | -0.367% |  |  | 15 |  | MC |  |  | 62.4803 | 32.6142 | 1.97 | 14.151 | 33.88 | 5 |  | Check |  | BP_Solar
BP Solar | BP 180 B, I | poly | 180 |  | +5/-5 | 5 | -5 | 13.7824 | 14.4 | 36.1 | 4.9 | 43.6 | 5.4 | -0.47% | -0.367% |  |  | 15 |  | MC |  |  | 62.4803 | 31.1 | 1.97 | 13.494 | 33.88 | 5 |  | Check |  | BP_Solar
BP Solar | BP 3115J | poly | 115 |  | +3/-3 | 3 | -3 | 10.4976 | 11.3 | 17.1 | 6.7 | 21.8 | 7.5 | -0.47% | -0.367% |  |  | 15 |  | J-Box |  |  | 59.4488 | 26.5354 | 1.9685 | 10.9549 | 26.64 | 5 |  | Check |  | BP_Solar
BP Solar | BP 3125J | poly | 125 |  | +3/-3 | 3 | -3 | 11.4105 | 12.3 | 17.4 | 7.2 | 22 | 8.1 | -0.47% | -0.3636% |  |  | 15 |  | J-Box |  |  | 59.4488 | 26.5354 | 1.9685 | 10.9549 | 26.64 | 5 |  | Check |  | BP_Solar
BP Solar | BP 3215B | poly | 215 | 193.6 | +5/-3 | 5 | -3 | 11.9821 | 12.9 | 29.1 | 7.4 | 36.5 | 8.1 | -0.45% | -0.36% | 0.105 | 47 | 20 | yes | MC4 | black | black | 65.63 | 39.37 | 1.97 | 17.9434 | 42.77 | 5 |  | Check |  | BP_Solar
BP Solar | BP 3220T | poly | 220 | 196.6 | +5/-3 | 5 | -3 | 12.2608 | 13.2 | 28.9 | 7.6 | 36.6 | 8.2 | -0.45% | -0.36% | 0.105 | 47 | 20 | yes | MC4 | silver | white | 65.63 | 39.37 | 1.97 | 17.9434 | 42.77 | 5 |  | Check |  | BP_Solar
BP Solar | BP 3225T |  | 225 |  | +5/-3 | 5 | -3 |  |  | 29.1 | 7.7 | 36.6 | 8.3 | -0.5% | -0.36% | [10 empty] | 0 |  |  |  | Check |  | BP_Solar
BP Solar | BP 3225T | poly | 225 | 201 | +5/-3 | 5 | -3 | 12.5394 | 13.5 | 29.1 | 7.7 | 36.6 | 8.3 | -0.45% | -0.36% | 0.105 | 47 | 20 | yes | MC4 | silver | white | 65.63 | 39.37 | 1.97 | 17.9434 | 42.77 | 5 |  | Check |  | BP_Solar
BP Solar | BP 3230N | poly | 230 |  | +3/-3 | 3 | -3 | 12.8181 | 13.8 | 29.2 | 7.9 | 36.4 | 8.7 | -0.47% | -0.3659% |  |  | 20 |  | MC |  |  | 65.6299 | 39.3701 | 1.97 | 17.9434 | 42.68 | 5 |  | Check |  | BP_Solar
BP Solar | BP 3230T |  | 230 |  | +5/-3 | 5 | -3 |  |  | 29.1 | 7.9 | 36.7 | 8.4 | -0.5% | -0.36% | [10 empty] | 0 |  |  |  | Check |  | BP_Solar
BP Solar | BP 3230T | poly | 230 | 205.8 | +5/-3 | 5 | -3 | 12.8181 | 13.8 | 29.1 | 7.9 | 36.7 | 8.4 | -0.45% | -0.36% | 0.105 | 47 | 20 | yes | MC4 | silver | white | 65.63 | 39.37 | 1.97 | 17.9434 | 42.77 | 5 |  | Check |  | BP_Solar
BP Solar | BP 3235T | poly | 235 | 210.4 | +5/-3 | 5 | -3 | 13.0967 | 14.1 | 29.8 | 7.89 | 37.2 | 8.48 | -0.45% | -0.36% | 0.105 | 47 | 20 | yes | MC4 | silver | white | 65.63 | 39.37 | 1.97 | 17.9434 | 42.77 | 5 |  | Check |  | BP_Solar
BP Solar | BP 3270T |  | 270 |  | +5/-5 | 5 | -5 |  |  | 35.5 | 7.61 | 44.2 | 8.33 | -0.45% | -0.36% | [10 empty] | 0 |  |  |  | Check |  | BP_Solar
BP Solar | BP 4175B | mono | 175 | 156.2 | +5/-3 | 5 | -3 | 12.9646 | 14 | 35.4 | 4.94 | 43.6 | 5.45 | -0.45% | -0.36% | 0.105 | 47 | 20 | yes | MC4 | black | black | 62.5 | 31.1 | 1.97 | 13.4983 | 33.95 | 5 |  | Check |  | BP_Solar
BP Solar | BP 4175I | mono | 175 |  | +5/-5 | 5 | -5 | 12.7578 | 13.9 | 35.4 | 4.94 | 43.6 | 5.45 | -0.47% | -0.367% |  |  | 15 |  | MC |  |  | 62.4803 | 32.6142 | 1.9685 | 14.151 | 33.88 | 5 |  | Check |  | BP_Solar
BP Solar | BP 4175T | mono | 175 | 158.1 | +5/-3 | 5 | -3 | 12.9646 | 14 | 35.4 | 4.94 | 43.6 | 5.45 | -0.45% | -0.36% | 0.105 | 47 | 20 | yes | MC4 | silver | white | 62.5 | 31.1 | 1.97 | 13.4983 | 33.95 | 5 |  | Check |  | BP_Solar
BP Solar | BP 4180B | mono | 180 |  | +5/-5 | 5 | -5 | 13.289 | 14.3 | 35.5 | 5.1 | 43.6 | 5.6 | -0.47% | -0.367% |  |  | 15 |  | MC |  |  | 62.7165 | 31.1 | 1.9685 | 13.545 | 33.88 | 5 |  | Check |  | BP_Solar
BP Solar | BP 4180I | mono | 180 |  | +5/-5 | 5 | -5 | 13.1223 | 14.3 | 35.5 | 5.1 | 43.6 | 5.6 | -0.47% | -0.367% |  |  | 15 |  | MC |  |  | 62.4803 | 32.6142 | 1.9685 | 14.151 | 33.88 | 5 |  | Check |  | BP_Solar
BP Solar | BP 4180T | mono | 180 | 162.7 | +5/-3 | 5 | -3 | 13.335 | 14.4 | 35.8 | 5.03 | 43.6 | 5.58 | -0.45% | -0.36% | 0.105 | 47 | 20 | yes | MC4 | silver | white | 62.5 | 31.1 | 1.97 | 13.4983 | 33.95 | 5 |  | Check |  | BP_Solar
BP Solar | BP 4185T | mono | 185 | 167.3 | +5/-0 | 5 | -0 | 13.7055 | 14.8 | 36.2 | 5.11 | 44.7 | 5.58 | -0.45% | -0.36% | 0.105 | 47 | 20 | yes | MC4 | silver | white | 62.5 | 31.1 | 1.97 | 13.4983 | 33.95 | 5 |  | Check |  | BP_Solar
BP Solar | BP 4190T | mono | 190 | 172 | +5/-0 | 5 | -0 | 14.0759 | 15.2 | 37.1 | 5.12 | 45.3 | 5.56 | -0.45% | -0.36% | 0.105 | 47 | 20 | yes | MC4 | silver | white | 62.5 | 31.1 | 1.97 | 13.4983 | 33.95 | 5 |  | Check |  | BP_Solar
BP Solar | BP3195B,W | poly | 200 |  | +5/-5 | 5 | -5 | 13.2137 | 14.2 | 24.5 | 8.16 | 30.8 | 8.7 | -0.47% | -0.3604% |  |  | 15 |  | MC |  |  | 66.1417 | 32.9528 | 1.97 | 15.1358 | 37.84 | 5 |  | Check |  | BP_Solar
BP Solar | BP3200B, W | poly | 200 |  | +5/-5 | 5 | -5 | 13.2137 | 14.2 | 24.5 | 8.16 | 30.8 | 8.7 | -0.47% | -0.3604% |  |  | 15 |  | MC |  |  | 66.1417 | 32.9528 | 1.97 | 15.1358 | 37.84 | 5 |  | Check |  | BP_Solar
BP Solar | SX 3140J | poly | 140 |  | +9/-9 | 9 | -9 | 12.7797 | 13.8 | 17.5 | 8 | 22 | 8.2 | -0.47% | -0.3636% |  |  | 15 |  | J-Box |  |  | 59.4488 | 26.5354 | 1.9685 | 10.9549 | 26.64 | 5 |  | Check |  | BP_Solar
BP Solar | SX 3165B | poly | 165 |  | +9/-9 | 9 | -9 | 12.1807 | 13.1 | 35.2 | 4.7 | 44.2 | 5.1 | -0.47% | -0.362% |  |  | 15 |  | MC |  |  | 62.7165 | 31.1024 | 1.9685 | 13.5461 | 33.88 | 5 |  | Check |  | BP_Solar
BP Solar | SX 3170I | poly | 170 |  | +9/-9 | 9 | -9 | 12.395 | 13.1 | 35.4 | 4.8 | 44.2 | 5.27 | -0.47% | -0.362% |  |  | 15 |  | MC |  |  | 62.48 | 32.61 | 1.97 | 14.1491 | 33.88 | 5 |  | Check |  | BP_Solar
BP Solar | SX 3175B | poly | 175 |  | +9/-9 | 9 | -9 | 12.9199 | 13.9 | 36.1 | 4.9 | 44.2 | 5.3 | -0.47% | -0.362% |  |  | 15 |  | MC |  |  | 62.7165 | 31.1 | 1.9685 | 13.545 | 33.88 | 5 |  | Check |  | BP_Solar
BP Solar | SX 3190N, B | poly | 190 |  | +9/-9 | 9 | -9 | 12.553 | 13.5 | 24.3 | 7.82 | 30.6 | 8.5 | -0.47% | -0.3627% |  |  | 15 |  | MC |  |  | 66.1417 | 32.9528 | 1.97 | 15.1358 | 37.84 | 5 |  | Check |  | BP_Solar
BP Solar | SX 3195N, B | poly | 195 |  | +9/-9 | 9 | -9 | 12.8834 | 13.9 | 24.4 | 7.96 | 30.7 | 8.6 | -0.47% | -0.3616% |  |  | 15 |  | MC |  |  | 66.1417 | 32.9528 | 1.97 | 15.1358 | 37.84 | 5 |  | Check |  | BP_Solar
BP Solar | SX 3200B, W | poly | 200 |  | +9/-9 | 9 | -9 | 13.2137 | 14.2 | 24.5 | 8.16 | 30.8 | 8.7 | -0.47% | -0.3604% |  |  | 15 |  | MC |  |  | 66.1417 | 32.9528 | 1.97 | 15.1358 | 37.84 | 5 |  | Check |  | BP_Solar
BYD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | BYD
BYD | BYD 295P6C-36 | poly | 295 |  | +5/-0 | 5 | 0 |  |  | 35.76 | 8.25 | 44.9 | 8.75 | -0.43% | -0.32% |  |  | 15 | [11 empty] | 600 | 2015-02-19 | BYD
BYD | BYD 300P6C-36 | poly | 300 |  | +5/-0 | 5 | 0 |  |  | 35.97 | 8.34 | 45.19 | 8.83 | -0.43% | -0.32% |  |  | 15 | [11 empty] | 600 | 2015-02-19 | BYD
BYD | BYD 305P6C-36 | poly | 305 |  | +5/-0 | 5 | 0 |  |  | 36.18 | 8.43 | 45.49 | 8.91 | -0.43% | -0.32% |  |  | 15 | [11 empty] | 600 | 2015-02-19 | BYD
BYD | BYD 310P6C-36 | poly | 310 |  | +5/-0 | 5 | 0 |  |  | 36.38 | 8.52 | 45.79 | 8.99 | -0.43% | -0.32% |  |  | 15 | [11 empty] | 600 | 2015-02-19 | BYD
BYD | BYD 260P6C-30 | poly | 260 |  | +5/-0 | 5 | 0 |  |  | 30.67 | 8.48 | 38.38 | 8.97 | -0.43% | -0.32% |  |  | 15 | [11 empty] | 600 | 2015-12-02 | BYD
BYD | BYD 255P6C-30 | poly | 255 |  | +5/-0 | 5 | 0 |  |  | 30.4 | 8.39 | 38.07 | 8.89 | -0.43% | -0.32% |  |  | 15 | [11 empty] | 600 | 2015-12-02 | BYD
BYD | BYD 250P6C-30 | poly | 250 |  | +5/-0 | 5 | 0 |  |  | 30.13 | 8.3 | 37.76 | 8.81 | -0.43% | -0.32% |  |  | 15 | [11 empty] | 600 | 2015-12-02 | BYD
BYD | BYD 245P6C-30 | poly | 245 |  | +5/-0 | 5 | 0 |  |  | 29.85 | 8.21 | 37.45 | 8.73 | -0.43% | -0.32% |  |  | 15 | [11 empty] | 600 | 2015-12-02 | BYD
BYD | BYD 185P6C-24 | poly | 185 |  | +5/-0 | 5 | 0 |  |  | 23.11 | 8.01 | 29.03 | 8.58 | -0.43% | -0.32% |  |  | 15 | [11 empty] | 600 | 2017-11-28 | BYD
BYD | BYD 190P6C-24 | poly | 190 |  | +5/-0 | 5 | 0 |  |  | 23.47 | 8.1 | 29.33 | 8.66 | -0.43% | -0.32% |  |  | 15 | [11 empty] | 600 | 2017-11-28 | BYD
BYD | BYD 195P6C-24 | poly | 195 |  | +5/-0 | 5 | 0 |  |  | 23.82 | 8.19 | 29.63 | 8.74 | -0.43% | -0.32% |  |  | 15 | [11 empty] | 600 | 2017-11-28 | BYD
BYD | BYD 200P6C-24 | poly | 200 |  | +5/-0 | 5 | 0 |  |  | 24.17 | 8.28 | 29.93 | 8.82 | -0.43% | -0.32% |  |  | 15 | [11 empty] | 600 | 2017-11-28 | BYD
BYD | BYD 205P6C-24 | poly | 205 |  | +5/-0 | 5 | 0 |  |  | 24.5 | 8.37 | 30.23 | 8.9 | -0.43% | -0.32% |  |  | 15 | [11 empty] | 600 | 2017-11-28 | BYD
Canadian Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | Canadian_Solar
Canadian Solar | CS3K-300MS | MONO | 300 | 279 | +3/-3 | 3 | -3 | 9.4529 | 10.2 | 32.5 | 9.24 | 39.3 | 9.82 | -0.37% | -0.29% | 30 |  | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3K-305MS | MONO | 305 | 283.8 | +3/-3 | 3 | -3 | 9.8165 | 10.4 | 32.7 | 9.33 | 39.5 | 9.9 | -0.37% | -0.29% | 30 |  | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3K-310MS | MONO | 310 | 288.6 | +3/-3 | 3 | -3 | 10.1801 | 10.8 | 32.9 | 9.43 | 39.7 | 9.98 | -0.37% | -0.29% | 30 |  | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3K-315MS | MONO | 315 | 293.3 | +3/-3 | 3 | -3 | 10.5437 | 11.3 | 33.1 | 9.52 | 39.9 | 10.06 | -0.37% | -0.29% | 30 |  | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3K-275P G3 | POLY | 275 | 254.2 | +3/-3 | 3 | -3 | 10.9072 | 11.5 | 31 | 8.88 | 37.7 | 9.38 | -0.39% | -0.31% | 30 |  | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3K-280P G3 | POLY | 280 | 258.9 | +3/-3 | 3 | -3 | 11.2708 | 12.1 | 31.2 | 8.98 | 37.9 | 9.47 | -0.39% | -0.31% | 30 |  | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3K-285P G3 | POLY | 285 | 263.6 | +3/-3 | 3 | -3 | 11.6344 | 9.9 | 31.4 | 9.08 | 38.1 | 9.56 | -0.39% | -0.31% | 30 |  | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3K-290P G3 | POLY | 290 | 268.4 | +3/-3 | 3 | -3 | 11.998 | 9.7 | 31.6 | 9.18 | 38.3 | 9.64 | -0.39% | -0.31% | 30 |  | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3K-285P G4 | POLY | 285 | 263.6 | +3/-3 | 3 | -3 | 11.998 | 12.9 | 32.1 | 8.92 | 38.7 | 9.42 | -0.38% | -0.29% | 30 |  | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3K-290P G4 | POLY | 290 | 268.4 | +3/-3 | 3 | -3 | 12.3615 | 10.6 | 32.3 | 8.98 | 38.9 | 9.49 | -0.38% | -0.29% | 30 |  | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3K-295P G4 | POLY | 295 | 273.1 | +3/-3 | 3 | -3 | 12.7251 | 10.3 | 32.5 | 9.08 | 39.1 | 9.57 | -0.38% | -0.29% | 30 |  | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3K-300P G4 | POLY | 300 | 277.9 | +3/-0 | 3 | 0 | 12.7404 | 13.7 | 32.7 | 9.18 | 39.3 | 9.65 | -0.38% | -0.29% | 30 | 45 | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-270M All Black | MONO | 270 | 245.5 | +3/-0 | 3 | 0 | 13.1044 | 14.09 | 31.1 | 8.67 | 38.2 | 9.19 | -0.41% | -0.31% | 15 | 45 | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-275M All Black | MONO | 275 | 249.2 | +3/-0 | 3 | 0 | 13.4684 | 14.48 | 31.3 | 8.8 | 38.3 | 9.31 | -0.41% | -0.31% | 15 | 45 | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-280M All Black | MONO | 280 | 257.8 | +3/-0 | 3 | 0 | 13.8324 | 14.87 | 31.5 | 8.89 | 38.5 | 9.43 | -0.41% | -0.31% | 15 | 45 | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-285M All Black | MONO | 285 | 262.6 | +3/-0 | 3 | 0 | 14.1964 | 15.26 | 31.7 | 8.98 | 38.6 | 9.51 | -0.41% | -0.31% | 15 | 45 | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-290M All Black | MONO | 290 | 267.3 | +3/-3 | 3 | -3 | 10.9313 | 11.8 | 31.9 | 9.09 | 38.7 | 9.59 | -0.41% | -0.31% | 15 |  | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-280M (White Back Sheet) | MONO | 280 | 257.8 | +3/-3 | 3 | -3 | 11.2046 | 12.1 | 31.5 | 8.89 | 38.5 | 9.43 | -0.41% | -0.31% | 15 |  | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-285M (White Back Sheet) | MONO | 285 | 262.6 | +3/-3 | 3 | -3 | 11.4778 | 12.4 | 31.7 | 8.98 | 38.6 | 9.51 | -0.41% | -0.31% | 15 |  | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-290M (White Back Sheet) | MONO | 290 | 267.3 | +5/-0 | 5 | 0 | 11.7511 | 12.6 | 31.9 | 9.09 | 38.7 | 9.59 | -0.41% | -0.31% | 15 |  | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-295M (White Back Sheet) | MONO | 295 | 272 | +2/-0 | 2 | 0 | 12.0254 | 12.94 | 32.1 | 9.19 | 38.9 | 9.68 | -0.41% | -0.31% | 15 | 45 | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-285MS All Black | MONO | 285 | 261.4 | +5/-0 | 5 | 0 | 12.0244 | 12.9 | 31.9 | 8.94 | 39.1 | 9.59 | -0.39% | -0.29% | 15 |  | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-290MS All Black | MONO | 290 | 266.1 | +5/-0 | 5 | 0 | 12.2987 | 13.24 | 32.1 | 9.05 | 39.3 | 9.67 | -0.39% | -0.29% | 15 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-295MS All Black | MONO | 295 | 270.8 | +5/-0 | 5 | 0 | 12.2977 | 13.2 | 32.3 | 9.14 | 39.5 | 9.75 | -0.39% | -0.29% | 15 |  | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-300MS All Black | MONO | 300 | 275.6 | +5/-0 | 5 | 0 | 12.572 | 13.53 | 32.5 | 9.24 | 39.7 | 9.83 | -0.39% | -0.29% | 15 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-290MS (White Back Sheet) | MONO | 290 | 266.1 | +5/-0 | 5 | 0 | 12.571 | 13.5 | 32.1 | 9.05 | 39.3 | 9.67 | -0.39% | -0.29% | 15 |  | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-295MS (White Back Sheet) | MONO | 295 | 270.8 | +5/-0 | 5 | 0 | 12.8453 | 13.83 | 32.3 | 9.14 | 39.5 | 9.75 | -0.39% | -0.29% | 15 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-300MS (White Back Sheet) | MONO | 300 | 275.6 | +5/-0 | 5 | 0 | 12.8442 | 13.8 | 32.5 | 9.24 | 39.7 | 9.83 | -0.39% | -0.29% | 15 |  | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-305MS (White Back Sheet) | MONO | 305 | 280.3 | +5/-0 | 5 | 0 | 13.1186 | 14.12 | 32.7 | 9.3272 | 39.9 | 9.91 | -0.39% | -0.29% | 15 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-260P | POLY | 260 | 239.2 | +5/-0 | 5 | 0 | 13.1175 | 14.1 | 30.4 | 8.56 | 37.5 | 9.12 | -0.41% | -0.31% | 15 |  | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-265P | POLY | 265 | 243.9 | +2/-0 | 2 | 0 | 13.3919 | 14.41 | 30.6 | 8.66 | 37.7 | 9.23 | -0.41% | -0.31% | 15 | 45 | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-270P | POLY | 270 | 248.6 | +2/-0 | 2 | 0 | 13.6652 | 14.71 | 30.8 | 8.75 | 37.9 | 9.32 | -0.41% | -0.31% | 15 | 45 | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-275P | POLY | 275 | 253.3 | +2/-0 | 2 | 0 | 13.9385 | 15 | 31 | 8.88 | 38 | 9.45 | -0.41% | -0.31% | 15 | 45 | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-280P | POLY | 280 | 258 | +5/-0 | 5 | 0 |  |  | 31.3 | 8.95 | 38.2 | 9.52 | -0.41% | -0.31% | 15 |  | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-270P-FG Dymond | POLY | 270 | 248.7 | +3/-0 | 3 | 0 | 12.4983 | 13.46 | 30.8 | 8.75 | 37.9 | 9.32 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6K-275P-FG Dymond | POLY | 275 | 253.5 | +3/-0 | 3 | 0 | 12.8554 | 13.84 | 31 | 8.88 | 38 | 9.45 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6X-310P | POLY | 310 | 283.4 | +5/-0 | 5 | 0 |  |  | 36.4 | 8.52 | 44.9 | 9.08 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1000 | 2018-01-29 | Canadian_Solar
Canadian Solar | CS6X-315P | POLY | 315 | 288.1 | +5/-0 | 5 | 0 |  |  | 36.6 | 8.61 | 45.1 | 9.18 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1000 | 2018-01-29 | Canadian_Solar
Canadian Solar | CS6X-320P | POLY | 320 | 292.8 | +5/-0 | 5 | 0 |  |  | 36.8 | 8.69 | 45.3 | 9.26 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1000 | 2018-01-29 | Canadian_Solar
Canadian Solar | CS6X-325P | POLY | 325 | 297.5 | +5/-0 | 5 | 0 | 13.2125 | 14.23 | 37 | 8.78 | 45.5 | 9.34 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6X-330P | POLY | 330 | 302.2 | +3/-0 | 3 | 0 | 13.5696 | 14.61 | 37.2 | 8.88 | 45.6 | 9.45 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3U-355MS | MONO | 355 | 330.1 | +3/-3 | 3 | -3 | 9.3938 | 10.1 | 39 | 9.11 | 46.8 | 9.61 | -0.37% | -0.29% | 30 |  | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3U-360MS | MONO | 360 | 334.9 | +3/-3 | 3 | -3 | 9.8635 | 10.6 | 39.2 | 9.19 | 47 | 9.69 | -0.37% | -0.29% | 30 |  | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3U-365MS | MONO | 365 | 339.6 | +3/-3 | 3 | -3 | 10.3332 | 11.1 | 39.4 | 9.27 | 47.2 | 9.77 | -0.37% | -0.29% | 30 |  | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3U-370MS | MONO | 370 | 344.4 | +3/-3 | 3 | -3 | 10.8029 | 11.6 | 39.6 | 9.35 | 47.4 | 9.85 | -0.37% | -0.29% | 30 |  | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3U-375MS | MONO | 375 | 349.2 | +3/-3 | 3 | -3 | 11.2726 | 12.1 | 39.8 | 9.43 | 47.6 | 9.93 | -0.37% | -0.29% | 30 |  | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3U-380MS | MONO | 380 | 353.9 | +3/-3 | 3 | -3 | 11.7422 | 12.6 | 40 | 9.5 | 47.8 | 10.01 | -0.37% | -0.29% | 30 |  | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3U-330P | POLY | 330 | 305 | +3/-0 | 3 | 0 | 10.3947 | 11.19 | 37.2 | 8.88 | 45.6 | 9.45 | -0.41% | -0.31% | 30 | 45 | 15 | [11 empty] | 1500 | 2018-06-12 | Canadian_Solar
Canadian Solar | CS3U-335P | POLY | 335 | 309.7 | +3/-0 | 3 | 0 | 10.6835 | 11.5 | 38.2 | 8.77 | 45.7 | 9.28 | -0.39% | -0.31% | 30 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3U-340P | POLY | 340 | 314.5 | +3/-0 | 3 | 0 | 10.9739 | 11.81 | 38.4 | 8.86 | 45.9 | 9.36 | -0.39% | -0.31% | 30 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3U-345P | POLY | 345 | 319.2 | +3/-0 | 3 | 0 | 11.2633 | 12.12 | 38.6 | 8.94 | 46.1 | 9.44 | -0.39% | -0.31% | 30 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3U-350P | POLY | 350 | 324 | +3/-0 | 3 | 0 | 11.5539 | 12.43 | 38.8 | 9.03 | 46.6 | 9.52 | -0.39% | -0.31% | 30 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3U-355P | POLY | 355 | 328.7 | +2/-0 | 2 | 0 | 11.8427 | 12.74 | 39.4 | 9.02 | 46.8 | 9.59 | -0.38% | -0.29% | 30 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS3U-360P | POLY | 360 | 333.5 | +2/-0 | 2 | 0 | 12.1335 | 13.06 | 39.6 | 9.1 | 47 | 9.67 | -0.38% | -0.29% | 30 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6U-315P | POLY | 315 | 289.9 | +2/-0 | 2 | 0 | 12.4224 | 13.37 | 36.6 | 8.61 | 45.1 | 9.18 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6U-320P | POLY | 320 | 294.6 | +2/-0 | 2 | 0 | 12.7132 | 13.68 | 36.8 | 8.69 | 45.3 | 9.26 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6U-325P | POLY | 325 | 299.3 | +2/-0 | 2 | 0 | 12.7122 | 13.68 | 37 | 8.78 | 45.5 | 9.34 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6U-330P | POLY | 330 | 304.1 | +2/-0 | 2 | 0 | 13.0032 | 13.99 | 37.2 | 8.88 | 45.6 | 9.45 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6U-335P | POLY | 335 | 308.8 | +2/-0 | 2 | 0 | 13.0022 | 13.99 | 37.4 | 8.96 | 45.8 | 9.54 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6U-340P | POLY | 340 | 313.5 | +5/0 | 5 | 0 | 13.2918 | 14.3 | 37.6 | 9.05 | 45.9 | 9.62 | -0.39% | -0.29% | 15 | 45 | 15 |  |  |  |  | 77.2 | 39.1 | 1.57 |  | 49.4 |  |  | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6U-345P | POLY | 345 | 319.4 | +5/0 | 5 | 0 |  |  | 37.8 | 9.13 | 46 | 9.69 | -0.39% | -0.29% |  |  | 15 |  |  |  |  | 77.2 | 39.1 | 1.57 |  | 49.4 |  |  | 1000 | 2018-01-29 | Canadian_Solar
Canadian Solar | CS6U-350P | POLY | 350 | 324.1 | +5/0 | 5 | 0 |  |  | 38.1 | 9.21 | 46.2 | 9.79 | -0.39% | -0.29% |  |  | 15 |  |  |  |  | 77.2 | 39.1 | 1.57 |  | 49.4 |  |  | 1000 | 2018-01-29 | Canadian_Solar
Canadian Solar | CS6U-330M | MONO | 330 | 303.8 | +2/-0 | 2 | 0 | 13.2911 | 14.3 | 37.5 | 8.8 | 45.9 | 9.31 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6U-330M (1500V) | MONO | 330 | 303.8 | +2/-0 | 2 | 0 | 13.2911 | 14.3 | 37.5 | 8.8 | 45.9 | 9.31 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1500 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6U-335M | MONO | 335 | 308.5 | +2/-0 | 2 | 0 | 13.2921 | 14.3 | 37.8 | 8.87 | 46.1 | 9.41 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6U-335M (1500V) | MONO | 335 | 308.5 | +2/-0 | 2 | 0 | 13.2921 | 14.3 | 37.8 | 8.87 | 46.1 | 9.41 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1500 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6U-340M | MONO | 340 | 313.3 | +2/-0 | 2 | 0 | 13.5807 | 14.61 | 37.9 | 8.97 | 46.2 | 9.48 | -0.41% | -0.31% | 15 | 45 | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6U-340M (1500V) | MONO | 340 | 313.3 | +2/-0 | 2 | 0 | 13.5807 | 14.61 | 37.9 | 8.97 | 46.2 | 9.48 | -0.41% | -0.31% | 15 | 45 | 10 | [11 empty] | 1500 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6U-345M | MONO | 345 | 318 | +2/-0 | 2 | 0 | 13.5811 | 14.61 | 38.1 | 9.06 | 46.4 | 9.56 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6U-345M (1500V) | MONO | 345 | 318 | +2/-0 | 2 | 0 | 13.5811 | 14.61 | 38.1 | 9.06 | 46.4 | 9.56 | -0.41% | -0.31% | 15 | 45 | 15 | [11 empty] | 1500 | 2017-10-10 | Canadian_Solar
Canadian Solar | CS6U-350M | MONO | 350 | 321.2 | +2/-0 | 2 | 0 | 13.8697 | 14.92 | 38.3 | 9.14 | 46.6 | 9.67 | -0.41% | -0.31% | 15 | 45 | 10 | [11 empty] | 1000 | 2017-10-10 | Canadian_Solar
Centrosolar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Centrosolar
Centrosolar | CP6-230 | poly | 230 | 206.6 | +/-3 | 3 | -3 | 12.6766 | 14.2 | 28.65 | 8.03 | 36.39 | 8.48 | -0.43% | -0.35% | 0.03 | 46 | 15 | yes | tyco | silver/black | white | 65.35 | 39.98 | 1.57 | 18.1437 | 44 | 10 |  | Check |  | Centrosolar
Centrosolar | CP6-235 | poly | 235 | 211.3 | +/-3 | 3 | -3 | 12.9522 | 14.6 | 28.7 | 8.19 | 36.46 | 8.59 | -0.43% | -0.35% | 0.03 | 46 | 15 | yes | tyco | silver/black | white | 65.35 | 39.98 | 1.57 | 18.1437 | 44 | 10 |  | Check |  | Centrosolar
Centrosolar | CP6-240 | poly | 240 | 215.9 | +/-3 | 3 | -3 | 13.2277 | 14.9 | 28.75 | 8.35 | 36.53 | 8.7 | -0.43% | -0.35% | 0.03 | 46 | 15 | yes | tyco | silver/black | white | 65.35 | 39.98 | 1.57 | 18.1437 | 44 | 10 |  | Check |  | Centrosolar
Centrosolar | TP6-245 | poly | 245 |  | +5/-0 | 5 | 0 |  |  | 30.2 | 8.11 | 37.3 | 8.65 | -0.4% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Centrosolar
Centrosolar | TP6-250 | poly | 250 |  | +5/-0 | 5 | 0 |  |  | 30.4 | 8.22 | 37.4 | 8.76 | -0.4% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Centrosolar
Centrosolar | TP6-255 | poly | 255 |  | +5/-0 | 5 | 0 |  |  | 30.6 | 8.33 | 38.1 | 8.88 | -0.4% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Centrosolar
Centrosolar | E250B | poly | 250 |  | +5/-0 | 5 | 0 |  |  | 30.34 | 8.24 | 37.47 | 8.76 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Centrosolar
Centrosolar | E255B | poly | 255 |  | +5/-0 | 5 | 0 |  |  | 30.91 | 8.25 | 37.54 | 8.82 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Centrosolar
Centrosolar | E260B | poly | 260 |  | +5/-0 | 5 | 0 |  |  | 31.48 | 8.26 | 38.09 | 8.84 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Centrosolar
Centrosolar | BP7 300S(B)W | poly | 300 |  | +5/-0 | 5 | 0 |  |  | 37.25 | 8.05 | 45.22 | 8.63 | -0.46% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-12-02 | Centrosolar
Centrosolar | BP7 295S(B)W | poly | 295 |  | +5/-0 | 5 | 0 |  |  | 36.97 | 7.98 | 45.1 | 8.56 | -0.46% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-12-02 | Centrosolar
Centrosolar | DP60-250 | Poly | 250 |  | +3/-0 | 3 | 0 |  |  | 30.83 | 8.11 | 37.65 | 8.61 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2017-02-14 | Centrosolar
Centrosolar | DP60-255 | poly | 255 |  | +3/-0 | 3 | 0 |  |  | 31.25 | 8.16 | 37.9 | 8.66 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2017-02-14 | Centrosolar
Centrosolar | DP60-260 | poly | 260 |  | +3/-0 | 3 | 0 |  |  | 31.71 | 8.2 | 38.15 | 8.7 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2017-02-14 | Centrosolar
Centrosolar | CP60-260BW | poly | 260 |  | +5/-0 | 5 | 0 |  |  | 30.93 | 8.43 | 37.67 | 8.83 | -0.42% | -0.313% |  |  | 15 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | CP60-270BW | Poly | 270 |  | +5/-0 | 5 | 0 |  |  | 31.04 | 8.73 | 38.39 | 9.15 | -0.42% | -0.313% |  |  | 15 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | BM60-260BB | Mono | 260 |  | +5/-0 | 5 | 0 |  |  | 30.7 | 8.56 | 38.9 | 9.18 | -0.43% | -0.31% |  |  | 16 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | BM60-265BB | Mono | 265 |  | +5/-0 | 5 | 0 |  |  | 30.8 | 8.69 | 39 | 9.31 | -0.43% | -0.31% |  |  | 16 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | BM60-270BB | Mono | 270 |  | +5/-0 | 5 | 0 |  |  | 30.9 | 8.81 | 39.2 | 9.44 | -0.43% | -0.31% |  |  | 16 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | BM60-275BB | Mono | 275 |  | +5/-0 | 5 | 0 |  |  | 31 | 8.94 | 39.4 | 9.58 | -0.44% | -0.31% |  |  | 25 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | BM60-285BB | Mono | 285 |  | +5/-0 | 5 | 0 |  |  | 31.3 | 9.2 | 39.7 | 9.84 | -0.43% | -0.31% |  |  | 25 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | BM60-290BB | Mono | 290 |  | +/-1 | 1 | -1 |  |  | 31.4 | 9.33 | 39.9 | 9.97 | -0.43% | -0.31% |  |  | 25 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | CM60-265BB | mono | 265 |  | +5/-0 | 5 | 0 |  |  | 30.98 | 8.56 | 38.29 | 9.08 | -0.427% | -0.318% |  |  | 15 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | CM60-270BB | mono | 270 |  | +5/-0 | 5 | 0 |  |  | 31.15 | 8.67 | 38.37 | 9.23 | -0.427% | -0.318% |  |  | 15 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | CM60-275BB | mono | 275 |  | +5/-0 | 5 | 0 |  |  | 31.43 | 8.75 | 38.74 | 9.3 | -0.427% | -0.318% |  |  | 15 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | CM60-280BB | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 31.69 | 8.84 | 39.05 | 9.39 | -0.427% | -0.318% |  |  | 15 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | CM60-285BB | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 31.81 | 8.96 | 39.16 | 9.49 | -0.427% | -0.318% |  |  | 15 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | CM60-290BB | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 32.02 | 9.06 | 39.31 | 9.59 | -0.427% | -0.318% |  |  | 15 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | EM60-280BW | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 31.01 | 9.03 | 39.26 | 9.23 | -0.42% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-11-28 | Centrosolar
Centrosolar | EM60-285BW | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 31.85 | 8.95 | 39.18 | 9.46 | -0.42% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-11-28 | Centrosolar
Centrosolar | EM60-290BW | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 31.12 | 9.03 | 39.68 | 9.59 | -0.42% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-11-28 | Centrosolar
Centrosolar | EP60-260BW | poly | 260 |  | +5/-0 | 5 | 0 |  |  | 30.59 | 8.5 | 38.16 | 9.07 | -0.4% | -0.34% |  |  | 15 | [11 empty] | 1000 | 2017-11-28 | Centrosolar
Centrosolar | EP60-265BW | poly | 265 |  | +5/-0 | 5 | 0 |  |  | 30.74 | 8.62 | 38.29 | 9.24 | -0.4% | -0.34% |  |  | 15 | [11 empty] | 1000 | 2017-11-28 | Centrosolar
Centrosolar | EP60-270BW | poly | 270 |  | +5/-0 | 5 | 0 |  |  | 30.97 | 8.72 | 38.72 | 9.31 | -0.4% | -0.34% |  |  | 15 | [11 empty] | 1000 | 2017-11-28 | Centrosolar
Centrosolar | E285(B) | poly | 285 |  | +5/-0 | 5 | 0 |  |  | 35.86 | 7.95 | 44.72 | 8.55 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Centrosolar
Centrosolar | E290(B) | poly | 290 |  | +5/-0 | 5 | 0 |  |  | 35.92 | 8.08 | 44.75 | 8.62 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Centrosolar
Centrosolar | E295(B) | poly | 295 |  | +5/-0 | 5 | 0 |  |  | 36.17 | 8.16 | 44.78 | 8.68 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Centrosolar
Centrosolar | E300(B) | poly | 300 |  | +5/-0 | 5 | 0 |  |  | 36.68 | 8.18 | 44.89 | 8.72 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Centrosolar
Centrosolar | E305(B) | poly | 305 |  | +5/-0 | 5 | 0 |  |  | 37.18 | 8.21 | 45.12 | 8.78 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Centrosolar
Centrosolar | CP72-315SW | Poly | 315 |  | +5/-0 | 5 | 0 |  |  | 37.18 | 8.49 | 45.91 | 9.01 | -0.42% | -0.313% |  |  | 15 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | CP72-320SW | Poly | 320 |  | +5/-0 | 5 | 0 |  |  | 37.36 | 8.58 | 46.15 | 9.1 | -0.42% | -0.313% |  |  | 15 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | CM72-325SW | Mono | 325 |  | +5/-0 | 5 | 0 |  |  | 37.22 | 8.74 | 45.65 | 9.24 | -0.427% | -0.318% |  |  | 15 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | CM72-330SW | Mono | 330 |  | +5/-0 | 5 | 0 |  |  | 37.38 | 8.85 | 45.92 | 9.32 | -0.427% | -0.318% |  |  | 15 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | CM72-335SW | mono | 335 |  | +5/-0 | 5 | 0 |  |  | 37.47 | 8.96 | 46.04 | 9.41 | -0.427% | -0.318% |  |  | 15 | [11 empty] | 1000 | 2017-02-14 | Centrosolar
Centrosolar | EM72-330BW | mono | 330 |  | +5/-0 | 5 | 0 |  |  | 37.55 | 8.79 | 46.64 | 9.29 | -0.43% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-11-28 | Centrosolar
Centrosolar | EM72-335BW | mono | 335 |  | +5/-0 | 5 | 0 |  |  | 37.94 | 8.83 | 46.75 | 9.33 | -0.43% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-11-28 | Centrosolar
Centrosolar | EM72-340BW | mono | 340 |  | +5/-0 | 5 | 0 |  |  | 38.17 | 8.91 | 46.91 | 9.41 | -0.43% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-11-28 | Centrosolar
Centrosolar | EP72-315BW | Poly | 315 |  | +5/-0 | 5 | 0 |  |  | 36.81 | 8.56 | 45.75 | 9.12 | -0.41% | -0.34% |  |  | 15 | [11 empty] | 1000 | 2017-11-28 | Centrosolar
Centrosolar | EP72-320BW | Poly | 320 |  | +5/-0 | 5 | 0 |  |  | 37.13 | 8.62 | 45.94 | 9.24 | -0.41% | -0.34% |  |  | 15 | [11 empty] | 1000 | 2017-11-28 | Centrosolar
Centrosolar | EP72-325BW | Poly | 325 |  | +5/-0 | 5 | 0 |  |  | 37.28 | 8.72 | 46.31 | 9.28 | -0.41% | -0.34% |  |  | 15 | [11 empty] | 1000 | 2017-11-28 | Centrosolar
Centrosolar | DP72-300 | Poly | 300 |  | +3/-0 | 3 | 0 |  |  | 36.52 | 8.21 | 44.82 | 8.63 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2017-02-14 | Centrosolar
Centrosolar | DP72-305 | poly | 305 |  | +3/-0 | 3 | 0 |  |  | 36.85 | 8.27 | 44.96 | 8.67 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2017-02-14 | Centrosolar
Centrosolar | DP72-310 | Poly | 310 |  | +3/-0 | 3 | 0 |  |  | 37.3 | 8.31 | 45.18 | 8.7 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2017-02-14 | Centrosolar
Certainteed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Certainteed
Certainteed | CT260P00-01 | Polycrystalline | 260 | 233.3 | +3/-0 | 3 | 0 |  |  | 31.12 | 8.37 | 37.73 | 8.92 | -0.4953% | -0.3577% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT260P10-01 | Polycrystalline | 260 | 233.3 | +3/-0 | 3 | 0 |  |  | 31.12 | 8.37 | 37.73 | 8.92 | -0.4953% | -0.3577% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT265M11-01 | Monocrystalline | 265 | 237.4 | +3/-0 | 3 | 0 |  |  | 31.27 | 8.47 | 38.09 | 9.05 | -0.4579% | -0.322% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT270M11-01 | Monocrystalline | 270 | 242 | +3/-0 | 3 | 0 |  |  | 31.41 | 8.59 | 38.23 | 9.17 | -0.4579% | -0.322% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT280M10-02 | Monocrystalline | 280 | 256.7 | +3/-0 | 3 | 0 |  |  | 31.53 | 8.88 | 39.1 | 9.34 | -0.41% | -0.3% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT280M11-02 | Monocrystalline | 280 | 256.7 | +3/-0 | 3 | 0 |  |  | 31.53 | 8.88 | 39.1 | 9.34 | -0.41% | -0.3% | 15 |  | 15 | [11 empty] | 1000 | 2018-01-03 | Certainteed
Certainteed | CT285M10-01 | Monocrystalline | 285 | 258.9 | +3/-0 | 3 | 0 |  |  | 31.8 | 8.9 | 38.7 | 9.5 | -0.4068% | -0.2928% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT285M10-02 | Monocrystalline | 285 | 261.4 | +3/-0 | 3 | 0 |  |  | 31.76 | 8.97 | 39.43 | 9.48 | -0.41% | -0.3% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT285M11-01 | Monocrystalline | 285 | 258 | +3/-0 | 3 | 0 |  |  | 31.8 | 8.9 | 38.7 | 9.5 | -0.4096% | -0.3021% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT290M10-01 | Monocrystalline | 290 | 263.5 | +3/-0 | 3 | 0 |  |  | 32 | 9.1 | 38.8 | 9.7 | -0.4068% | -0.2928% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT290M10-02 | Monocrystalline | 290 | 266.1 | +3/-0 | 3 | 0 |  |  | 32 | 9.06 | 39.77 | 9.62 | -0.41% | -0.3% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT290M11-01 | Monocrystalline | 290 | 262.6 | +3/-0 | 3 | 0 |  |  | 32 | 9.1 | 38.8 | 9.7 | -0.4096% | -0.3021% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT290M11-02 | Monocrystalline | 290 | 266.1 | +3/-0 | 3 | 0 |  |  | 32 | 9.06 | 39.77 | 9.62 | -0.41% | -0.3% | 15 |  | 15 | [11 empty] | 1000 | 2018-01-03 | Certainteed
Certainteed | CT295M10-01 | Monocrystalline | 295 | 268.3 | +3/-0 | 3 | 0 |  |  | 32.1 | 9.2 | 39 | 9.8 | -0.4068% | -0.2928% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT295M10-02 | Monocrystalline | 295 | 270.4 | +3/-0 | 3 | 0 |  |  | 32.24 | 9.15 | 40.11 | 9.77 | -0.381% | -0.282% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT295M11-01 | Monocrystalline | 295 | 267.3 | +3/-0 | 3 | 0 |  |  | 32.1 | 9.2 | 39 | 9.8 | -0.4096% | -0.3021% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT295M11-02 | Monocrystalline | 295 | 270.4 | +3/-0 | 3 | 0 |  |  | 32.24 | 9.15 | 40.11 | 9.77 | -0.381% | -0.282% | 15 |  | 15 | [11 empty] | 1000 | 2018-01-03 | Certainteed
Certainteed | CT300M10-01 | Monocrystalline | 300 | 272.9 | +3/-0 | 3 | 0 |  |  | 32.3 | 9.3 | 39.1 | 9.9 | -0.4068% | -0.2928% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT300M10-02 | Monocrystalline | 300 | 275.1 | +3/-0 | 3 | 0 |  |  | 32.48 | 9.24 | 40.45 | 9.91 | -0.381% | -0.282% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT300M11-01 | Monocrystalline | 300 | 270.3 | +3/-0 | 3 | 0 |  |  | 32.3 | 9.3 | 39.1 | 9.9 | -0.4438% | -0.3286% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT300M11-02 | Monocrystalline | 300 | 275.1 | +3/-0 | 3 | 0 |  |  | 32.48 | 9.24 | 40.45 | 9.91 | -0.381% | -0.282% | 15 |  | 15 | [11 empty] | 1000 | 2018-01-03 | Certainteed
Certainteed | CT300M10-03 | Monocrystalline | 300 | 277.2 | +3/-0 | 3 | 0 |  |  | 32.5 | 9.24 | 40.3 | 9.75 | -0.381% | -0.282% | 15 |  | 20 | [11 empty] | 1500 | 2018-06-01 | Certainteed
Certainteed | CT305M10-02 | Monocrystalline | 305 | 279.8 | +3/-0 | 3 | 0 |  |  | 32.7286 | 9.3191 | 40.792 | 10.0618 | -0.381% | -0.282% | 15 |  | 15 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT305M11-02 | Monocrystalline | 305 | 279.8 | +3/-0 | 3 | 0 |  |  | 32.7286 | 9.3191 | 40.792 | 10.0618 | -0.381% | -0.282% | 15 |  | 15 | [11 empty] | 1000 | 2018-01-03 | Certainteed
Certainteed | CT340M10-03 | Monocrystalline | 340 | 310.6 | +3/-0 | 3 | 0 |  |  | 38.3 | 8.88 | 46.1 | 9.5 | -0.381% | -0.282% | 15 |  | 20 | [11 empty] | 1500 | 2018-06-01 | Certainteed
Certainteed | CT355M10-02 | Monocrystalline | 355 | 325.5 | +3/-0 | 3 | 0 |  |  | 38.5524 | 9.2082 | 47.4657 | 9.8985 | -0.381% | -0.282% | 15 |  | 20 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT355M10-03 | Monocrystalline | 355 | 324.7 | +3/-0 | 3 | 0 |  |  | 39.3 | 9.04 | 47 | 9.64 | -0.38% | -0.28% |  |  | 20 | [11 empty] | 1500 | 2018-06-01 | Certainteed
Certainteed | CT355M11-02 | Monocrystalline | 355 | 325.5 | +3/-0 | 3 | 0 |  |  | 38.5524 | 9.2082 | 47.4657 | 9.8985 | -0.381% | -0.282% | 15 |  | 20 | [11 empty] | 1000 | 2018-01-03 | Certainteed
Certainteed | CT360M10-02 | Monocrystalline | 360 | 330.2 | +3/-0 | 3 | 0 |  |  | 38.6295 | 9.3193 | 47.5606 | 9.9876 | -0.381% | -0.282% | 15 |  | 20 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT360M11-02 | Monocrystalline | 360 | 330.2 | +3/-0 | 3 | 0 |  |  | 38.6295 | 9.3193 | 47.5606 | 9.9876 | -0.381% | -0.282% | 15 |  | 20 | [11 empty] | 1000 | 2018-01-03 | Certainteed
Certainteed | CT360M10-03 | Monocrystalline | 360 | 329.4 | +3/-0 | 3 | 0 |  |  | 39.7 | 9.07 | 47.4 | 9.67 | -0.38% | -0.28% |  |  | 20 | [11 empty] | 1500 | 2018-06-01 | Certainteed
Certainteed | CT365M10-02 | Monocrystalline | 365 | 334.9 | +3/-0 | 3 | 0 |  |  | 38.7068 | 9.4299 | 47.6557 | 10.0775 | -0.381% | -0.282% | 15 |  | 20 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT365M11-02 | Monocrystalline | 365 | 334.9 | +3/-0 | 3 | 0 |  |  | 38.7068 | 9.4299 | 47.6557 | 10.0775 | -0.381% | -0.282% | 15 |  | 20 | [11 empty] | 1000 | 2018-01-03 | Certainteed
Certainteed | CT320P00-01 | Polycrystalline | 320 | 293.6 | +3/-0 | 3 | 0 |  |  | 36.4 | 8.8 | 45.7 | 9.0 | -0.16% | -0.29% | 15 |  | 20 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT325P00-01 | Polycrystalline | 325 | 298.3 | +3/-0 | 3 | 0 |  |  | 36.6 | 8.8 | 45.9 | 9.1 | -0.16% | -0.29% | 15 |  | 20 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT350M00-01 | Monocrystalline | 350 | 321.8 | +3/-0 | 3 | 0 |  |  | 38.7 | 9.0 | 47.1 | 9.6 | -0.164% | -0.29% | 15 |  | 20 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT350M10-01 | Monocrystalline | 350 | 321.8 | +3/-0 | 3 | 0 |  |  | 38.7 | 9.0 | 47.1 | 9.6 | -0.164% | -0.29% | 15 |  | 20 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT355M00-01 | Monocrystalline | 355 | 326.6 | +3/-0 | 3 | 0 |  |  | 38.9 | 9.1 | 47.3 | 9.7 | -0.164% | -0.29% | 15 |  | 20 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT355M10-01 | Monocrystalline | 355 | 326.6 | +3/-0 | 3 | 0 |  |  | 38.9 | 9.1 | 47.3 | 9.7 | -0.164% | -0.29% | 15 |  | 20 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT360M00-01 | Monocrystalline | 360 | 331.3 | +3/-0 | 3 | 0 |  |  | 39.1 | 9.2 | 47.4 | 9.8 | -0.164% | -0.29% | 15 |  | 20 | [11 empty] | Check | 2018-01-03 | Certainteed
Certainteed | CT360M10-01 | Monocrystalline | 360 | 331.3 | +3/-0 | 3 | 0 |  |  | 39.1 | 9.2 | 47.4 | 9.8 | -0.164% | -0.29% | 15 |  | 20 | [11 empty] | Check | 2018-01-03 | Certainteed
Chaori Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Chaori_Solar
Chaori Solar | CRM210S156P-60 | poly | 210 |  | +/-0 | 0 | 0 |  | 14.9 | 28.3 | 7.42 | 36.1 | 7.99 | -0.462% | -0.343% |  |  | 15 | [11 empty] | Check | 2012-07-25 | Chaori_Solar
Chaori Solar | CRM215S156P-60 | poly | 215 |  | +/-0 | 0 | 0 |  | 14.9 | 28.8 | 7.47 | 36.5 | 8.04 | -0.462% | -0.343% |  |  | 15 | [11 empty] | Check | 2012-07-25 | Chaori_Solar
Chaori Solar | CRM220S156P-60 | poly | 220 |  | +/-0 | 0 | 0 |  | 14.9 | 29.2 | 7.53 | 36.8 | 8.08 | -0.462% | -0.343% |  |  | 15 | [11 empty] | Check | 2012-07-25 | Chaori_Solar
Chaori Solar | CRM225S156P-60 | poly | 225 |  | +/-0 | 0 | 0 |  | 14.9 | 29.5 | 7.63 | 37 | 8.15 | -0.462% | -0.343% |  |  | 15 | [11 empty] | Check | 2012-07-25 | Chaori_Solar
Chaori Solar | CRM230S156P-60 | poly | 230 |  | +/-0 | 0 | 0 |  | 14.9 | 29.8 | 7.71 | 37.1 | 8.21 | -0.462% | -0.343% |  |  | 15 | [11 empty] | Check | 2012-07-25 | Chaori_Solar
Chaori Solar | CRM235S156P-60 | poly | 235 |  | +/-0 | 0 | 0 |  | 14.9 | 30.1 | 7.81 | 37.3 | 8.31 | -0.462% | -0.343% |  |  | 15 | [11 empty] | Check | 2012-07-25 | Chaori_Solar
Chaori Solar | CRM240S156P-60 | poly | 240 |  | +/-0 | 0 | 0 |  | 14.9 | 30.3 | 7.91 | 37.5 | 8.4 | -0.462% | -0.343% |  |  | 15 | [11 empty] | Check | 2012-07-25 | Chaori_Solar
Chaori Solar | CRM265S156P-72 | poly | 265 |  | +3/-0 | 3 | 0 |  |  | 35.1 | 7.56 | 44.1 | 8.12 | -0.48% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Chaori_Solar
Chaori Solar | CRM270S156P-72 | poly | 270 |  | +3/-0 | 3 | 0 |  |  | 35.4 | 7.64 | 44.4 | 8.15 | -0.48% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Chaori_Solar
Chaori Solar | CRM275S156P-72 | poly | 275 |  | +3/-0 | 3 | 0 |  |  | 35.6 | 7.72 | 44.7 | 8.23 | -0.48% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Chaori_Solar
Chaori Solar | CRM280S156P-72 | poly | 280 |  | +3/-0 | 3 | 0 |  |  | 36 | 7.77 | 44.9 | 8.28 | -0.48% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Chaori_Solar
Chaori Solar | CRM285S156P-72 | poly | 285 |  | +3/-0 | 3 | 0 |  |  | 36.4 | 7.83 | 45 | 8.34 | -0.48% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Chaori_Solar
Chaori Solar | CRM290S156P-72 | poly | 290 |  | +3/-0 | 3 | 0 |  |  | 36.6 | 7.92 | 45.1 | 8.41 | -0.48% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Chaori_Solar
Chaori Solar | CRM295S156P-72 | poly | 295 |  | +3/-0 | 3 | 0 |  |  | 36.9 | 7.99 | 45.2 | 8.48 | -0.48% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Chaori_Solar
Chaori Solar | CRM300S156P-72 | poly | 300 |  | +3/-0 | 3 | 0 |  |  | 37.3 | 8.06 | 45.3 | 8.56 | -0.48% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Chaori_Solar
Chaori Solar | CRM280S156M-72 | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 35.7 | 7.84 | 44.4 | 8.56 | -0.49% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Chaori_Solar
Chaori Solar | CRM285S156M-72 | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 35.9 | 7.94 | 44.5 | 8.62 | -0.49% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Chaori_Solar
Chaori Solar | CRM290S156M-72 | mono | 290 |  | +3/-0 | 3 | 0 |  |  | 36.1 | 8.03 | 44.6 | 8.67 | -0.49% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Chaori_Solar
Chaori Solar | CRM295S156M-72 | mono | 295 |  | +3/-0 | 3 | 0 |  |  | 36.3 | 8.12 | 44.7 | 8.73 | -0.49% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Chaori_Solar
Chaori Solar | CRM300S156M-72 | mono | 300 |  | +3/-0 | 3 | 0 |  |  | 36.5 | 8.22 | 44.8 | 8.79 | -0.49% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Chaori_Solar
Chaori Solar | CRM305S156M-72 | mono | 305 |  | +3/-0 | 3 | 0 |  |  | 36.7 | 8.31 | 44.9 | 8.85 | -0.49% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Chaori_Solar
Chaori Solar | CRM310S156M-72 | mono | 310 |  | +3/-0 | 3 | 0 |  |  | 37 | 8.4 | 45 | 8.9 | -0.49% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Chaori_Solar
Chaori Solar | CRM315S156M-72 | mono | 315 |  | +3/-0 | 3 | 0 |  |  | 37.1 | 8.48 | 45.1 | 8.96 | -0.49% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Chaori_Solar
China Sunergy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | China_Sunergy
China Sunergy | SST215-54M | mono | 215 | 185.8 | +/-3 | 3 | -3 | 15.6525 | 14.7 | 26.9 | 7.99 | 33.4 | 8.75 | -0.423% | -0.307% | 0.039 | 45 | 15 | yes | N/A | silver | white | 62.2 | 31.8 | 1.97 | 13.7358 | DNR | 5 |  | Check |  | China_Sunergy
China Sunergy | SST215-54M-BB | mono | 215 | 187.4 | +/-3 | 3 | -3 | 15.6525 | 14.7 | 26.9 | 5.09 | 44.6 | 5.4 | -0.423% | -0.307% | 0.039 | 45 | 15 | yes | N/A | silver | white | 62.2 | 31.8 | 1.97 | 13.7358 | DNR | 5 |  | Check |  | China_Sunergy
China Sunergy | SST220-54M | mono | 220 | 190.3 | +/-3 | 3 | -3 | 16.0165 | 15 | 27 | 5.17 | 44.8 | 5.48 | -0.423% | -0.307% | 0.039 | 45 | 15 | yes | N/A | silver | white | 62.2 | 31.8 | 1.97 | 13.7358 | DNR | 5 |  | Check |  | China_Sunergy
China Sunergy | SST220-54M-BB | mono | 220 | 191.9 | +/-3 | 3 | -3 | 13.9524 | 15 | 27 | 7.94 | 36.8 | 8.54 | -0.423% | -0.307% | 0.039 | 45 | 15 | yes | N/A | black | black | 58.25 | 38.98 | 1.97 | 15.768 | DNR | 5 |  | Check |  | China_Sunergy
China Sunergy | SST220-60P | poly | 220 | 195.5 | +/-3 | 3 | -3 | 12.5867 | 13.55 | 29.3 | 7.55 | 36.5 | 8.38 | -0.408% | -0.292% | 0.045 | 45 | 15 | yes | N/A | silver | white | 64.57 | 38.98 | 1.97 | 17.4787 | 43.7 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST225-54M | mono | 225 | 194.8 | +/-3 | 3 | -3 | 14.2695 | 15.4 | 27.1 | 8.17 | 37.2 | 8.69 | -0.423% | -0.307% | 0.039 | 45 | 15 | yes | N/A | silver | white | 58.25 | 38.98 | 1.97 | 15.768 | DNR | 5 |  | Check |  | China_Sunergy
China Sunergy | SST225-54M-BB | mono | 225 | 196.4 | +/-3 | 3 | -3 | 14.2695 | 15.4 | 27.1 | 8.31 | 37.3 | 8.78 | -0.423% | -0.307% | 0.039 | 45 | 15 | yes | N/A | black | black | 58.25 | 38.98 | 1.97 | 15.768 | DNR | 5 |  | Check |  | China_Sunergy
China Sunergy | SST225-60P | poly | 225 | 200.1 | +/-3 | 3 | -3 | 12.8728 | 13.86 | 29.3 | 7.69 | 36.6 | 8.45 | -0.408% | -0.292% | 0.045 | 45 | 15 | yes | N/A | silver | white | 64.57 | 38.98 | 1.97 | 17.4787 | 43.7 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST230-60P | poly | 230 | 204.7 | +/-3 | 3 | -3 | 13.1588 | 14.17 | 29.5 | 7.83 | 36.7 | 8.52 | -0.408% | -0.292% | 0.045 | 45 | 15 | yes | N/A | silver | white | 64.57 | 38.98 | 1.97 | 17.4787 | 43.7 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST235-60M-BB | mono | 235 | 204.6 | +/-3 | 3 | -3 | 13.4449 | 14.47 | 29.7 | 7.93 | 36.8 | 8.55 | -0.423% | -0.307% | 0.039 | 45 | 15 | yes | N/A | black | black | 64.57 | 38.98 | 1.97 | 17.4787 | 43.7 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST235-60P | poly | 235 | 209.2 | +/-3 | 3 | -3 | 13.4449 | 14.47 | 29.5 | 7.97 | 36.8 | 8.59 | -0.408% | -0.292% | 0.045 | 45 | 15 | yes | N/A | silver | white | 64.57 | 38.98 | 1.97 | 17.4787 | 43.7 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST240-60M-BB | mono | 240 | 209.1 | +/-3 | 3 | -3 | 13.731 | 14.78 | 29.8 | 8.06 | 37 | 8.62 | -0.423% | -0.307% | 0.039 | 45 | 15 | yes | N/A | black | black | 64.57 | 38.98 | 1.97 | 17.4787 | 43.7 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST240-60P | poly | 240 | 213.8 | +/-3 | 3 | -3 | 13.731 | 14.78 | 29.6 | 8.11 | 36.9 | 8.67 | -0.408% | -0.292% | 0.045 | 45 | 15 | yes | N/A | silver | white | 64.57 | 38.98 | 1.97 | 17.4787 | 43.7 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST245-60M-BB | mono | 245 | 213.6 | +/-3 | 3 | -3 | 14.017 | 15.09 | 30 | 8.17 | 37.2 | 8.69 | -0.423% | -0.307% | 0.039 | 45 | 15 | yes | N/A | black | black | 64.57 | 38.98 | 1.97 | 17.4787 | 43.7 | 5 |  | Check |  | China_Sunergy
China Sunergy | CSUN255-60M-BB | Mono | 255 | 228 | +3/-0 | 3 | 0 |  |  | 30.7 | 8.3 | 38 | 8.82 | -0.423% | -0.307% |  |  | 20 | [11 empty] | Check | 2017-02-14 | China_Sunergy
China Sunergy | CSUN260-60M-BB | Mono | 260 | 232.6 | +3/-0 | 3 | 0 |  |  | 30.8 | 8.44 | 38.1 | 8.9 | -0.423% | -0.307% |  |  | 20 | [11 empty] | Check | 2017-02-14 | China_Sunergy
China Sunergy | CSUN265-60M-BB | Mono | 265 | 237.8 | +3/-0 | 3 | 0 |  |  | 31 | 8.55 | 38.2 | 8.98 | -0.423% | -0.307% |  |  | 20 | [11 empty] | Check | 2017-02-14 | China_Sunergy
China Sunergy | CSUN270-60M-BB | Mono | 270 | 242.5 | +3/-0 | 3 | 0 |  |  | 31.2 | 8.65 | 38.3 | 9.07 | -0.423% | -0.307% |  |  | 20 | [11 empty] | Check | 2017-02-14 | China_Sunergy
China Sunergy | SST275-72P | poly | 275 | 241.6 | +/-3 | 3 | -3 | 13.197 | 14.2 | 35.2 | 7.82 | 43.8 | 8.48 | -0.408% | -0.292% | 0.045 | 45 | 15 | yes | N/A | silver | white | 76.98 | 38.98 | 1.97 | 20.8381 | 52.4 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST280-72M-BB | mono | 280 | 243.4 | +/-3 | 3 | -3 | 13.437 | 14.46 | 35.6 | 7.89 | 44.3 | 8.53 | -0.423% | -0.307% | 0.039 | 45 | 15 | yes | N/A | black | black | 76.98 | 38.98 | 1.97 | 20.8381 | 52.4 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST280-72P | poly | 280 | 246.1 | +/-3 | 3 | -3 | 13.437 | 14.46 | 35.3 | 7.94 | 44 | 8.58 | -0.408% | -0.292% | 0.045 | 45 | 15 | yes | N/A | silver | white | 76.98 | 38.98 | 1.97 | 20.8381 | 52.4 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST285-72M-BB | mono | 285 | 247.9 | +/-3 | 3 | -3 | 13.6769 | 14.46 | 35.7 | 7.99 | 44.4 | 8.6 | -0.423% | -0.307% | 0.039 | 45 | 15 | yes | N/A | black | black | 76.98 | 38.98 | 1.97 | 20.8381 | 52.4 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST285-72P | poly | 285 | 250.6 | +/-3 | 3 | -3 | 13.6769 | 14.46 | 35.4 | 8.05 | 44.1 | 8.67 | -0.408% | -0.292% | 0.045 | 45 | 15 | yes | N/A | silver | white | 76.98 | 38.98 | 1.97 | 20.8381 | 52.4 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST290-72M | mono | 290 | 253.5 | +/-3 | 3 | -3 | 13.9168 | 14.98 | 35.8 | 8.11 | 44.5 | 8.67 | -0.423% | -0.307% | 0.039 | 45 | 15 | yes | N/A | silver | white | 76.98 | 38.98 | 1.97 | 20.8381 | 52.4 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST290-72M-BB | mono | 290 | 252.4 | +/-3 | 3 | -3 | 13.9168 | 14.98 | 35.8 | 8.11 | 44.5 | 8.67 | -0.423% | -0.307% | 0.039 | 45 | 15 | yes | N/A | black | black | 76.98 | 38.98 | 1.97 | 20.8381 | 52.4 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST290-72P | poly | 295 | 255.2 | +/-3 | 3 | -3 | 14.1568 | 14.98 | 35.6 | 8.15 | 44.3 | 8.75 | -0.408% | -0.292% | 0.045 | 45 | 15 | yes | N/A | silver | white | 76.98 | 38.98 | 1.97 | 20.8381 | 52.4 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST295-72M | mono | 295 | 258.1 | +/-3 | 3 | -3 | 14.1568 | 15.24 | 35.9 | 8.22 | 44.6 | 8.73 | -0.423% | -0.307% | 0.039 | 45 | 15 | yes | N/A | silver | white | 76.98 | 38.98 | 1.97 | 20.8381 | 52.4 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST295-72M-BB | mono | 295 | 256.9 | +/-3 | 3 | -3 | 14.1568 | 15.24 | 35.9 | 8.22 | 44.6 | 8.73 | -0.423% | -0.307% | 0.039 | 45 | 15 | yes | N/A | black | black | 76.98 | 38.98 | 1.97 | 20.8381 | 52.4 | 5 |  | Check |  | China_Sunergy
China Sunergy | SST300-72M | mono | 300 | 262.6 | +/-3 | 3 | -3 | 14.3967 | 15.49 | 36.1 | 8.32 | 44.8 | 8.8 | -0.423% | -0.307% | 0.039 | 45 | 15 | yes | N/A | silver | white | 76.98 | 38.98 | 1.97 | 20.8381 | 52.4 | 5 |  | Check |  | China_Sunergy
China Sunergy | CSUN255-60P | Poly | 255 | 225.5 | +3/-0 | 3 | 0 |  |  | 30.1 | 8.47 | 37.5 | 8.88 | -0.408% | -0.292% |  |  | 20 |  |  |  |  | 64.54 | 38.96 | 1.38 |  | 40.34 |  |  | 1000 | 2018-06-29 | China_Sunergy
China Sunergy | CSUN260-60P | poly | 260 | 230.1 | +3/-0 | 3 | 0 |  |  | 30.3 | 8.58 | 37.7 | 8.95 | -0.408% | -0.292% |  |  | 20 |  |  |  |  | 64.54 | 38.96 | 1.38 |  | 40.34 |  |  | 1000 | 2018-06-29 | China_Sunergy
China Sunergy | CSUN265-60P | Poly | 265 | 238.9 | +3/-0 | 3 | 0 |  |  | 30.5 | 8.69 | 37.8 | 9.01 | -0.408% | -0.292% |  |  | 20 |  |  |  |  | 64.54 | 38.96 | 1.38 |  | 40.34 |  |  | 1000 | 2018-06-29 | China_Sunergy
China Sunergy | CSUN270-60P | Poly | 270 | 243.6 | +3/-0 | 3 | 0 |  |  | 30.7 | 8.8 | 37.9 | 9.08 | -0.408% | -0.292% |  |  | 20 |  |  |  |  | 64.54 | 38.96 | 1.38 |  | 40.34 |  |  | 1000 | 2018-06-29 | China_Sunergy
China Sunergy | CSUN275-60P | Poly | 275 | 248.2 | +3/-0 | 3 | 0 |  |  | 30.9 | 8.91 | 38 | 9.15 | -0.408% | -0.292% |  |  | 20 |  |  |  |  | 64.54 | 38.96 | 1.38 |  | 40.34 |  |  | 1000 | 2018-06-29 | China_Sunergy
China Sunergy | CSUN 265-60M | mono | 265 | 237.8 | +3/-0 | 3 | 0 |  |  | 31 | 8.55 | 38.2 | 8.98 | -0.42% | -0.31% |  |  | 20 | [11 empty] | Check | 2015-12-02 | China_Sunergy
China Sunergy | CSUN 270-60M | mono | 270 | 242.5 | +3/-0 | 3 | 0 |  |  | 31.2 | 8.65 | 38.3 | 9.07 | -0.42% | -0.31% |  |  | 20 | [11 empty] | Check | 2015-12-02 | China_Sunergy
China Sunergy | CSUN 275-60M | mono | 275 | 247.1 | +3/-0 | 3 | 0 |  |  | 31.3 | 8.79 | 38.5 | 9.13 | -0.42% | -0.31% |  |  | 20 | [11 empty] | Check | 2015-12-02 | China_Sunergy
China Sunergy | CSUN 280-60M | mono | 280 | 251.7 | +3/-0 | 3 | 0 |  |  | 31.5 | 8.99 | 39.1 | 9.33 | -0.423% | -0.307% |  |  | 20 | [11 empty] | Check | 2017-02-14 | China_Sunergy
China Sunergy | CSUN285-60M | mono | 285 | 257.1 | +3/-0 | 3 | 0 |  |  | 31.7 | 9.04 | 39.3 | 9.4 | -0.423% | -0.307% |  |  | 20 | [11 empty] | Check | 2017-02-14 | China_Sunergy
China Sunergy | CSUN290-60M | Mono | 290 | 261.8 | +3/-0 | 3 | 0 |  |  | 31.9 | 9.1 | 39.1 | 9.47 | -0.423% | -0.307% |  |  | 20 | [11 empty] | Check | 2017-02-14 | China_Sunergy
China Sunergy | CSUN 290-72P | poly | 290 | 261.4 | +3/-0 | 3 | 0 |  |  | 35.6 | 8.15 | 44.3 | 8.75 | -0.41% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2015-12-02 | China_Sunergy
China Sunergy | CSUN 295-72P | poly | 295 | 266.1 | +3/-0 | 3 | 0 |  |  | 35.7 | 8.26 | 44.4 | 8.83 | -0.41% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2015-12-02 | China_Sunergy
China Sunergy | CSUN 300-72P | poly | 300 | 270.8 | +3/-0 | 3 | 0 |  |  | 35.8 | 8.37 | 44.5 | 8.91 | -0.41% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2015-12-02 | China_Sunergy
China Sunergy | CSUN 305-72P | poly | 305 | 275.4 | +3/-0 | 3 | 0 |  |  | 36.7 | 8.31 | 45.2 | 8.87 | -0.408% | -0.292% |  |  | 20 | [11 empty] | 1000 | 2018-06-01 | China_Sunergy
China Sunergy | CSUN 310-72P | mono | 310 | 280.1 | +3/-0 | 3 | 0 |  |  | 37 | 8.39 | 45.6 | 8.91 | -0.408% | -0.292% |  |  | 20 |  |  |  |  | 77 | 39 | 1.57 |  | 48.5 |  |  | 1000 | 2018-06-01 | China_Sunergy
China Sunergy | CSUN 315-72P | mono | 315 | 284.8 | +3/-0 | 3 | 0 |  |  | 37.1 | 8.48 | 45.7 | 9.01 | -0.408% | -0.292% |  |  | 20 |  |  |  |  | 77 | 39 | 1.57 |  | 48.5 |  |  | 1000 | 2018-06-01 | China_Sunergy
China Sunergy | CSUN 320-72P | mono | 320 | 288.6 | +3/-0 | 3 | 0 |  |  | 37.3 | 8.57 | 45.9 | 9.1 | -0.408% | -0.292% |  |  | 20 |  |  |  |  | 77 | 39 | 1.57 |  | 48.5 |  |  | 1000 | 2018-06-01 | China_Sunergy
China Sunergy | CSUN 325-72P | mono | 325 | 291.1 | +3/-0 | 3 | 0 |  |  | 37.6 | 8.66 | 46 | 9.19 | -0.408% | -0.292% |  |  | 20 |  |  |  |  | 77 | 39 | 1.57 |  | 48.5 |  |  | 1000 | 2018-06-01 | China_Sunergy
China Sunergy | CSUN 305-72M | mono | 305 | 273.4 | +3/-0 | 3 | 0 |  |  | 37.2 | 8.47 | 45.8 | 8.92 | -0.423% | -0.307% |  |  | 20 | [11 empty] | Check | 2017-02-14 | China_Sunergy
China Sunergy | CSUN 310-72M | mono | 310 | 278.1 | +3/-0 | 3 | 0 |  |  | 37.2 | 8.47 | 45.8 | 8.92 | -0.423% | -0.307% |  |  | 20 | [11 empty] | Check | 2017-02-14 | China_Sunergy
China Sunergy | CSUN 315-72M | mono | 315 | 282.7 | +3/-0 | 3 | 0 |  |  | 37.2 | 8.47 | 45.8 | 8.92 | -0.423% | -0.307% |  |  | 20 | [11 empty] | Check | 2017-02-14 | China_Sunergy
China Sunergy | CSUN 320-72M | mono | 320 | 278.3 | +3/-0 | 3 | 0 |  |  | 37.4 | 8.56 | 45.9 | 9.01 | -0.423% | -0.307% |  |  | 20 | [11 empty] | Check | 2017-02-14 | China_Sunergy
China Sunergy | CSUN 325-72M | mono | 325 | 291.9 | +3/-0 | 3 | 0 |  |  | 37.7 | 8.62 | 46 | 9.12 | -0.423% | -0.307% |  |  | 20 |  |  |  |  | 76.98 | 38.96 | 1.97 |  | 49.2 |  |  | 1000 | 2018-06-29 | China_Sunergy
China Sunergy | CSUN 330-72M | mono | 330 | 296.6 | +3/-0 | 3 | 0 |  |  | 37.9 | 8.72 | 46.1 | 9.23 | -0.423% | -0.307% |  |  | 20 |  |  |  |  | 76.98 | 38.96 | 1.97 |  | 49.2 |  |  | 1000 | 2018-06-29 | China_Sunergy
China Sunergy | CSUN 335-72M | mono | 335 | 302.1 | +3/-0 | 3 | 0 |  |  | 38.1 | 8.79 | 46.3 | 9.32 | -0.423% | -0.307% |  |  | 20 |  |  |  |  | 76.98 | 38.96 | 1.97 |  | 49.2 |  |  | 1000 | 2018-06-29 | China_Sunergy
China Sunergy | CSUN 340-72M | mono | 340 | 306.7 | +3/-0 | 3 | 0 |  |  | 38.3 | 8.89 | 46.5 | 9.41 | -0.423% | -0.307% |  |  | 20 |  |  |  |  | 76.98 | 38.96 | 1.97 |  | 49.2 |  |  | 1000 | 2018-06-29 | China_Sunergy
China Sunergy | CSUN 345-72M | mono | 345 | 311.4 | +3/-0 | 3 | 0 |  |  | 38 | 9.09 | 46.3 | 9.2 | -0.423% | -0.307% |  |  | 20 |  |  |  |  | 76.98 | 38.96 | 1.97 |  | 49.2 |  |  | 1000 | 2018-06-29 | China_Sunergy
China Sunergy | QSAR 305-72M | mono | 305 |  | +3/-0 | 3 | 0 |  |  | 36.9 | 8.27 | 45.6 | 8.79 | -0.42% | -0.31% |  |  | 20 | [11 empty] | Check | 2015-12-02 | China_Sunergy
China Sunergy | QSAR 310-72M | mono | 310 |  | +3/-0 | 3 | 0 |  |  | 37.1 | 8.36 | 45.7 | 8.86 | -0.42% | -0.31% |  |  | 20 | [11 empty] | Check | 2015-12-02 | China_Sunergy
China Sunergy | QSAR 315-72M | mono | 315 |  | +3/-0 | 3 | 0 |  |  | 37.2 | 8.47 | 45.8 | 8.92 | -0.42% | -0.31% |  |  | 20 | [11 empty] | Check | 2015-12-02 | China_Sunergy
China Sunergy | QSAR 320-72M | mono | 320 |  | +3/-0 | 3 | 0 |  |  | 37.4 | 8.56 | 45.9 | 9.01 | -0.42% | -0.31% |  |  | 20 | [11 empty] | Check | 2015-12-02 | China_Sunergy
China Sunergy | QSAR 325-72M | mono | 325 |  | +3/-0 | 3 | 0 |  |  | 37.7 | 8.62 | 46 | 9.12 | -0.423% | -0.307% |  |  | 20 | [11 empty] | Check | 2017-02-14 | China_Sunergy
China Sunergy | CSUN330-72M(-DG) | Mono | 330 |  | +3/-0 | 3 | 0 |  |  | 37.3 | 8.85 | 46.1 | 9.2 | -0.423% | -0.307% |  |  | 20 | [11 empty] | Check | 2017-02-16 | China_Sunergy
China Sunergy | CSUN335-72M(-DG) | mono | 335 |  | +3/-0 | 3 | 0 |  |  | 37.6 | 8.93 | 46.3 | 9.26 | -0.423% | -0.307% |  |  | 20 | [11 empty] | Check | 2017-02-16 | China_Sunergy
China Sunergy | CSUN340-72M(-DG) | mono | 340 |  | +3/-0 | 3 | 0 |  |  | 37.8 | 9.01 | 46.5 | 9.32 | -0.423% | -0.307% |  |  | 20 | [11 empty] | Check | 2017-02-16 | China_Sunergy
China Sunergy | CSUN345-72M(-DG) | mono | 345 |  | +3/-0 | 3 | 0 |  |  | 38 | 9.09 | 46.7 | 9.38 | -0.423% | -0.307% |  |  | 20 | [11 empty] | Check | 2017-02-16 | China_Sunergy
Conergy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Conergy
Conergy | Conergy Black 225PA | poly | 225 | 201.8 | +/-3 | 3 | -3 | 12.6513 | 13.51 | 29.9 | 7.53 | 36.7 | 8.18 | -0.45% | -0.32% | 0.04 | 45.9 | 15 | yes | MC4 | black | black | 65 | 39.4 | 2 | 17.7847 | 48.5 | 5 |  | Check |  | Conergy
Conergy | Conergy Black 230PA | poly | 230 | 206.4 | +/-3 | 3 | -3 | 12.9324 | 13.9 | 30 | 7.67 | 36.8 | 8.34 | -0.45% | -0.32% | 0.04 | 45.9 | 15 | yes | MC4 | black | black | 65 | 39.4 | 2 | 17.7847 | 48.5 | 5 |  | Check |  | Conergy
Conergy | Conergy P 180M |  | 180 |  | +3/-0 | 3 | 0 |  |  | 36 | 5 | 45 | 5.2 | -0.44% | -0.33% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | Conergy
Conergy | Conergy P 185M | mono | 185 | 165.6 | +/-3 | 3 | -3 | 13.4684 | 14.5 | 36.1 | 5.12 | 45.3 | 5.23 | -0.44% | -0.33% | 0.03 | 45.9 | 10 | yes | MC4 | silver | white | 62.2 | 31.8 | 1.6 | 13.7358 | 33 | 5 |  | Check |  | Conergy
Conergy | Conergy P 230PA | poly | 230 | 207.6 | +/-3 | 3 | -3 | 12.9324 | 13.9 | 30 | 7.67 | 36.8 | 8.34 | -0.45% | -0.32% | 0.04 | 45.3 | 15 | yes | MC4 | silver | white | 65 | 39.4 | 2 | 17.7847 | 48.5 | 5 |  | Check |  | Conergy
Conergy | Conergy P 235PA | poly | 235 | 212.2 | +/-3 | 3 | -3 | 13.2136 | 14.2 | 30.01 | 7.81 | 36.8 | 8.44 | -0.45% | -0.32% | 0.04 | 45.3 | 15 | yes | MC4 | silver | white | 65 | 39.4 | 2 | 17.7847 | 48.5 | 5 |  | Check |  | Conergy
Conergy | Conergy PowerPlus 215P |  | 215 |  | +2.5/-0 | 2.5 | 0 |  |  | 28.8 | 7.54 | 36 | 8.04 | -0.45% | -0.34% |  |  | 20 | [7 empty] | 0 |  |  |  | Check |  | Conergy
Conergy | Conergy PowerPlus 220P | poly | 220 | 200.5 | +2.5/-0 | 2.5 | 0 | 12.5615 | 13.51 | 29.01 | 7.65 | 36.23 | 8.15 | -0.45% | -0.34% | 0.05 | 44.3 | 20 | yes | MC4 | black | white | 65 | 38.8 | 1.8 | 17.5139 | 48.5 | 5 |  | Check |  | Conergy
Conergy | Conergy PowerPlus 225P | poly | 225 | 205.2 | +2.5/-0 | 2.5 | 0 | 12.8469 | 13.82 | 29.23 | 7.74 | 36.43 | 8.24 | -0.45% | -0.34% | 0.05 | 44.3 | 20 | yes | MC4 | black | white | 65 | 38.8 | 1.8 | 17.5139 | 48.5 | 5 |  | Check |  | Conergy
Conergy | PE Noir 245M | mono | 245 |  | +2/-0 | 2 | 0 |  |  | 30.03 | 8.16 | 37.54 | 8.68 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE Noir 250M | mono | 250 |  | +2/-0 | 2 | 0 |  |  | 30.31 | 8.25 | 37.72 | 8.76 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE Noir 255M | mono | 255 |  | +2/-0 | 2 | 0 |  |  | 30.58 | 8.34 | 37.9 | 8.84 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE Noir 260M | mono | 260 |  | +2/-0 | 2 | 0 |  |  | 30.81 | 8.44 | 38.08 | 8.92 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE Noir 265M | mono | 265 |  | +2/-0 | 2 | 0 |  |  | 31.11 | 8.52 | 38.26 | 9 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PowerPlus 245P | poly | 245 |  | +3/-0 | 3 | 0 |  |  | 30.12 | 8.2 | 36.78 | 8.68 | -0.42% | -0.32% |  |  | 20 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PowerPlus 250P | poly | 250 |  | +3/-0 | 3 | 0 |  |  | 30.38 | 8.29 | 37.12 | 8.76 | -0.42% | -0.32% |  |  | 20 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PowerPlus 255P | poly | 255 |  | +3/-0 | 3 | 0 |  |  | 30.64 | 8.39 | 37.45 | 8.85 | -0.42% | -0.32% |  |  | 20 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PowerPlus 260P | poly | 260 |  | +3/-0 | 3 | 0 |  |  | 30.9 | 8.48 | 37.78 | 8.93 | -0.42% | -0.32% |  |  | 20 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PowerPlus 265P | poly | 265 |  | +3/-0 | 3 | 0 |  |  | 31.16 | 8.57 | 38.12 | 9.01 | -0.42% | -0.32% |  |  | 20 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE265M-R | mono | 265 |  | +2/-0 | 2 | 0 |  |  | 30.78 | 8.61 | 38.52 | 9.13 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE 270M-R | mono | 270 |  | +2/-0 | 2 | 0 |  |  | 31.08 | 8.69 | 38.71 | 9.21 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE 275M-R | mono | 275 |  | +2/-0 | 2 | 0 |  |  | 31.36 | 8.77 | 38.89 | 9.3 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE 280M-R | mono | 280 |  | +2/-0 | 2 | 0 |  |  | 31.64 | 8.85 | 39.07 | 9.39 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE 275M-L-PR | mono | 275 |  | +2/-0 | 2 | 0 |  |  | 31.51 | 8.72 | 38.86 | 9.27 | -0.39% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE 280M-L-PR | mono | 280 |  | +1.5/-0 | 1.5 | 0 |  |  | 31.68 | 8.84 | 39.05 | 9.36 | -0.39% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE 285M-L-PR | mono | 285 |  | +1.5/-0 | 1.5 | 0 |  |  | 31.85 | 8.97 | 39.25 | 9.45 | -0.39% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE 290M-L-PR | mono | 290 |  | +1.5/-0 | 1.5 | 0 |  |  | 32.07 | 9.11 | 39.46 | 9.56 | -0.39% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE 295M-L-PR | mono | 295 |  | +1.5/-0 | 1.5 | 0 |  |  | 32.29 | 9.23 | 39.64 | 9.67 | -0.39% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE 295P | poly | 295 |  | +3/-0 | 3 | 0 |  |  | 36.25 | 8.14 | 45 | 8.65 | -0.43% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE 300P | poly | 300 |  | +3/-0 | 3 | 0 |  |  | 36.41 | 8.24 | 45.2 | 8.73 | -0.43% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE 305P | poly | 305 |  | +3/-0 | 3 | 0 |  |  | 36.71 | 8.31 | 45.35 | 8.79 | -0.43% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE 310P | poly | 310 |  | +3/-0 | 3 | 0 |  |  | 37 | 8.38 | 45.45 | 8.85 | -0.43% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
Conergy | PE 315P | poly | 315 |  | +3/-0 | 3 | 0 |  |  | 37.28 | 8.45 | 45.6 | 8.91 | -0.43% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Conergy
CSG PVTech | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | CSG_PVTech
CSG PVTech | CSG 220M2-30 | poly | 220 | 198.5 | +/-3 | 3 | -3 | 12.5609 | 13.5 | 29.9 | 7.36 | 36.5 | 7.8 | -0.48% | -0.34% | 0.02 | 47 | 15 | DNR | MC4 | silver | white | 64.57 | 39.06 | 1.77 | 17.5146 | 43.1 | 5 |  | Check |  | CSG_PVTech
CSG PVTech | CSG 225M2-30 | poly | 225 | 203.1 | +/-3 | 3 | -3 | 12.8464 | 13.8 | 30 | 7.5 | 36.7 | 8.12 | -0.48% | -0.34% | 0.02 | 47 | 15 | DNR | MC4 | silver | white | 64.57 | 39.06 | 1.77 | 17.5146 | 43.1 | 5 |  | Check |  | CSG_PVTech
CSG PVTech | CSG 230M2-30 | poly | 230 | 207.7 | +/-3 | 3 | -3 | 13.1319 | 14.1 | 30.2 | 7.62 | 36.9 | 8.22 | -0.48% | -0.34% | 0.02 | 47 | 15 | DNR | MC4 | silver | white | 64.57 | 39.06 | 1.77 | 17.5146 | 43.1 | 5 |  | Check |  | CSG_PVTech
CSG PVTech | CSG 270M2-36 | poly | 270 | 242.7 | +/-3 | 3 | -3 | 12.9255 | 13.9 | 36 | 7.5 | 44 | 8.12 | -0.48% | -0.34% | 0.02 | 47 | 15 | DNR | MC4 | silver | white | 77.01 | 39.06 | 1.97 | 20.889 | 51.01 | 5 |  | Check |  | CSG_PVTech
CSG PVTech | CSG 275M2-36 | poly | 275 | 247.3 | +/-3 | 3 | -3 | 13.1648 | 14.2 | 36.1 | 7.62 | 44.2 | 8.22 | -0.48% | -0.34% | 0.02 | 47 | 15 | DNR | MC4 | silver | white | 77.01 | 39.06 | 1.97 | 20.889 | 51.01 | 5 |  | Check |  | CSG_PVTech
CSG PVTech | CSG 280M2-36 | poly | 280 | 252 | +/-3 | 3 | -3 | 13.4042 | 14.4 | 36.3 | 7.71 | 44.4 | 8.3 | -0.48% | -0.34% | 0.02 | 47 | 15 | DNR | MC4 | silver | white | 77.01 | 39.06 | 1.97 | 20.889 | 51.01 | 5 |  | Check |  | CSG_PVTech
CSG PVTech | CSG245M2 | poly | 245 |  | +6/-0 | 6 | 0 |  |  | 30.7 | 7.98 | 37.5 | 8.58 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG250M2 | poly | 250 |  | +6/-0 | 6 | 0 |  |  | 30.9 | 8.09 | 37.7 | 8.76 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG255M2 | poly | 255 |  | +6/-0 | 6 | 0 |  |  | 31.1 | 8.2 | 37.9 | 8.87 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG260M2 | poly | 260 |  | +6/-0 | 6 | 0 |  |  | 31.3 | 8.31 | 38.2 | 8.99 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG265M2 | poly | 265 |  | +6/-0 | 6 | 0 |  |  | 31.5 | 8.41 | 38.4 | 9.1 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG270M2 | poly | 270 |  | +6/-0 | 6 | 0 |  |  | 31.7 | 8.52 | 38.7 | 9.22 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG290M2 | poly | 290 |  | +6/-0 | 6 | 0 |  |  | 36.5 | 7.95 | 44.8 | 8.46 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG295M2 | poly | 295 |  | +6/-0 | 6 | 0 |  |  | 36.6 | 8.06 | 44.9 | 8.46 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG300M2 | poly | 300 |  | +6/-0 | 6 | 0 |  |  | 36.7 | 8.17 | 45 | 8.79 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG305M2 | poly | 305 |  | +6/-0 | 6 | 0 |  |  | 36.8 | 8.29 | 45.1 | 8.97 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG310M2 | poly | 310 |  | +6/-0 | 6 | 0 |  |  | 36.9 | 8.4 | 45.2 | 9.09 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG315M2 | poly | 315 |  | +6/-0 | 6 | 0 |  |  | 37.1 | 8.49 | 45.2 | 9.19 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG320M2 | poly | 320 |  | +6/-0 | 6 | 0 |  |  | 37.3 | 8.58 | 45.5 | 9.28 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG300M2-72 | poly | 300 |  | +6/-0 | 6 | 0 |  |  | 36.7 | 8.17 | 45 | 8.79 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2017-02-16 | CSG_PVTech
CSG PVTech | CSG305M2-72 | poly | 305 |  | +6/-0 | 6 | 0 |  |  | 36.8 | 8.29 | 45.1 | 8.97 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2017-02-16 | CSG_PVTech
CSG PVTech | CSG310M2-72 | poly | 310 |  | +6/-0 | 6 | 0 |  |  | 36.9 | 8.4 | 45.2 | 9.09 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2017-02-16 | CSG_PVTech
CSG PVTech | CSG315M2-72 | poly | 315 |  | +6/-0 | 6 | 0 |  |  | 37 | 8.51 | 45.3 | 9.21 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2017-02-16 | CSG_PVTech
CSG PVTech | CSG320M2-72 | poly | 320 |  | +6/-0 | 6 | 0 |  |  | 37.1 | 8.63 | 45.4 | 9.33 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2017-02-16 | CSG_PVTech
CSG PVTech | CSG325M2-72 | poly | 325 |  | +6/-0 | 6 | 0 |  |  | 37.2 | 8.74 | 45.5 | 9.46 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2017-02-16 | CSG_PVTech
CSG PVTech | CSG330M2-72 | Poly | 330 |  | +6/-0 | 6 | 0 |  |  | 37.3 | 8.84 | 45.6 | 9.55 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2017-02-16 | CSG_PVTech
CSG PVTech | CSG255S2 | mono | 255 |  | +6/-0 | 6 | 0 |  |  | 30.8 | 8.28 | 37.6 | 8.96 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG260S2 | mono | 260 |  | +6/-0 | 6 | 0 |  |  | 31 | 8.39 | 37.8 | 9.08 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG265S2 | mono | 265 |  | +6/-0 | 6 | 0 |  |  | 31.2 | 8.49 | 38.1 | 9.19 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG270S2 | mono | 270 |  | +6/-0 | 6 | 0 |  |  | 31.4 | 8.6 | 38.3 | 9.31 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG275S2 | mono | 275 |  | +6/-0 | 6 | 0 |  |  | 31.6 | 8.7 | 38.5 | 9.42 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG280S2 | mono | 280 |  | +6/-0 | 6 | 0 |  |  | 31.8 | 8.81 | 38.8 | 9.53 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG310S2-72 | mono | 310 |  | +6/-0 | 6 | 0 |  |  | 37.2 | 8.33 | 45.4 | 9.02 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG315S2-72 | mono | 315 |  | +6/-0 | 6 | 0 |  |  | 37.4 | 8.42 | 45.5 | 9.12 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG320S2-72 | mono | 320 |  | +6/-0 | 6 | 0 |  |  | 37.6 | 8.51 | 45.8 | 9.21 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG325S2-72 | mono | 325 |  | +6/-0 | 6 | 0 |  |  | 37.8 | 8.6 | 46.1 | 9.31 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG330S2-72 | mono | 330 |  | +6/-0 | 6 | 0 |  |  | 38 | 8.68 | 46.3 | 9.4 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
CSG PVTech | CSG335S2-72 | mono | 335 |  | +6/-0 | 6 | 0 |  |  | 38.2 | 8.77 | 46.5 | 9.49 | -0.45% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-12-02 | CSG_PVTech
Dahai | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Dahai
Dahai | DHM60-250M | mono | 250 |  | +3/-0 | 3 | 0 |  |  | 30.8 | 8.11 | 37.4 | 8.8 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Dahai
Dahai | DHM60-255M | mono | 255 |  | +3/-0 | 3 | 0 |  |  | 31.25 | 8.16 | 37.6 | 8.91 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Dahai
Dahai | DHM60-260M | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 31.7 | 8.2 | 37.8 | 9.02 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Dahai
Dahai | DHP60-250 | poly | 250 |  | +3/-0 | 3 | 0 |  |  | 31.4 | 7.96 | 37.5 | 8.62 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Dahai
Dahai | DHP60-255 | poly | 255 |  | +3/-0 | 3 | 0 |  |  | 31.8 | 8.02 | 37.65 | 8.68 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Dahai
Dahai | DHP60-260 | poly | 260 |  | +3/-0 | 3 | 0 |  |  | 32.2 | 8.07 | 37.8 | 8.74 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Dahai
Dahai | DHP72-280 | poly | 280 |  | +3/-0 | 3 | 0 |  |  | 35.76 | 7.83 | 44.8 | 8.12 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Dahai
Dahai | DHP72-285 | poly | 285 |  | +3/-0 | 3 | 0 |  |  | 36.12 | 7.89 | 45 | 8.16 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Dahai
Dahai | DHP72-290 | poly | 290 |  | +3/-0 | 3 | 0 |  |  | 36.48 | 7.95 | 45.08 | 8.21 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Dahai
Dahai | DHP72-295 | poly | 295 |  | +3/-0 | 3 | 0 |  |  | 36.97 | 7.98 | 45.16 | 8.25 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Dahai
Dahai | DHP72-300 | poly | 300 |  | +3/-0 | 3 | 0 |  |  | 37.31 | 8.04 | 45.24 | 8.29 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Dahai
Dahai | DHP72-305 | poly | 305 |  | +3/-0 | 3 | 0 |  |  | 37.7 | 8.09 | 45.31 | 8.34 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Dahai
Dahai | DHP72-310 | poly | 310 |  | +3/-0 | 3 | 0 |  |  | 38.08 | 8.14 | 45.37 | 8.4 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Dahai
Day4 Energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Day4_Energy
Day4 Energy | Day4 36MC 115 | poly | 115 |  | +3.5/-3.5 | 3.5 | -3.5 | 10.7925 | 11.6 | 16.8 | 6.89 | 20.98 | 7.6 | -0.48% | -0.5243% |  |  | 15 |  | Solarlok |  |  | 57.697 | 26.594 | 1.378 | 10.6555 | 28.44 | 5 |  | Check |  | Day4_Energy
Day4 Energy | Day4 36MC 120 | poly | 120 |  | +3.5/-3.5 | 3.5 | -3.5 | 11.2618 | 12.1 | 16.95 | 7.08 | 21.23 | 7.7 | -0.48% | -0.5181% |  |  | 15 |  | Solarlok |  |  | 57.697 | 26.594 | 1.378 | 10.6555 | 28.44 | 5 |  | Check |  | Day4_Energy
Day4 Energy | Day4 36MC 125 | poly | 125 |  | +3.5/-3.5 | 3.5 | -3.5 | 11.731 | 12.6 | 17.21 | 7.3 | 21.52 | 7.9 | -0.48% | -0.5112% |  |  | 15 |  | Solarlok |  |  | 57.697 | 26.594 | 1.378 | 10.6555 | 28.44 | 5 |  | Check |  | Day4_Energy
Day4 Energy | Day4 36MC 130 | poly | 130 |  | +3.5/-3.5 | 3.5 | -3.5 | 12.2003 | 13.1 | 17.55 | 7.46 | 21.9 | 8.05 | -0.48% | -0.5023% |  |  | 15 |  | Solarlok |  |  | 57.697 | 26.594 | 1.378 | 10.6555 | 28.44 | 5 |  | Check |  | Day4_Energy
Day4 Energy | Day4 36MC 135 | poly | 135 |  | +3.5/-3.5 | 3.5 | -3.5 | 12.6695 | 13.6 | 17.78 | 7.6 | 22.05 | 8.1 | -0.48% | -0.4989% |  |  | 15 |  | Solarlok |  |  | 57.697 | 26.594 | 1.378 | 10.6555 | 28.44 | 5 |  | Check |  | Day4_Energy
Day4 Energy | Day4 36MC 140 | poly | 140 |  | +3.5/-3.5 | 3.5 | -3.5 | 13.1387 | 14.1 | 17.98 | 7.79 | 22.28 | 8.2 | -0.48% | -0.4937% |  |  | 15 |  | Solarlok |  |  | 57.697 | 26.594 | 1.378 | 10.6555 | 28.44 | 5 |  | Check |  | Day4_Energy
Day4 Energy | Day4 36MC 145 | poly | 145 |  | +3.5/-3.5 | 3.5 | -3.5 | 13.608 | 14.6 | 18.24 | 7.95 | 22.57 | 8.3 | -0.48% | -0.4874% |  |  | 15 |  | Solarlok |  |  | 57.697 | 26.594 | 1.378 | 10.6555 | 28.44 | 5 |  | Check |  | Day4_Energy
Day4 Energy | Day4 48MC 160 | poly | 160 |  | +3.5/-3.5 | 3.5 | -3.5 | 11.4772 | 12.35 | 22.6 | 7.08 | 28.3 | 7.7 | -0.48% | -0.3887% |  |  | 15 |  | Solarlok |  |  | 51.46 | 39.01 | 1.38 | 13.9407 | 38.28 | 5 |  | Check |  | Day4_Energy
Day4 Energy | Day4 48MC 165 | poly | 165 |  | +3.5/-3.5 | 3.5 | -3.5 | 11.8359 | 12.74 | 22.95 | 7.19 | 28.6 | 7.8 | -0.48% | -0.3846% |  |  | 15 |  | Solarlok |  |  | 51.46 | 39.01 | 1.38 | 13.9407 | 38.28 | 5 |  | Check |  | Day4_Energy
Day4 Energy | Day4 48MC 170 | poly | 170 |  | +3.5/-3.5 | 3.5 | -3.5 | 12.1945 | 13.13 | 23.04 | 7.38 | 28.8 | 7.9 | -0.48% | -0.3819% |  |  | 15 |  | Solarlok |  |  | 51.46 | 39.01 | 1.38 | 13.9407 | 38.28 | 5 |  | Check |  | Day4_Energy
Day4 Energy | Day4 48MC 175 | poly | 175 | 157.1 | +/-3.5 | 3.5 | -3.5 | 12.5532 | 13.5 | 23.4 | 7.48 | 29.2 | 8.05 | -0.44% | -0.33% | 0.03 | 42.9 | 15 | yes | tyco | silver | white | 51.46 | 39.01 | 1.38 | 13.9407 | 35.2 | 10 |  | Check |  | Day4_Energy
Day4 Energy | Day4 48MC 180 | poly | 180 | 161.7 | +/-3.5 | 3.5 | -3.5 | 12.9119 | 13.9 | 23.7 | 7.6 | 29.4 | 8.1 | -0.44% | -0.33% | 0.03 | 42.9 | 15 | yes | tyco | silver | white | 51.46 | 39.01 | 1.38 | 13.9407 | 35.2 | 10 |  | Check |  | Day4_Energy
Day4 Energy | Day4 48MC 185 | poly | 185 | 166.3 | +/-3.5 | 3.5 | -3.5 | 13.2705 | 14.3 | 23.8 | 7.77 | 29.5 | 8.2 | -0.44% | -0.33% | 0.03 | 42.9 | 15 | yes | tyco | silver | white | 51.46 | 39.01 | 1.38 | 13.9407 | 35.2 | 10 |  | Check |  | Day4_Energy
Day4 Energy | Day4 48MC 190 | poly | 190 | 170.9 | +/-3.5 | 3.5 | -3.5 | 13.6292 | 14.7 | 24 | 7.92 | 29.7 | 8.3 | -0.44% | -0.33% | 0.03 | 42.9 | 15 | yes | tyco | silver | white | 51.46 | 39.01 | 1.38 | 13.9407 | 35.2 | 10 |  | Check |  | Day4_Energy
Day4 Energy | Day4 48MC-S 160 | poly | 160 |  | +/-3.5 | 3.5 | -3.5 |  |  | 22.6 | 7.08 | 28.3 | 7.7 | -0.44% | -0.3534% |  |  | 15 | [11 empty] | 600 |  | Day4_Energy
Day4 Energy | Day4 48MC-S 165 | poly | 165 |  | +/-3.5 | 3.5 | -3.5 |  |  | 22.95 | 7.19 | 28.6 | 7.8 | -0.44% | -0.3497% |  |  | 15 | [11 empty] | 600 |  | Day4_Energy
Day4 Energy | Day4 48MC-S 170 | poly | 170 |  | +/-3.5 | 3.5 | -3.5 |  |  | 23.04 | 7.38 | 28.8 | 7.9 | -0.44% | -0.3472% |  |  | 15 | [11 empty] | 600 |  | Day4_Energy
Day4 Energy | Day4 48MC-S 175 | poly | 175 |  | +/-3.5 | 3.5 | -3.5 |  |  | 23.4 | 7.48 | 29.2 | 8.05 | -0.44% | -0.3425% |  |  | 15 | [11 empty] | 600 |  | Day4_Energy
Day4 Energy | Day4 48MC-S 180 | poly | 180 |  | +/-3.5 | 3.5 | -3.5 |  |  | 23.7 | 7.6 | 29.4 | 8.1 | -0.44% | -0.3401% |  |  | 15 | [11 empty] | 600 |  | Day4_Energy
Day4 Energy | Day4 48MC-S 185 | poly | 185 |  | +/-3.5 | 3.5 | -3.5 |  |  | 23.82 | 7.77 | 29.51 | 8.2 | -0.44% | -0.3389% |  |  | 15 | [11 empty] | 600 |  | Day4_Energy
Day4 Energy | Day4 48MC-S 190 | poly | 190 |  | +/-3.5 | 3.5 | -3.5 |  |  | 24 | 7.92 | 29.7 | 8.3 | -0.44% | -0.3367% |  |  | 15 | [11 empty] | 600 |  | Day4_Energy
Day4 Energy | Day4 48MC-S 195 | poly | 195 |  | +/-3.5 | 3.5 | -3.5 |  |  | 24.2 | 8.06 | 29.9 | 8.4 | -0.44% | -0.3344% |  |  | 15 | [11 empty] | 600 |  | Day4_Energy
Day4 Energy | Day4 48MC-S 200 | poly | 200 |  | +/-3.5 | 3.5 | -3.5 |  |  | 24.38 | 8.21 | 30.14 | 8.55 | -0.44% | -0.3318% |  |  | 15 | [11 empty] | 600 |  | Day4_Energy
Day4 Energy | Day4 60MC-I 225 | poly | 225 | 201.6 | +/-3.5 | 3.5 | -3.5 | 12.5061 | DNR | 29.47 | 7.62 | 36.48 | 8.12 | -0.44% | -0.27% | 0.03 | 42.9 | 15 | DNR | MC4 | silver | white | 64.96 | 39.882 | 1.591 | 17.9912 | 42.3 | 10 |  | Check |  | Day4_Energy
Day4 Energy | Day4 60MC-I 230 | poly | 230 | 206.2 | +/-3.5 | 3.5 | -3.5 | 12.784 | DNR | 29.52 | 7.8 | 36.71 | 8.32 | -0.44% | -0.27% | 0.03 | 42.9 | 15 | DNR | MC4 | silver | white | 64.96 | 39.882 | 1.591 | 17.9912 | 42.3 | 10 |  | Check |  | Day4_Energy
Day4 Energy | Day4 60MC-I 235 | poly | 235 | 210.8 | +/-3.5 | 3.5 | -3.5 | 13.0619 | DNR | 29.77 | 7.89 | 36.9 | 8.42 | -0.44% | -0.27% | 0.03 | 42.9 | 15 | DNR | MC4 | silver | white | 64.96 | 39.882 | 1.591 | 17.9912 | 42.3 | 10 |  | Check |  | Day4_Energy
Day4 Energy | Day4 60MC-I 240 | poly | 240 | 215.4 | +/-3.5 | 3.5 | -3.5 | 13.3398 | DNR | 30.03 | 7.98 | 37.12 | 8.54 | -0.44% | -0.27% | 0.03 | 42.9 | 15 | DNR | MC4 | silver | white | 64.96 | 39.882 | 1.591 | 17.9912 | 42.3 | 10 |  | Check |  | Day4_Energy
Day4 Energy | Day4 60MC-I 245 | poly | 245 | 220 | +/-3.5 | 3.5 | -3.5 | 13.6178 | DNR | 30.29 | 8.08 | 37.32 | 8.58 | -0.44% | -0.27% | 0.03 | 42.9 | 15 | DNR | MC4 | silver | white | 64.96 | 39.882 | 1.591 | 17.9912 | 42.3 | 10 |  | Check |  | Day4_Energy
Day4 Energy | Day4 60MC-I 250 | poly | 250 | 224.6 | +/-3.5 | 3.5 | -3.5 | 13.8957 | DNR | 30.55 | 8.17 | 37.54 | 8.64 | -0.44% | -0.27% | 0.03 | 42.9 | 15 | DNR | MC4 | silver | white | 64.96 | 39.882 | 1.591 | 17.9912 | 42.3 | 10 |  | Check |  | Day4_Energy
Day4 Energy | D4-MC60-250 | poly | 250 |  | +5/-0 | 5 | 0 |  |  | 31.02 | 8.06 | 36.99 | 8.62 | -0.41% | -0.32% |  |  | 15 | [11 empty] | 1000 | 2018-01-30 | Day4_Energy
Day4 Energy | D4-MC60-255 | poly | 255 |  | +5/-0 | 5 | 0 |  |  | 31.18 | 8.18 | 37.07 | 8.75 | -0.41% | -0.32% | -0.32% |  | 15 | [11 empty] | 1000 | 2018-01-30 | Day4_Energy
Day4 Energy | D4-MC60-260 | poly | 260 |  | +5/-0 | 5 | 0 |  |  | 31.35 | 8.29 | 37.22 | 8.87 | -0.41% | -0.32% | -0.32% |  | 15 | [11 empty] | 1000 | 2018-01-30 | Day4_Energy
Day4 Energy | D4-MC60-265 | poly | 265 |  | +5/-0 | 5 | 0 |  |  | 31.48 | 8.42 | 37.38 | 8.98 | -0.41% | -0.32% | -0.32% |  | 15 | [11 empty] | 1000 | 2018-01-30 | Day4_Energy
Day4 Energy | D4-MC60-270 | poly | 270 |  | +5/-0 | 5 | 0 |  |  | 31.61 | 8.54 | 37.54 | 9.14 | -0.41% | -0.32% | -0.32% |  | 15 | [11 empty] | 1000 | 2018-01-30 | Day4_Energy
Day4 Energy | D4-MC60-275 | poly | 275 |  | +5/-0 | 5 | 0 |  |  | 31.74 | 8.66 | 37.7 | 9.27 | -0.41% | -0.32% | -0.32% |  | 15 | [11 empty] | 1000 | 2018-01-30 | Day4_Energy
Day4 Energy | D4-MC60-280 | poly | 280 |  | +5/-0 | 5 | 0 |  |  | 31.88 | 8.78 | 37.86 | 9.4 | -0.41% | -0.32% | -0.32% |  | 15 | [11 empty] | 1000 | 2018-01-30 | Day4_Energy
Day4 Energy | D4-MC60-285 | poly | 285 |  | +5/-0 | 5 | 0 |  |  | 32.03 | 8.9 | 38.02 | 9.53 | -0.41% | -0.32% | -0.32% |  | 15 | [11 empty] | 1000 | 2018-01-30 | Day4_Energy
Day4 Energy | D4-MN60-250 | mono | 250 |  | +5/-0 | 5 | 0 |  |  | 31.65 | 7.9 | 37.37 | 8.45 | -0.44% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Day4_Energy
Day4 Energy | D4-MN60-255 | mono | 255 |  | +5/-0 | 5 | 0 |  |  | 31.82 | 8.01 | 37.45 | 8.57 | -0.44% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Day4_Energy
Day4 Energy | D4-MN60-260 | mono | 260 |  | +5/-0 | 5 | 0 |  |  | 31.99 | 8.13 | 37.53 | 8.7 | -0.44% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Day4_Energy
Day4 Energy | D4-MN60-265 | mono | 265 |  | +5/-0 | 5 | 0 |  |  | 32.15 | 8.24 | 37.62 | 8.82 | -0.44% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Day4_Energy
Day4 Energy | D4-MN60-270 | mono | 270 |  | +5/-0 | 5 | 0 |  |  | 32.31 | 8.35 | 38 | 8.94 | -0.44% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Day4_Energy
Neo Solar Power/DelSolar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | DelSolar
Neo Solar Power/DelSolar | D6P210A3E | poly | 210 | 187.1 | +3/-0 | 3 | 0 | 12.1154 | 13 | 28.72 | 7.32 | 36.6 | 7.93 | -0.46% | -0.35% | 0.05 | 46 | 15 | yes | tyco | silver | white | 64 | 39 | 1.5 | 17.3333 | 44.1 | 5 |  | Check |  | DelSolar
Neo Solar Power/DelSolar | D6P215A3E | poly | 215 | 191.6 | +3/-0 | 3 | 0 | 12.4038 | 13.4 | 28.86 | 7.45 | 36.72 | 8 | -0.46% | -0.35% | 0.05 | 46 | 15 | yes | tyco | silver | white | 64 | 39 | 1.5 | 17.3333 | 44.1 | 5 |  | Check |  | DelSolar
Neo Solar Power/DelSolar | D6P215A3F | poly | 215 | 192 | +3/-0 | 3 | 0 | 12.3978 | 13.35 | 29.02 | 7.41 | 36.39 | 7.96 | -0.4631% | -0.3315% | 0.0443 | 43 | 15 | yes | tyco | silver/black | white | 64.13 | 38.94 | 1.78 | 17.3418 | 41.9 | 5 |  | Check |  | DelSolar
Neo Solar Power/DelSolar | D6P220A3E | poly | 220 | 196.2 | +3/-0 | 3 | 0 | 12.6923 | 13.6 | 29.2 | 7.54 | 36.9 | 8.13 | -0.46% | -0.35% | 0.05 | 46 | 15 | yes | tyco | silver | white | 64 | 39 | 1.5 | 17.3333 | 44.1 | 5 |  | Check |  | DelSolar
Neo Solar Power/DelSolar | D6P220A3F | poly | 220 | 196.5 | +3/-0 | 3 | 0 | 12.6861 | 13.66 | 29.11 | 7.56 | 36.57 | 8.1 | -0.46% | -0.3315% | 0.0443 | 43 | 15 | yes | tyco | silver/black | white | 64.13 | 38.94 | 1.78 | 17.3418 | 41.9 | 5 |  | Check |  | DelSolar
Neo Solar Power/DelSolar | D6P225A3E | poly | 225 | 200.8 | +3/-0 | 3 | 0 | 12.9808 | 14 | 29.34 | 7.67 | 37.08 | 8.27 | -0.46% | -0.35% | 0.05 | 46 | 15 | yes | tyco | silver | white | 64 | 39 | 1.5 | 17.3333 | 44.1 | 5 |  | Check |  | DelSolar
Neo Solar Power/DelSolar | D6P225A3F | poly | 225 | 201.1 | +3/-0 | 3 | 0 | 12.9744 | 13.97 | 29.19 | 7.71 | 36.75 | 8.21 | -0.4569% | -0.3315% | 0.0443 | 43 | 15 | yes | tyco | silver/black | white | 64.13 | 38.94 | 1.78 | 17.3418 | 41.9 | 5 |  | Check |  | DelSolar
Neo Solar Power/DelSolar | D6P230A3E | poly | 230 | 205.4 | +3/-0 | 3 | 0 | 13.2692 | 14.3 | 29.49 | 7.8 | 37.2 | 8.39 | -0.46% | -0.35% | 0.05 | 46 | 15 | yes | tyco | silver | white | 64 | 39 | 1.5 | 17.3333 | 44.1 | 5 |  | Check |  | DelSolar
Neo Solar Power/DelSolar | D6P230A3F | poly | 230 | 205.7 | +3/-0 | 3 | 0 | 13.2627 | 14.28 | 29.3 | 7.85 | 36.87 | 8.32 | -0.4538% | -0.3315% | 0.0443 | 43 | 15 | yes | tyco | silver/black | white | 64.13 | 38.94 | 1.78 | 17.3418 | 41.9 | 5 |  | Check |  | DelSolar
Neo Solar Power/DelSolar | D6P235A3F | poly | 235 | 210.3 | +3/-0 | 3 | 0 | 13.5511 | 14.59 | 29.34 | 8.01 | 37.06 | 8.45 | -0.4507% | -0.3315% | 0.0443 | 43 | 15 | yes | tyco | silver/black | white | 64.13 | 38.94 | 1.78 | 17.3418 | 41.9 | 5 |  | Check |  | DelSolar
Neo Solar Power/DelSolar | D6P240A3F | poly | 240 | 214.9 | +3/-0 | 3 | 0 | 13.8394 | 14.9 | 29.4 | 8.16 | 37.18 | 8.55 | -0.4476% | -0.3315% | 0.0443 | 43 | 15 | yes | tyco | silver/black | white | 64.13 | 38.94 | 1.78 | 17.3418 | 41.9 | 5 |  | Check |  | DelSolar
Neo Solar Power/DelSolar | D6P245A3F | poly | 245 | 219.5 | +3/-0 | 3 | 0 | 14.1277 | 15.21 | 29.56 | 8.29 | 37.31 | 8.67 | -0.4445% | -0.3315% | 0.0443 | 43 | 15 | yes | tyco | silver/black | white | 64.13 | 38.94 | 1.78 | 17.3418 | 41.9 | 5 |  | Check |  | DelSolar
Neo Solar Power/DelSolar | D6P-260-E3A | poly | 260 |  | +5/-0 | 5 | 0 |  |  | 30.73 | 8.47 | 37.67 | 8.87 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-265-E3A | poly | 265 |  | +5/-0 | 5 | 0 |  |  | 30.76 | 8.63 | 38.17 | 9.07 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-270-E3A | poly | 270 |  | +5/-0 | 5 | 0 |  |  | 30.85 | 8.77 | 38.39 | 9.19 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-275-E3A | poly | 275 |  | +5/-0 | 5 | 0 |  |  | 30.98 | 8.89 | 38.63 | 9.28 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-250-B3A | Poly | 250 |  | +5/-0 | 5 | 0 |  |  | 30.34 | 8.24 | 37.33 | 8.69 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-255-B3A | poly | 255 |  | +5/-0 | 5 | 0 |  |  | 30.64 | 8.32 | 37.5 | 8.76 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-260-B3A | poly | 260 |  | +5/-0 | 5 | 0 |  |  | 30.93 | 8.43 | 37.67 | 8.83 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-265-B3A | poly | 265 |  | +5/-0 | 5 | 0 |  |  | 30.97 | 8.58 | 38.17 | 9.02 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-270-B3A | Poly | 270 |  | +5/-0 | 5 | 0 |  |  | 31.04 | 8.73 | 38.39 | 9.15 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-275-E3A | mono | 275 |  | +5/-0 | 5 | 0 |  |  | 31.27 | 8.8 | 38.99 | 9.37 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-280-E3A | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 31.33 | 8.95 | 39.04 | 9.53 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-285-E3A | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 31.5 | 9.07 | 39.12 | 9.62 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-290-E3A | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 31.61 | 9.18 | 39.18 | 9.68 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-295-E3A | mono | 295 |  | +5/-0 | 5 | 0 |  |  | 31.86 | 9.26 | 39.27 | 9.73 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-300-E3A | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 32.09 | 9.35 | 39.39 | 9.78 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-305-E3A | mono | 305 |  | +5/-0 | 5 | 0 |  |  | 32.35 | 9.43 | 39.49 | 9.86 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-310-E3A | Mono | 310 |  | +5/-0 | 5 | 0 |  |  | 32.57 | 9.52 | 39.75 | 9.91 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-275-B3A | mono | 275 |  | +5/-0 | 5 | 0 |  |  | 31.27 | 8.8 | 38.99 | 9.37 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-280-B3A | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 31.33 | 8.95 | 39.04 | 9.53 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-285-B3A | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 31.5 | 9.07 | 39.12 | 9.62 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-290-B3A | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 31.61 | 9.18 | 39.18 | 9.68 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-295-B3A | mono | 295 |  | +5/-0 | 5 | 0 |  |  | 31.86 | 9.26 | 39.27 | 9.73 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-300-B3A | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 32.09 | 9.35 | 39.39 | 9.78 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-305-B3A | mono | 305 |  | +5/-0 | 5 | 0 |  |  | 32.35 | 9.43 | 39.49 | 9.86 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6H-305-E3A | mono | 305 |  | +5/-0 | 5 | 0 |  |  | 35.22 | 8.66 | 43.89 | 9.38 | -0.28% | -0.21% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6H-310-E3A | mono | 310 |  | +5/-0 | 5 | 0 |  |  | 35.35 | 8.77 | 43.94 | 9.48 | -0.28% | -0.21% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6H-315-E3A | mono | 315 |  | +5/-0 | 5 | 0 |  |  | 35.48 | 8.88 | 43.99 | 9.59 | -0.28% | -0.21% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6H-320-E3A | mono | 320 |  | +5/-0 | 5 | 0 |  |  | 35.6 | 8.99 | 44.05 | 9.68 | -0.28% | -0.21% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6H-325-E3A | Mono | 325 |  | +5/-0 | 5 | 0 |  |  | 35.72 | 9.1 | 44.11 | 9.77 | -0.28% | -0.21% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-305-B4A | poly | 305 |  | +5/-0 | 5 | 0 |  |  | 36.71 | 8.31 | 45.35 | 8.79 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-310-B4A | poly | 310 |  | +5/-0 | 5 | 0 |  |  | 37.01 | 8.39 | 45.68 | 8.92 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-315-B4A | poly | 315 |  | +5/-0 | 5 | 0 |  |  | 37.18 | 8.49 | 45.91 | 9.01 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-320-B4A | poly | 320 |  | +5/-0 | 5 | 0 |  |  | 37.36 | 8.58 | 46.15 | 9.1 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-325-B4A | Poly | 325 |  | +5/-0 | 5 | 0 |  |  | 37.52 | 8.68 | 46.38 | 9.19 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-310-E4A | poly | 310 |  | +5/-0 | 5 | 0 |  |  | 36.78 | 8.43 | 45.68 | 8.96 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-315-E4A | poly | 315 |  | +5/-0 | 5 | 0 |  |  | 36.94 | 8.53 | 45.91 | 9.06 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-320-E4A | poly | 320 |  | +5/-0 | 5 | 0 |  |  | 37.12 | 8.63 | 46.15 | 9.15 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-325-E4A | poly | 325 |  | +5/-0 | 5 | 0 |  |  | 37.28 | 8.72 | 46.38 | 9.24 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6P-330-E4A | Poly | 330 |  | +5/-0 | 5 | 0 |  |  | 37.42 | 8.82 | 46.62 | 9.33 | -0.42% | -0.313% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-330-B4A | mono | 330 |  | +5/-0 | 5 | 0 |  |  | 37.38 | 8.85 | 45.92 | 9.32 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-335-B4A | mono | 335 |  | +5/-0 | 5 | 0 |  |  | 37.47 | 8.96 | 46.04 | 9.41 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-340-B4A | mono | 340 |  | +5/-0 | 5 | 0 |  |  | 37.57 | 9.06 | 46.16 | 9.48 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-345-B4A | mono | 345 |  | +5/-0 | 5 | 0 |  |  | 37.96 | 9.09 | 46.61 | 9.51 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-350-B4A | mono | 350 |  | +5/-0 | 5 | 0 |  |  | 38.34 | 9.13 | 46.89 | 9.54 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-355-B4A | mono | 355 |  | +5/-0 | 5 | 0 |  |  | 38.63 | 9.19 | 47.16 | 9.7 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-360-B4A | mono | 360 |  | +5/-0 | 5 | 0 |  |  | 39.01 | 9.23 | 47.44 | 9.77 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-365-B4A | mono | 365 |  | +5/-0 | 5 | 0 |  |  | 39.38 | 9.27 | 47.67 | 9.84 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-335-E4A | mono | 335 |  | +5/-0 | 5 | 0 |  |  | 37.47 | 8.96 | 46.04 | 9.41 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-340-E4A | mono | 340 |  | +5/-0 | 5 | 0 |  |  | 37.57 | 9.06 | 46.16 | 9.48 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-345-E4A | mono | 345 |  | +5/-0 | 5 | 0 |  |  | 37.96 | 9.09 | 46.61 | 9.51 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-350-E4A | mono | 350 |  | +5/-0 | 5 | 0 |  |  | 38.34 | 9.13 | 46.89 | 9.54 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-355-E4A | mono | 355 |  | +5/-0 | 5 | 0 |  |  | 38.63 | 9.19 | 47.16 | 9.7 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-360-E4A | mono | 360 |  | +5/-0 | 5 | 0 |  |  | 39.01 | 9.23 | 47.44 | 9.77 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-365-E4A | mono | 365 |  | +5/-0 | 5 | 0 |  |  | 39.38 | 9.27 | 47.67 | 9.84 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
Neo Solar Power/DelSolar | D6M-370-E4A | Mono | 370 |  | +5/-0 | 5 | 0 |  |  | 39.4 | 9.41 | 47.81 | 9.89 | -0.427% | -0.318% |  |  | 15 | [11 empty] | Check | 2017-02-16 | DelSolar
ecoSolargy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | ecoSolargy
ecoSolargy | ECO210S156P-60 | poly | 210 | 189.3 | +/-3 | 3 | -3 | 11.9983 | 12.9 | 28.3 | 7.42 | 36.1 | 7.99 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 64.41 | 39.13 | 1.57 | 17.5025 | 41.88 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO215S156P-60 | poly | 215 | 193.9 | +/-3 | 3 | -3 | 12.2839 | 13.2 | 28.8 | 7.47 | 36.5 | 8.04 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 64.41 | 39.13 | 1.57 | 17.5025 | 41.88 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO220S156P-60 | poly | 220 | 195.8 | +/-3 | 3 | -3 | 12.5696 | 13.53 | 29.2 | 7.53 | 36.8 | 8.08 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 64.41 | 39.13 | 1.57 | 17.5025 | 41.88 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO225S156P-60 | poly | 225 | 200.3 | +/-3 | 3 | -3 | 12.8553 | 13.84 | 29.5 | 7.63 | 37 | 8.15 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 64.41 | 39.13 | 1.57 | 17.5025 | 41.88 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO230S156P-60 | poly | 230 | 201.4 | +/-3 | 3 | -3 | 13.141 | 14.14 | 29.8 | 7.71 | 37.1 | 8.21 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 64.41 | 39.13 | 1.57 | 17.5025 | 41.88 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO235S156P-60 | poly | 235 | 206 | +/-3 | 3 | -3 | 13.4266 | 14.45 | 30.1 | 7.81 | 37.3 | 8.31 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 64.41 | 39.13 | 1.57 | 17.5025 | 41.88 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO240S156P-60 | poly | 240 | 210.5 | +/-3 | 3 | -3 | 13.7123 | 14.76 | 30.3 | 7.91 | 37.5 | 8.4 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 64.41 | 39.13 | 1.57 | 17.5025 | 41.88 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO245S156P-60 | poly | 245 | 215 | +/-3 | 3 | -3 | 13.998 | 15.07 | 30.7 | 7.98 | 37.7 | 8.47 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 64.41 | 39.13 | 1.57 | 17.5025 | 41.88 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO250S156P-60 | poly | 250 | 224.8 | +/-3 | 3 | -3 | 14.2837 | 15.37 | 31 | 8.06 | 37.8 | 8.56 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 64.41 | 39.13 | 1.57 | 17.5025 | 41.88 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO255S156P-60 | poly | 255 | 229.4 | +/-3 | 3 | -3 | 14.5693 | 15.68 | 31.3 | 8.15 | 37.9 | 8.65 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 64.41 | 39.13 | 1.57 | 17.5025 | 41.88 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO260S156P-60 | poly | 260 | 234.1 | +/-3 | 3 | -3 | 14.855 | 16 | 31.6 | 8.24 | 38 | 8.75 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 64.41 | 39.13 | 1.57 | 17.5025 | 41.88 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO265S156P-72 | poly | 265 | 235.1 | +/-3 | 3 | -3 | 12.6898 | 13.66 | 35.1 | 7.56 | 44.1 | 8.12 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 76.85 | 39.13 | 1.57 | 20.8829 | 50.706 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO270S156P-72 | poly | 270 | 239.6 | +/-3 | 3 | -3 | 12.9292 | 13.92 | 35.4 | 7.64 | 44.4 | 8.15 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 76.85 | 39.13 | 1.57 | 20.8829 | 50.706 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO275S156P-72 | poly | 275 | 244.2 | +/-3 | 3 | -3 | 13.1687 | 14.17 | 35.6 | 7.72 | 44.7 | 8.23 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 76.85 | 39.13 | 1.57 | 20.8829 | 50.706 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO280S156P-72 | poly | 280 | 248.8 | +/-3 | 3 | -3 | 13.4081 | 14.43 | 36 | 7.77 | 44.9 | 8.28 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 76.85 | 39.13 | 1.57 | 20.8829 | 50.706 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO285S156P-72 | poly | 285 | 253.4 | +/-3 | 3 | -3 | 13.6475 | 14.69 | 36.4 | 7.83 | 45 | 8.34 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 76.85 | 39.13 | 1.57 | 20.8829 | 50.706 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO290S156P-72 | poly | 290 | 257.9 | +/-3 | 3 | -3 | 13.8869 | 14.95 | 36.6 | 7.92 | 45.1 | 8.41 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 76.85 | 39.13 | 1.57 | 20.8829 | 50.706 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO295S156P-72 | poly | 295 | 262.5 | +/-3 | 3 | -3 | 14.1264 | 15.2 | 36.9 | 7.99 | 45.2 | 8.48 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 76.85 | 39.13 | 1.57 | 20.8829 | 50.706 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO300S156P-72 | poly | 300 | 267.1 | +/-3 | 3 | -3 | 14.3658 | 15.46 | 37.3 | 8.06 | 45.3 | 8.56 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 76.85 | 39.13 | 1.57 | 20.8829 | 50.706 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO305S156P-72 | poly | 305 | 271.7 | +/-3 | 3 | -3 | 14.6052 | 15.8 | 37.5 | 8.14 | 45.4 | 8.63 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 76.85 | 39.13 | 1.57 | 20.8829 | 50.706 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO310S156P-72 | poly | 310 | 276.3 | +/-3 | 3 | -3 | 14.8447 | 16.1 | 37.7 | 8.22 | 45.5 | 8.72 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 76.85 | 39.13 | 1.57 | 20.8829 | 50.706 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO315S156P-72 | poly | 315 | 283.8 | +/-3 | 3 | -3 | 15.0841 | 16.3 | 37.9 | 8.31 | 45.6 | 8.78 | -0.48% | -0.33% | 0.054 | 46 | 15 | no | MC4 | silver | white | 76.85 | 39.13 | 1.57 | 20.8829 | 50.706 | 5 |  | Check |  | ecoSolargy
ecoSolargy | SDM-170/(175)-72M | mono | 175 | 154.3 | +/-3 | 3 | -3 | 12.7404 | 15.6 | 36.2 | 4.85 | 44.7 | 5.2 | -0.48% | -0.34% | 0.038 | 45 | 10 | no | MC4 | silver | white | 62.2 | 31.8 | 1.38 | 13.7358 | 33 | 5 |  | Check |  | ecoSolargy
ecoSolargy | SDM-170/(180)-72M | mono | 180 | 158.9 | +/-3 | 3 | -3 | 13.1044 | 16 | 36.8 | 4.9 | 44.8 | 5.25 | -0.48% | -0.34% | 0.038 | 45 | 10 | no | MC4 | silver | white | 62.2 | 31.8 | 1.38 | 13.7358 | 33 | 5 |  | Check |  | ecoSolargy
ecoSolargy | SDM-170/(185)-72M | mono | 185 | 163.4 | +/-3 | 3 | -3 | 13.4684 | 16.5 | 37.5 | 5.14 | 44.9 | 5.3 | -0.48% | -0.34% | 0.038 | 45 | 10 | no | MC4 | silver | white | 62.2 | 31.8 | 1.38 | 13.7358 | 33 | 5 |  | Check |  | ecoSolargy
ecoSolargy | TWES-(175)72M | mono | 175 | 153 | +/-3 | 3 | -3 | 12.7404 | 13.71 | 35.35 | 4.3 | 42.6 | 5.52 | -0.43% | -0.34% | 0.05 | 47 | 15 | no | MC4 | silver | white | 62.2 | 31.8 | 1.57 | 13.7358 | 34.2 | 5 |  | Check |  | ecoSolargy
ecoSolargy | TWES-(180)72M | mono | 180 | 157.5 | +/-3 | 3 | -3 | 13.1044 | 14.1 | 36 | 5 | 43.2 | 5.6 | -0.43% | -0.34% | 0.05 | 47 | 15 | no | MC4 | silver | white | 62.2 | 31.8 | 1.57 | 13.7358 | 34.2 | 5 |  | Check |  | ecoSolargy
ecoSolargy | TWES-(200)60P | poly | 200 | 173.4 | +/-3 | 3 | -3 | 11.296 | 12.16 | 28.29 | 7.06 | 36.4 | 7.72 | -0.44% | -0.34% | 0.06 | 47 | 15 | no | MC4 | silver | white | 65.09 | 39.17 | 1.77 | 17.7054 | 44.1 | 5 |  | Check |  | ecoSolargy
ecoSolargy | TWES-(205)60P | poly | 205 | 177.9 | +/-3 | 3 | -3 | 11.5784 | 12.46 | 28.35 | 7.23 | 36.42 | 7.9 | -0.44% | -0.34% | 0.06 | 47 | 15 | no | MC4 | silver | white | 65.09 | 39.17 | 1.77 | 17.7054 | 44.1 | 5 |  | Check |  | ecoSolargy
ecoSolargy | TWES-(210)60P | poly | 210 | 182.4 | +/-3 | 3 | -3 | 11.8608 | 12.77 | 28.49 | 7.37 | 36.44 | 8.1 | -0.44% | -0.34% | 0.06 | 47 | 15 | no | MC4 | silver | white | 65.09 | 39.17 | 1.77 | 17.7054 | 44.1 | 5 |  | Check |  | ecoSolargy
ecoSolargy | TWES-(215)60P | poly | 215 | 186.8 | +/-3 | 3 | -3 | 12.1432 | 13.07 | 28.7 | 7.49 | 36.5 | 8.27 | -0.44% | -0.34% | 0.06 | 47 | 15 | no | MC4 | silver | white | 65.09 | 39.17 | 1.77 | 17.7054 | 44.1 | 5 |  | Check |  | ecoSolargy
ecoSolargy | TWES-(220)60P | poly | 220 | 191.3 | +/-3 | 3 | -3 | 12.4256 | 13.38 | 29 | 7.59 | 36.6 | 8.45 | -0.44% | -0.34% | 0.06 | 47 | 15 | no | MC4 | silver | white | 65.09 | 39.17 | 1.77 | 17.7054 | 44.1 | 5 |  | Check |  | ecoSolargy
ecoSolargy | TWES-(225)60P | poly | 225 | 195.8 | +/-3 | 3 | -3 | 12.708 | 13.68 | 29.3 | 7.68 | 36.65 | 8.6 | -0.44% | -0.34% | 0.06 | 47 | 15 | no | MC4 | silver | white | 65.09 | 39.17 | 1.77 | 17.7054 | 44.1 | 5 |  | Check |  | ecoSolargy
ecoSolargy | TWES-(230)60P | poly | 230 | 200.3 | +/-3 | 3 | -3 | 12.9904 | 13.98 | 29.7 | 7.74 | 36.7 | 8.72 | -0.44% | -0.34% | 0.06 | 47 | 15 | no | MC4 | silver | white | 65.09 | 39.17 | 1.77 | 17.7054 | 44.1 | 5 |  | Check |  | ecoSolargy
ecoSolargy | TWES-(235)60P | poly | 235 | 204.8 | +/-3 | 3 | -3 | 13.2728 | 14.29 | 30.1 | 7.81 | 36.74 | 8.86 | -0.44% | -0.34% | 0.06 | 47 | 15 | no | MC4 | silver | white | 65.09 | 39.17 | 1.77 | 17.7054 | 44.1 | 5 |  | Check |  | ecoSolargy
ecoSolargy | ECO250H156P-60 | poly | 250 |  | +5/-0 | 5 | 0 |  |  | 31.2 | 8.01 | 37.8 | 8.65 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO255H156P-60 | poly | 255 |  | +5/-0 | 5 | 0 |  |  | 31.6 | 8.06 | 37.9 | 8.73 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO260H156P-60 | poly | 260 |  | +5/-0 | 5 | 0 |  |  | 32 | 8.13 | 38 | 8.81 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO265H156P-60 | poly | 265 |  | +5/-0 | 5 | 0 |  |  | 32.4 | 8.18 | 38.1 | 8.89 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO270H156P-60 | poly | 270 |  | +5/-0 | 5 | 0 |  |  | 32.8 | 8.24 | 38.2 | 8.97 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO275H156P-60 | poly | 275 |  | +5/-0 | 5 | 0 |  |  | 33.2 | 8.89 | 38.3 | 9.05 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO280A156P-72 | poly | 280 |  | +3/-0 | 3 | 0 |  |  | 35.85 | 7.81 | 45.22 | 8.25 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO285A156P-72 | poly | 285 |  | +3/-0 | 3 | 0 |  |  | 36.1 | 7.89 | 45.3 | 8.31 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO290A156P-72 | poly | 290 |  | +3/-0 | 3 | 0 |  |  | 36.29 | 7.98 | 45.38 | 8.42 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO295A156P-72 | poly | 295 |  | +3/-0 | 3 | 0 |  |  | 36.4 | 8.09 | 45.46 | 8.53 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO300S156P-72 | poly | 300 |  | +3/-0 | 3 | 0 |  |  | 37.3 | 8.06 | 45.3 | 8.56 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO300H156P-72 | poly | 300 |  | +5/-0 | 5 | 0 |  |  | 37.6 | 7.98 | 45.6 | 8.68 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO305H156P-72 | poly | 305 |  | +5/-0 | 5 | 0 |  |  | 38 | 8.03 | 45.8 | 8.75 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO310H156P-72 | poly | 310 |  | +5/-0 | 5 | 0 |  |  | 38.4 | 8.08 | 46 | 8.82 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO315H156P-72 | poly | 315 |  | +5/-0 | 5 | 0 |  |  | 38.8 | 8.13 | 46.2 | 8.89 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO320H156P-72 | poly | 320 |  | +5/-0 | 5 | 0 |  |  | 39.1 | 8.19 | 46.4 | 8.96 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO325H156P-72 | poly | 325 |  | +5/-0 | 5 | 0 |  |  | 39.5 | 8.23 | 46.6 | 9.02 | -0.43% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO280A156M-72 | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 36.21 | 7.88 | 45.42 | 8.46 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO285A156M-72 | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 36.49 | 7.95 | 45.54 | 8.56 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO290A156M-72 | mono | 290 |  | +3/-0 | 3 | 0 |  |  | 36.78 | 8.03 | 45.62 | 8.65 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO295A156M-72 | mono | 295 |  | +3/-0 | 3 | 0 |  |  | 36.78 | 8.03 | 45.62 | 8.65 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
ecoSolargy | ECO300A156M-72 | mono | 300 |  | +3/-0 | 3 | 0 |  |  | 37.12 | 8.09 | 45.73 | 8.71 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-02 | ecoSolargy
EGING PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | EGING_PV
EGING PV | EGM Series 185W |  | 185 |  | +3/-0 | 3 | -0 |  |  | 35.18 | 5.26 | 44.08 | 5.69 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EGM Series 190W |  | 190 |  | +3/-0 | 3 | -0 |  |  | 35.65 | 5.33 | 44.18 | 5.73 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EGM Series 195W |  | 195 |  | +3/-0 | 3 | -0 |  |  | 35.92 | 5.43 | 44.38 | 5.8 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EGM Series 200W |  | 200 |  | +3/-0 | 3 | -0 |  |  | 36.25 | 5.52 | 44.61 | 5.86 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EGM Series AR Coated 190W |  | 190 |  | +3/-1 | 3 | -0 |  |  | 35.52 | 5.35 | 43.96 | 5.76 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EGM Series AR Coated 195W |  | 195 |  | +3/-2 | 3 | -0 |  |  | 35.77 | 5.45 | 44.14 | 5.87 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EGM Series AR Coated 200W |  | 200 |  | +3/-3 | 3 | -0 |  |  | 36.05 | 5.55 | 44.32 | 5.98 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EG-(SERIES) M60-C 235W |  | 235 |  | +3/-0 | 3 | -0 |  |  | 28.95 | 8.12 | 37.26 | 8.76 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EG-(SERIES) M60-C 240W |  | 240 |  | +3/-0 | 3 | -0 |  |  | 29.24 | 8.21 | 37.51 | 8.88 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EG-(SERIES) M60-C 245W |  | 245 |  | +3/-0 | 3 | -0 |  |  | 29.49 | 8.31 | 37.72 | 9.01 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EG-(SERIES) M60-C 250W |  | 250 |  | +3/-0 | 3 | -0 |  |  | 30.71 | 8.15 | 37.55 | 8.64 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EG-(SERIES) M60-C AR Coated 235W |  | 235 |  | +3/-0 | 3 | -0 |  |  | 28.88 | 8.14 | 37.16 | 8.83 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EG-(SERIES) M60-C AR Coated 240W |  | 240 |  | +3/-0 | 3 | -0 |  |  | 29.36 | 8.18 | 37.42 | 8.92 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EG-(SERIES) M60-C AR Coated 245W |  | 245 |  | +3/-0 | 3 | -0 |  |  | 29.85 | 8.21 | 37.68 | 9.01 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EG-(SERIES) M60-C AR Coated 250W |  | 250 |  | +3/-0 | 3 | -0 |  |  | 30.2 | 8.28 | 37.4 | 8.77 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EG-(SERIES) P60-C 235W |  | 235 |  | +3/-0 | 3 | -0 |  |  | 29.49 | 7.97 | 37.16 | 8.51 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EG-(SERIES) P60-C 240W |  | 240 |  | +3/-0 | 3 | -0 |  |  | 29.82 | 8.05 | 37.46 | 8.55 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EG-(SERIES) P60-C 245W |  | 245 |  | +3/-0 | 3 | -0 |  |  | 30.14 | 8.13 | 37.64 | 8.62 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EG-(SERIES) P60-C AR Coated 235W |  | 235 |  | +3/-0 | 3 | -0 |  |  | 29.42 | 7.99 | 36.95 | 8.55 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EG-(SERIES) P60-C AR Coated 240W |  | 240 |  | +3/-0 | 3 | -0 |  |  | 29.71 | 8.08 | 37.25 | 8.62 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EG-(SERIES) P60-C AR Coated 245W |  | 245 |  | +3/-0 | 3 | -0 |  |  | 29.92 | 8.19 | 37.47 | 8.73 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EG-(SERIES) P60-C AR Coated 250W |  | 250 |  | +3/-0 | 3 | -0 |  |  | 30.2 | 8.28 | 37.72 | 8.81 | -0.43% | -0.325% | [14 empty] | Check |  | EGING_PV
EGING PV | EG-250P60-C | poly | 250 |  | +3/-0 | 3 | 0 |  |  | 30.2 | 8.28 | 37.72 | 8.81 | -0.43% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-12-02 | EGING_PV
EGING PV | EG-255P60-C | poly | 255 |  | +3/-0 | 3 | 0 |  |  | 30.47 | 8.37 | 37.97 | 8.89 | -0.43% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-12-02 | EGING_PV
EGING PV | EG-260P60-C | poly | 260 |  | +3/-0 | 3 | 0 |  |  | 30.74 | 8.46 | 38.24 | 8.98 | -0.43% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-12-02 | EGING_PV
EGING PV | EG-270M60-C | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 31.15 | 8.67 | 38.03 | 9.11 | -0.43% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-12-02 | EGING_PV
EGING PV | EG-275M60-C | mono | 275 |  | +3/-0 | 3 | 0 |  |  | 31.43 | 8.75 | 38.22 | 9.16 | -0.43% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-12-02 | EGING_PV
EGING PV | EG-280M60-C | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 31.72 | 8.83 | 38.39 | 9.22 | -0.43% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-12-02 | EGING_PV
EGING PV | EG-285M60-0 | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 32.03 | 8.9 | 38.57 | 9.28 | -0.43% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-12-02 | EGING_PV
Eoplly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Eoplly
Eoplly | EP156P/60-230W | poly | 230 |  | +3/-0 | 3 | -0 |  |  | 30.05 | 7.705 | 36.42 | 8.561 | -0.48% | -0.35% |  |  | 15 | [11 empty] | Check | 2013-12-20 | Eoplly
Eoplly | EP156P/60-235W | poly | 235 |  | +3/-0 | 3 | -0 |  |  | 30.29 | 7.792 | 36.72 | 8.644 | -0.48% | -0.35% |  |  | 15 | [11 empty] | Check | 2013-12-20 | Eoplly
Eoplly | EP156P/60-240W | poly | 240 |  | +3/-0 | 3 | -0 |  |  | 30.54 | 7.9 | 37.02 | 8.681 | -0.48% | -0.35% |  |  | 15 | [11 empty] | Check | 2013-12-20 | Eoplly
Eoplly | EP156P/60-245W | poly | 245 |  | +3/-0 | 3 | -0 |  |  | 31.02 | 7.96 | 37.38 | 8.747 | -0.48% | -0.35% |  |  | 15 | [11 empty] | Check | 2013-12-20 | Eoplly
Eoplly | 156P60-270W | poly | 270 |  | +3/-0 | 3 | -0 |  |  | 35.19 | 7.7 | 43.17 | 8.529 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check | 2014-05-23 | Eoplly
Eoplly | 156P60-275W | poly | 275 |  | +3/-0 | 3 | -0 |  |  | 35.67 | 7.743 | 43.53 | 8.562 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check | 2014-05-23 | Eoplly
Eoplly | 156P60-280W | poly | 280 |  | +3/-0 | 3 | -0 |  |  | 36.15 | 7.772 | 43.83 | 8.586 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check | 2014-05-23 | Eoplly
Eoplly | 156P60-285W | poly | 285 |  | +3/-0 | 3 | -0 |  |  | 36.65 | 7.831 | 44.43 | 8.634 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check | 2014-05-23 | Eoplly
Eoplly | 156P60-290W | poly | 290 |  | +3/-0 | 3 | -0 |  |  | 37.15 | 7.89 | 44.64 | 8.699 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check | 2014-05-23 | Eoplly
Eoplly | 156P60-295W | poly | 295 |  | +3/-0 | 3 | -0 |  |  | 37.22 | 7.96 | 44.86 | 8.776 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check | 2014-05-23 | Eoplly
Eoplly | EP156MB/72-280 | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 35.83 | 7.838 | 43.43 | 8.65 | -0.45% | -0.4% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
Eoplly | EP156MB/72-285 | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 36.12 | 7.918 | 43.78 | 8.721 | -0.45% | -0.4% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
Eoplly | EP156MB/72-290 | mono | 290 |  | +3/-0 | 3 | 0 |  |  | 36.41 | 7.999 | 44.14 | 8.79 | -0.45% | -0.4% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
Eoplly | EP156MB/72-295 | mono | 295 |  | +3/-0 | 3 | 0 |  |  | 36.71 | 8.08 | 44.5 | 8.85 | -0.45% | -0.4% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
Eoplly | EP156MB/72-300 | mono | 300 |  | +3/-0 | 3 | 0 |  |  | 37.01 | 8.15 | 44.86 | 8.88 | -0.45% | -0.4% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
Eoplly | EP156MB/72-305 | mono | 305 |  | +3/-0 | 3 | 0 |  |  | 37.44 | 8.22 | 45.07 | 8.935 | -0.45% | -0.4% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
Eoplly | EP156M/72-310 | mono | 310 |  | +3/-0 | 3 | 0 |  |  | 37.73 | 8.27 | 45.22 | 8.989 | -0.45% | -0.4% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
Eoplly | EP156M/72-315 | mono | 315 |  | +3/-0 | 3 | 0 |  |  | 37.94 | 8.31 | 45.29 | 9.033 | -0.45% | -0.4% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
Eoplly | EP156P/72-280 | poly | 280 |  | +3/-0 | 3 | 0 |  |  | 36.16 | 7.772 | 43.83 | 8.586 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
Eoplly | EP156P/72-285 | poly | 285 |  | +3/-0 | 3 | 0 |  |  | 36.65 | 7.831 | 44.43 | 8.634 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
Eoplly | EP156P/72-290 | poly | 290 |  | +3/-0 | 3 | 0 |  |  | 37.15 | 7.89 | 44.64 | 8.699 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
Eoplly | EP156P/72-295 | poly | 295 |  | +3/-0 | 3 | 0 |  |  | 37.22 | 7.96 | 44.86 | 8.776 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
Eoplly | EP156P/72-300 | poly | 300 |  | +3/-0 | 3 | 0 |  |  | 37.58 | 8 | 45.07 | 8.82 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
Eoplly | EP156P/72-305 | Poly | 305 |  | +3/-0 | 3 | 0 |  |  | 37.87 | 8.1 | 45.22 | 8.931 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
Eoplly | EP156P/72-310 | poly | 310 |  | +3/-0 | 3 | 0 |  |  | 37.99 | 8.185 | 45.36 | 9.025 | -0.44% | -0.41% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
Eoplly | EP156P/72-315 | Poly | 315 |  | +3/-0 | 3 | 0 |  |  | 38.11 | 8.272 | 45.51 | 9.12 | -0.44% | -0.41% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
Eoplly | EP156P/72-320 | Poly | 320 |  | +3/-0 | 3 | 0 |  |  | 38.35 | 8.359 | 45.65 | 9.216 | -0.44% | -0.41% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Eoplly
ET Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | ET_Solar
ET Solar | ET-M572175 | mono | 175 |  | +3/-3 | 3 | -3 | 12.7 | 13.7 | 36.24 | 7.95 | 44.16 | 5.61 | -0.37% | -0.34% |  |  | 12 |  |  |  |  | 62.2 | 31.8 | 2 | 13.7358 | 34.2 |  |  | Check |  | ET_Solar
ET Solar | ET-M572180 | mono | 180 | 160.7 | +3/-0 | 3 | 0 | 13.1003 | 14.1 | 36.58 | 4.92 | 44.51 | 5.42 | -0.47% | -0.336% | 0.042 | 44 | 12 | no | MC4 | silver | white | 62.2 | 31.81 | 1.97 | 13.7402 | 35.05 | 10 |  | Check |  | ET_Solar
ET Solar | ET-M572180(B) | mono | 180 | 160.1 | +3/-0 | 3 | 0 | 13.1003 | 14.1 | 36.58 | 4.92 | 44.51 | 5.42 | -0.47% | -0.336% | 0.042 | 44 | 10 | no | MC4 | black | black | 62.2 | 31.81 | 1.97 | 13.7402 | 35.05 | 10 |  | Check |  | ET_Solar
ET Solar | ET-M572185 | mono | 185 |  | +5/-0 | 5 | 0 | 13.4642 | 14.49 | 36.29 | 5.11 | 45.03 | 5.47 | -0.47% | -0.336% | 0.042 | 44.2 | 15 |  |  |  |  | 62.2 | 31.81 | 1.57 | 13.7402 | 33.74 | 10 |  | Check | 2012-01-10 | ET_Solar
ET Solar | ET-M572185(B) | mono | 185 | 164.6 | +3/-0 | 3 | 0 | 13.4642 | 14.49 | 36.9 | 5.02 | 44.75 | 5.54 | -0.47% | -0.336% | 0.042 | 44 | 10 | no | MC4 | black | black | 62.2 | 31.81 | 1.97 | 13.7402 | 35.05 | 10 |  | Check |  | ET_Solar
ET Solar | ET-M572190 | mono | 190 |  | +5/-0 | 5 | 0 | 13.8281 | 14.88 | 36.68 | 5.18 | 45.21 | 5.56 | -0.47% | -0.336% | 0.042 | 44.2 | 15 |  |  |  |  | 62.2 | 31.81 | 1.57 | 13.7402 | 33.74 | 10 |  | Check | 2012-01-10 | ET_Solar
ET Solar | ET-M572190(B) | mono | 190 | 169.3 | +3/-0 | 3 | 0 | 13.8281 | 14.88 | 37.2 | 5.11 | 44.85 | 5.62 | -0.47% | -0.336% | 0.042 | 44 | 10 | no | MC4 | silver/black | black | 62.2 | 31.81 | 1.97 | 13.7402 | 35.05 | 10 |  | Check |  | ET_Solar
ET Solar | ET-M572195 | mono | 195 |  | +5/-0 | 5 | 0 | 14.192 | 15.27 | 36.94 | 5.28 | 45.33 | 5.68 | -0.47% | -0.336% | 0.042 | 44.2 | 15 |  |  |  |  | 62.2 | 31.81 | 1.57 | 13.7402 | 33.74 | 10 |  | Check | 2012-01-10 | ET_Solar
ET Solar | ET-M572200 | mono | 200 |  | +5/-0 | 5 | 0 | 14.5559 | 15.67 | 36.97 | 5.41 | 45.84 | 5.7 | -0.47% | -0.336% | 0.042 | 44.2 | 15 |  |  |  |  | 62.2 | 31.81 | 1.57 | 13.7402 | 33.74 | 10 |  | Check | 2012-01-10 | ET_Solar
ET Solar | ET-M572205 | mono | 205 |  | +3/-3 | 3 | -3 | 131.2 | 16.06 | 37.13 | 5.53 | 46.15 | 5.81 | -0.47% | -0.336% | 0.042 | 44.2 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | Check | 2012-01-10 | ET_Solar
ET Solar | ET-M672295BB | mono | 295 |  | +5/-0 | 5 | 0 |  |  | 35.78 | 8.25 | 44.8 | 8.72 | -0.44% | -0.31% |  |  | 20 | [11 empty] | Check | 2014-03-05 | ET_Solar
ET Solar | ET-M672300BB | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 36.24 | 8.28 | 44.92 | 8.81 | -0.44% | -0.31% |  |  | 20 | [11 empty] | Check | 2014-03-05 | ET_Solar
ET Solar | ET-M672305BB | mono | 305 |  | +5/-0 | 5 | 0 |  |  | 36.75 | 8.3 | 45.12 | 8.88 | -0.44% | -0.31% |  |  | 20 | [11 empty] | Check | 2014-03-05 | ET_Solar
ET Solar | ET-M672310BB | mono | 310 |  | +5/-0 | 5 | 0 |  |  | 37.26 | 8.32 | 45.4 | 8.95 | -0.44% | -0.31% |  |  | 20 | [11 empty] | Check | 2014-03-05 | ET_Solar
ET Solar | ET-P654180 | poly | 180 |  | +3/-3 | 3 | -3 | 11.4 | 12.2 | 26.45 | 6.81 | 32.35 | 7.6 | -0.488% | -0.3462% |  |  | 12 |  | Solarlok |  |  | 58.3 | 39.1 | 2 | 15.8301 | 39.3 | 5 |  | Check |  | ET_Solar
ET Solar | ET-P654185 | poly | 185 |  | +3/-3 | 3 | -3 | 11.7 | 12.6 | 26.45 | 6.99 | 32.3 | 7.7 | -0.488% | -0.3467% |  |  | 12 |  | Solarlok |  |  | 58.3 | 39.1 | 2 | 15.8301 | 39.3 | 5 |  | Check |  | ET_Solar
ET Solar | ET-P654190 | poly | 190 |  | +3/-3 | 3 | -3 | 12 | 12.9 | 26.78 | 7.1 | 32.5 | 7.72 | -0.488% | -0.3446% |  |  | 12 |  | Solarlok |  |  | 58.3 | 39.1 | 2 | 15.8301 | 39.3 | 5 |  | Check |  | ET_Solar
ET Solar | ET-P654195 | poly | 195 |  | +3/-3 | 3 | -3 | 12.3 | 13.3 | 27 | 7.22 | 32.75 | 7.98 | -0.488% | -0.345% |  |  | 12 |  | Solarlok |  |  | 58.3 | 39.1 | 2 | 15.8301 | 39.3 | 5 |  | Check |  | ET_Solar
ET Solar | ET-P654200(B) | poly | 200 | 176.9 | +3/-0 | 3 | 0 | 12.6363 | 13.6 | 27.21 | 7.36 | 32.72 | 7.86 | -0.46% | -0.346% | 0.065 | 45 | 15 | no | tyco | silver/black | white | 58.35 | 39.06 | 1.97 | 15.8274 | 40.34 | 10 |  | Check |  | ET_Solar
ET Solar | ET-P654205(B) | poly | 205 | 181.5 | +2/-0 | 2 | 0 | 12.9522 | 13.94 | 27.3 | 7.5 | 32.8 | 8.1 | -0.46% | -0.346% | 0.065 | 45 | 15 | no | tyco | silver/black | white | 58.35 | 39.06 | 1.97 | 15.8274 | 40.34 | 10 |  | Check |  | ET_Solar
ET Solar | ET-P654210(B) | poly | 210 | 186.1 | +2/-0 | 2 | 0 | 13.2681 | 14.28 | 27.54 | 7.63 | 32.83 | 8.3 | -0.46% | -0.346% | 0.065 | 45 | 15 | no | tyco | silver/black | white | 58.35 | 39.06 | 1.97 | 15.8274 | 40.34 | 10 |  | Check |  | ET_Solar
ET Solar | ET-P654215 | poly | 215 |  | +3/-3 | 3 | -3 | 13.6 | 14.6 | 27.54 | 7.81 | 33.2 | 8.5 | -0.488% | -0.3464% |  |  | 12 |  | Solarlok |  |  | 58.3 | 39.1 | 2 | 15.8301 | 39.3 | 5 |  | Check |  | ET_Solar
ET Solar | ET-P660220(B) | poly | 220 | 198.2 | +2/-0 | 2 | 0 | 12.5609 | 13.52 | 29.25 | 7.52 | 36.3 | 8.2 | -0.46% | -0.346% | 0.065 | 45 | 15 | no | tyco | silver/black | white | 64.57 | 39.06 | 1.97 | 17.5146 | 42.55 | 10 |  | Check |  | ET_Solar
ET Solar | ET-P660225 | poly | 225 |  | +5/-0 | 5 | 0 | 12.8464 | 13.83 | 28.35 | 7.94 | 36.63 | 8.51 | -0.46% | -0.346% | 0.065 | 45.3 | 20 |  |  |  |  | 64.57 | 39.06 | 1.57 | 17.5146 | 42.59 | 10 |  | Check | 2012-01-09 | ET_Solar
ET Solar | ET-P660225(B) | poly | 225 | 202.8 | +2/-0 | 2 | 0 | 12.8464 | 13.83 | 29.33 | 7.67 | 36.35 | 8.25 | -0.46% | -0.346% | 0.065 | 45 | 15 | no | tyco | silver/black | white | 64.57 | 39.06 | 1.97 | 17.5146 | 42.55 | 10 |  | Check |  | ET_Solar
ET Solar | ET-P660230 | poly | 230 |  | +5/-0 | 5 | 0 | 13.1319 | 14.14 | 28.81 | 8 | 36.88 | 8.6 | -0.46% | -0.346% | 0.065 | 45.3 | 20 |  |  |  |  | 64.57 | 39.06 | 1.57 | 17.5146 | 42.59 | 10 |  | Check | 2012-01-09 | ET_Solar
ET Solar | ET-P660230(B) | poly | 230 | 207.5 | +2/-0 | 2 | 0 | 13.1319 | 14.14 | 29.4 | 7.82 | 36.5 | 8.3 | -0.46% | -0.346% | 0.065 | 45 | 15 | no | tyco | silver/black | white | 64.57 | 39.06 | 1.97 | 17.5146 | 42.55 | 10 |  | Check |  | ET_Solar
ET Solar | ET-P660235 | poly | 235 |  | +5/-0 | 5 | 0 | 13.4174 | 14.44 | 29.08 | 8.08 | 36.96 | 8.7 | -0.46% | -0.346% | 0.065 | 45.3 | 20 |  |  |  |  | 64.57 | 39.06 | 1.57 | 17.5146 | 42.59 | 10 |  | Check | 2012-01-09 | ET_Solar
ET Solar | ET-P660235(B) | poly | 235 | 212.1 | +2/-0 | 2 | 0 | 13.4174 | 14.44 | 29.9 | 7.86 | 36.96 | 8.4 | -0.46% | -0.346% | 0.065 | 45 | 15 | no | tyco | silver/black | white | 64.57 | 39.06 | 1.97 | 17.5146 | 42.55 | 10 |  | Check |  | ET_Solar
ET Solar | ET-P660240 | poly | 240 |  | +5/-0 | 5 | 0 | 13.7028 | 14.75 | 29.2 | 8.22 | 37.25 | 8.78 | -0.46% | -0.346% | 0.065 | 45.3 | 20 |  |  |  |  | 64.57 | 39.06 | 1.57 | 17.5146 | 42.59 | 10 |  | Check | 2012-01-09 | ET_Solar
ET Solar | ET-P660240(B) | poly | 240 | 214.9 | +2/-0 | 2 | 0 | 13.7028 | 14.75 | 30.23 | 7.94 | 37.02 | 8.49 | -0.46% | -0.346% | 0.065 | 45 | 15 | no | tyco | silver/black | white | 64.57 | 39.06 | 1.97 | 17.5146 | 42.55 | 10 |  | Check |  | ET_Solar
ET Solar | ET-P660245 | poly | 245 |  | +5/-0 | 5 | 0 | 13.9883 | 15.06 | 29.4 | 8.32 | 37.41 | 8.86 | -0.46% | -0.346% | 0.065 | 45.3 | 20 |  |  |  |  | 64.57 | 39.06 | 1.57 | 17.5146 | 42.59 | 10 |  | Check | 2012-01-09 | ET_Solar
ET Solar | ET-P660250 | poly | 250 |  | +3/-3 | 3 | -3 | 14.2738 | 15.37 | 30.02 | 8.33 | 37.58 | 8.98 | -0.46% | -0.346% | 0.065 | 45.3 | 20 |  |  |  |  | 64.57 | 39.06 | 1.57 | 17.5146 | 42.59 | 10 |  | Check | 2012-01-09 | ET_Solar
ET Solar | ET-P660255WB/WW | poly | 255 |  | +5/-0 | 5 | 3 |  | 15.67 | 30.91 | 8.25 | 37.54 | 8.82 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-06-26 | ET_Solar
ET Solar | ET-P660260WB/WW | poly | 260 |  | +5/-0 | 5 | 3 |  | 15.98 | 31.48 | 8.26 | 38.09 | 8.84 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-06-26 | ET_Solar
ET Solar | ET-P660265WB/WW | poly | 265 |  | +5/-0 | 5 | 3 |  | 16.29 | 32.01 | 8.28 | 38.59 | 8.85 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-06-26 | ET_Solar
ET Solar | ET-P672240 | poly | 240 |  | +3/-3 | 3 | -3 | 11.5 | 12.4 | 34.95 | 6.88 | 43.85 | 7.63 | -0.488% | -0.3466% |  |  | 12 |  | Solarlok |  |  | 77 | 39.1 | 2 | 20.9076 | 50.7 | 5 |  | Check |  | ET_Solar
ET Solar | ET-P672245 | poly | 245 |  | +3/-3 | 3 | -3 | 11.7 | 12.6 | 34.95 | 7.01 | 43.85 | 7.7 | -0.488% | -0.3466% |  |  | 12 |  | Solarlok |  |  | 77 | 39.1 | 2 | 20.9076 | 50.7 | 5 |  | Check |  | ET_Solar
ET Solar | ET-P672250 | poly | 250 |  | +3/-3 | 3 | -3 | 12 | 12.9 | 35.2 | 7.12 | 43.88 | 7.81 | -0.488% | -0.3464% |  |  | 12 |  | Solarlok |  |  | 77 | 39.1 | 2 | 20.9076 | 50.7 | 5 |  | Check |  | ET_Solar
ET Solar | ET-P672255 | poly | 255 |  | +3/-3 | 3 | -3 | 12.2 | 13.1 | 35.2 | 7.23 | 43.88 | 7.85 | -0.488% | -0.3464% |  |  | 12 |  | Solarlok |  |  | 77 | 39.1 | 2 | 20.9076 | 50.7 | 5 |  | Check |  | ET_Solar
ET Solar | ET-P672260 | poly | 260 |  | +3/-3 | 3 | -3 | 12.4 | 13.4 | 36 | 7.23 | 43.49 | 7.79 | -0.488% | -0.3449% |  |  | 12 |  | Solarlok |  |  | 77 | 39.1 | 2 | 20.9076 | 50.7 | 5 |  | Check |  | ET_Solar
ET Solar | ET-P672265 | poly | 265 |  | +3/-3 | 3 | -3 | 12.7 | 13.7 | 36.4 | 7.28 | 43.63 | 7.9 | -0.488% | -0.3461% |  |  | 12 |  | Solarlok |  |  | 77 | 39.1 | 2 | 20.9076 | 50.7 | 5 |  | Check |  | ET_Solar
ET Solar | ET-P672270 | poly | 270 |  | +3/-3 | 3 | -3 | 12.9 | 13.9 | 36.4 | 7.42 | 43.63 | 7.9 | -0.488% | -0.3461% |  |  | 12 |  | Solarlok |  |  | 77 | 39.1 | 2 | 20.9076 | 50.7 | 5 |  | Check |  | ET_Solar
ET Solar | ET-P672270(B) | poly | 270 | 241.6 | +2/-0 | 2 | 0 | 12.9272 | 13.92 | 35.77 | 7.55 | 43.94 | 8.19 | -0.46% | -0.346% | 0.065 | 45 | 15 | no | tyco | silver/black | white | 77 | 39.06 | 1.97 | 20.8863 | 50.4 | 10 |  | Check |  | ET_Solar
ET Solar | ET-P672275 | poly | 275 |  | +3/-3 | 3 | -3 | 13.2 | 14.2 | 36.72 | 7.49 | 43.78 | 7.96 | -0.488% | -0.3449% |  |  | 12 |  | Solarlok |  |  | 77 | 39.1 | 2 | 20.9076 | 50.7 | 5 |  | Check |  | ET_Solar
ET Solar | ET-P672275(B) | poly | 275 | 246.2 | +2/-0 | 2 | 0 | 13.1666 | 14.17 | 35.86 | 7.67 | 44.12 | 8.31 | -0.46% | -0.346% | 0.065 | 45 | 15 | no | tyco | silver/black | white | 77 | 39.06 | 1.97 | 20.8863 | 50.4 | 10 |  | Check |  | ET_Solar
ET Solar | ET-P672280 | poly | 280 |  | +3/-3 | 3 | -3 | 13.4 | 14.4 | 36.72 | 7.63 | 43.78 | 7.98 | -0.488% | -0.3449% |  |  | 12 |  | Solarlok |  |  | 77 | 39.1 | 2 | 20.9076 | 50.7 | 5 |  | Check |  | ET_Solar
ET Solar | ET-P672280(B) | poly | 280 | 250.8 | +2/-0 | 2 | 0 | 13.4059 | 14.43 | 35.94 | 7.79 | 44.24 | 8.41 | -0.46% | -0.346% | 0.065 | 45 | 15 | no | tyco | silver/black | white | 77 | 39.06 | 1.97 | 20.8863 | 50.4 | 10 |  | Check |  | ET_Solar
ET Solar | ET-P672285(B) | poly | 285 | 254.7 | +2/-0 | 2 | 0 | 13.6453 | 14.69 | 36.03 | 7.91 | 44.35 | 8.52 | -0.46% | -0.346% | 0.065 | 45 | 15 | no | tyco | silver/black | white | 77 | 39.06 | 1.97 | 20.8863 | 50.4 | 10 |  | Check |  | ET_Solar
ET Solar | ET-P672290(B) | poly | 290 | 259.3 | +/-3 | 3 | -3 | 13.8847 | 14.95 | 36.25 | 8 | 44.5 | 8.61 | -0.46% | -0.346% | 0.065 | 45 | 15 | no | tyco | silver/black | white | 77 | 39.06 | 1.97 | 20.8863 | 50.4 | 10 |  | Check |  | ET_Solar
ET Solar | ET-P672280WW | poly | 280 |  | +5/-0 | 5 | 0 |  |  | 35.5 | 7.88 | 44.27 | 8.48 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2014-03-05 | ET_Solar
ET Solar | ET-P672285WW | poly | 285 |  | +5/-0 | 5 | 0 |  |  | 35.86 | 7.95 | 44.72 | 8.55 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2014-03-05 | ET_Solar
ET Solar | ET-P672290WW | poly | 290 |  | +5/-0 | 5 | 0 |  |  | 35.92 | 8.08 | 44.75 | 8.62 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2014-03-05 | ET_Solar
ET Solar | ET-P672295WW | poly | 295 |  | +5/-0 | 5 | 0 |  |  | 36.17 | 8.16 | 44.78 | 8.68 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2014-03-05 | ET_Solar
ET Solar | ET-P672300WW | poly | 300 |  | +5/-0 | 5 | 0 |  |  | 36.68 | 8.18 | 44.89 | 8.72 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2014-03-05 | ET_Solar
ET Solar | ET-P672305WW | poly | 305 |  | +3/-1 | 3 | -1 |  |  | 37.18 | 8.21 | 45.12 | 8.78 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2014-03-05 | ET_Solar
ET Solar | ET-P672310WW | poly | 310 |  | +3/-3 | 3 | -3 |  |  | 37.71 | 8.23 | 45.8 | 8.79 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2014-03-05 | ET_Solar
ET Solar | ET-M672295BB | mono | 295 |  | +5/-0 | 5 | 0 |  |  | 35.78 | 8.25 | 44.8 | 8.72 | -0.44% | -0.31% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ET_Solar
ET Solar | ET-M672300BB | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 36.24 | 8.28 | 44.92 | 8.81 | -0.44% | -0.31% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ET_Solar
ET Solar | ET-M672305BB | mono | 305 |  | +5/-0 | 5 | 0 |  |  | 36.75 | 8.3 | 45.12 | 8.88 | -0.44% | -0.31% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ET_Solar
ET Solar | ET-M672310BB | mono | 310 |  | +5/-0 | 5 | 0 |  |  | 37.26 | 8.32 | 45.4 | 8.95 | -0.44% | -0.31% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ET_Solar
ET Solar | ET-M672300WW | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 36.24 | 8.28 | 44.92 | 8.81 | -0.44% | -0.31% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ET_Solar
ET Solar | ET-M672305WW | mono | 305 |  | +5/-0 | 5 | 0 |  |  | 36.75 | 8.3 | 45.12 | 8.88 | -0.44% | -0.31% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ET_Solar
ET Solar | ET-M672310WW | mono | 310 |  | +5/-0 | 5 | 0 |  |  | 37.26 | 8.32 | 45.4 | 8.95 | -0.44% | -0.31% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ET_Solar
ET Solar | ET-M672315WW | mono | 315 |  | +5/-0 | 5 | 0 |  |  | 37.82 | 8.33 | 45.98 | 8.96 | -0.44% | -0.31% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ET_Solar
ET Solar | ET-P672290WB/WW | poly | 290 |  | +5/-0 | 5 | 0 |  |  | 35.92 | 8.08 | 44.75 | 8.62 | -0.44% | -0.34% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ET_Solar
ET Solar | ET-P672295WB/WW | poly | 295 |  | +5/-0 | 5 | 0 |  |  | 36.17 | 8.16 | 44.78 | 8.68 | -0.44% | -0.34% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ET_Solar
ET Solar | ET-P672300WB/WW | poly | 300 |  | +5/-0 | 5 | 0 |  |  | 36.68 | 8.18 | 44.89 | 8.72 | -0.44% | -0.34% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ET_Solar
ET Solar | ET-P672305WB/WW | poly | 305 |  | +5/-0 | 5 | 0 |  |  | 37.18 | 8.21 | 45.12 | 8.78 | -0.44% | -0.34% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ET_Solar
ET Solar | ET-P672310WB/WW | poly | 310 |  | +5/-0 | 5 | 0 |  | 15.98 | 37.71 | 8.23 | 45.8 | 8.79 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-06-26 | ET_Solar
ET Solar | ET-P672315WB/WW | poly | 315 |  | +5/-0 | 5 | 0 |  | 16.23 | 38.23 | 8.24 | 46.43 | 8.81 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-06-26 | ET_Solar
ET Solar | ET-P672290BB | poly | 290 |  | +5/-0 | 5 | 0 |  |  | 35.92 | 8.08 | 44.75 | 8.62 | -0.44% | -0.34% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ET_Solar
ET Solar | ET-P672295BB | poly | 295 |  | +5/-0 | 5 | 0 |  |  | 36.17 | 8.16 | 44.78 | 8.68 | -0.44% | -0.34% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ET_Solar
ET Solar | ET-P672300BB | poly | 300 |  | +5/-0 | 5 | 0 |  |  | 36.68 | 8.18 | 44.89 | 8.72 | -0.44% | -0.34% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ET_Solar
ET Solar | ET-P672305BB | poly | 305 |  | +5/-0 | 5 | 0 |  | 15.72 | 37.18 | 8.21 | 45.12 | 8.78 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-06-26 | ET_Solar
ET Solar | ET-P672310BB | poly | 310 |  | +5/-0 | 5 | 0 |  | 15.98 | 37.71 | 8.23 | 45.8 | 8.79 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-06-26 | ET_Solar
Evergreen Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Evergreen_Solar
Evergreen Solar | ES-170 | poly ribbon | 170 |  | +4/-5 | 4 | -5 | 10.5631 | 11.4 | 25.3 | 6.72 | 32.4 | 7.55 | -0.49% | -0.31% |  |  | 15 |  | MC |  |  | 61.8 | 37.5 | 1.6 | 16.0938 | 40.1 | 5 |  | Check |  | Evergreen_Solar
Evergreen Solar | ES-180 | poly ribbon | 180 |  | +4/-2 | 4 | -2 | 11.1845 | 12 | 25.9 | 6.95 | 32.6 | 7.78 | -0.49% | -0.31% |  |  | 15 |  | MC |  |  | 61.8 | 37.5 | 1.6 | 16.0938 | 40.1 | 5 |  | Check |  | Evergreen_Solar
Evergreen Solar | ES-190 | poly ribbon | 190 |  | +4/-2 | 4 | -2 | 11.8058 | 12.7 | 26.7 | 7.12 | 32.8 | 8.05 | -0.49% | -0.31% |  |  | 15 |  | MC |  |  | 61.8 | 37.5 | 1.6 | 16.0938 | 40.1 | 5 |  | Check |  | Evergreen_Solar
Evergreen Solar | ES-195 | poly ribbon | 195 |  | +2.5/-0 | 2.5 | 0 | 12.1165 | 13.1 | 27.1 | 7.2 | 32.9 | 8.15 | -0.49% | -0.31% |  |  | 15 |  | MC |  |  | 61.8 | 37.5 | 1.6 | 16.0938 | 40.1 | 5 |  | Check |  | Evergreen_Solar
Evergreen Solar | ES-A-200-fa3 | ribbon | 200 | 180.7 | +2.5/-0 | 2.5 | 0 | 11.8154 | 12.7 | 18.1 | 11.05 | 22.6 | 11.8 | -0.43% | -0.31% | 0.05 | 45.4 | 20 | yes | MC4 | black | white | 65 | 37.5 | 1.8 | 16.9271 | 41 | 10 |  | Check |  | Evergreen_Solar
Evergreen Solar | ES-A-205-fa3 | ribbon | 205 | 185.4 | +2.4/-0 | 2.4 | 0 | 12.1108 | 13.1 | 18.2 | 11.27 | 22.7 | 11.93 | -0.43% | -0.31% | 0.05 | 45.4 | 20 | yes | MC4 | black | white | 65 | 37.5 | 1.8 | 16.9271 | 41 | 10 |  | Check |  | Evergreen_Solar
Evergreen Solar | ES-A-210-fa3 | ribbon | 210 | 190 | +2.4/-0 | 2.4 | 0 | 12.4062 | 13.4 | 18.3 | 11.48 | 22.8 | 12.11 | -0.43% | -0.31% | 0.05 | 45.4 | 20 | yes | MC4 | black | white | 65 | 37.5 | 1.8 | 16.9271 | 41 | 10 |  | Check |  | Evergreen_Solar
Evergreen Solar | ES-A-215-fa3 | ribbon | 215 | 194.6 | +2.3/-0 | 2.3 | 0 | 12.7015 | 13.7 | 18.4 | 11.69 | 22.9 | 12.3 | -0.43% | -0.31% | 0.05 | 45.4 | 20 | yes | MC4 | black | white | 65 | 37.5 | 1.8 | 16.9271 | 41 | 10 |  | Check |  | Evergreen_Solar
Evergreen Solar | ES-E-210-fc3 | ribbon | 210 | 186.5 | +2.4/-0 | 2.4 | 0 | 11.8938 | 12.8 | 28.7 | 7.32 | 35.4 | 8.01 | -0.43% | -0.31% | 0.05 | DNR | 15 | DNR | MC4 | black | white | 67.8 | 37.5 | 1.8 | 17.6562 | 42.9 | 10 |  | Check |  | Evergreen_Solar
Evergreen Solar | ES-E-215-fc3 | ribbon | 215 | 191.9 | +2.3/-0 | 2.3 | 0 | 12.177 | 13.1 | 29 | 7.43 | 35.6 | 8.12 | -0.43% | -0.31% | 0.05 | DNR | 15 | DNR | MC4 | black | white | 67.8 | 37.5 | 1.8 | 17.6562 | 42.9 | 10 |  | Check |  | Evergreen_Solar
Evergreen Solar | ES-E-220-fc3 | ribbon | 220 | 196.5 | +2.3/-0 | 2.3 | 0 | 12.4602 | 13.4 | 29.2 | 7.54 | 35.9 | 8.22 | -0.43% | -0.31% | 0.05 | DNR | 15 | DNR | MC4 | black | white | 67.8 | 37.5 | 1.8 | 17.6562 | 42.9 | 10 |  | Check |  | Evergreen_Solar
First Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | First_Solar
First Solar | FS-270 | thin film | 70 | 67.2 | +5/-5 | 5 | -5 | 9.0338 | 9.7 | 65.5 | 1.07 | 88 | 1.23 | -0.25% | -0.2% |  |  | 10 |  | SOLALINE |  |  | 47.24 | 23.62 | 0.26 | 7.7487 | 26.5 |  |  | Check |  | First_Solar
First Solar | FS-272 | thin film | 72.5 | 69.8 | +5/-5 | 5 | -5 | 9.3564 | 10.1 | 66.6 | 1.09 | 88.7 | 1.23 | -0.25% | -0.2% |  |  | 10 |  | SOLALINE |  |  | 47.24 | 23.62 | 0.26 | 7.7487 | 26.5 |  |  | Check |  | First_Solar
First Solar | FS-275 | thin film | 75 | 72.2 | +5/-5 | 5 | -5 | 9.6791 | 10.4 | 68.2 | 1.1 | 89.6 | 1.23 | -0.25% | -0.2% |  |  | 10 |  | SOLALINE |  |  | 47.24 | 23.62 | 0.26 | 7.7487 | 26.5 |  |  | Check |  | First_Solar
First Solar | FS-277 | thin film | 77.5 | 74.6 | +5/-5 | 5 | -5 | 10.0017 | 10.8 | 69.9 | 1.11 | 90.5 | 1.22 | -0.25% | -0.2% |  |  | 10 |  | SOLALINE |  |  | 47.24 | 23.62 | 0.26 | 7.7487 | 26.5 |  |  | Check |  | First_Solar
First Solar | FS4110-3 | thin film | 110 | 102.6 | +5/-5 | 5 | -5 | 10.0017 | 15.3 | 67.8 | 1.62 | 86.4 | 1.82 | -0.28% | -0.28% |  |  | 4 |  |  |  |  | 47.24 | 23.62 | 0.26 | 7.7487 | 26.5 |  |  | 1500 | 2018-06-29 | First_Solar
First Solar | FS4112-3 | thin film | 112.5 | 104.5 | +5/-5 | 5 | -5 | 10.0017 | 15.6 | 68.5 | 1.64 | 87 | 1.83 | -0.28% | -0.28% |  |  | 4 |  |  |  |  | 47.24 | 23.62 | 0.26 | 7.7487 | 26.5 |  |  | 1500 | 2018-06-29 | First_Solar
First Solar | FS4115-3 | thin film | 115 | 107.3 | +5/-5 | 5 | -5 | 10.0017 | 16 | 69.3 | 1.66 | 87.6 | 1.83 | -0.28% | -0.28% |  |  | 4 |  |  |  |  | 47.24 | 23.62 | 0.26 | 7.7487 | 26.5 |  |  | 1500 | 2018-06-29 | First_Solar
First Solar | FS4117-3 | thin film | 117.5 | 109.7 | +5/-5 | 5 | -5 | 10.0017 | 16.3 | 70.1 | 1.68 | 88.1 | 1.83 | -0.28% | -0.28% |  |  | 4 |  |  |  |  | 47.24 | 23.62 | 0.26 | 7.7487 | 26.5 |  |  | 1500 | 2018-06-29 | First_Solar
First Solar | FS4120-3 | thin film | 120 | 112.1 | +5/-5 | 5 | -5 | 10.0017 | 16.7 | 70.8 | 1.7 | 88.7 | 1.84 | -0.28% | -0.28% |  |  | 4 |  |  |  |  | 47.24 | 23.62 | 0.26 | 7.7487 | 26.5 |  |  | 1500 | 2018-06-29 | First_Solar
First Solar | FS4122-3 | thin film | 122.5 | 114.5 | +5/-5 | 5 | -5 | 10.0017 | 17 | 71.5 | 1.71 | 88.7 | 1.85 | -0.28% | -0.28% |  |  | 4 |  |  |  |  | 47.24 | 23.62 | 0.26 | 7.7487 | 26.5 |  |  | 1500 | 2018-06-29 | First_Solar
First Solar | FS6420 | thin film | 420 |  | +5/-5 | 5 | -5 | 10.0017 | 17 | 180.4 | 2.33 | 218.5 | 2.54 | -0.32% | -0.28% |  |  | 6 |  |  |  |  | 79.1 | 48.5 | 1.9 |  | 77.16 |  |  | 1500 | 2018-06-29 | First_Solar
First Solar | FS6425 | thin film | 425 |  | +5/-5 | 5 | -5 | 10.0017 | 17.2 | 181.5 | 2.34 | 218.9 | 2.54 | -0.32% | -0.28% |  |  | 6 |  |  |  |  | 79.1 | 48.5 | 1.9 |  | 77.16 |  |  | 1500 | 2018-06-29 | First_Solar
First Solar | FS6430 | thin film | 430 |  | +5/-5 | 5 | -5 | 10.0017 | 17.4 | 182.6 | 2.36 | 219.2 | 2.54 | -0.32% | -0.28% |  |  | 6 |  |  |  |  | 79.1 | 48.5 | 1.9 |  | 77.16 |  |  | 1500 | 2018-06-29 | First_Solar
First Solar | FS6435 | thin film | 435 |  | +5/-5 | 5 | -5 | 10.0017 | 17.6 | 183.6 | 2.37 | 219.6 | 2.55 | -0.32% | -0.28% |  |  | 6 |  |  |  |  | 79.1 | 48.5 | 1.9 |  | 77.16 |  |  | 1500 | 2018-06-29 | First_Solar
First Solar | FS6440 | thin film | 440 |  | +5/-5 | 5 | -5 | 10.0017 | 17.8 | 184.7 | 2.38 | 220 | 2.55 | -0.32% | -0.28% |  |  | 6 |  |  |  |  | 79.1 | 48.5 | 1.9 |  | 77.16 |  |  | 1500 | 2018-06-29 | First_Solar
First Solar | FS6445 | thin film | 445 |  | +5/-5 | 5 | -5 | 10.0017 | 18 | 185.7 | 2.4 | 220.4 | 2.56 | -0.32% | -0.28% |  |  | 6 |  |  |  |  | 79.1 | 48.5 | 1.9 |  | 77.16 |  |  | 1500 | 2018-06-29 | First_Solar
GE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | GE
GE | GEPVc-170-MS | mono | 170 |  | +5/-5 | 5 | -5 | 12.5137 | 13.45 | 36.5 | 4.65 | 43.9 | 5.1 | -0.5% | -0.3417% |  |  | 15 |  | Solarlok |  |  | 62.5 | 31.3 | 1.4 | 13.5851 | 32.3 | 5 |  | Check |  | GE
GE | GEPVp-066-G | poly | 66 |  | +5/-5 | 5 | -5 | 9.2308 | 10.11 | 9 | 7.4 | 10.9 | 8.2 | -0.4% | -0.2752% |  |  | 15 |  | Solarlok |  |  | 58.5 | 17.6 | 1.2 | 7.15 | 18 | 5 |  | Check |  | GE
GE | GEPVp-200-MS | poly | 200 |  | +5/-5 | 5 | -5 | 12.7541 | 13.73 | 26.3 | 7.6 | 32.9 | 8.1 | -0.5% | -0.3647% |  |  | 15 |  | Solarlok |  |  | 58.5 | 38.6 | 1.4 | 15.6813 | 39 | 5 |  | Check |  | GE
Global Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Global_Solar
Global Solar | PowerFLEX BIPV 250 | CIGS | 250 |  | +7/-7 | 7 | -7 |  | 7 | 46.5 | 5.4 | 65.7 | 6.2 | -0.43% | -0.33% |  |  | n/a | [11 empty] | Check | 2012-04-06 | Global_Solar
Global Solar | PowerFLEX BIPV 275 | CIGS | 275 |  | +10/-7 | 10 | -7 |  | 7 | 51.5 | 5.3 | 67.6 | 6.3 | -0.38% | -0.33% |  |  | n/a | [11 empty] | Check | 2015-12-02 | Global_Solar
Global Solar | PowerFLEX BIPV 300 | CIGS | 300 |  | +10/-7 | 10 | -7 |  | 7 | 54.3 | 5.5 | 69.7 | 6.4 | -0.38% | -0.33% |  |  | n/a | [11 empty] | Check | 2015-12-02 | Global_Solar
Gloria Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Gloria_Solar
Gloria Solar | GSM6-200D-E1 | poly | 200 | 170 | +/-3 | 3 | -3 | 12.5374 | 13.49 | 26 | 7.69 | 33 | 8.42 | -0.405% | -0.312% | 0.075 | 47 | 15 | DNR | N/A | silver | white | 58.81 | 39.06 | 1.38 | 15.9522 | 38.36 | 5 |  | Check |  | Gloria_Solar
Gloria Solar | GSM6-205D-E1 | poly | 205 | 174.4 | +/-3 | 3 | -3 | 12.8509 | 13.83 | 26.3 | 7.79 | 33.2 | 8.49 | -0.405% | -0.312% | 0.075 | 47 | 15 | DNR | N/A | silver | white | 58.81 | 39.06 | 1.38 | 15.9522 | 38.36 | 5 |  | Check |  | Gloria_Solar
Gloria Solar | GSM6-210D-E1 | poly | 210 | 178.8 | +/-3 | 3 | -3 | 13.1643 | 14.17 | 26.6 | 7.89 | 33.4 | 8.56 | -0.405% | -0.312% | 0.075 | 47 | 15 | DNR | N/A | silver | white | 58.81 | 39.06 | 1.38 | 15.9522 | 38.36 | 5 |  | Check |  | Gloria_Solar
Gloria Solar | GSM6-215D-E1 | poly | 215 | 183.2 | +/-3 | 3 | -3 | 12.1885 | 13.12 | 28.5 | 7.54 | 36.96 | 8.34 | -0.415% | -0.3% | 0.0254 | 47 | 15 | DNR | N/A | silver | white | 65.039 | 39.055 | 1.968 | 17.6396 | 48.4 | 5 |  | Check |  | Gloria_Solar
Gloria Solar | GSM6-220D-E1 | poly | 220 | 187.6 | +/-3 | 3 | -3 | 12.472 | 13.42 | 28.84 | 7.64 | 37.08 | 8.38 | -0.415% | -0.3% | 0.0254 | 47 | 15 | DNR | N/A | silver | white | 65.039 | 39.055 | 1.968 | 17.6396 | 48.4 | 5 |  | Check |  | Gloria_Solar
Gloria Solar | GSM6-225D-E1 | poly | 225 | 202.2 | +/-3 | 3 | -3 | 12.7554 | 13.73 | 29.05 | 7.77 | 37.26 | 8.47 | -0.415% | -0.3% | 0.0254 | 47 | 15 | DNR | N/A | silver | white | 65.039 | 39.055 | 1.968 | 17.6396 | 48.4 | 5 |  | Check |  | Gloria_Solar
Gloria Solar | GSM6-230D-E1 | poly | 230 | 206.8 | +/-3 | 3 | -3 | 13.0389 | 14.03 | 29.38 | 7.84 | 37.42 | 8.51 | -0.415% | -0.3% | 0.0254 | 47 | 15 | DNR | N/A | silver | white | 65.039 | 39.055 | 1.968 | 17.6396 | 48.4 | 5 |  | Check |  | Gloria_Solar
Gloria Solar | GSM6-235D-E1 | poly | 235 | 211.4 | +/-3 | 3 | -3 | 13.3223 | 14.34 | 29.72 | 7.93 | 37.8 | 8.59 | -0.415% | -0.3% | 0.0254 | 47 | 15 | DNR | N/A | silver | white | 65.039 | 39.055 | 1.968 | 17.6396 | 48.4 | 5 |  | Check |  | Gloria_Solar
Gloria Solar | GSS5-175A-E1 | mono | 175 | 157.4 | +/-3 | 3 | -3 | 12.6164 | 13.58 | 36.13 | 4.85 | 44.83 | 5.21 | -0.381% | -0.282% | 0.0248 | DNR | 10 | DNR | tyco | silver | white | 62.95 | 31.73 | 1.57 | 13.8709 | 34.8 | 5 |  | Check |  | Gloria_Solar
Gloria Solar | GSS5-180A-E1 | mono | 180 | 162 | +/-3 | 3 | -3 | 12.9768 | 13.97 | 35.44 | 4.94 | 45.16 | 5.31 | -0.381% | -0.282% | 0.0248 | DNR | 10 | DNR | tyco | silver | white | 62.95 | 31.73 | 1.57 | 13.8709 | 34.8 | 5 |  | Check |  | Gloria_Solar
Gloria Solar | GSM6-275 | multi | 275 |  | +/-3 | 3 | -3 |  |  | 35.84 | 7.67 | 43.48 | 8.21 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Gloria_Solar
Gloria Solar | GSM6-280 | multi | 280 |  | +/-3 | 3 | -3 |  |  | 36.15 | 7.74 | 43.74 | 8.28 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Gloria_Solar
Gloria Solar | GSM6-285 | multi | 285 |  | +/-3 | 3 | -3 |  |  | 36.46 | 7.82 | 44.09 | 8.35 | -0.405% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Gloria_Solar
Gloria Solar | GSS6-250 | mono | 250 |  | +/-3 | 3 | -3 |  |  | 30.91 | 8.09 | 37.41 | 8.65 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Gloria_Solar
Gloria Solar | GSS6-255 | mono | 255 |  | +/-3 | 3 | -3 |  |  | 31.07 | 8.21 | 37.53 | 8.77 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Gloria_Solar
Gloria Solar | GSS6-260 | mono | 260 |  | +/-3 | 3 | -3 |  |  | 31.24 | 8.32 | 37.64 | 8.87 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Gloria_Solar
Gloria Solar | GSS6-265 | mono | 265 |  | +/-3 | 3 | -3 |  |  | 31.39 | 8.44 | 37.74 | 8.97 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Gloria_Solar
Gloria Solar | GSS6-300 | mono | 300 |  | +/-3 | 3 | -3 |  |  | 37.09 | 8.09 | 44.9 | 8.65 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Gloria_Solar
Gloria Solar | GSS6-305 | mono | 305 |  | +/-3 | 3 | -3 |  |  | 37.25 | 8.19 | 45.01 | 8.75 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Gloria_Solar
Gloria Solar | GSS6-310 | mono | 310 |  | +/-3 | 3 | -3 |  |  | 37.42 | 8.28 | 45.12 | 8.84 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Gloria_Solar
Gloria Solar | GSS6-315 | mono | 315 |  | +/-3 | 3 | -3 |  |  | 37.59 | 8.38 | 45.23 | 8.92 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Gloria_Solar
Gloria Solar | GSS6-320 | mono | 320 |  | +/-3 | 3 | -3 |  |  | 37.74 | 8.48 | 45.29 | 9 | -0.412% | -0.328% |  |  | 15 | [11 empty] | Check | 2015-12-02 | Gloria_Solar
Grape Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Grape_Solar
Grape Solar | CS-P-220-DJ | poly | 220 | 194 | +3/-0 | 3 | 0 | 12.5122 | 13.468 | 29.4 | 7.48 | 35.9 | 8.4 | -0.45% | -0.35% | 0.05 | 48 | 15 | yes | MC4 | silver | white | 64.9606 | 38.9764 | 1.5748 | 17.5828 | 42.9515 | 10 |  | Check |  | Grape_Solar
Grape Solar | CS-P-230-DJ | poly | 230 | 203.1 | +3/-0 | 3 | 0 | 13.0809 | 14.0802 | 29.7 | 7.74 | 36.2 | 8.7 | -0.45% | -0.35% | 0.050575 | 48 | 15 | yes | MC4 | silver | white | 64.9606 | 38.9764 | 1.5748 | 17.5828 | 42.9515 | 10 |  | Check |  | Grape_Solar
Grape Solar | CS-P-240-DJ | poly | 240 | 211.7 | +/-2 | 2 | -2 | 13.7052 | 14.7522 | 30.5 | 7.87 | 37.3 | 8.46 | -0.48% | -0.34% | 0.019976 | 47 | 15 | yes | MC4 | silver | white | 64.5669 | 39.0551 | 1.811 | 17.5116 | 43.1718 | 10 |  | Check |  | Grape_Solar
Grape Solar | CS-P-270-DJ | poly | 270 | 238.9 | +3/-0 | 3 | 0 | 12.947 | 13.936 | 35.2 | 7.67 | 43.7 | 8.59 | -0.45% | -0.35% | 0.051804 | 48 | 15 | yes | MC4 | silver | white | 77.0472 | 38.9764 | 1.9685 | 20.8543 | 55.0661 | 10 |  | Check |  | Grape_Solar
Grape Solar | CS-P-280-DJ | poly | 280 | 248 | +3/-0 | 3 | 0 | 13.4265 | 14.4521 | 35.3 | 7.93 | 43.8 | 8.76 | -0.45% | -0.35% | 0.050913 | 48 | 15 | yes | MC4 | silver | white | 77.0472 | 38.9764 | 1.9685 | 20.8543 | 55.0661 | 10 |  | Check |  | Grape_Solar
Grape Solar | CS-S-175-DJ | mono | 175 |  | +3/-0 | 3 | 0 | 12.6801 | 13.6 | 35.8 | 4.89 | 44.2 | 5.25 | -0.37% | -0.34% |  |  | 10 |  | MC |  |  | 62.3 | 31.9 | 1.57 | 13.8012 | 34.2 | 10 |  | Check |  | Grape_Solar
Grape Solar | CS-S-180-DJ | mono | 180 | 161 | +3/-0 | 3 | 0 | 13.0989 | 14.0995 | 36.2 | 4.97 | 44.2 | 5.36 | -0.37% | -0.34% | 0.089925 | 48 | 10 | yes | MC4 | silver | white | 62.2047 | 31.811 | 1.5748 | 13.7416 | 34.141 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-210-OR | poly | 210 | 188.5 | +/-1.25 | 1.25 | -1.25 | 12.129 | 13.0555 | 28.5 | 7.4 | 36.5 | 7.9 | -0.44% | -0.32% | 0.040506 | 46 | 15 | yes | MC4 | silver | white | 64.4882 | 38.6614 | 1.378 | 17.3139 | 50 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-215-OR | poly | 215 | 193.1 | +/-1.25 | 1.25 | -1.25 | 12.4178 | 13.3664 | 28.9 | 7.47 | 36.8 | 7.96 | -0.44% | -0.32% | 0.040201 | 46 | 15 | yes | MC4 | silver | white | 64.4882 | 38.6614 | 1.378 | 17.3139 | 50 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-220-Fab1 | poly | 220 | 196.6 | +3/-0 | 3 | 0 | 12.3721 | 13.3172 | 29.5 | 7.46 | 36.7 | 8.02 | -0.48% | -0.36% | 0.033042 | 45 | 15 | yes | MC4 | silver | white | 65.0394 | 39.3701 | 1.9685 | 17.782 | 44.0529 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-220-Fab5 | poly | 220 | 197.2 | +3/-0 | 3 | 0 | 12.5885 | 13.5501 | 30.1 | 7.31 | 36.3 | 7.81 | -0.47% | -0.38% | 0.039949 | 47 | 15 | yes | MC4 | silver | white | 64.5669 | 38.9764 | 1.5748 | 17.4763 | 40.9692 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-225-EUG | poly | 225 | 203.1 | +3/-0 | 3 | 0 | 12.8486 | 13.8302 | 30.1 | 7.48 | 36.8 | 8.1 | -0.48% | -0.34% | 0.02 | 47 | 15 | yes | MC4 | silver | white | 64.5669 | 39.0551 | 1.811 | 17.5116 | 43.1718 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-225-Fab1 | poly | 225 | 201.2 | +3/-0 | 3 | 0 | 12.6533 | 13.6199 | 29.7 | 7.58 | 36.8 | 8.13 | -0.48% | -0.36% | 0.033042 | 45 | 15 | yes | MC4 | silver | white | 65.0394 | 39.3701 | 1.9685 | 17.782 | 44.0529 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-225-Fab5 | poly | 225 | 201.8 | +3/-0 | 3 | 0 | 12.8746 | 13.8581 | 30.2 | 7.46 | 36.3 | 7.97 | -0.47% | -0.38% | 0.040151 | 47 | 15 | yes | MC4 | silver | white | 64.5669 | 38.9764 | 1.5748 | 17.4763 | 40.9692 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-230-EUG | poly | 230 | 207.7 | +3/-0 | 3 | 0 | 13.1342 | 14.1375 | 30.3 | 7.6 | 37 | 8.2 | -0.48% | -0.34% | 0.02 | 47 | 15 | yes | MC4 | silver | white | 64.5669 | 39.0551 | 1.811 | 17.5116 | 43.1718 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-230-Fab1 | poly | 230 | 205.8 | +3/-0 | 3 | 0 | 12.9344 | 13.9225 | 29.9 | 7.69 | 37 | 8.24 | -0.48% | -0.36% | 0.033042 | 45 | 15 | yes | MC4 | silver | white | 65.0394 | 39.3701 | 1.9685 | 17.782 | 44.0529 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-230-Fab5 | poly | 230 | 206.4 | +3/-0 | 3 | 0 | 13.1607 | 14.1661 | 30.4 | 7.58 | 36.4 | 8.11 | -0.47% | -0.38% | 0.039951 | 47 | 15 | yes | MC4 | silver | white | 64.5669 | 38.9764 | 1.5748 | 17.4763 | 40.9692 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-235-Fab1 | poly | 235 | 210.4 | +3/-0 | 3 | 0 | 13.2156 | 14.2252 | 30.1 | 7.81 | 37.2 | 8.35 | -0.48% | -0.36% | 0.033042 | 45 | 15 | yes | MC4 | silver | white | 65.0394 | 39.3701 | 1.9685 | 17.782 | 44.0529 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-235-Fab5 | poly | 235 | 211 | +3/-0 | 3 | 0 | 13.4468 | 14.474 | 30.6 | 7.68 | 36.5 | 8.22 | -0.47% | -0.38% | 0.040024 | 47 | 15 | yes | MC4 | silver | white | 64.5669 | 38.9764 | 1.5748 | 17.4763 | 40.9692 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-235-PDX | poly | 235 | 208.7 | +3/-0 | 3 | 0 | 13.4197 | 14.4448 | 29.1 | 8.09 | 37.1 | 8.69 | -0.47% | -0.34% | 0.045109 | 45 | 15 | yes | MC4 | silver | white | 64.5669 | 39.0551 | 1.9685 | 17.5116 | 43.1718 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-240-Fab1 | poly | 240 | 214.9 | +/-2 | 2 | -2 | 13.4968 | 14.5278 | 30.3 | 7.92 | 37.3 | 8.47 | -0.48% | -0.36% | 0.033058 | 45 | 15 | yes | MC4 | silver | white | 65.0394 | 39.3701 | 1.9685 | 17.782 | 44.0529 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-270-EUG | poly | 270 | 242.7 | +3/-0 | 3 | 0 | 12.9275 | 13.915 | 36.1 | 7.48 | 44.1 | 8.1 | -0.48% | -0.34% | 0.02 | 47 | 15 | yes | MC4 | silver | white | 77.0079 | 39.0551 | 1.9685 | 20.8858 | 51.1013 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-275-EUG | poly | 275 | 247.3 | +3/-0 | 3 | 0 | 13.1669 | 14.1727 | 36.2 | 7.6 | 44.3 | 8.2 | -0.48% | -0.34% | 0.02 | 47 | 15 | yes | MC4 | silver | white | 77.0079 | 39.0551 | 1.9685 | 20.8858 | 51.1013 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-280-EUG | poly | 280 | 252 | +3/-0 | 3 | 0 | 13.4063 | 14.4304 | 36.4 | 7.7 | 44.5 | 8.28 | -0.48% | -0.34% | 0.020048 | 47 | 15 | yes | MC4 | silver | white | 77.0079 | 39.0551 | 1.9685 | 20.8858 | 51.1013 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-280-Fab1 | poly | 280 | 251 | +3/-0 | 3 | 0 | 13.2179 | 14.2276 | 35.8 | 7.82 | 44.6 | 8.43 | -0.45% | -0.35% | 0.060024 | 45 | 15 | yes | MC4 | silver | white | 77.4803 | 39.3701 | 1.9685 | 21.1834 | 52.8634 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-285-Fab1 | poly | 285 | 255.6 | +/-2 | 2 | -2 | 13.4539 | 14.4817 | 36 | 7.92 | 44.6 | 8.56 | -0.45% | -0.35% | 0.060047 | 45 | 15 | yes | MC4 | silver | white | 77.4803 | 39.3701 | 1.9685 | 21.1834 | 52.8634 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-290-Fab1 | poly | 290 | 260.2 | +/-2 | 2 | -2 | 13.69 | 14.7358 | 36 | 8.05 | 44.8 | 8.75 | -0.45% | -0.35% | 0.06 | 45 | 15 | yes | MC4 | silver | white | 77.4803 | 39.3701 | 1.9685 | 21.1834 | 52.8634 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-P-295-Fab1 | poly | 295 | 264.8 | +/-2 | 2 | -2 | 13.926 | 14.9898 | 36.2 | 8.15 | 45 | 8.92 | -0.45% | -0.35% | 0.059978 | 45 | 15 | yes | MC4 | silver | white | 77.4803 | 39.3701 | 1.9685 | 21.1834 | 52.8634 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-185-SF | mono | 185 | 163.7 | +3/-0 | 3 | 0 | 13.4627 | 14.4912 | 36 | 5.15 | 44.8 | 5.5 | -0.5% | -0.35% | 0.060364 | 50 | 10 | yes | MC4 | silver | white | 62.2047 | 31.811 | 1.5748 | 13.7416 | 34.141 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-185-SF5 | mono | 185 |  | +3/-3 | 3 | -3 | 13.4047 | 14.4 | 36.2 | 5.15 | 45 | 5.5 | -0.37% | -0.34% |  |  | 10 |  | MC |  |  | 62.3 | 31.9 | 1.4 | 13.8012 | 35.2 | 5 |  | Check |  | Grape_Solar
Grape Solar | GS-S-190-Fab3 | mono | 190 | 169 | +3/-0 | 3 | 0 | 13.8266 | 14.8828 | 36.2 | 5.25 | 45.4 | 5.44 | -0.45% | -0.35% | 0.055147 | 45 | 10 | yes | MC4 | silver | white | 62.2047 | 31.811 | 1.5748 | 13.7416 | 34.141 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-195-Fab3 | mono | 195 | 173.5 | +3/-0 | 3 | 0 | 14.1904 | 15.2745 | 36.2 | 5.38 | 45.5 | 5.58 | -0.45% | -0.35% | 0.055556 | 45 | 10 | yes | MC4 | silver | white | 62.2047 | 31.811 | 1.5748 | 13.7416 | 34.141 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-200-Fab1 | mono | 200 | 178.4 | +/-2 | 2 | -2 | 14.5543 | 15.6661 | 36.3 | 5.51 | 45.6 | 5.71 | -0.45% | -0.35% | 0.056042 | 45 | 10 | yes | MC4 | silver | white | 62.2047 | 31.811 | 1.5748 | 13.7416 | 34.141 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-230-CS | mono | 230 | 209.4 | +3/-0 | 3 | 0 | 12.5713 | 13.5316 | 47.5 | 4.84 | 59.1 | 5.18 | -0.45% | -0.35% | 0.061776 | 45 | 10 | yes | MC4 | silver | white | 63.0709 | 41.7717 | 1.5748 | 18.2957 | 44.0529 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-240-Fab1 | mono | 240 | 214.9 | +3/-0 | 3 | 0 | 13.4968 | 14.5278 | 30.3 | 7.92 | 37.3 | 8.47 | -0.48% | -0.36% | 0.033058 | 45 | 15 | yes | MC4 | silver | white | 65.0394 | 39.3701 | 1.9685 | 17.782 | 44.0529 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-250-Fab3 | mono | 250 | 223.7 | +3/-0 | 3 | 0 | 13.7463 | 14.7964 | 48.7 | 5.14 | 59.6 | 5.49 | -0.45% | -0.35% | 0.06 | 45 | 10 | yes | MC4 | silver | white | 62.9921 | 41.5748 | 1.5748 | 18.1867 | 42.9515 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-250-Fab5 | mono | 250 | 222.1 | +/-2 | 2 | -2 | 14.0592 | 15.1332 | 30.7 | 8.15 | 37.7 | 8.72 | -0.48% | -0.34% | 0.040023 | 45 | 15 | yes | MC4 | silver | white | 65.0394 | 39.3701 | 1.9685 | 17.782 | 44.0529 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-250-Fab8 | mono | 250 | 223 | +3/-0 | 3 | 0 | 13.7463 | 14.7964 | 50.8 | 4.92 | 59.9 | 5.26 | -0.47% | -0.38% | 0.039924 | 47 | 10 | yes | MC4 | silver | white | 62.9921 | 41.5748 | 1.5748 | 18.1867 | 42.9515 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-255-Fab3 | mono | 255 | 228.3 | +/-2 | 2 | -2 | 14.0214 | 15.0925 | 49 | 5.2 | 59.7 | 5.57 | -0.45% | -0.35% | 0.059246 | 45 | 10 | yes | MC4 | silver | white | 62.2835 | 42.0472 | 1.9685 | 18.1864 | 44.0529 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-270-Fab1 | mono | 270 | 241.5 | +3/-0 | 3 | 0 | 12.7458 | 13.7195 | 35.8 | 7.54 | 44.6 | 8.16 | -0.45% | -0.35% | 0.060049 | 45 | 15 | yes | MC4 | silver | white | 77.4803 | 39.3701 | 1.9685 | 21.1834 | 52.8634 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-280-Fab1 | mono | 280 | 250.7 | +3/-0 | 3 | 0 | 13.2179 | 14.2276 | 35.8 | 7.82 | 44.6 | 8.43 | -0.45% | -0.35% | 0.060049 | 45 | 15 | yes | MC4 | silver | white | 77.4803 | 39.3701 | 1.9685 | 21.1834 | 52.8634 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-285-Fab1 | mono | 285 | 255.3 | +3/-0 | 3 | 0 | 13.4539 | 14.4817 | 36 | 7.92 | 44.6 | 8.56 | -0.45% | -0.35% | 0.060049 | 45 | 15 | yes | MC4 | silver | white | 77.4803 | 39.3701 | 1.9685 | 21.1834 | 52.8634 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-290-Fab1 | mono | 290 | 259.9 | +3/-0 | 3 | 0 | 13.69 | 14.7358 | 36 | 8.05 | 44.8 | 8.75 | -0.45% | -0.35% | 0.060049 | 45 | 15 | yes | MC4 | silver | white | 77.4803 | 39.3701 | 1.9685 | 21.1834 | 52.8634 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-295-Fab1 | mono | 295 | 264.5 | +/-2 | 2 | -2 | 13.926 | 14.9898 | 36.2 | 8.15 | 45 | 8.92 | -0.45% | -0.35% | 0.060049 | 45 | 15 | yes | MC4 | silver | white | 77.4803 | 39.3701 | 1.9685 | 21.1834 | 52.8634 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-385-TS | mono | 385 | 336.4 | +/-2 | 2 | -2 | 13.9517 | 15.0175 | 49 | 7.87 | 59.5 | 8.36 | -0.5% | -0.4% | 0.045455 | 47 | 15 | yes | MC4 | silver | white | 77.1654 | 51.4961 | 1.5748 | 27.5952 | 78.1938 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-390-TS | mono | 390 | 341 | +/-2 | 2 | -2 | 14.1329 | 15.2125 | 49.4 | 7.92 | 59.6 | 8.42 | -0.5% | -0.4% | 0.045455 | 47 | 15 | yes | MC4 | silver | white | 77.1654 | 51.4961 | 1.5748 | 27.5952 | 78.1938 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-395-Platinum | mono | 395 | 345.5 | +/-2 | 2 | -2 | 14.3141 | 15.4075 | 49.5 | 7.98 | 59.7 | 8.49 | -0.5% | -0.4% | 0.045455 | 47 | 15 | yes | MC4 | silver | white | 77.1654 | 51.4961 | 1.5748 | 27.5952 | 78.1938 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-400-Platinum | mono | 400 | 350 | +/-2 | 2 | -2 | 14.4953 | 15.6026 | 49.8 | 8.04 | 60 | 8.56 | -0.5% | -0.4% | 0.045455 | 47 | 15 | yes | MC4 | silver | white | 77.1654 | 51.4961 | 1.5748 | 27.5952 | 78.1938 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-405-Platinum | mono | 405 | 354.6 | +/-2 | 2 | -2 | 14.6765 | 15.7976 | 50.1 | 8.1 | 60.4 | 8.66 | -0.5% | -0.4% | 0.045455 | 47 | 15 | yes | MC4 | silver | white | 77.1654 | 51.4961 | 1.5748 | 27.5952 | 78.1938 | 10 |  | Check |  | Grape_Solar
Grape Solar | GS-S-410-Platinum | mono | 410 | 359.1 | +/-2 | 2 | -2 | 14.8576 | 15.9926 | 50.3 | 8.15 | 61.1 | 8.77 | -0.5% | -0.4% | 0.045455 | 47 | 15 | yes | MC4 | silver | white | 77.1654 | 51.4961 | 1.5748 | 27.5952 | 78.1938 | 10 |  | Check |  | Grape_Solar
Hanwha SolarOne | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Hanwha_SolarOne
Hanwha SolarOne | SF160-24-1M175 | mono | 175 | 156.4 | +/-3 | 3 | -3 | 12.7404 | 13.7 | 35.2 | 4.98 | 44 | 5.48 | -0.44% | -0.33% | 0.03 | 45 | 10 | yes | MC4/H4 | silver/black | white/black | 62.2 | 31.8 | 1.38 | 13.7358 | 28.6 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF160-24-1M180 | mono | 180 | 161 | +/-3 | 3 | -3 | 13.1044 | 14.1 | 35.4 | 5.11 | 44.3 | 5.59 | -0.44% | -0.33% | 0.03 | 45 | 10 | yes | MC4/H4 | silver/black | white/black | 62.2 | 31.8 | 1.38 | 13.7358 | 28.6 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF160-24-1M185 | mono | 185 | 165.6 | +/-3 | 3 | -3 | 13.4684 | 14.5 | 35.6 | 5.21 | 44.6 | 5.68 | -0.44% | -0.33% | 0.03 | 45 | 10 | yes | MC4/H4 | silver/black | white/black | 62.2 | 31.8 | 1.38 | 13.7358 | 28.6 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF160-24-1M190 | mono | 190 | 170.2 | +/-3 | 3 | -3 | 13.8324 | 14.9 | 35.8 | 5.33 | 44.8 | 5.78 | -0.44% | -0.33% | 0.03 | 45 | 10 | yes | MC4/H4 | silver/black | white/black | 62.2 | 31.8 | 1.38 | 13.7358 | 28.6 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF160-24-1M195 | mono | 195 | 174.5 | +/-3 | 3 | -3 | 14.1964 | 15.3 | 36 | 5.42 | 45 | 5.85 | -0.44% | -0.33% | 0.03 | 45 | 10 | yes | MC4/H4 | silver/black | white/black | 62.2 | 31.8 | 1.38 | 13.7358 | 28.6 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF190-27-1P200 | poly | 200 | 177.7 | +/-3 | 3 | -3 | 12.4408 | 13.4 | 26.9 | 7.44 | 32.8 | 8.24 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 58.8 | 39.37 | 1.38 | 16.0761 | 35.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF190-27-1P205 | poly | 205 | 182.3 | +/-3 | 3 | -3 | 12.7519 | 13.7 | 27 | 7.6 | 32.9 | 8.35 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 58.8 | 39.37 | 1.38 | 16.0761 | 35.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF190-27-1P210 | poly | 210 | 186.5 | +/-3 | 3 | -3 | 13.0629 | 14 | 27.1 | 7.75 | 33 | 8.48 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 58.8 | 39.37 | 1.38 | 16.0761 | 35.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF190-27-1P215 | poly | 215 | 190 | +/-3 | 3 | -3 | 13.3739 | 14.4 | 27.2 | 7.91 | 33.1 | 8.54 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 58.8 | 39.37 | 1.38 | 16.0761 | 35.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF190-27-1P220 | poly | 220 | 193.8 | +/-3 | 3 | -3 | 13.6849 | 14.7 | 27.3 | 8.06 | 33.2 | 8.68 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 58.8 | 39.37 | 1.38 | 16.0761 | 35.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF190-27-1P225 | poly | 225 | 197.2 | +/-3 | 3 | -3 | 13.9959 | 15.1 | 27.5 | 8.18 | 33.3 | 8.75 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 58.8 | 39.37 | 1.38 | 16.0761 | 35.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF220-30-1P230 | poly | 230 | 207.6 | +/-3 | 3 | -3 | 12.9343 | 13.9 | 30 | 7.67 | 36.8 | 8.34 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 65.04 | 39.37 | 1.77 | 17.7821 | 46.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF220-30-1P235 | poly | 235 | 212.2 | +/-3 | 3 | -3 | 13.2155 | 14.2 | 30.1 | 7.81 | 36.8 | 8.44 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 65.04 | 39.37 | 1.77 | 17.7821 | 46.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF220-30-1P240 | poly | 240 | 216.9 | +/-3 | 3 | -3 | 13.4967 | 14.5 | 30.2 | 7.95 | 37 | 8.54 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 65.04 | 39.37 | 1.77 | 17.7821 | 46.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF220-30-1P245 | poly | 245 | 221.5 | +/-3 | 3 | -3 | 13.7779 | 14.8 | 30.3 | 8.08 | 37.1 | 8.64 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 65.04 | 39.37 | 1.77 | 17.7821 | 46.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF220-30-1P250 | poly | 250 | 225.2 | +/-3 | 3 | -3 | 14.0591 | 15.1 | 30.4 | 8.22 | 37.2 | 8.74 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 65.04 | 39.37 | 1.77 | 17.7821 | 46.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF220-30-1P255 | poly | 255 | 229 | +/-3 | 3 | -3 | 14.3403 | 15.4 | 30.5 | 8.35 | 37.4 | 8.85 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 65.04 | 39.37 | 1.77 | 17.7821 | 46.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF260-36-1P275 | poly | 275 | 247 | +/-3 | 3 | -3 | 12.9954 | 14 | 36.1 | 7.62 | 44.1 | 8.35 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 77.4 | 39.37 | 1.97 | 21.1614 | 57.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF260-36-1P280 | poly | 280 | 251.6 | +/-3 | 3 | -3 | 13.2317 | 14.3 | 36.1 | 7.76 | 44.3 | 8.4 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 77.4 | 39.37 | 1.97 | 21.1614 | 57.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF260-36-1P285 | poly | 285 | 256.2 | +/-3 | 3 | -3 | 13.4679 | 14.5 | 36.2 | 7.87 | 44.5 | 8.45 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 77.4 | 39.37 | 1.97 | 21.1614 | 57.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF260-36-1P290 | poly | 290 | 260.8 | +/-3 | 3 | -3 | 13.7042 | 14.7 | 36.3 | 7.99 | 44.7 | 8.5 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 77.4 | 39.37 | 1.97 | 21.1614 | 57.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF260-36-1P295 | poly | 295 | 264.2 | +/-3 | 3 | -3 | 13.9405 | 15 | 36.4 | 8.11 | 44.9 | 8.55 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 77.4 | 39.37 | 1.97 | 21.1614 | 57.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | SF260-36-1P300 | poly | 300 | 269 | +/-3 | 3 | -3 | 14.1768 | 15.2 | 36.5 | 8.22 | 45 | 8.6 | -0.45% | -0.32% | 0.04 | 45 | 15 | yes | MC4/H4 | silver/black | white/black | 77.4 | 39.37 | 1.97 | 21.1614 | 57.2 | 5 |  | Check |  | Hanwha_SolarOne
Hanwha SolarOne | HSL60P6-PC-1-245 | poly | 245 |  | +3/-0 | 3 | 0 |  |  | 30.2 | 8.12 | 37.4 | 8.62 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | HSL60P6-PC-1-250 | poly | 250 |  | +3/-0 | 3 | 0 |  |  | 30.5 | 8.2 | 37.6 | 8.72 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | HSL60P6-PC-1-255 | poly | 255 |  | +3/-0 | 3 | 0 |  |  | 30.7 | 8.31 | 37.8 | 8.86 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | HSL60P6-PC-1-260 | poly | 260 |  | +3/-0 | 3 | 0 |  |  | 30.9 | 8.42 | 38.1 | 8.98 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | HSL60P6-PC-1-265 | poly | 265 |  | +3/-0 | 3 | 0 |  |  | 31.1 | 8.53 | 38.3 | 9.12 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | HSL60P6-PC-1-270 | poly | 270 |  | +3/-0 | 3 | 0 |  |  | 31.2 | 8.66 | 38.5 | 9.22 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | HSL72P6-PC-1-290 |  | 290 |  | +3/-0 | 3 | 0 |  |  | 36.2 | 8.02 | 44.4 | 8.49 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | HSL72P6-PC-1-295 |  | 295 |  | +3/-0 | 3 | 0 |  |  | 36.4 | 8.11 | 44.6 | 8.6 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | HSL72P6-PC-1-300 |  | 300 |  | +3/-0 | 3 | 0 |  |  | 36.6 | 8.2 | 44.8 | 8.7 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | HSL72P6-PC-1-305 |  | 305 |  | +3/-0 | 3 | 0 |  |  | 36.8 | 8.29 | 45 | 8.81 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | HSL72P6-PC-1-310 |  | 310 |  | +3/-0 | 3 | 0 |  |  | 37.1 | 8.36 | 45.1 | 8.91 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | HSL72P6-PC-1-315 |  | 315 |  | +3/-0 | 3 | 0 |  |  | 37.3 | 8.45 | 45.3 | 9.02 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | Q.PEAK-G4.1-290 | mono | 290 | 265.9 | +5/-0 | 5 | 0 |  |  | 31.96 | 9.07 | 39.19 | 9.63 | -0.39% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Hanwha_SolarOne
Hanwha SolarOne | Q.PEAK-G4.1-295 | mono | 295 | 272.6 | +5/-0 | 5 | 0 |  |  | 32.19 | 9.17 | 39.48 | 9.7 | -0.39% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Hanwha_SolarOne
Hanwha SolarOne | Q.PEAK-G4.1-300 | mono | 300 | 277.4 | +5/-0 | 5 | 0 |  |  | 32.41 | 9.26 | 39.76 | 9.76 | -0.39% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Hanwha_SolarOne
Hanwha SolarOne | Q.PEAK-G4.1-305 | mono | 305 | 282.1 | +5/-0 | 5 | 0 |  |  | 32.62 | 9.35 | 40.05 | 9.84 | -0.39% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Hanwha_SolarOne
Hanwha SolarOne | Q.PEAK BLK-G4.1-285 | mono | 285 | 261.2 | +5/-0 | 5 | 0 |  |  | 31.73 | 8.98 | 38.91 | 9.56 | -0.39% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Hanwha_SolarOne
Hanwha SolarOne | Q.PEAK BLK-G4.1-290 | mono | 290 | 265.9 | +5/-0 | 5 | 0 |  |  | 31.96 | 9.07 | 39.19 | 9.63 | -0.39% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Hanwha_SolarOne
Hanwha SolarOne | Q.PEAK BLK-G4.1-295 | mono | 295 | 270.6 | +5/-0 | 5 | 0 |  |  | 32.19 | 9.17 | 39.48 | 9.7 | -0.39% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Hanwha_SolarOne
Hanwha SolarOne | Q.PEAK DUO-G5-315 | mono | 315 | 291.2 | +5/-0 | 5 | 0 |  |  | 32.98 | 9.55 | 39.87 | 10.04 | -0.37% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Hanwha_SolarOne
Hanwha SolarOne | Q.PEAK DUO-G5-320 | mono | 320 | 295.9 | +5/-0 | 5 | 0 |  |  | 33.32 | 9.6 | 40.13 | 10.09 | -0.37% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Hanwha_SolarOne
Hanwha SolarOne | Q.PEAK DUO-G5-325 | mono | 325 | 300.7 | +5/-0 | 5 | 0 |  |  | 33.65 | 9.66 | 40.4 | 10.14 | -0.37% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Hanwha_SolarOne
Hanwha SolarOne | Q.PEAK DUO-G5-330 | mono | 330 | 305.1 | +5/-0 | 5 | 0 |  |  | 33.98 | 9.71 | 40.66 | 10.2 | -0.37% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Hanwha_SolarOne
Hanwha SolarOne | Q.PEAK BLK-DUO-G5-305 | mono | 305 | 280.3 | +5/-0 | 5 | 0 |  |  | 32.78 | 9.31 | 39.75 | 9.78 | -0.37% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Hanwha_SolarOne
Hanwha SolarOne | Q.PEAK BLK-DUO-G5-310 | mono | 310 | 287.4 | +5/-0 | 5 | 0 |  |  | 33.12 | 9.36 | 40.02 | 9.83 | -0.37% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Hanwha_SolarOne
Hanwha SolarOne | Q.PEAK BLK-DUO-G5-315 | mono | 315 | 292.2 | +5/-0 | 5 | 0 |  |  | 33.46 | 9.41 | 40.29 | 9.89 | -0.37% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Hanwha_SolarOne
Hanwha SolarOne | Q.PEAK BLK-DUO-G5-320 | mono | 320 | 297 | +5/-0 | 5 | 0 |  |  | 33.8 | 9.47 | 40.56 | 9.94 | -0.37% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-10 | Hanwha_SolarOne
Hanwha SolarOne | Q.PRO-G4-255 |  | 255 | 230.8 | +3/-3 | 3 | -3 |  |  | 30.18 | 8.45 | 37.54 | 9.07 | -0.41% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | Q.PRO-G4-260 |  | 260 | 235.4 | +3/-3 | 3 | -3 |  |  | 30.46 | 8.53 | 37.77 | 9.15 | -0.41% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | Q.PRO-G4-265 |  | 265 | 240.1 | +3/-3 | 3 | -3 |  |  | 30.75 | 8.62 | 38.01 | 9.23 | -0.41% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | Q.PRO-G4.1-260 | poly | 260 | 236.9 | +5/-0 | 5 | 0 |  |  | 30.46 | 8.53 | 37.77 | 9.15 | -0.41% | -0.3% |  |  | 20 |  |  |  |  | 65.75 | 39.4 | 1.26 |  | 41.45 |  |  | 1000 | 2018-06-12 | Hanwha_SolarOne
Hanwha SolarOne | Q.PRO-G4.1-265 | poly | 265 | 241.4 | +5/-0 | 5 | 0 |  |  | 30.75 | 8.62 | 38.01 | 9.23 | -0.41% | -0.3% |  |  | 20 |  |  |  |  | 65.75 | 39.4 | 1.26 |  | 41.45 |  |  | 1000 | 2018-06-12 | Hanwha_SolarOne
Hanwha SolarOne | Q.PRO-G4.1-270 | poly | 270 | 245.9 | +5/-0 | 5 | 0 |  |  | 31.02 | 8.7 | 38.24 | 9.31 | -0.41% | -0.3% |  |  | 20 |  |  |  |  | 65.75 | 39.4 | 1.26 |  | 41.45 |  |  | 1000 | 2018-06-12 | Hanwha_SolarOne
Hanwha SolarOne | Q.PLUS-G4.2-345 | mono | 345 | 316.8311 | +5/-0 | 5 | 0 |  | 17.3 | 37.93 | 9.09 | 47.46 | 9.64 | -0.4% | -0.29% |  |  | 20 |  |  |  |  | 78.5 | 39.4 | 1.38 |  | 52.9 |  |  | 1500 | 2018-07-06 | Hanwha_SolarOne | [11 empty] | 45
Hanwha SolarOne | Q.PLUS-G4.2-350 | mono | 350 | 321.5454 | +5/-0 | 5 | 0 |  | 17.6 | 38.23 | 9.15 | 47.71 | 9.69 | -0.4% | -0.29% |  |  | 20 |  |  |  |  | 78.5 | 39.4 | 1.38 |  |  |  |  | 1500 | 2018-07-06 | Hanwha_SolarOne | [11 empty] | 45
Hanwha SolarOne | Q.PLUS-G4.2-355 | mono | 355 | 326.2633 | +5/-0 | 5 | 0 |  | 17.8 | 38.52 | 9.21 | 47.97 | 9.74 | -0.4% | -0.29% |  |  | 20 |  |  |  |  | 78.5 | 39.4 | 1.38 |  |  |  |  | 1500 | 2018-07-06 | Hanwha_SolarOne | [11 empty] | 45
Hanwha SolarOne | Q.PLUS-G4-270 |  | 270 | 246.1 | +/-3 | 3 | -3 |  |  | 30.53 | 8.84 | 38.65 | 9.43 | -0.4% | -0.29% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | Q.PLUS-G4-275 |  | 275 | 250.7 | +3/-3 | 3 | -3 |  |  | 30.85 | 8.91 | 38.9 | 9.49 | -0.4% | -0.29% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Hanwha SolarOne | Q.PLUS-G4-280 |  | 280 | 255.4 | +3/-3 | 3 | -3 |  |  | 31.16 | 8.99 | 39.16 | 9.55 | -0.4% | -0.29% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Hanwha_SolarOne
Helios Solar Works | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Helios_Solar_Works
Helios Solar Works | 6T 240 | mono | 240 | 216.3 | +/-3 | 3 | -3 | 13.405 | 14.46 | 30 | 8 | 36.8 | 8.7 | -0.44% | -0.34% | 0.07 | 45 | 15 | DNR | MC4 | silver | white | 66.14 | 38.98 | 1.58 | 17.9037 | 53.9 | 5 |  | Check |  | Helios_Solar_Works
Helios Solar Works | 6T 245 | mono | 245 | 220.9 | +/-3 | 3 | -3 | 13.6843 | 14.76 | 30.03 | 8.18 | 37.26 | 8.71 | -0.44% | -0.34% | 0.07 | 45 | 15 | DNR | MC4 | silver | white | 66.14 | 38.98 | 1.58 | 17.9037 | 53.9 | 5 |  | Check |  | Helios_Solar_Works
Helios Solar Works | 6T 250 | mono | 250 | 225.6 | +/-3 | 3 | -3 | 13.9636 | 15.06 | 30.3 | 8.22 | 37.4 | 8.72 | -0.44% | -0.34% | 0.07 | 45 | 15 | DNR | MC4 | silver | white | 66.14 | 38.98 | 1.58 | 17.9037 | 53.9 | 5 |  | Check |  | Helios_Solar_Works
Helios Solar Works | 7T2 280 | mono | 280 | 351 | +/-3 | 3 | -3 | 13.3246 | 14.36 | 35.9 | 7.8 | 44.16 | 8.35 | -0.44% | -0.34% | 0.07 | 45 | 15 | DNR | MC4 | silver | white | 78.11 | 38.74 | 1.58 | 21.0138 | 57.2 | 5 |  | Check |  | Helios_Solar_Works
Helios Solar Works | 7T2 285 | mono | 285 | 255.6 | +/-3 | 3 | -3 | 13.5625 | 14.62 | 36.1 | 7.9 | 44.4 | 8.45 | -0.44% | -0.34% | 0.07 | 45 | 15 | DNR | MC4 | silver | white | 78.11 | 38.74 | 1.58 | 21.0138 | 57.2 | 5 |  | Check |  | Helios_Solar_Works
Helios Solar Works | 7T2 290 | mono | 290 | 260.2 | +/-3 | 3 | -3 | 13.8005 | 14.87 | 36.25 | 8 | 44.65 | 8.56 | -0.44% | -0.34% | 0.07 | 45 | 15 | DNR | MC4 | silver | white | 78.11 | 38.74 | 1.58 | 21.0138 | 57.2 | 5 |  | Check |  | Helios_Solar_Works
Helios Solar Works | 7T2 295 | mono | 295 | 264.8 | +/-3 | 3 | -3 | 14.0384 | 15.13 | 36.4 | 8.1 | 44.77 | 8.67 | -0.44% | -0.34% | 0.07 | 45 | 15 | DNR | MC4 | silver | white | 78.11 | 38.74 | 1.58 | 21.0138 | 57.2 | 5 |  | Check |  | Helios_Solar_Works
Helios Solar Works | 7T2 300 | mono | 300 | 269.4 | +/-3 | 3 | -3 | 14.2764 | 15.38 | 36.55 | 8.2 | 44.96 | 8.77 | -0.44% | -0.34% | 0.07 | 45 | 15 | DNR | MC4 | silver | white | 78.11 | 38.74 | 1.58 | 21.0138 | 57.2 | 5 |  | Check |  | Helios_Solar_Works
Hyundai Heavy Industries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M194SF | poly | 194 | 175.4 | +3/-0 | 3 | -0 | 12.4223 | 13.4 | 26.2 | 7.5 | 32.9 | 8.1 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 58.11 | 38.7 | 1.38 | 15.6171 | 37.5 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M197SF | poly | 197 | 178.2 | +3/-0 | 3 | -0 | 12.6144 | 13.6 | 26.4 | 7.5 | 33 | 8.1 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 58.11 | 38.7 | 1.38 | 15.6171 | 37.5 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M200SF | poly | 200 | 180.9 | +3/-0 | 3 | -0 | 12.8065 | 13.8 | 26.4 | 7.6 | 33.1 | 8.2 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 58.11 | 38.7 | 1.38 | 15.6171 | 37.5 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M203SF | poly | 203 | 183.7 | +3/-0 | 3 | -0 | 12.9986 | 14 | 26.6 | 7.7 | 33.3 | 8.2 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 58.11 | 38.7 | 1.38 | 15.6171 | 37.5 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M206SF | poly | 206 | 186.5 | +3/-0 | 3 | -0 | 13.1907 | 14.2 | 26.8 | 7.7 | 33.4 | 8.2 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 58.11 | 38.7 | 1.38 | 15.6171 | 37.5 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M209SF | poly | 209 | 189.3 | +3/-0 | 3 | -0 | 13.3828 | 14.4 | 26.9 | 7.8 | 33.5 | 8.3 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 58.11 | 38.7 | 1.38 | 15.6171 | 37.5 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M212SF | poly | 212 | 188.5 | +3/-0 | 3 | -0 | 13.5749 | 14.6 | 27 | 7.9 | 33.6 | 8.3 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 58.11 | 38.7 | 1.38 | 15.6171 | 37.5 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M215SG | poly | 215 | 193.7 | +3/-0 | 3 | -0 | 12.3533 | 13.3 | 28.7 | 7.5 | 36.3 | 8.2 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M218SG | poly | 218 | 196.5 | +3/-0 | 3 | -0 | 12.5257 | 13.5 | 28.9 | 7.6 | 36.4 | 8.3 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M221SG | poly | 221 | 199.3 | +3/-0 | 3 | -0 | 12.698 | 13.7 | 29 | 7.7 | 36.6 | 8.3 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M223MG | poly | 223 | 200.6 | +3/-0 | 3 | -0 | 12.813 | 13.8 | 30 | 7.4 | 36.8 | 8 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M223MG(Black) | poly | 223 | 200.6 | +3/-0 | 3 | -0 | 12.813 | 13.8 | 30.1 | 7.5 | 36.7 | 8 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | black | black | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M224SG | poly | 224 | 202 | +3/-0 | 3 | -0 | 12.8704 | 13.9 | 29.2 | 7.7 | 36.7 | 8.3 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M225MG | poly | 225 | 202.4 | +3/-0 | 3 | -0 | 12.9279 | 13.9 | 30 | 7.5 | 37.1 | 8.2 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M225MG(Black) | poly | 225 | 202.4 | +3/-0 | 3 | -0 | 12.9279 | 13.9 | 30.1 | 7.5 | 36.8 | 8 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | black | black | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M227SG | poly | 227 | 204.8 | +3/-0 | 3 | -0 | 13.0428 | 14 | 29.3 | 7.8 | 36.8 | 8.3 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M228MG | poly | 228 | 205.7 | +3/-0 | 3 | -0 | 13.1002 | 14.1 | 30 | 7.6 | 37.1 | 8.2 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M228MG(Black) | poly | 228 | 205.2 | +3/-0 | 3 | -0 | 13.1002 | 14.1 | 30.2 | 7.6 | 36.9 | 8.1 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | black | black | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M230MG | poly | 230 | 207.6 | +3/-0 | 3 | -0 | 13.2152 | 14.2 | 30.1 | 7.7 | 37.1 | 8.2 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M230MG(Black) | poly | 230 | 207 | +3/-0 | 3 | -0 | 13.2152 | 14.2 | 30.2 | 7.7 | 37.1 | 8.1 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | black | black | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M230SG | poly | 230 | 207.6 | +3/-0 | 3 | -0 | 13.2152 | 14.2 | 29.4 | 7.9 | 36.9 | 8.4 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M233MG | poly | 233 | 210.3 | +3/-0 | 3 | -0 | 13.3875 | 14.4 | 30.3 | 7.7 | 37.3 | 8.2 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M233MG(Black) | poly | 233 | 209.8 | +3/-0 | 3 | -0 | 13.3875 | 14.4 | 30.3 | 7.7 | 37.2 | 8.2 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | black | black | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M233SG | poly | 233 | 202.5 | +3/-0 | 3 | -0 | 13.3875 | 14.4 | 29.6 | 7.9 | 37.1 | 8.4 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M235MG | poly | 235 | 212.2 | +3/-0 | 3 | -0 | 13.5024 | 14.5 | 30.3 | 7.8 | 37.4 | 8.3 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M235MG(Black) | poly | 235 | 211.6 | +3/-0 | 3 | -0 | 13.5024 | 14.5 | 30.4 | 7.8 | 37.3 | 8.2 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | black | black | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M238MG | poly | 238 | 215 | +3/-0 | 3 | -0 | 13.6748 | 14.7 | 30.4 | 7.8 | 37.4 | 8.3 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M275MI | poly | 275 | 240 | +3/-0 | 3 | -0 | 13.1693 | 14.2 | 36.3 | 7.6 | 44 | 8.2 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 77.38 | 38.86 | 1.97 | 20.8819 | 55.1 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M278MI | poly | 278 | 242.7 | +3/-0 | 3 | -0 | 13.313 | 14.3 | 36.4 | 7.7 | 44.2 | 8.3 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 77.38 | 38.86 | 1.97 | 20.8819 | 55.1 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M280MI | poly | 280 | 244.5 | +3/-0 | 3 | -0 | 13.4088 | 14.4 | 36.5 | 7.7 | 44.4 | 8.3 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 77.38 | 38.86 | 1.97 | 20.8819 | 55.1 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M283MI | poly | 283 | 247.2 | +3/-0 | 3 | -0 | 13.5524 | 14.6 | 36.6 | 7.8 | 44.5 | 8.3 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 77.38 | 38.86 | 1.97 | 20.8819 | 55.1 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M285MI | poly | 285 | 249 | +3/-0 | 3 | -0 | 13.6482 | 14.7 | 36.7 | 7.8 | 44.7 | 8.3 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 77.38 | 38.86 | 1.97 | 20.8819 | 55.1 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M288MI | poly | 288 | 251.7 | +3/-0 | 3 | -0 | 13.7919 | 14.8 | 36.8 | 7.8 | 44.9 | 8.3 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 77.38 | 38.86 | 1.97 | 20.8819 | 55.1 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M290MI | multi | 290 | 253.5 | +3/-0 | 3 | -0 | 13.8877 | 14.9 | 37 | 7.9 | 45.1 | 8.3 | -0.43% | -0.32% | 0.056 | 46 | 15 | yes | tyco | silver | white | 77.38 | 38.86 | 1.97 | 20.8819 | 55.1 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M295MI | multi | 295 | 253.5 | +3/-0 | 3 | -0 |  |  | 37.3 | 7.9 | 45.4 | 8.3 | -0.43% | -0.32% |  |  | 15 | [11 empty] | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M300MI | multi | 300 | 253.5 | +3/-0 | 3 | -0 |  |  | 37.7 | 8 | 45.7 | 8.3 | -0.43% | -0.32% |  |  | 15 | [11 empty] | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S206SF | mono | 206 | 186.3 | +3/-0 | 3 | -0 | 13.1907 | 14.2 | 26.8 | 7.7 | 33.4 | 8.2 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 58.11 | 38.7 | 1.38 | 15.6171 | 37.5 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S209SF | mono | 209 | 189.1 | +3/-0 | 3 | -0 | 13.3828 | 14.4 | 26.9 | 7.8 | 33.5 | 8.2 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 58.11 | 38.7 | 1.38 | 15.6171 | 37.5 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S212SF | mono | 212 | 191.9 | +3/-0 | 3 | -0 | 13.5749 | 14.6 | 27 | 7.9 | 33.6 | 8.3 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 58.11 | 38.7 | 1.38 | 15.6171 | 37.5 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S215SF | mono | 215 | 194.6 | +3/-0 | 3 | -0 | 13.767 | 14.8 | 27.1 | 8 | 33.7 | 8.3 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 58.11 | 38.7 | 1.38 | 15.6171 | 37.5 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S218SF | mono | 218 | 197.4 | +3/-0 | 3 | -0 | 13.9591 | 15 | 27.2 | 8.1 | 33.8 | 8.4 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 58.11 | 38.7 | 1.38 | 15.6171 | 37.5 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S221SF | mono | 221 | 200.2 | +3/-0 | 3 | -0 | 14.1512 | 15.2 | 27.3 | 8.1 | 33.9 | 8.5 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 58.11 | 38.7 | 1.38 | 15.6171 | 37.5 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S224SG | mono | 224 | 196.9 | +3/-0 | 3 | -0 | 12.8704 | 14 | 29.2 | 7.7 | 36.7 | 8.3 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S227SG | mono | 227 | 198.9 | +3/-0 | 3 | -0 | 13.0428 | 14.2 | 29.3 | 7.7 | 36.8 | 8.3 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S230SG | mono | 230 | 201.6 | +3/-0 | 3 | -0 | 13.2152 | 14.4 | 29.4 | 7.9 | 37 | 8.4 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S233SG | mono | 233 | 204.4 | +3/-0 | 3 | -0 | 13.3875 | 14.6 | 29.6 | 7.9 | 37.1 | 8.4 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S235MG | mono | 235 | 207.7 | +3/-0 | 3 | -0 | 13.5024 | 14.5 | 29.8 | 7.9 | 37 | 8.4 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S236SG | mono | 236 | 207.1 | +3/-0 | 3 | -0 | 13.5599 | 14.8 | 29.7 | 8 | 37.2 | 8.4 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S238MG | mono | 238 | 214.6 | +3/-0 | 3 | -0 | 13.6748 | 14.7 | 29.8 | 8 | 37 | 8.5 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S238MG(Black) | mono | 238 | 210.5 | +3/-0 | 3 | -0 | 13.6748 | 14.7 | 30.8 | 7.8 | 37.3 | 8.3 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | black | black | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S240MG | mono | 240 | 216.5 | +3/-0 | 3 | -0 | 13.7897 | 14.8 | 30.1 | 8 | 37.3 | 8.5 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S240MG(Black) | mono | 240 | 212.3 | +3/-0 | 3 | -0 | 13.7897 | 14.8 | 30.9 | 7.8 | 37.4 | 8.3 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | black | black | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S243MG | mono | 243 | 219.2 | +3/-0 | 3 | -0 | 13.9621 | 15 | 30.1 | 8.1 | 37.3 | 8.6 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S243MG(Black) | mono | 243 | 215 | +3/-0 | 3 | -0 | 13.9621 | 15 | 31 | 7.9 | 37.5 | 8.4 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | black | black | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S245MG | mono | 245 | 221.1 | +3/-0 | 3 | -0 | 14.077 | 15.2 | 30.3 | 8.1 | 37.4 | 8.6 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S248MG | mono | 248 | 223.9 | +3/-0 | 3 | -0 | 14.2494 | 15.3 | 30.3 | 8.2 | 37.5 | 8.7 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S250MG | mono | 250 | 225.7 | +3/-0 | 3 | -0 | 14.3643 | 15.5 | 30.5 | 8.2 | 37.5 | 8.7 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 64.76 | 38.7 | 1.38 | 17.4043 | 41.9 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S260MG | mono | 260 |  | +3/-0 | 3 | -0 |  |  | 31 | 8.4 | 37.8 | 8.9 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S265MG | mono | 265 |  | +3/-1 | 3 | -0 |  |  | 31.2 | 8.5 | 37.9 | 9 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S280MI | mono | 280 | 246.4 | +3/-0 | 3 | -0 | 13.4088 | 14.4 | 36.5 | 7.7 | 44.5 | 8.3 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 77.38 | 38.86 | 1.97 | 20.8819 | 55.1 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S283MI | mono | 283 | 249.2 | +3/-0 | 3 | -0 | 13.5524 | 14.6 | 36.6 | 7.8 | 44.6 | 8.3 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 77.38 | 38.86 | 1.97 | 20.8819 | 55.1 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S285MI | mono | 285 | 251 | +3/-0 | 3 | -0 | 13.6482 | 14.7 | 36.7 | 7.8 | 44.7 | 8.3 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 77.38 | 38.86 | 1.97 | 20.8819 | 55.1 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S288MI | mono | 288 | 253.7 | +3/-0 | 3 | -0 | 13.7919 | 14.8 | 36.9 | 7.8 | 44.8 | 8.3 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 77.38 | 38.86 | 1.97 | 20.8819 | 55.1 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S290MI | mono | 290 | 255.5 | +3/-0 | 3 | -0 | 13.8877 | 14.9 | 37 | 7.9 | 45 | 8.3 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 77.38 | 38.86 | 1.97 | 20.8819 | 55.1 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S293MI | mono | 293 | 258.3 | +3/-0 | 3 | -0 | 14.0313 | 15.1 | 37.1 | 7.9 | 45 | 8.3 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 77.38 | 38.86 | 1.97 | 20.8819 | 55.1 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S295MI | mono | 295 | 260.1 | +3/-0 | 3 | -0 | 14.1271 | 15.2 | 37.2 | 8 | 45.1 | 8.4 | -0.44% | -0.34% | 0.052 | 46 | 15 | yes | tyco | silver | white | 77.38 | 38.86 | 1.97 | 20.8819 | 55.1 | 5 |  | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S300MI | mono | 300 |  | +3/-0 | 3 | -0 |  |  | 37.4 | 8 | 45.4 | 8.4 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S303MI | mono | 303 |  | +3/-0 | 3 | 0 |  |  | 37.5 | 8 | 45.5 | 8.4 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S305MI | mono | 305 |  | +3/-0 | 3 | -0 |  |  | 37.6 | 8 | 45.6 | 8.4 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2013-12-02 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S310MI | mono | 310 |  | +3/-0 | 3 | -0 |  |  | 37.8 | 8.2 | 45.9 | 8.5 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2013-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S315MI | mono | 315 |  | +3/-0 | 3 | -0 |  |  | 38 | 8.3 | 46.1 | 8.5 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2013-12-04 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M300TI | poly | 300 |  | +3/-0 | 3 | 0 |  |  | 35.8 | 8.4 | 44.9 | 8.7 | -0.49% | -0.35% |  |  | 15 | [11 empty] | 1000 | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M305TI | poly | 305 |  | +3/-0 | 3 | 0 |  |  | 36 | 8.5 | 45.1 | 8.8 | -0.41% | -0.32% |  |  | 15 | [11 empty] | 1000 | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S305TI | mono | 305 |  | +3/-0 | 3 | 0 |  |  | 37 | 8.2 | 45.3 | 8.8 | -0.5% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S310TI | mono | 310 |  | +3/-0 | 3 | 0 |  |  | 37.2 | 8.3 | 45.5 | 8.9 | -0.5% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M310TI | poly | 310 |  | +3/-0 | 3 | 0 |  |  | 36 | 8.6 | 45.3 | 8.9 | -0.41% | -0.32% |  |  | 15 | [11 empty] | 1000 | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S315TI | mono | 315 |  | +3/-0 | 3 | 0 |  |  | 37.4 | 8.4 | 45.7 | 9 | -0.5% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S320TI | mono | 320 |  | +3/-0 | 3 | 0 |  |  | 37.6 | 8.5 | 45.9 | 9.1 | -0.5% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S325TI | mono | 325 |  | +3/-0 | 3 | 0 |  |  | 37.8 | 8.6 | 46.1 | 9.2 | -0.42% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S330TI | mono | 330 |  | +3/-0 | 3 | 0 |  |  | 38 | 8.7 | 46.3 | 9.3 | -0.42% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S335TI | mono | 335 |  | +3/-0 | 3 | 0 |  |  | 38.2 | 8.78 | 46.5 | 9.4 | -0.42% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S340TI | mono | 340 |  | +3/-0 | 3 | 0 |  |  | 38.4 | 8.9 | 46.7 | 9.5 | -0.42% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S345TI | mono | 345 |  | +3/-0 | 3 | 0 |  |  | 38.6 | 9 | 46.9 | 9.6 | -0.42% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S350TI | mono | 350 |  | +3/-0 | 3 | 0 |  |  | 38.7 | 9 | 47.1 | 9.6 | -0.42% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S250RF | mono | 250 |  | +3/-0 | 3 | 0 |  |  | 28.5 | 8.8 | 34.6 | 9.4 | -0.4% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S255RF | mono | 255 |  | +3/-0 | 3 | 0 |  |  | 28.6 | 8.9 | 34.7 | 9.5 | -0.4% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S260RF | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 28.7 | 9 | 34.9 | 9.6 | -0.4% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M250RG | poly | 250 |  | +3/-0 | 3 | 0 |  |  | 30.9 | 8.1 | 37.4 | 8.7 | -0.41% | -0.31% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M255RG | poly | 255 |  | +3/-0 | 3 | 0 |  |  | 31 | 8.2 | 37.6 | 8.8 | -0.41% | -0.31% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M260RG | poly | 260 |  | +3/-0 | 3 | 0 |  |  | 31.1 | 8.4 | 37.7 | 8.9 | -0.41% | -0.31% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M265RG | poly | 265 |  | +3/-0 | 3 | 0 |  |  | 31.3 | 8.5 | 37.9 | 9.1 | -0.41% | -0.31% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S260RG | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 31.1 | 8.4 | 37.9 | 8.9 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2016-06-30 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S265RG | mono | 265 |  | +3/-0 | 3 | 0 |  |  | 31.3 | 8.5 | 38.1 | 9 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2016-06-30 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S270RG | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 31.4 | 8.6 | 38.2 | 9.2 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2016-06-30 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S275RG | mono | 275 |  | +3/-0 | 3 | 0 |  |  | 31.6 | 8.7 | 38.4 | 9.3 | -0.4% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S280RG | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 31.7 | 8.8 | 38.5 | 9.4 | -0.4% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S285RG | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 31.8 | 8.9 | 38.7 | 9.5 | -0.4% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S290RG | mono | 290 |  | +3/-0 | 3 | 0 |  |  | 32 | 9.1 | 38.8 | 9.7 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S295RG | mono | 295 |  | +3/-0 | 3 | 0 |  |  | 32.1 | 9.2 | 39 | 9.8 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S300RG | mono | 300 |  | +3/-0 | 3 | 0 |  |  | 32.3 | 9.3 | 39.1 | 9.9 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M300RI | poly | 300 |  | +3/-0 | 3 | 0 |  |  | 35.8 | 8.4 | 44.9 | 8.7 | -0.48% | -0.366% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M305RI | poly | 305 |  | +3/-0 | 3 | 0 |  |  | 36 | 8.5 | 45.1 | 8.8 | -0.48% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M310RI | poly | 310 |  | +3/-0 | 3 | 0 |  |  | 36 | 8.6 | 45.3 | 8.9 | -0.41% | -0.31% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M315RI | poly | 315 |  | +3/-0 | 3 | 0 |  |  | 36.2 | 8.7 | 45.3 | 9 | -0.41% | -0.31% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-M320RI | poly | 320 |  | +3/-0 | 3 | 0 |  |  | 36.4 | 8.8 | 45.5 | 9 | -0.41% | -0.31% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S305RI | mono | 305 |  | +3/-0 | 3 | 0 |  |  | 37 | 8.2 | 45.3 | 8.8 | -0.51% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S310RI | mono | 310 |  | +3/-0 | 3 | 0 |  |  | 37.2 | 8.3 | 45.5 | 8.9 | -0.51% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S315RI | mono | 315 |  | +3/-0 | 3 | 0 |  |  | 37.4 | 8.4 | 45.7 | 9 | -0.51% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S320RI | mono | 320 |  | +3/-0 | 3 | 0 |  |  | 37.6 | 8.5 | 45.9 | 9.1 | -0.51% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S330RI | mono | 330 | 298.2 | +3/-0 | 3 | 0 |  |  | 38 | 8.7 | 46.3 | 9.3 | -0.4% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S335RI | mono | 335 | 303.6 | +3/-0 | 3 | 0 |  |  | 38.2 | 8.8 | 46.5 | 9.4 | -0.4% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S340RI | mono | 340 | 308.3 | +3/-0 | 3 | 0 |  |  | 38.4 | 8.9 | 46.7 | 9.5 | -0.4% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S345RI | mono | 345 | 313 | +3/-0 | 3 | 0 |  |  | 38.6 | 9 | 46.9 | 9.6 | -0.4% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S350RI | mono | 350 | 317.6 | +3/-0 | 3 | 0 |  |  | 38.7 | 9 | 47.1 | 9.6 | -0.4% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S355RI | mono | 355 | 322.3 | +3/-0 | 3 | 0 |  |  | 38.9 | 9.1 | 47.3 | 9.7 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S360RI | mono | 360 | 327 | +3/-0 | 3 | 0 |  |  | 39.1 | 9.2 | 47.4 | 9.8 | -0.4% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2018-02-12 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S300HI | mono | 300 |  | +3/-0 | 3 | 0 |  |  | 37.44 | 8 | 45.4 | 8.35 | -0.54% | -0.39% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S305HI | mono | 305 |  | +3/-0 | 3 | 0 |  |  | 37.65 | 8.03 | 45.61 | 8.36 | -0.54% | -0.39% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S310HI | mono | 310 |  | +3/-0 | 3 | 0 |  |  | 37.8 | 8.2 | 45.9 | 8.5 | -0.54% | -0.39% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Hyundai_Heavy_Industries
Hyundai Heavy Industries | HiS-S315HI | mono | 315 |  | +3/-0 | 3 | 0 |  |  | 38.03 | 8.33 | 46.13 | 8.53 | -0.54% | -0.39% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Hyundai_Heavy_Industries
Instalaciones Pevafersa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Instalaciones_Pevafersa
Instalaciones Pevafersa | IP-VA180 | mono | 180 | 159.2 | +3/-2 | 3 | -2 | 13.0739 | 14.1 | 35.3 | 5.1 | 43.1 | 5.4 | -0.5% | -0.37% | 0.106 | 47 | 10 | yes | tyco | silver | white | 62.72 | 31.61 | 1.81 | 13.7679 | 41.14 | 5 |  | Check |  | Instalaciones_Pevafersa
Instalaciones Pevafersa | IP-VAP210 | poly | 210 | 183.7 | +3/-2 | 3 | -2 | 12.0214 | 13 | 29.1 | 7.4 | 37.1 | 8 | -0.5% | -0.37% | 0.135 | 48 | 10 | yes | tyco | silver | white | 64.6 | 38.94 | 1.91 | 17.4689 | 51.7 | 5 |  | Check |  | Instalaciones_Pevafersa
Instalaciones Pevafersa | IP-VAP230 | poly | 230 | 201 | +3/-2 | 3 | -2 | 13.1662 | 14.2 | 29.45 | 7.91 | 37.54 | 8.38 | -0.5% | -0.36% | 0.125 | 49 | 10 | yes | tyco | silver | white | 64.6 | 38.94 | 1.91 | 17.4689 | 51.7 | 5 |  | Check |  | Instalaciones_Pevafersa
itek energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | itek_energy
itek energy | IT 225 | mono | 225 |  | +/-3 | 3 | -3 |  |  | 29.7 | 7.8 | 37.6 | 8.4 | -0.53% | -0.35% |  |  | 15 | [9 empty] | 10 |  | Check | 2012-02-03 | itek_energy
itek energy | IT 230 | mono | 230 |  | +/-3 | 3 | -3 |  |  | 29.8 | 7.9 | 37.7 | 8.5 | -0.53% | -0.35% |  |  | 15 | [9 empty] | 10 |  | Check | 2012-02-03 | itek_energy
itek energy | IT 235 | mono | 235 |  | +/-3 | 3 | -3 |  |  | 29.9 | 8.1 | 37.9 | 8.6 | -0.53% | -0.35% |  |  | 15 | [9 empty] | 10 |  | Check | 2012-02-03 | itek_energy
itek energy | IT 240 | mono | 240 |  | +/-3 | 3 | -3 |  |  | 30 | 8.2 | 38 | 8.7 | -0.53% | -0.35% |  |  | 15 | [9 empty] | 10 |  | Check | 2012-02-03 | itek_energy
itek energy | IT 245 | mono | 245 |  | +/-3 | 3 | -3 |  |  | 30.1 | 8.4 | 38.2 | 8.8 | -0.53% | -0.35% |  |  | 15 | [9 empty] | 10 |  | Check | 2012-02-03 | itek_energy
itek energy | IT 250 | mono | 250 |  | +/-3 | 3 | -3 |  |  | 30.3 | 8.5 | 38.3 | 8.9 | -0.53% | -0.35% |  |  | 15 | [9 empty] | 10 |  | Check | 2012-02-03 | itek_energy
itek energy | IT 255 | mono | 255 |  | +/-3 | 3 | -3 |  |  | 30.4 | 8.7 | 38.4 | 9 | -0.53% | -0.35% |  |  | 15 | [9 empty] | 10 |  | Check | 2012-02-03 | itek_energy
itek energy | IT 295 SE | mono | 295 |  | +/-2 | 2 | -2 |  |  | 32.8 | 8.9 | 37.8 | 9.6 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-01-03 | itek_energy
itek energy | IT 300 SE | mono | 300 |  | +/-2 | 2 | -2 |  |  | 32.9 | 9 | 37.9 | 9.7 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-01-03 | itek_energy
itek energy | IT 305 SE | mono | 305 |  | +/-2 | 2 | -2 |  |  | 33.1 | 9.1 | 38.1 | 9.8 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-01-03 | itek_energy
itek energy | IT 310 SE | mono | 310 |  | +/-2 | 2 | -2 |  |  | 33.2 | 9.2 | 38.2 | 9.8 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-01-03 | itek_energy
itek energy | IT 315 SE | mono | 315 |  | +/-2 | 2 | -2 |  |  | 33.3 | 9.3 | 38.4 | 10 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-01-03 | itek_energy
itek energy | IT 350 SE-72 | mono | 350 | 322.9 | +/-2 | 2 | -2 |  |  | 38.55 | 9.08 | 47.43 | 9.49 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-01-03 | itek_energy
itek energy | IT 355 SE-72 | mono | 355 | 327.7 | +/-2 | 2 | -2 |  |  | 38.74 | 9.16 | 47.64 | 9.55 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-01-03 | itek_energy
itek energy | IT 360 SE-72 | mono | 360 | 332.4 | +/-2 | 2 | -2 |  |  | 38.94 | 9.25 | 47.87 | 9.62 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-01-03 | itek_energy
itek energy | IT 365 SE-72 | mono | 365 | 337.2 | +/-2 | 2 | -2 |  |  | 39.12 | 9.33 | 48.08 | 9.69 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-01-03 | itek_energy
itek energy | IT 370 SE-72 | mono | 370 | 341.9 | +/-2 | 2 | -2 |  |  | 39.32 | 9.41 | 48.31 | 9.76 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2018-01-03 | itek_energy
itek energy | IT 270 HE | mono | 270 |  | +/-2 | 2 | -2 |  |  | 32 | 8.4 | 38.9 | 9.1 | -0.47% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | itek_energy
itek energy | IT 275 HE | mono | 275 |  | +/-2 | 2 | -2 |  |  | 32.1 | 8.5 | 39 | 9.2 | -0.47% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | itek_energy
itek energy | IT 280 HE | mono | 280 |  | +/-2 | 2 | -2 |  |  | 32.3 | 8.6 | 39.2 | 9.3 | -0.47% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | itek_energy
itek energy | IT 285 HE | mono | 285 |  | +/-2 | 2 | -2 |  |  | 32.4 | 8.7 | 39.3 | 9.4 | -0.47% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | itek_energy
itek energy | IT 290 HE | mono | 290 |  | +/-2 | 2 | -2 |  |  | 32.6 | 8.8 | 39.5 | 9.5 | -0.47% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | itek_energy
itek energy | IT 295 HE | mono | 295 |  | +/-2 | 2 | -2 |  |  | 32.8 | 8.9 | 39.7 | 9.6 | -0.47% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | itek_energy
itek energy | IT 300 HE | mono | 300 |  | +/-2 | 2 | -2 |  |  | 32.9 | 9 | 39.8 | 9.8 | -0.47% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | itek_energy
itek energy | IT 305 HE | mono | 305 |  | +/-2 | 2 | -2 |  |  | 33.1 | 9.1 | 40 | 9.8 | -0.47% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | itek_energy
itek energy | IT 310 HE | mono | 310 |  | +/-2 | 2 | -2 |  |  | 33.2 | 9.2 | 40.1 | 9.9 | -0.47% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | itek_energy
JA Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | JA_Solar
JA Solar | JAM6(T) 60-250/SI |  | 250 |  | +5/-0 | 5 | 0 |  |  | 30.35 | 8.24 | 37.88 | 8.66 | -0.43% | -0.34% |  |  | 15 | [11 empty] | Check | 2013-09-24 | JA_Solar
JA Solar | JAM6(T) 60-255/SI |  | 255 |  | +5/-0 | 5 | 0 |  |  | 30.62 | 8.31 | 38.1 | 8.72 | -0.43% | -0.34% |  |  | 15 | [11 empty] | Check | 2013-09-24 | JA_Solar
JA Solar | JAM6(T) 60-260/SI |  | 260 |  | +5/-0 | 5 | 0 |  |  | 30.98 | 8.39 | 38.24 | 8.76 | -0.43% | -0.34% |  |  | 15 | [11 empty] | Check | 2013-09-24 | JA_Solar
JA Solar | JAM6(T) 60-265/SI |  | 265 |  | +5/-0 | 5 | 0 |  |  | 31.24 | 8.48 | 38.38 | 8.8 | -0.43% | -0.34% |  |  | 15 | [11 empty] | Check | 2013-09-24 | JA_Solar
JA Solar | JAM6(T) 60-270/SI |  | 270 |  | +5/-0 | 5 | 0 |  |  | 31.54 | 8.56 | 38.62 | 8.82 | -0.43% | -0.34% |  |  | 15 | [11 empty] | Check | 2013-09-24 | JA_Solar
JA Solar | JAM6(K) 60-280/PR | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 31.6 | 8.86 | 39.05 | 9.38 | -0.39% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | JA_Solar
JA Solar | JAM6(K) 60-285/PR | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 31.7 | 8.99 | 39.25 | 9.46 | -0.39% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | JA_Solar
JA Solar | JAM6(K) 60-290/PR | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 31.8 | 9.12 | 39.46 | 9.57 | -0.39% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | JA_Solar
JA Solar | JAM6(K) 60-295/PR | mono | 295 |  | +5/-0 | 5 | 0 |  |  | 32.03 | 9.21 | 39.64 | 9.66 | -0.39% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | JA_Solar
JA Solar | JAM6(K) 60-300/PR | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 32.26 | 9.3 | 39.84 | 9.75 | -0.39% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | JA_Solar
JA Solar | JAM6(K) 72-335/PR | mono | 335 |  | +5/-0 | 5 | 0 |  |  | 37.96 | 8.83 | 46.68 | 9.38 | -0.39% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | JA_Solar
JA Solar | JAM6(K) 72-340/PR | mono | 340 |  | +5/-0 | 5 | 0 |  |  | 38.18 | 8.91 | 46.86 | 9.46 | -0.39% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | JA_Solar
JA Solar | JAM6(K) 72-345/PR | mono | 345 |  | +5/-0 | 5 | 0 |  |  | 38.39 | 8.99 | 47.05 | 9.54 | -0.39% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | JA_Solar
JA Solar | JAM6(K) 72-350/PR | mono | 350 |  | +5/-0 | 5 | 0 |  |  | 38.58 | 9.07 | 47.24 | 9.61 | -0.39% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | JA_Solar
JA Solar | JAM6(K) 72-355/PR | mono | 355 |  | +5/-0 | 5 | 0 |  |  | 38.76 | 9.16 | 47.45 | 9.69 | -0.39% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-10 | JA_Solar
JA Solar | JAM6(K)(DG) 60-265/4BB/1500V | mono | 265 |  | +5/-0 | 5 | 0 |  |  | 31.4 | 8.44 | 39.48 | 8.89 | -0.41% | -0.33% |  |  | 15 | [11 empty] | 1500 | 2017-10-10 | JA_Solar
JA Solar | JAM6(K)(DG) 60-270/4BB/1500V | mono | 270 |  | +5/-0 | 5 | 0 |  |  | 31.69 | 8.52 | 39.64 | 9.01 | -0.41% | -0.33% |  |  | 15 | [11 empty] | 1500 | 2017-10-10 | JA_Solar
JA Solar | JAM6(K)(DG) 60-275/4BB/1500V | mono | 275 |  | +5/-0 | 5 | 0 |  |  | 31.79 | 8.65 | 39.77 | 9.1 | -0.41% | -0.33% |  |  | 15 | [11 empty] | 1500 | 2017-10-10 | JA_Solar
JA Solar | JAM6(K)(DG) 60-280/4BB/1500V | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 31.96 | 8.76 | 39.9 | 9.21 | -0.41% | -0.33% |  |  | 15 | [11 empty] | 1500 | 2017-10-10 | JA_Solar
JA Solar | JAM6(K)(DG) 60-285/4BB/1500V | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 32.13 | 8.87 | 40.03 | 9.3 | -0.41% | -0.33% |  |  | 15 | [11 empty] | 1500 | 2017-10-10 | JA_Solar
JA Solar | JAM6(FA)-60-250/SI | mono | 250 |  | +5/-0 | 5 | 0 |  |  | 30.31 | 8.25 | 37.72 | 8.76 | -0.41% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAM6(FA)-60-255/SI | mono | 255 |  | +5/-0 | 5 | 0 |  |  | 30.58 | 8.34 | 37.9 | 8.84 | -0.41% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAM6(FA)-60-260/SI | mono | 260 |  | +5/-0 | 5 | 0 |  |  | 30.81 | 8.44 | 38.08 | 8.92 | -0.41% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAM6(FA)-60-265/SI | mono | 265 |  | +5/-0 | 5 | 0 |  |  | 31.11 | 8.52 | 38.26 | 9 | -0.41% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAM6(FA)-60-270/SI | mono | 270 |  | +5/-0 | 5 | 0 |  |  | 31.33 | 8.62 | 38.46 | 9.09 | -0.41% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAM6 60-250/SI | mono | 250 |  | +5/-0 | 5 | 0 |  |  | 30.31 | 8.25 | 37.72 | 8.76 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAM6 60-255/SI | mono | 255 |  | +5/-0 | 5 | 0 |  |  | 30.58 | 8.34 | 37.9 | 8.84 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAM6 60-260/SI | mono | 260 |  | +5/-0 | 5 | 0 |  |  | 30.81 | 8.44 | 38.08 | 8.92 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAM6 60-265/SI | mono | 265 |  | +5/-0 | 5 | 0 |  |  | 31.11 | 8.52 | 38.26 | 9 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAM6 60-270/SI | mono | 270 |  | +5/-0 | 5 | 0 |  |  | 31.33 | 8.62 | 38.46 | 9.09 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAM6 72-290/SI | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 36.76 | 7.89 | 45.67 | 8.52 | -0.43% | -0.34% |  |  | 15 | [11 empty] | Check | 2013-09-24 | JA_Solar
JA Solar | JAM6 72-295/SI | mono | 295 |  | +5/-0 | 5 | 0 |  |  | 36.93 | 7.99 | 45.78 | 8.56 | -0.43% | -0.34% |  |  | 15 | [11 empty] | Check | 2013-09-24 | JA_Solar
JA Solar | JAM6 72-300/SI | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 36.77 | 8.16 | 45.28 | 8.71 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAM6 72-305/SI | mono | 305 |  | +5/-0 | 5 | 0 |  |  | 36.93 | 8.26 | 45.41 | 8.78 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAM6 72-310/SI | mono | 310 |  | +5/-0 | 5 | 0 |  |  | 37.04 | 8.37 | 45.57 | 8.85 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAM6 72-315/SI | mono | 315 |  | +5/-0 | 5 | 0 |  |  | 37.15 | 8.48 | 45.73 | 8.92 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAM6 72-320/SI | mono | 320 |  | +5/-0 | 5 | 0 |  |  | 37.35 | 8.57 | 45.86 | 8.99 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAM6 72-325/SI | mono | 325 |  | +5/-0 | 5 | 0 |  |  | 37.64 | 8.63 | 46.15 | 9.06 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAM6 72-330/SI | mono | 330 |  | +5/-0 | 5 | 0 |  |  | 37.93 | 8.7 | 46.47 | 9.13 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAM6(R)-60-260 | mono | 260 |  | +5/-0 | 5 | 0 |  |  | 30.49 | 8.53 | 38.32 | 9.04 | -0.41% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAM6(R)-60-265 | mono | 265 |  | +5/-0 | 5 | 0 |  |  | 30.78 | 8.61 | 38.52 | 9.13 | -0.41% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAM6(R)-60-270 | mono | 270 |  | +5/-0 | 5 | 0 |  |  | 31.08 | 8.69 | 38.71 | 9.21 | -0.41% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAM6(R)-60-275 | mono | 275 |  | +5/-0 | 5 | 0 |  |  | 31.36 | 8.77 | 38.89 | 9.3 | -0.41% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAM6(R)-60-280 | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 31.64 | 8.85 | 39.07 | 9.39 | -0.41% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAM6(R)-72-315 | mono | 315 |  | +5/-0 | 5 | 0 |  |  | 36.81 | 8.56 | 45.69 | 9.08 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAM6(R)-72-320 | mono | 320 |  | +5/-0 | 5 | 0 |  |  | 36.91 | 8.67 | 45.83 | 9.15 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAM6(R)-72-325 | mono | 325 |  | +5/-0 | 5 | 0 |  |  | 37.02 | 8.78 | 45.97 | 9.22 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAM6(R)-72-330 | mono | 330 |  | +5/-0 | 5 | 0 |  |  | 37.13 | 8.89 | 46.11 | 9.29 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAM6(R)-72-335 | mono | 335 |  | +5/-0 | 5 | 0 |  |  | 37.27 | 8.99 | 46.25 | 9.36 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-03 | JA_Solar
JA Solar | JAP60S01-260/PR | mono | 260 | 238.2688 | +5/-0 | 5 | 0 |  |  | 30.71 | 8.47 | 37.74 | 9.04 | -0.4% | -0.33% |  |  | 20 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.12 |  |  | 1500 | 2018-07-02 | JA_Solar | [11 empty] | 45
JA Solar | JAP60S01-265/PR | mono | 265 | 242.9642 | +5/-0 | 5 | 0 |  |  | 30.92 | 8.57 | 37.95 | 9.11 | -0.4% | -0.33% |  |  | 20 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.12 |  |  | 1500 | 2018-07-02 | JA_Solar | [11 empty] | 45
JA Solar | JAP60S01-270/PR | mono | 270 | 247.6639 | +5/-0 | 5 | 0 |  |  | 31.13 | 8.67 | 38.17 | 9.18 | -0.4% | -0.33% |  |  | 20 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.12 |  |  | 1500 | 2018-07-02 | JA_Solar | [11 empty] | 45
JA Solar | JAP60S01-275/PR | mono | 275 | 252.3679 | +5/-0 | 5 | 0 |  |  | 31.34 | 8.77 | 38.38 | 9.29 | -0.4% | -0.33% |  |  | 20 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.12 |  |  | 1500 | 2018-07-02 | JA_Solar | [11 empty] | 45
JA Solar | JAP60S01-280/PR | mono | 280 | 257.0761 | +5/-0 | 5 | 0 |  |  | 31.61 | 8.86 | 38.65 | 9.37 | -0.4% | -0.33% |  |  | 20 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.12 |  |  | 1500 | 2018-07-02 | JA_Solar | [11 empty] | 45
JA Solar | JAP72S01-310/SC | poly | 310 | 286 | +5/-0 | 5 | 0 |  | 15.96 | 36.89 | 8.4 | 45.56 | 8.92 | -0.41% | -0.33% |  |  | 20 |  |  |  |  | 77.16 | 39 | 1.57 |  | 49.6 |  |  | 1500 | 2018-07-02 | JA_Solar
JA Solar | JAP72S01-315/SC | poly | 315 | 290.7 | +5/-0 | 5 | 0 |  | 16.22 | 37.09 | 8.49 | 45.85 | 9.01 | -0.4% | -0.33% |  |  | 20 |  |  |  |  | 77.16 | 39 | 1.57 |  | 48.5 |  |  | 1500 | 2018-07-02 | JA_Solar
JA Solar | JAP72S01-320/SC | poly | 320 | 295.4 | +5/-0 | 5 | 0 |  | 16.47 | 37.28 | 8.58 | 46.12 | 9.09 | -0.4% | -0.33% |  |  | 20 |  |  |  |  | 77.16 | 39 | 1.57 |  | 48.5 |  |  | 1500 | 2018-07-02 | JA_Solar
JA Solar | JAP72S01-325/SC | poly | 325 | 300.1 | +5/-0 | 5 | 0 |  | 16.73 | 37.39 | 8.69 | 46.38 | 9.17 | -0.4% | -0.33% |  |  | 20 |  |  |  |  | 77.16 | 39 | 1.57 |  | 48.5 |  |  | 1500 | 2018-07-02 | JA_Solar
JA Solar | JAP72S01-330/SC | poly | 330 | 304.9 | +5/-0 | 5 | 0 |  | 16.99 | 37.65 | 8.77 | 46.4 | 9.28 | -0.4% | -0.33% |  |  | 20 |  |  |  |  | 77.16 | 39 | 1.57 |  | 48.5 |  |  | 1500 | 2018-07-02 | JA_Solar
JA Solar | JAP72S01-335/SC | poly | 335 | 309.1 | +5/-0 | 5 | 0 |  | 17.2 | 37.83 | 8.87 | 46.7 | 9.35 | -0.4% | -0.33% |  |  | 20 |  |  |  |  | 77.16 | 39 | 1.57 |  | 48.5 |  |  | 1500 | 2018-07-02 | JA_Solar
JA Solar | JAM60S01-290/PR | mono | 290 | 267.6802 | +5/-0 | 5 | 0 |  | 17.7 | 31.8 | 9.12 | 39.46 | 9.57 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.12 |  |  | 1500 | 2018-07-03 | JA_Solar | [11 empty] | 45
JA Solar | JAM60S01-295/PR | mono | 295 | 272.4152 | +5/-0 | 5 | 0 |  | 18 | 32.03 | 9.21 | 39.64 | 9.66 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.12 |  |  | 1500 | 2018-07-03 | JA_Solar | [11 empty] | 45
JA Solar | JAM60S01-300/PR | mono | 300 | 277.1543 | +5/-0 | 5 | 0 |  | 18.3 | 32.26 | 9.3 | 39.84 | 9.75 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.12 |  |  | 1500 | 2018-07-03 | JA_Solar | [11 empty] | 45
JA Solar | JAM60S01-305/PR | mono | 305 | 281.8974 | +5/-0 | 5 | 0 |  | 18.7 | 32.57 | 9.37 | 40.05 | 9.85 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.12 |  |  | 1500 | 2018-07-03 | JA_Solar | [11 empty] | 45
JA Solar | JAM60S01-310/PR | mono | 310 | 286.6447 | +5/-0 | 5 | 0 |  | 19 | 32.84 | 9.44 | 40.3 | 9.91 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.12 |  |  | 1500 | 2018-07-03 | JA_Solar | [11 empty] | 45
JA Solar | JAM72S01-350/PR | mono | 350 | 323.3 | +5/-0 | 5 | 0 |  | 18 | 38.58 | 9.07 | 47.24 | 9.61 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 77.16 | 39 | 1.57 |  | 48.5 |  |  | 1500 | 2018-07-03 | JA_Solar | [11 empty] | 45
JA Solar | JAM72S01-355/PR | mono | 355 | 328.1 | +5/-0 | 5 | 0 |  | 18.3 | 38.76 | 9.16 | 47.45 | 9.69 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 77.16 | 39 | 1.57 |  | 48.5 |  |  | 1500 | 2018-07-03 | JA_Solar | [11 empty] | 45
JA Solar | JAM72S01-360/PR | mono | 360 | 332.8 | +5/-0 | 5 | 0 |  | 18.5 | 38.96 | 9.24 | 47.66 | 9.81 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 77.16 | 39 | 1.57 |  | 48.5 |  |  | 1500 | 2018-07-03 | JA_Solar | [11 empty] | 45
JA Solar | JAM72S01-365/PR | mono | 365 | 337.4206 | +5/-0 | 5 | 0 |  | 18.8 | 39.21 | 9.31 | 47.93 | 9.85 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 77.16 | 39 | 1.57 |  | 48.5 |  |  | 1500 | 2018-07-03 | JA_Solar | [11 empty] | 45
JA Solar | JAM72S01-370/PR | mono | 370 | 342.1693 | +5/-0 | 5 | 0 |  | 19 | 39.45 | 9.38 | 48.18 | 9.91 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 77.16 | 39 | 1.57 |  | 48.5 |  |  | 1500 | 2018-07-03 | JA_Solar | [11 empty] | 45
JA Solar | JAP6 60-260/4BB/RE | poly | 260 |  | +5/-0 | 5 | 0 |  |  | 30.55 | 8.51 | 37.98 | 9.04 | -0.4% | -0.33% |  |  | 15 | [11 empty] | 1000 | 2015-12-03 | JA_Solar
JA Solar | JAP6 60-265/4BB/RE | poly | 265 |  | +5/-0 | 5 | 0 |  |  | 30.89 | 8.58 | 38.14 | 9.1 | -0.4% | -0.33% |  |  | 15 | [11 empty] | 1000 | 2015-12-03 | JA_Solar
JA Solar | JAP6 60-270/4BB/RE | poly | 270 |  | +5/-0 | 5 | 0 |  |  | 31.21 | 8.65 | 38.3 | 9.16 | -0.4% | -0.33% |  |  | 15 | [11 empty] | 1000 | 2015-12-03 | JA_Solar
JA Solar | JAP6 60-275/4BB/RE | poly | 275 |  | +5/-0 | 5 | 0 |  |  | 31.54 | 8.72 | 38.46 | 9.22 | -0.4% | -0.33% |  |  | 15 | [11 empty] | 1000 | 2015-12-03 | JA_Solar
JA Solar | JAP6 60-280/4BB/RE | poly | 280 |  | +5/-0 | 5 | 0 |  |  | 31.88 | 8.78 | 38.85 | 9.33 | -0.4% | -0.33% |  |  | 15 | [11 empty] | 1000 | 2015-12-03 | JA_Solar
JA Solar | JAP6 72-305/4BB/RE | poly | 305 |  | +5/-0 | 5 | 0 |  |  | 36.28 | 8.41 | 45.48 | 8.76 | -0.4% | -0.33% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | JA_Solar
JA Solar | JAP6 72-310/4BB/RE | poly | 310 |  | +5/-0 | 5 | 0 |  |  | 36.51 | 8.49 | 45.68 | 8.83 | -0.4% | -0.33% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | JA_Solar
JA Solar | JAP6 72-315/4BB/RE | poly | 315 |  | +5/-0 | 5 | 0 |  |  | 36.73 | 8.58 | 45.98 | 8.89 | -0.4% | -0.33% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | JA_Solar
JA Solar | JAP6 72-320/4BB/RE | poly | 320 |  | +5/-0 | 5 | 0 |  |  | 36.95 | 8.66 | 46.19 | 8.98 | -0.4% | -0.33% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | JA_Solar
JA Solar | JAP6 72-325/4BB/RE | poly | 325 |  | +5/-0 | 5 | 0 |  |  | 37.17 | 8.74 | 46.48 | 9.05 | -0.4% | -0.33% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | JA_Solar
JA Solar | JAP6(K)(DG) 60-255/4BB/1500V | poly | 255 |  | +5/-0 | 5 | 0 |  |  | 31.64 | 8.06 | 38.89 | 8.62 | -0.41% | -0.33% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | JA_Solar
JA Solar | JAP6(K)(DG) 60-260/4BB/1500V | poly | 260 |  | +5/-0 | 5 | 0 |  |  | 31.87 | 8.16 | 39.12 | 8.73 | -0.41% | -0.33% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | JA_Solar
JA Solar | JAP6(K)(DG) 60-265/4BB/1500V | poly | 265 |  | +5/-0 | 5 | 0 |  |  | 32.09 | 8.26 | 39.33 | 8.8 | -0.41% | -0.33% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | JA_Solar
JA Solar | JAP6(K)(DG) 60-270/4BB/1500V | poly | 270 |  | +5/-0 | 5 | 0 |  |  | 32.26 | 8.37 | 39.55 | 8.87 | -0.41% | -0.33% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | JA_Solar
JA Solar | JAP6(K)(DG) 60-275/4BB/1500V | poly | 275 |  | +5/-0 | 5 | 0 |  |  | 32.47 | 8.47 | 39.76 | 8.98 | -0.41% | -0.33% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | JA_Solar
JA Solar | JAP6 60-240/3BB | Poly | 240 |  | +5/-0 | 5 | 0 |  |  | 29.38 | 8.17 | 37.3 | 8.65 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2013-09-24 | JA_Solar
JA Solar | JAP6 60-245/3BB | Poly | 245 |  | +5/-0 | 5 | 0 |  |  | 29.59 | 8.28 | 37.50 | 8.86 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAP6 60-250/3BB | Poly | 250 |  | +5/-0 | 5 | 0 |  |  | 29.94 | 8.35 | 37.66 | 8.92 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAP6 60-255/3BB | Poly | 255 |  | +5/-0 | 5 | 0 |  |  | 30.29 | 8.42 | 37.82 | 8.98 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAP6 60-260/3BB | Poly | 260 |  | +5/-0 | 5 | 0 |  |  | 30.63 | 8.49 | 37.98 | 9.1 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAP6 60-265/3BB | poly | 265 |  | +5/-0 | 5 | 0 |  |  | 30.96 | 8.56 | 38.14 | 9.1 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAP6 72-280/3BB | Poly | 280 |  | +5/-0 | 5 | 0 |  |  | 35.99 | 7.78 | 45.38 | 8.29 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2013-09-24 | JA_Solar
JA Solar | JAP6 72-285/3BB | Poly | 285 |  | +5/-0 | 5 | 0 |  |  | 36.08 | 7.9 | 45.41 | 8.38 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2013-09-24 | JA_Solar
JA Solar | JAP6 72-290/3BB | Poly | 290 |  | +5/-0 | 5 | 0 |  |  | 36.39 | 7.97 | 45.72 | 8.42 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2013-09-24 | JA_Solar
JA Solar | JAP6 72-295/3BB | Poly | 295 |  | +5/-0 | 5 | 0 |  |  | 36.6 | 8.06 | 45.9 | 8.48 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2013-09-24 | JA_Solar
JA Solar | JAP6 72-300/3BB | Poly | 300 |  | +5/-0 | 5 | 0 |  |  | 36.41 | 8.24 | 45.2 | 8.73 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAP6 72-305/3BB | Poly | 305 |  | +5/-0 | 5 | 0 |  |  | 36.71 | 8.31 | 45.35 | 8.79 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAP6 72-310/3BB | Poly | 310 |  | +5/-0 | 5 | 0 |  |  | 37 | 8.38 | 45.45 | 8.85 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAP6 72-315/3BB | poly | 315 |  | +5/-0 | 5 | 0 |  |  | 37.28 | 8.45 | 45.6 | 8.91 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
JA Solar | JAP6 72-320/3BB | poly | 320 |  | +5/-0 | 5 | 0 |  |  | 37.56 | 8.52 | 45.82 | 9.03 | -0.41% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | JA_Solar
Jinko Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Jinko_Solar
Jinko Solar | JKM180M-72 | mono | 180 | 160.7 | +/-3 | 3 | -3 | 13.1003 | 14.1 | 36 | 5 | 44.8 | 5.29 | -0.43% | -0.32% | 0.04 | 45 | 10 | DNR | N/A | silver | white | 62.2 | 31.81 | 1.38 | 13.7402 | 31.9 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM185M-72 | mono | 185 | 165.1 | +/-3 | 3 | -3 | 13.4642 | 14.49 | 36.4 | 5.09 | 45 | 5.43 | -0.43% | -0.32% | 0.04 | 45 | 10 | DNR | N/A | silver | white | 62.2 | 31.81 | 1.38 | 13.7402 | 31.9 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM190M-72 | mono | 190 | 169.6 | +/-3 | 3 | -3 | 13.8281 | 14.88 | 36.6 | 5.19 | 45.2 | 5.56 | -0.43% | -0.32% | 0.04 | 45 | 10 | DNR | N/A | silver | white | 62.2 | 31.81 | 1.38 | 13.7402 | 31.9 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM195M-72 | mono | 195 | 174 | +/-3 | 3 | -3 | 14.192 | 15.28 | 36.8 | 5.3 | 45.4 | 5.67 | -0.43% | -0.32% | 0.04 | 45 | 10 | DNR | N/A | silver | white | 62.2 | 31.81 | 1.38 | 13.7402 | 31.9 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM200M-72 | mono | 200 | 178.5 | +/-3 | 3 | -3 | 14.5559 | 15.67 | 36.9 | 5.42 | 45.6 | 5.8 | -0.43% | -0.32% | 0.04 | 45 | 10 | DNR | N/A | silver | white | 62.2 | 31.81 | 1.38 | 13.7402 | 31.9 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM230M-60 | mono | 230 | 205.3 | +/-3 | 3 | -3 | 13.045 | 14.05 | 29.9 | 7.69 | 37.1 | 8.2 | -0.43% | -0.3% | 0.04 | 45 | 15 | DNR | N/A | silver | white | 65 | 39.06 | 1.77 | 17.6313 | 41.9 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM235M-60 | mono | 235 | 209.7 | +/-3 | 3 | -3 | 13.3286 | 14.36 | 30 | 7.83 | 37.2 | 8.31 | -0.43% | -0.3% | 0.04 | 45 | 15 | DNR | N/A | silver | white | 65 | 39.06 | 1.77 | 17.6313 | 41.9 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM240M-60 | mono | 240 | 214.2 | +/-3 | 3 | -3 | 13.6122 | 14.66 | 30.2 | 7.95 | 37.3 | 8.45 | -0.43% | -0.3% | 0.04 | 45 | 15 | DNR | N/A | silver | white | 65 | 39.06 | 1.77 | 17.6313 | 41.9 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM245M-60 | mono | 245 | 218.7 | +/-3 | 3 | -3 | 13.8958 | 14.97 | 30.4 | 8.06 | 37.4 | 8.58 | -0.43% | -0.3% | 0.04 | 45 | 15 | DNR | N/A | silver | white | 65 | 39.06 | 1.77 | 17.6313 | 41.9 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM250M-60 | mono | 250 | 223.1 | +/-3 | 3 | -3 | 14.1794 | 15.27 | 30.6 | 8.17 | 37.6 | 8.7 | -0.43% | -0.3% | 0.04 | 45 | 15 | DNR | N/A | silver | white | 65 | 39.06 | 1.77 | 17.6313 | 41.9 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM255M-60 | mono | 255 |  | +3/-0 | 3 | 0 |  |  | 30.8 | 8.28 | 37.8 | 8.96 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM260M-60 | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 30.9 | 8.42 | 37.9 | 9.1 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM265M-60 | mono | 265 |  | +3/-0 | 3 | 0 |  |  | 31.2 | 8.5 | 38.2 | 9.19 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM270M-60 | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 31.4 | 8.6 | 38.4 | 9.28 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM275M-60 | mono | 275 |  | +3/-0 | 3 | 0 |  |  | 31.6 | 8.7 | 38.5 | 9.4 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM280M-72 | mono | 280 | 249.9 | +/-3 | 3 | -3 | 13.4042 | 14.43 | 36.3 | 7.71 | 45.4 | 8.39 | -0.43% | -0.3% | 0.04 | 45 | 15 | DNR | N/A | silver | white | 77.01 | 39.06 | 1.97 | 20.889 | 59.6 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM285M-72 | mono | 285 | 254.4 | +/-3 | 3 | -3 | 13.6436 | 14.69 | 36.8 | 7.74 | 45.5 | 8.41 | -0.43% | -0.3% | 0.04 | 45 | 15 | DNR | N/A | silver | white | 77.01 | 39.06 | 1.97 | 20.889 | 59.6 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM290M-72 | mono | 290 | 258.8 | +/-3 | 3 | -3 | 13.8829 | 14.95 | 37.2 | 7.79 | 45.7 | 8.5 | -0.43% | -0.3% | 0.04 | 45 | 15 | DNR | N/A | silver | white | 77.01 | 39.06 | 1.97 | 20.889 | 59.6 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM295M-72 | mono | 295 | 263.3 | +/-3 | 3 | -3 | 14.1223 | 15.2 | 37.6 | 7.85 | 46 | 8.59 | -0.43% | -0.3% | 0.04 | 45 | 15 | DNR | N/A | silver | white | 77.01 | 39.06 | 1.97 | 20.889 | 59.6 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM300M-72 | mono | 300 | 267.8 | +/-3 | 3 | -3 | 14.3617 | 15.46 | 38 | 7.9 | 46.4 | 8.67 | -0.43% | -0.3% | 0.04 | 45 | 15 | DNR | N/A | silver | white | 77.01 | 39.06 | 1.97 | 20.889 | 59.6 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM255M-96 | mono | 255 |  | +3/-0 | 3 | 0 |  |  | 50 | 5.1 | 60.5 | 5.66 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM260M-96 | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 50.5 | 5.15 | 61.1 | 5.72 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM265M-96 | mono | 265 |  | +3/-0 | 3 | 0 |  |  | 51 | 5.2 | 61.7 | 5.77 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM270M-96 | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 51.5 | 5.24 | 62.3 | 5.82 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM275M-96 | mono | 275 |  | +3/-0 | 3 | 0 |  |  | 51.9 | 5.3 | 62.8 | 5.84 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM280M-60 | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 31.8 | 8.81 | 38.6 | 9.49 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM285M-60 | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 32 | 8.9 | 38.7 | 9.51 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM290M-60 | mono | 290 |  | +3/-0 | 3 | 0 |  |  | 32.2 | 9.02 | 39.5 | 9.55 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM295M-60 | mono | 295 |  | +3/-0 | 3 | 0 |  |  | 32.4 | 9.1 | 39.7 | 9.61 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM300M-60 | mono | 300 |  | +3/-0 | 3 | 0 |  |  | 32.6 | 9.21 | 40.1 | 9.72 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM280M-60-V | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 31.8 | 8.81 | 38.6 | 9.49 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM285M-60-V | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 32 | 8.9 | 38.7 | 9.51 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM290M-60-V | mono | 290 |  | +3/-0 | 3 | 0 |  |  | 32.2 | 9.02 | 39.5 | 9.55 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM295M-60-V | mono | 295 |  | +3/-0 | 3 | 0 |  |  | 32.4 | 9.1 | 39.7 | 9.61 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM300M-60-V | mono | 300 |  | +3/-0 | 3 | 0 |  |  | 32.6 | 9.21 | 40.1 | 9.72 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM340M-72 | mono | 340 |  | +3/-0 | 3 | 0 |  |  | 38.7 | 8.79 | 47.1 | 9.24 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM345M-72 | mono | 345 |  | +3/-0 | 3 | 0 |  |  | 38.9 | 8.87 | 47.3 | 9.31 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM350M-72 | mono | 350 |  | +3/-0 | 3 | 0 |  |  | 39.1 | 8.94 | 47.5 | 9.38 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM355M-72 | mono | 355 |  | +3/-0 | 3 | 0 |  |  | 39.3 | 9.04 | 47.8 | 9.45 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM360M-72 | mono | 360 |  | +3/-0 | 3 | 0 |  |  | 39.5 | 9.12 | 48 | 9.51 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM340M-72-V | mono | 340 |  | +3/-0 | 3 | 0 |  |  | 38.7 | 8.79 | 47.1 | 9.24 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM345M-72-V | mono | 345 |  | +3/-0 | 3 | 0 |  |  | 38.9 | 8.87 | 47.3 | 9.31 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM350M-72-V | mono | 350 |  | +3/-0 | 3 | 0 |  |  | 39.1 | 8.94 | 47.5 | 9.38 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM355M-72-V | mono | 355 |  | +3/-0 | 3 | 0 |  |  | 39.3 | 9.04 | 47.8 | 9.45 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM360M-72-V | mono | 360 |  | +3/-0 | 3 | 0 |  |  | 39.5 | 9.12 | 48 | 9.51 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM225P-60 | poly | 225 | 199.7 | +/-3 | 3 | -3 | 12.7614 | 13.74 | 29.4 | 7.65 | 36.7 | 8.25 | -0.45% | -0.27% | 0.05 | 45 | 15 | DNR | N/A | silver | white | 65 | 39.06 | 1.77 | 17.6313 | 41.9 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM230P-60 | poly | 230 | 204.1 | +/-3 | 3 | -3 | 13.045 | 14.05 | 29.6 | 7.78 | 36.8 | 8.35 | -0.45% | -0.27% | 0.05 | 45 | 15 | DNR | N/A | silver | white | 65 | 39.06 | 1.77 | 17.6313 | 41.9 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM235P-60 | poly | 235 | 208.6 | +/-3 | 3 | -3 | 13.3286 | 14.35 | 29.8 | 7.89 | 36.9 | 8.47 | -0.45% | -0.27% | 0.05 | 45 | 15 | DNR | N/A | silver | white | 65 | 39.06 | 1.77 | 17.6313 | 41.9 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM240P-60 | poly | 240 | 213 | +/-3 | 3 | -3 | 13.6122 | 14.66 | 30 | 8.01 | 37.2 | 8.56 | -0.45% | -0.27% | 0.05 | 45 | 15 | DNR | N/A | silver | white | 65 | 39.06 | 1.77 | 17.6313 | 41.9 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM245P-60 | poly | 245 | 217.4 | +/-3 | 3 | -3 | 13.8958 | 14.97 | 30.1 | 8.14 | 37.5 | 8.76 | -0.41% | -0.31% | 0.05 | 45 | 15 | DNR | N/A | silver | white | 65 | 39.06 | 1.77 | 17.6313 | 41.9 | 5 |  | Check | 7/14/15 RM | Jinko_Solar
Jinko Solar | JKM250P-60/JKM250P-60-B | poly | 250 |  | +3/-0 | 3 | -0 |  |  | 30.5 | 8.2 | 37.7 | 8.85 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 7/14/15 RM | Jinko_Solar
Jinko Solar | JKM255P(P)-60/JKM255P-60-B | poly | 255 |  | +3/-0 | 3 | -0 |  |  | 30.8 | 8.28 | 38 | 8.92 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 7/14/15 RM | Jinko_Solar
Jinko Solar | JKM260P(P)-60/JKM260P-60-B | poly | 260 |  | +3/-0 | 3 | -0 |  |  | 31.1 | 8.37 | 38.1 | 8.98 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 7/14/15 RM | Jinko_Solar
Jinko Solar | JKM265P(P)-60/JKM265P-60-B | poly | 265 |  | +3/-0 | 3 | -0 |  |  | 31.4 | 8.44 | 38.6 | 9.03 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 7/14/15 RM | Jinko_Solar
Jinko Solar | JKM270P(P)-60 | poly | 270 |  | +3/-0 | 3 | -0 |  |  | 31.7 | 8.52 | 38.8 | 9.09 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-11-25 | Jinko_Solar
Jinko Solar | JKM255P-60-V | Poly | 255 |  | +3/-0 | 3 | 0 |  |  | 30.8 | 8.28 | 38 | 8.92 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM260PP-60 | Poly | 260 |  | +3/-0 | 3 | 0 |  |  | 31.1 | 8.37 | 38.1 | 8.98 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM265PP-60 | Poly | 265 |  | +3/-0 | 3 | 0 |  |  | 31.4 | 8.44 | 38.6 | 9.03 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM270PP-60 | Poly | 270 |  | +3/-0 | 3 | 0 |  |  | 31.7 | 8.52 | 38.8 | 9.09 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM275PP-60 | Poly | 275 |  | +3/-0 | 3 | 0 |  |  | 32 | 8.61 | 39.1 | 9.15 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM280PP-60 | Poly | 280 |  | +3/-0 | 3 | 0 |  |  | 32.3 | 8.69 | 39.4 | 9.2 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM260PP-60-V | Poly | 260 |  | +3/-0 | 3 | 0 |  |  | 31.1 | 8.37 | 38.1 | 8.98 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM265PP-60-V | Poly | 265 |  | +3/-0 | 3 | 0 |  |  | 31.4 | 8.44 | 38.6 | 9.03 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM270PP-60-V | Poly | 270 |  | +3/-0 | 3 | 0 |  |  | 31.7 | 8.52 | 38.8 | 9.09 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM275PP-60-V | Poly | 275 |  | +3/-0 | 3 | 0 |  |  | 32 | 8.61 | 39.1 | 9.15 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM280PP-60-V | Poly | 280 |  | +3/-0 | 3 | 0 |  |  | 32.3 | 8.69 | 39.4 | 9.2 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM265PP-60-J4 | Poly | 265 |  | +3/-0 | 3 | 0 |  |  | 31.4 | 8.44 | 38.6 | 9.03 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM270PP-60-J4 | Poly | 270 |  | +3/-0 | 3 | 0 |  |  | 31.7 | 8.52 | 38.8 | 9.09 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM275PP-60-J4 | Poly | 275 |  | +3/-0 | 3 | 0 |  |  | 32 | 8.61 | 39.1 | 9.15 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM280PP-60-J4 | Poly | 280 |  | +3/-0 | 3 | 0 |  |  | 32.3 | 8.69 | 39.4 | 9.2 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM315PP-72 | poly | 315 |  | +3/-0 | 3 | -0 |  |  | 37.2 | 8.48 | 46.2 | 9.01 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM320PP-72 | poly | 320 |  | +3/-0 | 3 | -0 |  |  | 37.4 | 8.56 | 46.4 | 9.05 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM325PP-72 | poly | 325 |  | +3/-0 | 3 | -0 |  |  | 37.6 | 8.66 | 46.7 | 9.1 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM330PP-72 | poly | 330 |  | +3/-0 | 3 | -0 |  |  | 37.8 | 8.74 | 46.9 | 9.14 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM335PP-72 | poly | 335 |  | +3/-0 | 3 | -0 |  |  | 38 | 8.82 | 47.2 | 9.18 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM315PP-72-V | poly | 315 |  | +3/-0 | 3 | -0 |  |  | 37.2 | 8.48 | 46.2 | 9.01 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM320PP-72-V | poly | 320 |  | +3/-0 | 3 | -0 |  |  | 37.4 | 8.56 | 46.4 | 9.05 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM325PP-72-V | poly | 325 |  | +3/-0 | 3 | -0 |  |  | 37.6 | 8.66 | 46.7 | 9.1 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM330PP-72-V | poly | 330 |  | +3/-0 | 3 | -0 |  |  | 37.8 | 8.74 | 46.9 | 9.14 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM335PP-72 -V | poly | 335 |  | +3/-0 | 3 | -0 |  |  | 38 | 8.82 | 47.2 | 9.18 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM320PP-72-J4 | poly | 320 |  | +3/-0 | 3 | -0 |  |  | 37.4 | 8.56 | 46.4 | 9.05 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM325PP-72-J4 | poly | 325 |  | +3/-0 | 3 | -0 |  |  | 37.6 | 8.66 | 46.7 | 9.1 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM330PP-72-J4 | poly | 330 |  | +3/-0 | 3 | -0 |  |  | 37.8 | 8.74 | 46.9 | 9.14 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM335PP-72-J4 | poly | 335 |  | +3/-0 | 3 | -0 |  |  | 38 | 8.82 | 47.2 | 9.18 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1000 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM255PP-60-DV | poly | 255 |  | +3/-0 | 3 | -0 |  |  | 30.8 | 8.28 | 38 | 8.92 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM260PP-60-DV | poly | 260 |  | +3/-0 | 3 | -0 |  |  | 31.1 | 8.37 | 38.1 | 8.98 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM265PP-60-DV | poly | 265 |  | +3/-0 | 3 | -0 |  |  | 31.4 | 8.44 | 38.6 | 9.03 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM270PP-60-DV | poly | 270 |  | +3/-0 | 3 | -0 |  |  | 31.7 | 8.52 | 38.8 | 9.09 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM275PP-60-DV | poly | 275 |  | +3/-0 | 3 | -0 |  |  | 32 | 8.61 | 39.1 | 9.15 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM280PP-60-DV | poly | 280 |  | +3/-0 | 3 | -0 |  |  | 32.3 | 8.69 | 39.4 | 9.2 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM310PP-72-DV | poly | 310 |  | +3/-0 | 3 | -0 |  |  | 37 | 8.38 | 45.9 | 8.96 | -0.41% | -0.31% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM315PP-72-DV | poly | 315 |  | +3/-0 | 3 | -0 |  |  | 37.2 | 8.48 | 46.2 | 9.01 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM320PP-72-DV | poly | 320 |  | +3/-0 | 3 | -0 |  |  | 37.4 | 8.56 | 46.4 | 9.05 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM325PP-72-DV | poly | 325 |  | +3/-0 | 3 | -0 |  |  | 37.6 | 8.66 | 46.7 | 9.1 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM330PP-72-DV | poly | 330 |  | +3/-0 | 3 | -0 |  |  | 37.8 | 8.74 | 46.9 | 9.14 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM335PP-72-DV | poly | 335 |  | +3/-0 | 3 | -0 |  |  | 38 | 8.82 | 47.2 | 9.18 | -0.4% | -0.3% |  |  | 15 | [11 empty] | 1500 | 2017-10-11 | Jinko_Solar
Jinko Solar | JKM275P-72 | poly | 275 | 244.1 | +/-3 | 3 | -3 | 13.1648 | 14.17 | 35.4 | 8.44 | 44.4 | 8.7 | -0.45% | -0.27% | 0.05 | 45 | 15 | DNR | N/A | silver | white | 77.01 | 39.06 | 1.97 | 20.889 | 59.5 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM280P-72 | poly | 280 | 248.5 | +/-3 | 3 | -3 | 13.4042 | 14.43 | 35.5 | 7.89 | 44.5 | 8.81 | -0.45% | -0.27% | 0.05 | 45 | 15 | DNR | N/A | silver | white | 77.01 | 39.06 | 1.97 | 20.889 | 59.5 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM285P-72 | poly | 285 | 252.9 | +/-3 | 3 | -3 | 13.6436 | 14.69 | 36 | 7.92 | 44.7 | 8.85 | -0.45% | -0.27% | 0.05 | 45 | 15 | DNR | N/A | silver | white | 77.01 | 39.06 | 1.97 | 20.889 | 59.5 | 5 |  | Check |  | Jinko_Solar
Jinko Solar | JKM290P-72 | poly | 290 | 257.4 | +3/-0 | 3 | -0 | 13.8829 | 14.95 | 35.8 | 8.11 | 44.9 | 8.69 | -0.41% | -0.31% | 0.05 | 45 | 15 | DNR | N/A | silver | white | 77.01 | 39.06 | 1.97 | 20.889 | 59.5 | 5 |  | Check | 2015-02-18 | Jinko_Solar
Jinko Solar | JKM295P-72 | poly | 295 | 261.8 | +3/-0 | 3 | -0 | 14.1223 | 15.2 | 36.2 | 8.15 | 45.1 | 8.76 | -0.41% | -0.31% | 0.05 | 45 | 15 | DNR | N/A | silver | white | 77.01 | 39.06 | 1.97 | 20.889 | 59.5 | 5 |  | Check | 2015-02-18 | Jinko_Solar
Jinko Solar | JKM300PP-72-(D)(V) | poly | 300 |  | +3/-0 | 3 | 0 |  |  | 36.6 | 8.2 | 45.3 | 8.84 | -0.4% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM305PP-72-(D)(V) | poly | 305 |  | +3/-0 | 3 | 0 |  |  | 36.8 | 8.3 | 45.6 | 8.91 | -0.4% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM310PP-72-(D)(V) | poly | 310 |  | +3/-0 | 3 | 0 |  |  | 37 | 8.38 | 45.9 | 8.96 | -0.4% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM300P-72-V | Poly | 300 |  | +3/-0 | 3 | 0 |  |  | 36.6 | 8.2 | 45.3 | 8.84 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM305P-72-V | Poly | 305 |  | +3/-0 | 3 | 0 |  |  | 36.8 | 8.3 | 45.6 | 8.91 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM310P-72-V | Poly | 310 |  | +3/-0 | 3 | 0 |  |  | 37 | 8.38 | 45.9 | 8.96 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM315P-72-V | Poly | 315 |  | +3/-0 | 3 | 0 |  |  | 37.2 | 8.48 | 46.2 | 9.01 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM320P-72-V | poly | 320 |  | +3/-0 | 3 | 0 |  |  | 37.4 | 8.56 | 46.4 | 9.05 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM300P-72 | poly | 300 |  | +3/-0 | 3 | -0 |  |  | 36.6 | 8.2 | 45.3 | 8.84 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-02-18 | Jinko_Solar
Jinko Solar | JKM305P-72 | poly | 305 |  | +3/-0 | 3 | -0 |  |  | 36.8 | 8.3 | 45.6 | 8.91 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-25 | Jinko_Solar
Jinko Solar | JKM310P-72 | poly | 310 |  | +3/-0 | 3 | -0 |  |  | 37 | 8.38 | 45.9 | 8.96 | -0.41% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-25 | Jinko_Solar
Jinko Solar | JKM305M-72 | mono | 305 |  | +3/-0 | 3 | 0 |  |  | 37.2 | 8.2 | 45.7 | 8.72 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM310M-72 | mono | 310 |  | +3/-0 | 3 | 0 |  |  | 37.4 | 8.29 | 45.9 | 8.8 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM315M-72 | mono | 315 |  | +3/-0 | 3 | 0 |  |  | 37.6 | 8.38 | 46.1 | 8.87 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKM320M-72 | mono | 320 |  | +3/-0 | 3 | 0 |  |  | 37.8 | 8.47 | 46.4 | 8.98 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKMS255P | poly | 255 |  | +3/-0 | 3 | 0 |  |  | 29.3 | 8.72 | 36.1 | 9.39 | -0.4% | -0.3% |  |  | 12 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKMS260P | poly | 260 |  | +3/-0 | 3 | 0 |  |  | 29.5 | 8.81 | 36.2 | 9.45 | -0.4% | -0.3% |  |  | 12 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKMS265P | poly | 265 |  | +3/-0 | 3 | 0 |  |  | 29.8 | 8.88 | 36.7 | 9.51 | -0.4% | -0.3% |  |  | 12 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKMS270P | poly | 270 |  | +3/-0 | 3 | 0 |  |  | 30.1 | 8.97 | 36.9 | 9.57 | -0.4% | -0.3% |  |  | 12 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKMS305P | poly | 305 |  | +3/-0 | 3 | 0 |  |  | 34.9 | 8.74 | 43.3 | 9.38 | -0.4% | -0.3% |  |  | 12 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKMS310P | poly | 310 |  | +3/-0 | 3 | 0 |  |  | 35.2 | 8.82 | 43.6 | 9.43 | -0.4% | -0.3% |  |  | 12 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKMS315P | poly | 315 |  | +3/-0 | 3 | 0 |  |  | 35.3 | 8.93 | 43.9 | 9.48 | -0.4% | -0.3% |  |  | 12 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Jinko Solar | JKMS320P | poly | 320 |  | +3/-0 | 3 | 0 |  |  | 35.5 | 9.01 | 44.1 | 9.53 | -0.4% | -0.3% |  |  | 12 | [11 empty] | Check | 2015-12-03 | Jinko_Solar
Kaneka | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Kaneka
Kaneka | G-SA060 | amorphous | 60 |  | +10/-0 | 10 | 0 | 5.9 | 6.3 | 67 | 0.9 | 91.8 | 1.19 | -0.26% | -0.3105% |  |  | 7 |  | MC |  |  | 37.79 | 38.98 | 1.57 | 10.2295 | 30.2 | 5 |  | Check |  | Kaneka
Kaneka | U-EA100 | Thin Film | 100 |  | +10/-5 | 10 | -5 |  |  | 53.5 | 1.87 | 71 | 2.25 | -0.35% | -0.39% |  |  | 3.5 | [11 empty] | Check | 2015-12-03 | Kaneka
Kaneka | U-EA105 | Thin Film | 105 |  | +10/-5 | 10 | -5 |  |  | 53.5 | 1.96 | 71 | 2.4 | -0.35% | -0.39% |  |  | 3.5 | [11 empty] | Check | 2015-12-03 | Kaneka
Kaneka | U-EA110 | Thin Film | 110 |  | +10/-5 | 10 | -5 |  |  | 54 | 2.04 | 71 | 2.5 | -0.35% | -0.39% |  |  | 3.5 | [11 empty] | Check | 2015-12-03 | Kaneka
Kaneka | U-EA115 | Thin Film | 115 |  | +10/-5 | 10 | -5 |  |  | 55 | 2.09 | 71 | 2.5 | -0.35% | -0.39% |  |  | 3.5 | [11 empty] | Check | 2015-12-03 | Kaneka
Kaneka | U-EA120 | Thin Film | 120 |  | +10/-5 | 10 | -5 |  |  | 55 | 2.18 | 71 | 2.6 | -0.35% | -0.39% |  |  | 3.5 | [11 empty] | Check | 2015-12-03 | Kaneka
Kyocera Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Kyocera_Solar
Kyocera Solar | KC175 GT | poly | 175 |  | +10/-5 | 10 | -5 | 12.7196 | 13.7 | 23.6 | 7.42 | 29.2 | 8.09 | -0.49% | -0.362% |  |  | 15 |  | MC |  |  | 50.8 | 39 | 1.4 | 13.7583 | 35.3 | 1 |  | Check |  | Kyocera_Solar
Kyocera Solar | KC200GT | poly | 200 |  | +10/-5 | 10 | -5 | 13.1399 | 14.18 | 26.3 | 7.61 | 32.9 | 8.21 | -0.49% | -0.3733% |  |  | 15 |  | MC |  |  | 56.2 | 39 | 1.4 | 15.2208 | 40.8 | 1 |  | Check |  | Kyocera_Solar
Kyocera Solar | KD130GX-LP | poly | 130 |  | +5/-5 | 5 | -5 | 12.0438 | 13 | 17.7 | 7.35 | 22.1 | 8.06 | -0.46% | -0.3749% |  |  | 15 |  | MC |  |  | 59.1 | 26.3 | 1.41 | 10.794 | 28.7 | 1 |  | Check |  | Kyocera_Solar
Kyocera Solar | KD130SX | poly | 130 |  | +5/-5 | 5 | -5 | 12.0438 | 13 | 17.7 | 7.35 | 22.1 | 8.06 | -0.46% | -0.3749% |  |  | 15 |  | MC |  |  | 59.1 | 26.3 | 1.41 | 10.794 | 28.7 | 1 |  | Check |  | Kyocera_Solar
Kyocera Solar | KD135GX-LP | poly | 135 |  | +5/-5 | 5 | -5 | 12.507 | 13.5 | 17.7 | 7.63 | 22.1 | 8.37 | -0.46% | -0.362% |  |  | 15 |  | MC |  |  | 59.1 | 26.3 | 1.42 | 10.794 | 28.7 | 1 |  | Check |  | Kyocera_Solar
Kyocera Solar | KD135SX | poly | 135 |  | +5/-5 | 5 | -5 | 12.507 | 13.5 | 17.7 | 7.63 | 22.1 | 8.37 | -0.46% | -0.362% |  |  | 15 |  | MC |  |  | 59.1 | 26.3 | 1.42 | 10.794 | 28.7 | 1 |  | Check |  | Kyocera_Solar
Kyocera Solar | KD140SX-UFBS | multi | 140 |  | +7/-0 | 7 | 0 |  |  | 17.7 | 7.91 | 22.1 | 8.68 | -0.46% | -0.36% |  |  | 15 | [11 empty] | Check |  | Kyocera_Solar
Kyocera Solar | KD140GX-LFBS | multi | 140 |  | +7/-0 | 7 | 0 |  |  | 17.7 | 7.91 | 22.1 | 8.68 | -0.46% | -0.36% |  |  | 15 | [11 empty] | Check |  | Kyocera_Solar
Kyocera Solar | KD180GX-LP | poly | 180 |  | +5/-5 | 5 | -5 | 12.5874 | 13.6 | 23.6 | 7.63 | 29.5 | 8.35 | -0.46% | -0.362% |  |  | 15 |  | MC |  |  | 52.8 | 39 | 1.4 | 14.3 | 36.4 | 1 |  | Check |  | Kyocera_Solar
Kyocera Solar | KD205GX-LP | poly | 205 |  | +5/-5 | 5 | -5 | 12.8075 | 13.8 | 26.6 | 7.71 | 33.2 | 8.36 | -0.46% | -0.3593% |  |  | 15 |  | MC |  |  | 59.1 | 39 | 1.4 | 16.0062 | 40.8 | 1 |  | Check |  | Kyocera_Solar
Kyocera Solar | KD210GX-LPU-ZT | poly | 210 | 189.8 | +5/-0 | 5 | 0 | 13.1355 | 14.1 | 26.6 | 7.9 | 33.2 | 8.58 | -0.4571% | -0.3614% | 0.060023 | 45 | 15 | yes | MC4 | black | white | 59.06 | 38.98 | 1.81 | 15.9872 | 39.7 | 5 |  | Check |  | Kyocera_Solar
Kyocera Solar | KD215GX-LPU-ZT | poly | 215 | 194.4 | +5/-0 | 5 | 0 | 13.4482 | 14.4 | 26.6 | 8.09 | 33.2 | 8.78 | -0.4609% | -0.3614% | 0.060023 | 45 | 15 | yes | MC4 | black | white | 59.06 | 38.98 | 1.81 | 15.9872 | 39.7 | 5 |  | Check |  | Kyocera_Solar
Kyocera Solar | KD220GX-LFBS | multi | 220 |  | +5/-0 | 5 | 0 |  |  | 26.6 | 8.28 | 33.2 | 8.98 | -0.46% | -0.36% |  |  | 15 | [11 empty] | Check |  | Kyocera_Solar
Kyocera Solar | KD230GX-LPB | multi | 230 |  | +3/-3 | 3 | -3 |  |  | 29.8 | 7.72 | 36.9 | 8.36 | -0.452% | -0.3739% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | Kyocera_Solar
Kyocera Solar | KD245GX-LFB2 | multi | 245 |  | +5/-0 | 5 | 0 |  |  | 29.8 | 8.23 | 36.9 | 8.91 | -0.46% | -0.36% |  |  | 15 | [11 empty] | Check | 2015-02-18 | Kyocera_Solar
Kyocera Solar | KD250GX-LFB2 | multi | 250 |  | +5/-0 | 5 | 0 |  |  | 29.8 | 8.39 | 36.9 | 9.09 | -0.46% | -0.36% |  |  | 15 | [11 empty] | Check | 2015-02-18 | Kyocera_Solar
Kyocera Solar | KD260GX-LFB2 | multi | 260 |  | +5/-0 | 5 | 0 |  |  | 31 | 8.39 | 38.3 | 9.09 | -0.45% | -0.36% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Kyocera_Solar
Kyocera Solar | KDX265GX-LFB2 | multi | 265 |  | +5/-0 | 5 | 0 |  |  | 31 | 8.55 | 38.3 | 9.26 | -0.45% | -0.36% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Kyocera_Solar
Kyocera Solar | KD235GX-LPB | poly | 235 | 212.6 | +5/-3 | 5 | -3 | 13.2682 | 14.2 | 29.8 | 7.89 | 36.9 | 8.55 | -0.4553% | -0.3604% | 0.06 | 45 | 15 | yes | MC4 | black | white | 65.43 | 38.98 | 1.81 | 17.7115 | 46.3 | 5 |  | Check |  | Kyocera_Solar
Kyocera Solar | KD235GX-LPB-ZT | poly | 235 | 212.6 | +5/-0 | 5 | 0 | 13.2682 | 14.2 | 29.8 | 7.89 | 36.9 | 8.55 | -0.4553% | -0.3604% | 0.06 | 45 | 15 | yes | MC4 | black | white | 65.43 | 38.98 | 1.81 | 17.7115 | 46.3 | 5 |  | Check |  | Kyocera_Solar
Kyocera Solar | KD240GX-LPB | poly | 240 | 217.3 | +5/-3 | 5 | -3 | 13.5505 | 14.5 | 29.8 | 8.06 | 36.9 | 8.59 | -0.4583% | -0.3604% | 0.059953 | 45 | 15 | yes | MC4 | black | white | 65.43 | 38.98 | 1.81 | 17.7115 | 46.3 | 5 |  | Check |  | Kyocera_Solar
Kyocera Solar | KD240GX-LPB-ZT | poly | 240 | 217.3 | +5/-0 | 5 | 0 | 13.5505 | 14.5 | 29.8 | 8.06 | 36.9 | 8.59 | -0.4583% | -0.3604% | 0.059953 | 45 | 15 | yes | MC4 | black | white | 65.43 | 38.98 | 1.81 | 17.7115 | 46.3 | 5 |  | Check |  | Kyocera_Solar
Kyocera Solar | KD245GX-LPB | poly | 245 | 219.1 | +5/-3 | 5 | -3 | 13.8328 | 14.8 | 29.8 | 8.23 | 36.9 | 8.91 | -0.4571% | -0.3604% | 0.060045 | 45 | 15 | yes | MC4 | black | white | 65.43 | 38.98 | 1.81 | 17.7115 | 46.3 | 5 |  | Check |  | Kyocera_Solar
Kyocera Solar | KD245GX-LPB-ZT | poly | 245 | 219.1 | +5/-0 | 5 | 0 | 13.8328 | 14.8 | 29.8 | 8.23 | 36.9 | 8.91 | -0.4571% | -0.3604% | 0.060045 | 45 | 15 | yes | MC4 | black | white | 65.43 | 38.98 | 1.81 | 17.7115 | 46.3 | 5 |  | Check |  | Kyocera_Solar
Kyocera Solar | KD315GX-LFB | multi | 315 |  | +5/-3 | 5 | -3 |  |  | 39.8 | 7.92 | 49.2 | 8.5 | -0.52% | -0.36% |  |  | 15 | [11 empty] | Check |  | Kyocera_Solar
Kyocera Solar | KD320GX-LFB | multi | 320 |  | +5/-3 | 5 | -3 |  |  | 40.1 | 7.99 | 49.5 | 8.6 | -0.51% | -0.36% |  |  | 15 | [11 empty] | Check |  | Kyocera_Solar
Kyocera Solar | KD325GX-LFB | multi | 325 |  | +5/-0 | 5 | 0 |  |  | 40.3 | 8.07 | 49.7 | 8.69 | -0.45% | -0.36% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Kyocera_Solar
Kyocera Solar | KD330GX-LFB | multi | 330 |  | +5/-0 | 5 | 0 |  |  | 40.5 | 8.15 | 49.9 | 8.79 | -0.45% | -0.36% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Kyocera_Solar
Kyocera Solar | KU260-6MCA | multi | 260 |  | +5/-0 | 5 | 0 |  |  | 31 | 8.39 | 38.3 | 9.09 | -0.45% | -0.36% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Kyocera_Solar
Kyocera Solar | KU265-6MCA | multi | 265 |  | +5/-0 | 5 | 0 |  |  | 31 | 8.55 | 38.3 | 9.26 | -0.45% | -0.36% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Kyocera_Solar
Kyocera Solar | KU325-8BCA | multi | 325 |  | +5/-0 | 5 | 0 |  |  | 40.4 | 8.05 | 50 | 8.68 | -0.45% | -0.36% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Kyocera_Solar
Kyocera Solar | KU330-8BCA | multi | 330 |  | +5/-0 | 5 | 0 |  |  | 40.7 | 8.11 | 50.3 | 8.74 | -0.45% | -0.36% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Kyocera_Solar
Kyocera Solar | KU335-8BCA | multi | 335 |  | +5/-0 | 5 | 0 |  |  | 40.9 | 8.2 | 50.5 | 8.8 | -0.48% | -0.36% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Kyocera_Solar
Kyocera Solar | KU340-8BCA | multi | 340 |  | +5/-0 | 5 | 0 |  |  | 41.2 | 8.26 | 50.8 | 8.86 | -0.48% | -0.36% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Kyocera_Solar
Kyocera Solar | KT145-3UC | poly | 145 |  | +5/-5 | 5 | -5 |  |  | 18.3 | 7.93 | 22.4 | 8.58 | -0.45% | -0.36% |  |  | 15 |  |  |  |  | 59.06 | 26.3 | 1.81 |  | 27.6 |  |  | 1000 | 2018-03-09 | Kyocera_Solar
Kyocera Solar | KT260-6GC-A | poly | 260 |  | +5/-3 | 5 | -3 |  |  | 31 | 8.39 | 38.3 | 9.09 | -0.45% | -0.36% |  |  | 15 |  |  |  |  | 65.43 | 38.98 | 1.81 |  | 44.1 |  |  | 1000 | 2018-03-09 | Kyocera_Solar
Kyocera Solar | KT265-6MCA | poly | 265 |  | +5/-3 | 5 | -3 |  |  | 31 | 8.55 | 38.3 | 9.26 | -0.45% | -0.36% |  |  | 15 |  |  |  |  | 65.43 | 38.98 | 1.81 |  | 41.9 |  |  | 1000 | 2018-03-09 | Kyocera_Solar
Kyocera Solar | KT265-6MPA | poly | 265 |  | +5/-3 | 5 | -3 |  |  | 31 | 8.55 | 38.3 | 9.26 | -0.45% | -0.36% |  |  | 15 |  |  |  |  | 65.43 | 38.98 | 1.81 |  | 41.9 |  |  | 1000 | 2018-03-09 | Kyocera_Solar
Kyocera Solar | KK255P-3CB2CG | poly | 255 |  | +5/-3 | 5 | -3 |  |  | 30.4 | 8.39 | 37.6 | 9.09 | -0.45% | -0.36% |  |  | 15 |  |  |  |  | 65.43 | 38.98 | 1.81 |  | 44.1 |  |  | 1000 | 2018-03-09 | Kyocera_Solar
Kyocera Solar | KK270P-3CD8CG | poly | 270 |  | +5/-3 | 5 | -3 |  |  | 31 | 8.71 | 38.3 | 9.43 | -0.46% | -0.36% |  |  | 15 |  |  |  |  | 65.43 | 38.98 | 1.81 |  | 41.9 |  |  | 1000 | 2018-03-09 | Kyocera_Solar
LDK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | LDK
LDK | 245D-20 | mono | 245 |  | +2/-0 | 2 | 0 | 13.9567 | 15.01 | 29.5 | 8.32 | 37.6 | 8.92 | -0.47% | -0.34% | 0.06 | 45 | 20 |  | MC4 | silver | white | 64.65 | 39.1 | 1.57 | 17.5543 | 41.9 | 10 |  | Check |  | LDK
LDK | 250D-20 | mono | 250 |  | +2/-0 | 2 | 0 | 14.2415 | 15.32 | 29.9 | 8.38 | 37.8 | 8.92 | -0.47% | -0.34% | 0.06 | 45 | 20 |  | MC4 | silver | white | 64.65 | 39.1 | 1.57 | 17.5543 | 41.9 | 10 |  | Check |  | LDK
LDK | LDK-255D-20 | mono | 250 |  | +2/-0 | 2 | 0 |  |  | 30.3 | 8.43 | 38.1 | 8.93 | -0.47% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | LDK-260D-20 | mono | 260 |  | +2/-0 | 2 | 0 |  |  | 30.7 | 8.48 | 38.3 | 8.95 | -0.47% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | LDK-270P-24 | poly | 270 |  | +3/-0 | 3 | 0 |  |  | 34.4 | 7.87 | 44.1 | 8.37 | -0.45% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | LDK-275P-24 | poly | 275 |  | +3/-0 | 3 | 0 |  |  | 34.8 | 7.92 | 44.3 | 8.41 | -0.45% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | LDK-280P-24 | poly | 280 |  | +3/-0 | 3 | 0 |  |  | 35.3 | 7.95 | 44.6 | 8.44 | -0.45% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | LDK-285P-24 | poly | 285 |  | +2/-0 | 2 | 0 |  |  | 35.7 | 8 | 44.8 | 8.48 | -0.45% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | LDK-290P-24 | poly | 290 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.1 | 8.04 | 45.1 | 8.51 | -0.45% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | LDK-295P-24 | poly | 295 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.6 | 8.08 | 45.3 | 8.54 | -0.45% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | LDK-300P-24 | poly | 300 |  | +1.5/-0 | 1.5 | 0 |  |  | 37 | 8.12 | 45.6 | 8.58 | -0.45% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | 250 MA | mono | 250 |  | +2/-0 | 2 | 0 |  |  | 29.9 | 8.38 | 37.8 | 8.92 | -0.47% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | 255 MA | mono | 255 |  | +2/-0 | 2 | 0 |  |  | 30.3 | 8.43 | 38.1 | 8.93 | -0.47% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | 260 MA | mono | 260 |  | +2/-0 | 2 | 0 |  |  | 30.7 | 8.48 | 38.3 | 8.95 | -0.47% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | 265 MA | mono | 265 |  | +2/-0 | 2 | 0 |  |  | 31.1 | 8.53 | 38.6 | 8.97 | -0.47% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | 270MA | mono | 270 |  | +2/-0 | 2 | 0 |  |  | 31.5 | 8.58 | 38.9 | 8.99 | -0.47% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | 275 MA | mono | 275 |  | +2/-0 | 2 | 0 |  |  | 31.9 | 8.63 | 39.2 | 9.02 | -0.47% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | 295 PB | poly | 295 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.6 | 8.08 | 45.3 | 8.54 | -0.42% | -0.32% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | 300 PB | poly | 300 |  | +1.5/-0 | 1.5 | 0 |  |  | 37 | 8.12 | 45.6 | 8.58 | -0.42% | -0.32% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | 305 PB | poly | 305 |  | +1.5/-0 | 1.5 | 0 |  |  | 37.4 | 8.17 | 45.8 | 8.61 | -0.42% | -0.32% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | 310 PB | poly | 310 |  | +1.5/-0 | 1.5 | 0 |  |  | 37.8 | 8.21 | 46.1 | 8.65 | -0.42% | -0.32% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LDK | 315 PB | poly | 315 |  | +1.5/-0 | 1.5 | 0 |  |  | 38.2 | 8.25 | 46.4 | 8.7 | -0.42% | -0.32% |  |  | 20 | [11 empty] | Check | 2015-12-03 | LDK
LG Electronics | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | LG_Electronics
LG Electronics | LG220P1C-G2 | poly | 220 | 197.5 | +3/-0 | 3 | 0 | 12.7311 | 13.7 | 28.9 | 7.62 | 36.1 | 8.21 | -0.456% | -0.334% | 0.059 | 45.7 | 20 | yes | tyco | black | white | 64.25 | 38.82 | 1.65 | 17.3207 | 41.89 | 10 |  | Check |  | LG_Electronics
LG Electronics | LG225P1C-G2 | poly | 225 | 202.1 | +3/-0 | 3 | 0 | 13.0205 | 14 | 29 | 7.76 | 36.3 | 8.3 | -0.456% | -0.334% | 0.059 | 45.7 | 20 | yes | tyco | black | white | 64.25 | 38.82 | 1.65 | 17.3207 | 41.89 | 10 |  | Check |  | LG_Electronics
LG Electronics | LG230M1C-G2 | mono | 230 | 205.8 | +3/-0 | 3 | 0 | 13.3098 | 14.3 | 29.5 | 7.81 | 36.6 | 8.37 | -0.493% | -0.355% | 0.046 | 43.8 | 20 | yes | tyco | black | white | 64.25 | 38.82 | 1.65 | 17.3207 | 41.89 | 10 |  | Check |  | LG_Electronics
LG Electronics | LG230P1C-G2 | poly | 230 | 206.7 | +3/-0 | 3 | 0 | 13.3098 | 14.3 | 29.1 | 7.91 | 36.4 | 8.39 | -0.456% | -0.334% | 0.059 | 45.7 | 20 | yes | tyco | black | white | 64.25 | 38.82 | 1.65 | 17.3207 | 41.89 | 10 |  | Check |  | LG_Electronics
LG Electronics | LG235M1C-G2 | mono | 235 | 210.4 | +3/-0 | 3 | 0 | 13.5991 | 14.6 | 29.6 | 7.94 | 36.8 | 8.49 | -0.493% | -0.355% | 0.046 | 43.8 | 20 | yes | tyco | black | white | 64.25 | 38.82 | 1.65 | 17.3207 | 41.89 | 10 |  | Check |  | LG_Electronics
LG Electronics | LG240M1C-G2 | mono | 240 | 215 | +3/-0 | 3 | 0 | 13.8885 | 14.9 | 29.7 | 8.1 | 36.9 | 8.58 | -0.493% | -0.355% | 0.046 | 43.8 | 20 | yes | tyco | black | white | 64.25 | 38.82 | 1.65 | 17.3207 | 41.89 | 10 |  | Check |  | LG_Electronics
LG Electronics | LG245S1C-G2 | mono | 245 | 217.4 | +3/-0 | 3 | 0 | 14.1778 | 15.2 | 29.8 | 8.23 | 37 | 8.67 | -0.469% | -0.338% | 0.043 | 43.7 | 20 | yes | tyco | black | white | 64.25 | 38.82 | 1.65 | 17.3207 | 41.89 | 10 |  | Check |  | LG_Electronics
LG Electronics | LG250S1C-G2 | mono | 250 | 222 | +3/-0 | 3 | 0 | 14.4672 | 15.5 | 29.9 | 8.37 | 37.1 | 8.76 | -0.469% | -0.338% | 0.043 | 43.7 | 20 | yes | tyco | black | white | 64.25 | 38.82 | 1.65 | 17.3207 | 41.89 | 10 |  | Check |  | LG_Electronics
LG Electronics | LG255S1C-G2 | mono | 255 | 226.6 | +3/-0 | 3 | 0 | 14.7565 | 15.8 | 30 | 8.5 | 37.2 | 8.85 | -0.469% | -0.338% | 0.043 | 43.7 | 20 | yes | tyco | black | white | 64.25 | 38.82 | 1.65 | 17.3207 | 41.89 | 10 |  | Check |  | LG_Electronics
LG Electronics | LG260S1C-G2 | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 30.1 | 8.64 | 37.3 | 8.94 | -0.42% | -0.306% |  |  | 15 | [11 empty] | Check |  | LG_Electronics
LG Electronics | LG260S1C-A3 | mono | 260 |  | +3/-1 | 3 | 0 |  |  | 31.1 | 8.38 | 38.1 | 9.05 | -0.43% | -0.306% |  |  | 15 | [11 empty] | Check | 2014-01-24 | LG_Electronics
LG Electronics | LG250S1C-G3 | mono | 250 |  | +3/-0 | 3 | 0 |  |  | 29.8 | 8.39 | 37.6 | 9 | -0.459% | -0.343% |  |  | 15 | [11 empty] | Check |  | LG_Electronics
LG Electronics | LG250S1K-G3 | mono | 250 |  | +3/-0 | 3 | 0 |  |  | 30.8 | 8.13 | 38.3 | 8.62 | -0.445% | -0.325% |  |  | 15 | [11 empty] | Check |  | LG_Electronics
LG Electronics | LG2551C-G3 | mono | 255 |  | +3/-0 | 3 | 0 |  |  | 31 | 8.24 | 38.4 | 8.72 | -0.459% | -0.343% |  |  | 15 | [11 empty] | Check |  | LG_Electronics
LG Electronics | LG260S1C-G3 | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 31.2 | 8.35 | 38.6 | 8.82 | -0.459% | -0.343% |  |  | 15 | [11 empty] | Check |  | LG_Electronics
LG Electronics | LG265S1C-G3 | mono | 265 |  | +3/-0 | 3 | 0 |  |  | 30.4 | 8.72 | 38 | 9.3 | -0.459% | -0.343% |  |  | 15 | [11 empty] | Check |  | LG_Electronics
LG Electronics | LG275S1C-G4 | mono | 275 |  | +3/-0 | 3 | 0 |  |  | 31.7 | 8.68 | 98.7 | 9.26 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG280S1C-G4 | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 31.9 | 8.78 | 98.8 | 9.33 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG285S1C-G4 | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 32.3 | 8.88 | 39 | 9.43 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG260S1K-B3 | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 31.2 | 8.34 | 38.2 | 8.88 | -0.44% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG260S1C-B3 | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 31.1 | 8.38 | 38.1 | 9.05 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG265S1K-B3 | mono | 265 |  | +3/-0 | 3 | 0 |  |  | 31.5 | 8.42 | 38.4 | 9.03 | -0.44% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG270S1K-B3 | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 31.7 | 8.52 | 38.6 | 9.12 | -0.44% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG265S1C-B3 | mono | 265 |  | +3/-0 | 3 | 0 |  |  | 31.3 | 8.49 | 38.3 | 9.11 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG270S1C-B3 | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 31.5 | 8.58 | 38.5 | 9.17 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG275S1C-B3 | mono | 275 |  | +3/-0 | 3 | 0 |  |  | 31.7 | 8.68 | 38.7 | 9.26 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG280S1C-B3 | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 31.9 | 8.78 | 38.8 | 9.33 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG280N1C | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 31.5 | 8.97 | 38.9 | 9.56 | -0.42% | -0.31% |  |  | 15 | [11 empty] | Check |  | LG_Electronics
LG Electronics | LG285N1C | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 31.6 | 9.09 | 39 | 9.68 | -0.42% | -0.31% |  |  | 15 | [11 empty] | Check |  | LG_Electronics
LG Electronics | LG290N1C | mono | 290 |  | +3/-0 | 3 | 0 |  |  | 31.8 | 9.19 | 39.2 | 9.8 | -0.42% | -0.31% |  |  | 15 | [11 empty] | Check |  | LG_Electronics
LG Electronics | LG295N1C | mono | 295 |  | +3/-0 | 3 | 0 |  |  | 31.9 | 9.3 | 39.3 | 9.91 | -0.42% | -0.31% |  |  | 15 | [11 empty] | Check |  | LG_Electronics
LG Electronics | LG300N1C | mono | 300 |  | +3/-0 | 3 | 0 |  |  | 32 | 9.42 | 39.5 | 10 | -0.42% | -0.31% |  |  | 15 | [11 empty] | Check |  | LG_Electronics
LG Electronics | LG285N1C-A3 | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 31.6 | 9.03 | 39.5 | 9.59 | -0.41% | -0.29% |  |  | 20 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG290N1C-A3 | mono | 290 |  | +3/-0 | 3 | 0 |  |  | 31.8 | 9.15 | 39.6 | 9.7 | -0.41% | -0.29% |  |  | 20 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG295N1C-A3 | mono | 295 |  | +3/-0 | 3 | 0 |  |  | 31.8 | 9.28 | 39.7 | 9.85 | -0.41% | -0.29% |  |  | 20 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG300N1C-A3 | mono | 300 |  | +3/-0 | 3 | 0 |  |  | 32 | 9.4 | 39.8 | 9.98 | -0.41% | -0.29% |  |  | 20 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG290N1C-B3 | mono | 290 |  | +3/-0 | 3 | 0 |  |  | 31.8 | 9.15 | 39.6 | 9.7 | -0.41% | -0.29% |  |  | 20 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG295N1C-B3 | mono | 295 |  | +3/-0 | 3 | 0 |  |  | 31.8 | 9.28 | 39.7 | 9.85 | -0.41% | -0.29% |  |  | 20 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG300N1C-B3 | mono | 300 |  | +3/-0 | 3 | 0 |  |  | 32 | 9.4 | 39.8 | 9.98 | -0.41% | -0.29% |  |  | 20 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG305N1C-B3 | mono | 305 |  | +3/-0 | 3 | 0 |  |  | 32.1 | 9.52 | 40 | 10.1 | -0.41% | -0.29% |  |  | 20 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG305N1C-G4 | mono | 305 |  | +3/-0 | 3 | 0 |  |  | 32.5 | 9.39 | 40.1 | 9.93 | -0.38% | -0.28% |  |  | 20 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG310N1C-G4 | mono | 310 |  | +3/-0 | 3 | 0 |  |  | 32.8 | 9.45 | 40.4 | 9.96 | -0.38% | -0.28% |  |  | 20 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG315N1C-G4 | mono | 315 |  | +3/-0 | 3 | 0 |  |  | 33.2 | 9.5 | 40.6 | 10.02 | -0.38% | -0.28% |  |  | 20 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG320N1C-G4 | mono | 320 |  | +3/-0 | 3 | 0 |  |  | 33.6 | 9.53 | 40.9 | 10.05 | -0.38% | -0.28% |  |  | 20 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG300N1K-G4 | mono | 300 |  | +3/-0 | 3 | 0 |  |  | 32.5 | 9.26 | 39.7 | 9.7 | -0.38% | -0.28% |  |  | 20 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG305N1K-G4 | mono | 305 |  | +3/-0 | 3 | 0 |  |  | 32.9 | 9.28 | 40.1 | 9.74 | -0.38% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-11 | LG_Electronics
LG Electronics | LG335S2W-G4 | mono | 335 |  | +3/-0 | 3 | 0 |  |  | 37.5 | 8.94 | 46.2 | 9.48 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1000 | 2017-10-11 | LG_Electronics
LG Electronics | LG340S2W-G4 | mono | 340 |  | +3/-0 | 3 | 0 |  |  | 37.7 | 9.02 | 46.4 | 9.54 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1000 | 2017-10-11 | LG_Electronics
LG Electronics | LG360N2W-B3 | mono | 360 |  | +3/-0 | 3 | 0 |  |  | 38.4 | 9.39 | 48.3 | 9.84 | -0.41% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG365N2W-B3 | mono | 365 |  | +3/-0 | 3 | 0 |  |  | 38.6 | 9.46 | 48.4 | 9.89 | -0.41% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-25 | LG_Electronics
LG Electronics | LG365N2W-G4 | mono | 365 |  | +3/-0 | 3 | 0 |  |  | 38.9 | 9.39 | 47.7 | 9.92 | -0.38% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-11 | LG_Electronics
LG Electronics | LG370N2W-G4 | mono | 370 |  | +3/-0 | 3 | 0 |  |  | 39.2 | 9.44 | 48 | 9.98 | -0.38% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-10-11 | LG_Electronics
LG Electronics | LG375N2W-G4 | mono | 375 |  | +3/-0 | 3 | 0 |  |  | 39.6 | 9.5 | 48.3 | 10.04 | -0.38% | -0.28% |  |  | 20 | [11 empty] | 1000 | 2017-08-18 | LG_Electronics
LG Electronics | LG295S1C-A5 | mono | 295 |  | +3/-0 | 3 | 0 |  |  | 31.3 | 9.43 | 38.6 | 10.02 | -0.41% | -0.3% |  |  | 20 | [11 empty] | 1000 | 2017-10-11 | LG_Electronics
LG Electronics | LG300S1C-A5 | mono | 300 |  | +3/-0 | 3 | 0 |  |  | 31.6 | 9.5 | 38.9 | 10.07 | -0.41% | -0.3% |  |  | 20 | [11 empty] | 1000 | 2017-10-11 | LG_Electronics
LG Electronics | LG315N1K-A5 | mono | 315 |  | +3/-0 | 3 | 0 |  |  | 32.9 | 9.58 | 40.7 | 10.15 | -0.37% | -0.27% |  |  | 20 | [11 empty] | 1000 | 2017-10-11 | LG_Electronics
LG Electronics | LG320N1K-A5 | mono | 320 |  | +3/-0 | 3 | 0 |  |  | 33.3 | 9.62 | 40.8 | 10.19 | -0.37% | -0.27% |  |  | 20 | [11 empty] | 1000 | 2017-10-02 | LG_Electronics
LG Electronics | LG325N1C-A5 | mono | 325 | 301.5 | +3/-0 | 3 | 0 |  |  | 33.3 | 9.77 | 40.8 | 10.41 | -0.37% | -0.27% |  |  | 20 | [11 empty] | 1000 | 2017-10-11 | LG_Electronics
LG Electronics | LG330N1C-A5 | mono | 330 | 306.3 | +3/-0 | 3 | 0 |  |  | 33.7 | 9.8 | 40.9 | 10.45 | -0.37% | -0.27% |  |  | 20 | [11 empty] | 1000 | 2017-10-02 | LG_Electronics
LG Electronics | LG335N1C-A5 | mono | 335 | 311.1 | +3/-0 | 3 | 0 |  |  | 34.1 | 9.83 | 41 | 10.49 | -0.37% | -0.27% |  |  | 20 | [11 empty] | 1000 | 2017-10-02 | LG_Electronics
LG Electronics | LG350Q1C-A5 | mono | 350 | 328 | +3/-0 | 3 | 0 |  |  | 36.4 | 9.62 | 43.5 | 10.6 | -0.3% | -0.24% |  |  | 20 | [11 empty] | 1000 | 2017-10-02 | LG_Electronics
LG Electronics | LG355Q1C-A5 | mono | 355 | 332.8 | +3/-0 | 3 | 0 |  |  | 36.3 | 9.79 | 42.7 | 10.78 | -0.3% | -0.24% |  |  | 20 | [11 empty] | 1000 | 2017-10-11 | LG_Electronics
LG Electronics | LG360Q1C-A5 | mono | 360 | 337.6 | +3/-0 | 3 | 0 |  |  | 36.5 | 9.87 | 42.7 | 10.79 | -0.3% | -0.24% |  |  | 20 | [11 empty] | 1000 | 2017-10-11 | LG_Electronics
LG Electronics | LG365Q1C-A5 | mono | 365 | 342.4 | +3/-0 | 3 | 0 |  |  | 36.7 | 9.95 | 42.8 | 10.8 | -0.3% | -0.24% |  |  | 20 | [11 empty] | 1000 | 2017-10-02 | LG_Electronics
LG Electronics | LG355S2W-A5 | mono | 355 | 321.9 | +3/-0 | 3 | 0 |  |  | 37.4 | 9.5 | 46.4 | 10.07 | -0.41% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2017-10-11 | LG_Electronics
LG Electronics | LG360S2W-A5 | mono | 360 | 326.6 | +3/-0 | 3 | 0 |  |  | 37.7 | 9.56 | 46.6 | 10.12 | -0.41% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2017-10-11 | LG_Electronics
LG Electronics | LG390N2W-A5 | mono | 390 | 358.9 | +3/-0 | 3 | 0 |  |  | 39.8 | 9.81 | 49.1 | 10.39 | -0.36% | -0.26% |  |  | 20 |  |  |  |  | 79.69 | 40.31 | 1.57 |  | 47.8 |  |  | 1500 | 2018-11-09 | LG_Electronics
LG Electronics | LG395N2W-A5 | mono | 395 | 363.7 | +3/-0 | 3 | 0 |  | 19.1 | 40.2 | 9.83 | 49.2 | 10.43 | -0.36% | -0.26% |  |  | 20 |  |  |  |  | 79.69 | 40.31 | 1.57 |  | 47.8 |  |  | 1500 | 2017-08-18 | LG_Electronics
LG Electronics | LG400N2W-A5 | mono | 400 | 368.4 | +3/-0 | 3 | 0 |  | 19.3 | 40.6 | 9.86 | 49.3 | 10.47 | -0.36% | -0.26% |  |  | 20 |  |  |  |  | 79.69 | 40.31 | 1.57 |  | 47.8 |  |  | 1500 | 2018-11-09 | LG_Electronics
LG Electronics | LG405N2W-A5 | mono | 405 | 373.2 | +3/-0 | 3 | 0 |  | 19.5 | 40.5 | 9.89 | 41 | 10.51 | -0.36% | -0.26% |  |  | 20 |  |  |  |  | 79.69 | 40.31 | 1.57 |  | 47.8 |  |  | 1500 | 2018-11-09 | LG_Electronics
LG Electronics | LG320E1K-A5 @ 208 | mono | 320 | 294.7 | +3/-0 | 3 | 0 | [6 empty] | -0.37% | -0.27% | [15 empty] | 2018-07-23 | LG_Electronics |  | Yes | 290 | 280 | 208 | 1.35 | 96.5 | 11 | 20 | 208 | 1
LG Electronics | LG320E1K-A5 @ 240 | mono | 320 | 294.7 | +3/-0 | 3 | 0 | [6 empty] | -0.37% | -0.27% | [15 empty] | 2018-07-23 | LG_Electronics |  | Yes | 290 | 280 | 240 | 1.17 | 97 | 13 | 20 | 240 | 1
LG Electronics | LG330E1C-A5 @ 208 | mono | 330 | 306 | +3/-0 | 3 | 0 | [6 empty] | -0.37% | -0.27% | [15 empty] | 2017-01-02 | LG_Electronics |  | Yes | 290 | 280 | 208 | 1.35 | 96.5 | 11 | 20 | 208 | 1
LG Electronics | LG330E1C-A5 @ 240 | mono | 330 | 306 | +3/-0 | 3 | 0 | [6 empty] | -0.37% | -0.27% | [15 empty] | 2017-01-02 | LG_Electronics |  | Yes | 290 | 280 | 240 | 1.17 | 97 | 13 | 20 | 240 | 1
Lightway | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Lightway_Solar
Lightway | LW230(29) P1650 X 990 | poly | 230 |  | +5/0 | +5 | 0 |  |  | 29.2 | 7.87 | 36.6 | 8.38 | -0.441% | -0.334% |  |  | 15 | [11 empty] | Check | 2013-12-20 | Lightway_Solar
Lightway | LW235(29) P1640 X 990 | poly | 235 |  | +5/0 | +5 | 0 |  |  | 29.5 | 7.98 | 37.3 | 8.45 | -0.4204% | -0.3215% |  |  | 15 | [11 empty] | Check | 2014-01-02 | Lightway_Solar
Lightway | LW240(29) P1640 X 990 | poly | 240 |  | +5/0 | +5 | 0 |  |  | 29.65 | 8.11 | 37.4 | 8.56 | -0.4204% | -0.3215% |  |  | 15 | [11 empty] | Check | 2014-01-02 | Lightway_Solar
Lightway | LW245(29) P1640 X 990 | poly | 245 |  | +5/0 | +5 | 0 |  |  | 29.8 | 8.24 | 37.5 | 8.69 | -0.4204% | -0.3215% |  |  | 15 | [11 empty] | Check | 2014-01-02 | Lightway_Solar
Lightway | LW250(29) P1640 X 990 | poly | 250 |  | +5/0 | +5 | 0 |  |  | 29.95 | 8.36 | 37.8 | 8.78 | -0.4204% | -0.3215% |  |  | 15 | [11 empty] | Check | 2014-01-02 | Lightway_Solar
Lightway | LW255(29) P1640 X 990 | poly | 255 |  | +5/0 | +5 | 0 |  |  | 30.1 | 8.48 | 37.88 | 8.9 | -0.4204% | -0.3215% |  |  | 15 | [11 empty] | Check | 2014-01-02 | Lightway_Solar
Lightway | LW260(29) P1640 X 990 | poly | 260 |  | +5/0 | +5 | 0 |  |  | 30.25 | 8.61 | 37.95 | 9.06 | -0.4204% | -0.3215% |  |  | 15 | [11 empty] | Check | 2014-01-02 | Lightway_Solar
Lightway | LW6P60-260 | poly | 260 |  | +5/0 | +5 | 0 |  |  | 30.25 | 8.61 | 37.95 | 9.06 | -0.41% | -0.305% |  |  | 15 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.8 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6P60-265 | poly | 265 |  | +5/0 | +5 | 0 |  |  | 30.4 | 8.73 | 38.22 | 9.1 | -0.41% | -0.305% |  |  | 15 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.8 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6P60-270 | poly | 270 |  | +5/0 | +5 | 0 |  |  | 30.52 | 8.86 | 38.4 | 9.21 | -0.41% | -0.305% |  |  | 15 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.8 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6P60-275 | poly | 275 |  | +5/0 | +5 | 0 |  |  | 30.63 | 8.99 | 38.59 | 9.32 | -0.41% | -0.305% |  |  | 15 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.8 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6P60-280 | poly | 380 |  | +5/0 | +5 | 0 |  |  | 30.8 | 9.1 | 38.76 | 9.43 | -0.41% | -0.305% |  |  | 15 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.8 |  |  | 1000 | 2018-03-09 | Lightway_Solar
Lightway | LW6P72-310 | poly | 310 |  | +5/0 | +5 | 0 |  |  | 36.54 | 8.51 | 45.56 | 8.85 | -0.41% | -0.305% |  |  | 15 |  |  |  |  | 77.17 | 39 | 1.57 |  | 47.4 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6P72-315 | poly | 315 |  | +5/0 | +5 | 0 |  |  | 36.81 | 8.57 | 45.79 | 8.92 | -0.41% | -0.305% |  |  | 15 |  |  |  |  | 77.17 | 39 | 1.57 |  | 47.4 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6P72-320 | poly | 320 |  | +5/0 | +5 | 0 |  |  | 36.96 | 8.67 | 45.88 | 9.03 | -0.41% | -0.305% |  |  | 15 |  |  |  |  | 77.17 | 39 | 1.57 |  | 47.4 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6P72-325 | poly | 325 |  | +5/0 | +5 | 0 |  |  | 37.19 | 8.75 | 45.97 | 9.13 | -0.41% | -0.305% |  |  | 15 |  |  |  |  | 77.17 | 39 | 1.57 |  | 47.4 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6P72-330 | poly | 330 |  | +5/0 | +5 | 0 |  |  | 37.38 | 8.84 | 46.06 | 9.23 | -0.41% | -0.305% |  |  | 15 |  |  |  |  | 77.17 | 39 | 1.57 |  | 47.4 |  |  | 1000 | 2018-03-09 | Lightway_Solar
Lightway | LW6M60-270 | mono | 270 |  | +5/0 | +5 | 0 |  |  | 31.11 | 8.68 | 38.41 | 9.17 | -0.41% | -0.33% |  |  | 15 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.8 |  |  | 1000 | 2018-03-09 | Lightway_Solar
Lightway | LW6M60-275 | mono | 275 |  | +5/0 | +5 | 0 |  |  | 31.29 | 8.79 | 38.58 | 9.27 | -0.41% | -0.33% |  |  | 15 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.8 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6M60-280 | mono | 280 |  | +5/0 | +5 | 0 |  |  | 31.47 | 8.9 | 38.75 | 9.37 | -0.41% | -0.33% |  |  | 15 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.8 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6M60-285 | mono | 285 |  | +5/0 | +5 | 0 |  |  | 31.64 | 9.01 | 38.92 | 9.47 | -0.41% | -0.33% |  |  | 15 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.8 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6M60-290 | mono | 290 |  | +5/0 | +5 | 0 |  |  | 31.8 | 9.12 | 38.11 | 9.56 | -0.41% | -0.33% |  |  | 15 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.8 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6M60-295 | mono | 295 |  | +5/0 | +5 | 0 |  |  | 31.97 | 9.23 | 39.29 | 9.65 | -0.41% | -0.33% |  |  | 15 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.8 |  |  | 1000 | 2018-03-09 | Lightway_Solar
Lightway | LW6M60-300 | mono | 300 |  | +5/0 | +5 | 0 |  |  | 32.13 | 9.34 | 39.47 | 9.74 | -0.41% | -0.33% |  |  | 15 |  |  |  |  | 64.96 | 39 | 1.38 |  | 40.8 |  |  | 1000 | 2018-03-09 | Lightway_Solar
Lightway | LW6M72-320 | mono | 320 |  | +5/0 | +5 | 0 |  |  | 37.17 | 8.61 | 46.08 | 9.12 | -0.41% | -0.33% |  |  | 15 |  |  |  |  | 77.17 | 39 | 1.57 |  | 47.4 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6M72-325 | mono | 325 |  | +5/0 | +5 | 0 |  |  | 37.28 | 8.72 | 46.21 | 9.21 | -0.41% | -0.33% |  |  | 15 |  |  |  |  | 77.17 | 39 | 1.57 |  | 47.4 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6M72-330 | mono | 330 |  | +5/0 | +5 | 0 |  |  | 37.55 | 8.79 | 46.38 | 9.29 | -0.41% | -0.33% |  |  | 15 |  |  |  |  | 77.17 | 39 | 1.57 |  | 47.4 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6M72-335 | mono | 335 |  | +5/0 | +5 | 0 |  |  | 37.82 | 8.86 | 46.55 | 9.37 | -0.41% | -0.33% |  |  | 15 |  |  |  |  | 77.17 | 39 | 1.57 |  | 47.4 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6M72-340 | mono | 340 |  | +5/0 | +5 | 0 |  |  | 37.99 | 8.95 | 46.72 | 9.45 | -0.41% | -0.33% |  |  | 15 |  |  |  |  | 77.17 | 39 | 1.57 |  | 47.4 |  |  | 1000 | 2017-10-11 | Lightway_Solar
Lightway | LW6M72-345 | mono | 345 |  | +5/0 | +5 | 0 |  |  | 38.21 | 9.03 | 46.89 | 9.53 | -0.41% | -0.33% |  |  | 15 |  |  |  |  | 77.17 | 39 | 1.57 |  | 47.4 |  |  | 1000 | 2018-03-09 | Lightway_Solar
Lightway | LW6M72-350 | mono | 350 |  | +5/0 | +5 | 0 |  |  | 38.38 | 9.12 | 47.06 | 9.61 | -0.41% | -0.33% |  |  | 15 |  |  |  |  | 77.17 | 39 | 1.57 |  | 47.4 |  |  | 1000 | 2018-03-09 | Lightway_Solar
Lightway | LW6M72-355 | mono | 355 |  | +5/0 | +5 | 0 |  |  | 38.63 | 9.19 | 47.23 | 9.68 | -0.41% | -0.33% |  |  | 15 |  |  |  |  | 77.17 | 39 | 1.57 |  | 47.4 |  |  | 1000 | 2018-03-09 | Lightway_Solar
Lightway | LW6M72-360 | mono | 360 |  | +5/0 | +5 | 0 |  |  | 38.84 | 9.27 | 47.4 | 9.75 | -0.41% | -0.33% |  |  | 15 |  |  |  |  | 77.17 | 39 | 1.57 |  | 47.4 |  |  | 1000 | 2018-03-09 | Lightway_Solar
Lightway | LW6P72b-290 | poly | 290 |  | +1.5/-0 | 1.5 | 0 |  |  | 35.81 | 8.11 | 44.81 | 8.49 | -0.42% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Lightway_Solar
Lightway | LW6P72b-295 | poly | 295 |  | +1.5/-0 | 1.5 | 0 |  |  | 35.99 | 8.21 | 44.91 | 8.59 | -0.42% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Lightway_Solar
Lightway | LW6P72b-300 | poly | 300 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.15 | 8.31 | 45.08 | 8.68 | -0.42% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Lightway_Solar
Lightway | LW6P72b-305 | poly | 305 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.34 | 8.42 | 45.31 | 8.76 | -0.42% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Lightway_Solar
Lightway | LW6P72b-310 | poly | 310 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.54 | 8.51 | 45.56 | 8.85 | -0.42% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Lightway_Solar
Lightway | LW6P72b-315 | poly | 315 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.81 | 8.57 | 45.79 | 8.92 | -0.42% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Lightway_Solar
Lumos | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Lumos
Lumos | LS190-72M | mono | 190 | 167.3926 | +/-3 | 3 | -3 | 13.8266 | 14.8828 | 36.2 | 5.25 | 45 | 5.5 | -0.5% | -0.37% | 0.06 | 47.6 | 15 | yes | MC4 | black/silver | white | 62.2047 | 31.811 | 1.378 | 13.7416 | 34.4 | 5 |  | Check |  | Lumos
Lumos | LS190-72M-J | mono | 190 | 170.7862 | +/-3 | 3 | -3 | 13.8266 | 14.8828 | 36.6 | 5.19 | 45.2 | 5.56 | -0.4384% | -0.3931% | 0.0775 | 46.9 | 10 | yes | MC4 | black/silver | white | 62.2047 | 31.811 | 1.378 | 13.7416 | 31.9 | 5 |  | Check |  | Lumos
Lumos | LS195-72M-B | mono | 195 | 169 | +/-3 | 3 | -3 | 14.1904 | 15.2745 | 36.8 | 5.3 | 45.3 | 5.6 | -0.601% | -0.45% | 0.048 | 46.2 | 10 | yes | MC4 | black/silver | white | 62.2047 | 31.811 | 1.378 | 13.7416 | 33.0693 | 10 |  | Check |  | Lumos
Lumos | LS195-72M-J | mono | 195 | 175.4057 | +/-3 | 3 | -3 | 14.1904 | 15.2745 | 36.8 | 5.3 | 45.4 | 5.67 | -0.4384% | -0.3931% | 0.0775 | 46.9 | 10 | yes | MC4 | black/silver | white | 62.2047 | 31.811 | 1.378 | 13.7416 | 31.9 | 5 |  | Check |  | Lumos
Lumos | LS200-72M-B | mono | 200 | 173.5 | +/-3 | 3 | -3 | 14.5543 | 15.6661 | 37 | 5.4 | 45.5 | 5.86 | -0.601% | -0.45% | 0.048 | 46.2 | 10 | yes | MC4 | black/silver | white | 62.2047 | 31.811 | 1.378 | 13.7416 | 33.0693 | 10 |  | Check |  | Lumos
Lumos | LS200-72M-J | mono | 200 | 180.0316 | +/-3 | 3 | -3 | 14.5543 | 15.6661 | 36.9 | 5.42 | 45.6 | 5.8 | -0.4384% | -0.3931% | 0.0775 | 46.9 | 10 | yes | MC4 | black/silver | white | 62.2047 | 31.811 | 1.378 | 13.7416 | 31.9 | 5 |  | Check |  | Lumos
Lumos | LS205-72M-J | mono | 205 | 184.6639 | +/-3 | 3 | -3 | 14.9182 | 16.0578 | 37.2 | 5.52 | 45.9 | 5.9 | -0.4384% | -0.3931% | 0.0775 | 46.9 | 10 | yes | MC4 | black/silver | white | 62.2047 | 31.811 | 1.378 | 13.7416 | 31.9 | 5 |  | Check |  | Lumos
Lumos | LS235PB/C | poly | 235 | 210.0226 | +/-3 | 3 | -3 | 13.848 | 14.9058 | 29.4 | 8 | 37.1 | 8.5 | -0.441% | -0.339% | 0.08 | 47.9 | 15 | yes | tyco | black/silver | white | 64.0551 | 38.1496 | 1.9685 | 16.97 | 43.6515 | 5 |  | Check |  | Lumos
Lumos | LS240-60M | mono | 240 | 217.2867 | +/-3 | 3 | -3 | 13.7329 | 14.782 | 29.8 | 8.06 | 37 | 8.62 | -0.423% | -0.307% | 0.039 | 46.2 | 15 | yes | MC4 | black/silver | white | 64.5669 | 38.9764 | 1.9685 | 17.4763 | 43.65 | 5 |  | Check |  | Lumos
Lumos | LS240-60M-B | mono | 240 | 215.5 | +/-3 | 3 | -3 | 13.7052 | 14.7522 | 30.2 | 7.95 | 37.2 | 8.33 | -0.478% | -0.366% | 0.038 | 45.2 | 15 | yes | MC4 | black/silver | white | 64.5669 | 39.0551 | 1.7717 | 17.5116 | 44.0925 | 10 |  | Check |  | Lumos
Lumos | LS240-60M-BB | mono | 240 | 209.1087 | +/-3 | 3 | -3 | 13.7329 | 14.782 | 29.8 | 8.06 | 37 | 8.62 | -0.54% | -0.39% | 0.05 | 47.6 | 15 | yes | MC4 | black/silver | black | 64.5669 | 38.9764 | 1.9685 | 17.4763 | 43.65 | 5 |  | Check |  | Lumos
Lumos | LS240-60P-B | poly | 240 | 211.1 | +/-3 | 3 | -3 | 13.7052 | 14.7522 | 35.2 | 7.95 | 44.8 | 8.33 | -0.516% | -0.388% | 0.057 | 47.1 | 15 | yes | MC4 | black/silver | white | 64.5669 | 39.0551 | 1.7717 | 17.5116 | 44.0925 | 10 |  | Check |  | Lumos
Lumos | LS240-60P-J | poly | 240 | 214.6037 | +/-3 | 3 | -3 | 13.6221 | 14.6628 | 30 | 8.01 | 37.2 | 8.56 | -0.4634% | -0.3525% | 0.0738 | 46.6 | 15 | yes | MC4 | black/silver | white | 64.9606 | 39.0551 | 1.7717 | 17.6184 | 41.9 | 5 |  | Check |  | Lumos
Lumos | LS240PB/C | poly | 240 | 214.6213 | +/-3 | 3 | -3 | 14.1426 | 15.223 | 29.8 | 8.1 | 37.3 | 8.6 | -0.441% | -0.339% | 0.08 | 47.9 | 15 | yes | tyco | black/silver | white | 64.0551 | 38.1496 | 1.9685 | 16.97 | 43.6515 | 5 |  | Check |  | Lumos
Lumos | LS245-60M | mono | 245 | 221.9297 | +/-3 | 3 | -3 | 14.019 | 15.0899 | 30 | 8.17 | 37.2 | 8.69 | -0.423% | -0.307% | 0.039 | 46.2 | 15 | yes | MC4 | black/silver | white | 64.5669 | 38.9764 | 1.9685 | 17.4763 | 43.65 | 5 |  | Check |  | Lumos
Lumos | LS245-60M-A1 | mono | 245 | 220.9 | +/-3 | 3 | -3 | 13.6852 | 14.7306 | 30.03 | 8.18 | 37.26 | 8.71 | -0.443% | -0.315% | 0.016 | 46 | 15 | yes | MC4 | black/silver | white | 66.1417 | 38.9764 | 1.5748 | 17.9025 | 53.9 | 5 |  | Check |  | Lumos
Lumos | LS245-60M-BB | mono | 245 | 213.6213 | +/-3 | 3 | -3 | 14.019 | 15.0899 | 30 | 8.17 | 37.2 | 8.69 | -0.54% | -0.39% | 0.05 | 47.6 | 15 | yes | MC4 | black/silver | black | 64.5669 | 38.9764 | 1.9685 | 17.4763 | 43.65 | 5 |  | Check |  | Lumos
Lumos | LS245-60M-J | mono | 245 | 220.7798 | +/-3 | 3 | -3 | 13.9059 | 14.9682 | 30.4 | 8.06 | 37.4 | 8.58 | -0.4351% | -0.3037% | 0.04433 | 46.6 | 15 | yes | MC4 | black/silver | white | 64.9606 | 39.0551 | 1.7717 | 17.6184 | 41.9 | 5 |  | Check |  | Lumos
Lumos | LS245-60P-J | poly | 245 | 219.2027 | +/-3 | 3 | -3 | 13.9059 | 14.9682 | 30.2 | 8.12 | 37.4 | 8.69 | -0.4634% | -0.3525% | 0.0738 | 46.6 | 15 | yes | MC4 | black/silver | white | 64.9606 | 39.0551 | 1.7717 | 17.6184 | 41.9 | 5 |  | Check |  | Lumos
Lumos | LS245PB/C | poly | 245 | 219.2253 | +/-3 | 3 | -3 | 14.4373 | 15.5401 | 29.9 | 8.2 | 37.4 | 8.7 | -0.441% | -0.339% | 0.08 | 47.9 | 15 | yes | tyco | black/silver | white | 64.0551 | 38.1496 | 1.9685 | 16.97 | 43.6515 | 5 |  | Check |  | Lumos
Lumos | LS250-60M | mono | 250 | 226.5774 | +/-3 | 3 | -3 | 14.3051 | 15.3979 | 30.1 | 8.31 | 37.3 | 8.78 | -0.423% | -0.307% | 0.039 | 46.2 | 15 | yes | MC4 | black/silver | white | 64.5669 | 38.9764 | 1.9685 | 17.4763 | 43.65 | 5 |  | Check |  | Lumos
Lumos | LS250-60M-A1 | mono | 250 | 225.6 | +/-3 | 3 | -3 | 13.9645 | 15.0313 | 30.3 | 8.22 | 37.4 | 8.72 | -0.443% | -0.315% | 0.016 | 46 | 15 | yes | MC4 | black/silver | white | 66.1417 | 38.9764 | 1.5748 | 17.9025 | 53.9 | 5 |  | Check |  | Lumos
Lumos | LS250-60M-B | mono | 250 | 224.8 | +/-3 | 3 | -3 | 14.2763 | 15.3668 | 30.4 | 8.22 | 37.5 | 8.89 | -0.478% | -0.366% | 0.038 | 45.2 | 15 | yes | MC4 | black/silver | white | 64.5669 | 39.0551 | 1.7717 | 17.5116 | 44.0925 | 10 |  | Check |  | Lumos
Lumos | LS250-60M-J | mono | 250 | 224.696 | +/-3 | 3 | -3 | 14.1897 | 15.2737 | 30.6 | 8.17 | 37.6 | 8.7 | -0.4396% | -0.3598% | 0.0714 | 47 | 15 | yes | MC4 | black/silver | white | 64.9606 | 39.0551 | 1.7717 | 17.6184 | 41.9 | 5 |  | Check |  | Lumos
Lumos | LS280-72P-B | poly | 280 | 246.6 | +/-3 | 3 | -3 | 13.4063 | 14.4304 | 30.4 | 8.22 | 37.5 | 8.89 | -0.532% | -0.396% | 0.047 | 46.1 | 15 | yes | MC4 | black/silver | white | 77.0079 | 39.0551 | 1.9685 | 20.8858 | 44.0925 | 10 |  | Check |  | Lumos
Lumos | LS285-72P | poly | 285 | 250.6227 | +/-3 | 3 | -3 | 13.6732 | 14.7177 | 35.7 | 7.99 | 44.4 | 8.59 | -0.51% | -0.37% | 0.05 | 47.4 | 15 | yes | MC4 | black/silver | white | 77.0079 | 38.9764 | 1.9685 | 20.8437 | 52.47 | 5 |  | Check |  | Lumos
Lumos | LS285-72P-J | poly | 285 | 254.556 | +/-3 | 3 | -3 | 13.6457 | 14.6881 | 36 | 7.92 | 44.7 | 8.85 | -0.4575% | -0.2743% | 0.0564 | 47.1 | 15 | yes | MC4 | black/silver | white | 77.0079 | 39.0551 | 1.9685 | 20.8858 | 59.5 | 5 |  | Check |  | Lumos
Lumos | LS290-72M-B | mono | 290 | 249.9 | +/-3 | 3 | -3 | 13.885 | 14.9457 | 35.4 | 8.19 | 44.8 | 8.63 | -0.582% | -0.444% | 0.04 | 47.6 | 15 | yes | MC4 | black/silver | white | 77.0079 | 39.0551 | 1.9685 | 20.8858 | 51.8086 | 10 |  | Check |  | Lumos
Lumos | LS290-72M-BB | mono | 290 | 252.4267 | +/-3 | 3 | -3 | 13.9131 | 14.9759 | 35.8 | 8.11 | 44.5 | 8.68 | -0.56% | -0.4% | 0.04 | 47 | 15 | yes | MC4 | black/silver | black | 77.0079 | 38.9764 | 1.9685 | 20.8437 | 52.47 | 5 |  | Check |  | Lumos
Lumos | LS290-72P | poly | 290 | 255.165 | +/-3 | 3 | -3 | 13.9131 | 14.9759 | 35.8 | 8.11 | 44.5 | 8.68 | -0.51% | -0.37% | 0.05 | 47.4 | 15 | yes | MC4 | black/silver | white | 77.0079 | 38.9764 | 1.9685 | 20.8437 | 52.47 | 5 |  | Check |  | Lumos
Lumos | LS290-72P-J | poly | 290 | 259.1506 | +/-3 | 3 | -3 | 13.885 | 14.9457 | 36.4 | 7.97 | 44.9 | 8.89 | -0.4575% | -0.2743% | 0.0564 | 47.1 | 15 | yes | MC4 | black/silver | white | 77.0079 | 39.0551 | 1.9685 | 20.8858 | 59.5 | 5 |  | Check |  | Lumos
Lumos | LS295-72M | mono | 295 | 258.0644 | +/-3 | 3 | -3 | 14.153 | 15.2341 | 35.9 | 8.22 | 44.6 | 8.73 | -0.52% | -0.39% | 0.04 | 48 | 15 | yes | MC4 | black/silver | white | 77.0079 | 38.9764 | 1.9685 | 20.8437 | 52.47 | 5 |  | Check |  | Lumos
Lumos | LS295-72M-A1 | mono | 295 | 264.8 | +/-3 | 3 | -3 | 14.0383 | 15.1107 | 36.4 | 8.1 | 44.77 | 8.67 | -0.434% | -0.312% | 0.026 | 47.5 | 15 | yes | MC4 | black/silver | white | 78.1102 | 38.7402 | 1.5748 | 21.0139 | 57.2 | 5 |  | Check |  | Lumos
Lumos | LS295-72M-BB | mono | 295 | 256.9388 | +/-3 | 3 | -3 | 14.153 | 15.2341 | 35.9 | 8.22 | 44.6 | 8.73 | -0.56% | -0.4% | 0.04 | 47 | 15 | yes | MC4 | black/silver | black | 77.0079 | 38.9764 | 1.9685 | 20.8437 | 52.47 | 5 |  | Check |  | Lumos
Lumos | LS295-72M-J | mono | 295 | 265.5649 | +/-3 | 3 | -3 | 14.1244 | 15.2034 | 37.6 | 7.85 | 46 | 8.59 | -0.4388% | -0.3574% | 0.0731 | 46.7 | 15 | yes | MC4 | black/silver | white | 77.0079 | 39.0551 | 1.9685 | 20.8858 | 59.5 | 5 |  | Check |  | Lumos
Lumos | LS295-72P-J | poly | 295 | 263.7496 | +/-3 | 3 | -3 | 14.1244 | 15.2034 | 36.8 | 8.02 | 45.2 | 8.95 | -0.4575% | -0.2743% | 0.0564 | 47.1 | 15 | yes | MC4 | black/silver | white | 77.0079 | 39.0551 | 1.9685 | 20.8858 | 59.5 | 5 |  | Check |  | Lumos
Lumos | LS300-72M | mono | 300 | 262.5951 | +/-3 | 3 | -3 | 14.3929 | 15.4923 | 36.1 | 8.32 | 44.8 | 8.8 | -0.52% | -0.39% | 0.04 | 48 | 15 | yes | MC4 | black/silver | white | 77.0079 | 38.9764 | 1.9685 | 20.8437 | 52.47 | 5 |  | Check |  | Lumos
Lumos | LS300-72M-A1 | mono | 300 | 269.4 | +/-3 | 3 | -3 | 14.2763 | 15.3668 | 36.55 | 8.2 | 44.96 | 8.77 | -0.434% | -0.312% | 0.026 | 47.5 | 15 | yes | MC4 | black/silver | white | 78.1102 | 38.7402 | 1.5748 | 21.0139 | 57.2 | 5 |  | Check |  | Lumos
Lumos | LS300-72M-B | mono | 300 | 258.8 | +/-3 | 3 | -3 | 14.3638 | 15.4611 | 35.8 | 8.37 | 44.8 | 8.93 | -0.582% | -0.444% | 0.04 | 47.6 | 15 | yes | MC4 | black/silver | white | 77.0079 | 39.0551 | 1.9685 | 20.8858 | 51.8086 | 10 |  | Check |  | Lumos
Lumos | LS300-72M-J | mono | 300 | 270.1918 | +/-3 | 3 | -3 | 14.3638 | 15.4611 | 38 | 7.9 | 46.4 | 8.67 | -0.4388% | -0.3574% | 0.0731 | 46.7 | 15 | yes | MC4 | black/silver | white | 77.0079 | 39.0551 | 1.9685 | 20.8858 | 59.5 | 5 |  | Check |  | Lumos
Lumos | LS305-72M-B | mono | 305 | 263.3 | +/-3 | 3 | -3 | 14.6032 | 15.7188 | 36.1 | 8.47 | 45 | 9.15 | -0.582% | -0.444% | 0.04 | 47.6 | 15 | yes | MC4 | black/silver | white | 77.0079 | 39.0551 | 1.9685 | 20.8858 | 51.8086 | 10 |  | Check |  | Lumos
Lumos | LS305-72M-J | mono | 305 | 274.8229 | +/-3 | 3 | -3 | 14.6032 | 15.7188 | 38.2 | 7.99 | 46.8 | 8.72 | -0.4388% | -0.3574% | 0.0731 | 46.7 | 15 | yes | MC4 | black/silver | white | 77.0079 | 39.0551 | 1.9685 | 20.8858 | 59.5 | 5 |  | Check |  | Lumos
Lumos | LSX180-72M-B/W/C | mono | 180 | 160.9296 | +/-3 | 3 | -3 | 12.4243 | 13.3734 | 35.3 | 4.96 | 44.5 | 5.34 | -0.4651% | -0.345% | 0.0491 | 46.1 | 10 | yes | MC4 | frameless | black/white/clear | 63.3858 | 32.9134 | 0.29528 | 14.4878 | 49.8 | 5 |  | Check |  | Lumos
Lumos | LSX185-72M-B/W/C | mono | 185 | 165.5157 | +/-3 | 3 | -3 | 12.7694 | 13.7448 | 35.4 | 5.09 | 44.6 | 5.4 | -0.4651% | -0.345% | 0.0491 | 46.1 | 10 | yes | MC4 | frameless | black/white/clear | 63.3858 | 32.9134 | 0.29528 | 14.4878 | 49.8 | 5 |  | Check |  | Lumos
Lumos | LSX190-72M-B/W/C | mono | 190 | 170.1081 | +/-3 | 3 | -3 | 13.1145 | 14.1163 | 35.8 | 5.17 | 44.8 | 5.48 | -0.4651% | -0.345% | 0.0491 | 46.1 | 10 | yes | MC4 | frameless | black/white/clear | 63.3858 | 32.9134 | 0.29528 | 14.4878 | 49.8 | 5 |  | Check |  | Lumos
Lumos | LSX195-72M-B/W/C | mono | 195 | 174.7068 | +/-3 | 3 | -3 | 13.4596 | 14.4878 | 36.2 | 5.25 | 45 | 5.5 | -0.4651% | -0.345% | 0.0491 | 46.1 | 10 | yes | MC4 | frameless | black/white/clear | 63.3858 | 32.9134 | 0.29528 | 14.4878 | 49.8 | 5 |  | Check |  | Lumos
Lumos | LSX200-72M-B/W/C | mono | 200 | 179.3117 | +/-3 | 3 | -3 | 13.8047 | 14.8593 | 36.5 | 5.34 | 45.1 | 5.53 | -0.4651% | -0.345% | 0.0491 | 46.1 | 10 | yes | MC4 | frameless | black/white/clear | 63.3858 | 32.9134 | 0.29528 | 14.4878 | 49.8 | 5 |  | Check |  | Lumos
Lumos | LSX235-60M-B/W/C | mono | 235 | 208.7798 | +/-3 | 3 | -3 | 12.8225 | 13.802 | 29.6 | 7.94 | 36.8 | 8.54 | -0.4819% | -0.3519% | 0.0486 | 46.6 | 15 | yes | MC4 | frameless | black/white/clear | 65.5906 | 40.2362 | 0.29528 | 18.3272 | 62.8 | 5 |  | Check |  | Lumos
Lumos | LSX240-60M-B/W/C | mono | 240 | 213.3474 | +/-3 | 3 | -3 | 13.0953 | 14.0957 | 29.8 | 8.06 | 37 | 8.62 | -0.4819% | -0.3519% | 0.0486 | 46.6 | 15 | yes | MC4 | frameless | black/white/clear | 65.5906 | 40.2362 | 0.29528 | 18.3272 | 62.8 | 5 |  | Check |  | Lumos
Lumos | LSX245-60M-B/W/C | mono | 245 | 217.9203 | +/-3 | 3 | -3 | 13.3681 | 14.3893 | 30 | 8.17 | 37.2 | 8.69 | -0.4819% | -0.3519% | 0.0486 | 46.6 | 15 | yes | MC4 | frameless | black/white/clear | 65.5906 | 40.2362 | 0.29528 | 18.3272 | 62.8 | 5 |  | Check |  | Lumos
Lumos | LSX250-60M-B/W/C | mono | 250 | 222.4984 | +/-3 | 3 | -3 | 13.6409 | 14.683 | 30.1 | 8.31 | 37.3 | 8.78 | -0.4819% | -0.3519% | 0.0486 | 46.6 | 15 | yes | MC4 | frameless | black/white/clear | 65.5906 | 40.2362 | 0.29528 | 18.3272 | 62.8 | 5 |  | Check |  | Lumos
Lumos | LSX255-60M-B/C | mono | 255 |  | +3/-0 | 3 | 0 |  |  | 31.19 | 8.18 | 38.36 | 8.66 | -0.48% | -0.47% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Lumos
Lumos | LSX260-60M-B/C | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 31.2 | 8.3 | 38.53 | 8.75 | -0.48% | -0.47% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Lumos
Lumos | GSX260-60M-C | mono | 260 |  | +5/-0 | 5 | 0 |  |  | 30.8 | 8.49 | 37.8 | 9.04 | -0.38% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Lumos
Lumos | GSX265-60M-C | mono | 250 |  | +5/-0 | 5 | 0 |  |  | 31 | 8.55 | 38 | 9.11 | -0.38% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Lumos
Lumos | GSX270-60M-C | mono | 250 |  | +5/-0 | 5 | 0 |  |  | 31.2 | 8.65 | 38.2 | 9.22 | -0.38% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Lumos
MAGE Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | MAGE_Solar
MAGE Solar | 175/5ME |  | 175 |  | +5/-0 | 5 | 0 |  |  | 35.3 | 4.95 | 43.8 | 5.3 | -0.44% | -0.34% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | MAGE_Solar
MAGE Solar | 180/5MH |  | 180 |  | +5/-0 | 5 | 0 |  |  | 36.02 | 5 | 44.8 | 5.3 | -0.37% | -0.34% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | MAGE_Solar
MAGE Solar | 180/5MJ |  | 180 |  | +5/-0 | 5 | 0 |  |  | 36 | 5 | 44.8 | 5.3 | -0.48% | -0.347% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | MAGE_Solar
MAGE Solar | 185/5MH |  | 185 |  | +5/-0 | 5 | 0 |  |  | 36.42 | 5.08 | 45 | 5.4 | -0.37% | -0.34% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | MAGE_Solar
MAGE Solar | 185/5MI |  | 185 |  | +5/-0 | 5 | 0 |  |  | 36.4 | 5.09 | 45 | 5.43 | -0.47% | -0.35% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | MAGE_Solar
MAGE Solar | 225/6PI |  | 225 |  | +5/-0 | 5 | 0 |  |  | 29.5 | 7.63 | 35.4 | 8.55 | -0.48% | -0.33% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | MAGE_Solar
MAGE Solar | 225/6PJ |  | 225 |  | +5/-0 | 5 | 0 |  |  | 30.1 | 7.48 | 36.8 | 8.2 | -0.48% | -0.347% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | MAGE_Solar
MAGE Solar | 230/6PJ |  | 230 |  | +5/-0 | 5 | 0 |  |  | 30.2 | 7.62 | 36.9 | 8.31 | -0.48% | -0.347% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | MAGE_Solar
MAGE Solar | ME 170/5ME |  | 170 |  | +3/-0 | 3 | 0 |  |  | 35 | 4.85 | 43.4 | 5.2 | -0.44% | -0.34% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | MAGE_Solar
MAGE Solar | MH 175/5MH |  | 175 |  | +5/-0 | 5 | 0 |  |  | 35.87 | 4.88 | 44.4 | 5.21 | -0.37% | -0.34% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | MAGE_Solar
MAGE Solar | MI 180/5MI |  | 180 |  | +5/-0 | 5 | 0 |  |  | 36 | 5 | 43.2 | 5.6 | -0.47% | -0.35% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | MAGE_Solar
MAGE Solar | MJ 175/5MJ |  | 175 |  | +5/-0 | 5 | 0 |  |  | 35.3 | 4.96 | 44.2 | 5.2 | -0.48% | -0.347% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | MAGE_Solar
MAGE Solar | PH 220/6PH |  | 220 |  | +5/-0 | 5 | 0 |  |  | 29.4 | 7.63 | 36.4 | 8.27 | -0.37% | -0.34% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | MAGE_Solar
MAGE Solar | PI 220/6PI |  | 220 |  | +5/-0 | 5 | 0 |  |  | 29.5 | 7.46 | 35.4 | 8.36 | -0.48% | -0.33% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | MAGE_Solar
MAGE Solar | PJ 220/6PJ |  | 220 |  | +5/-0 | 5 | 0 |  |  | 30 | 7.34 | 36.6 | 8.1 | -0.48% | -0.347% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | MAGE_Solar
MAGE Solar | Powertec Plus 180/5ME | mono | 180 | 164.1 | +3/-0 | 3 | -0 | 13.1003 | 14.3 | 35.6 | 5.05 | 44.1 | 5.4 | -0.44% | -0.34% | 0.034 | 48 | 10 | no | tyco | silver | white | 62.2 | 31.81 | 1.97 | 13.7402 | 34.17 | 10 |  | Check |  | MAGE_Solar
MAGE Solar | Powertec Plus 185/5MH | mono | 185 | 165.3 | +3/-0 | 3 | -0 | 13.4642 | 14.88 | 36.42 | 5.21 | 45 | 5.4 | -0.37% | -0.34% | 0.09 | 48 | 15 | no | tyco | silver | white | 62.2 | 31.81 | 1.77 | 13.7402 | 34.2 | 10 |  | Check |  | MAGE_Solar
MAGE Solar | Powertec Plus 185/5MH-US | mono | 185 | 165.3 | +3/-0 | 3 | -0 | 13.4642 | 15.27 | 36.5 | 5.21 | 45.2 | 5.53 | -0.37% | -0.34% | 0.09 | 48 | 15 | yes | tyco | silver | white | 62.2 | 31.81 | 1.77 | 13.7402 | 34.2 | 10 |  | Check |  | MAGE_Solar
MAGE Solar | Powertec Plus 185/5MJB | mono | 185 | 163 | +3/-0 | 3 | -0 | 13.4642 | 14.69 | 36.27 | 5.1 | 45 | 5.5 | -0.48% | -0.347% | 0.055 | 47 | 15 | yes | MC4 | silver | white | 62.2 | 31.81 | 1.57 | 13.7402 | 34.17 | 10 |  | Check |  | MAGE_Solar
MAGE Solar | Powertec Plus 190/5MH | mono | 190 | 170.8 | +3/-0 | 3 | -0 | 13.8281 | 15.27 | 36.5 | 5.21 | 45.2 | 5.53 | -0.37% | -0.34% | 0.09 | 48 | 15 | no | tyco | silver | white | 62.2 | 31.81 | 1.77 | 13.7402 | 34.2 | 10 |  | Check |  | MAGE_Solar
MAGE Solar | Powertec Plus 190/5MI | mono | 190 | 163.9 | +3/-0 | 3 | -0 | 13.8281 | 15.27 | 36.6 | 5.2 | 45.2 | 5.56 | -0.47% | -0.35% | 0.05 | 48 | 10 | yes | tyco | silver | white | 62.2 | 31.81 | 1.77 | 13.7402 | 34.2 | 10 |  | Check |  | MAGE_Solar
MAGE Solar | Powertec Plus 220/6PH | poly | 220 | 198.2 | +2/-0 | 2 | 0 | 12.653 | 13.86 | 29.2 | 7.54 | 36.3 | 7.97 | -0.37% | -0.34% | 0.09 | 48 | 15 | no | tyco | silver | white | 64.1 | 39.06 | 1.77 | 17.3871 | 39.68 | 10 |  | Check |  | MAGE_Solar
MAGE Solar | Powertec Plus 230/6PH | poly | 230 | 206.2 | +2/-0 | 2 | 0 | 13.2282 | 14.99 | 29.38 | 7.85 | 36.4 | 8.3 | -0.37% | -0.34% | 0.09 | 48 | 15 | no | tyco | silver | white | 64.1 | 39.06 | 1.77 | 17.3871 | 39.68 | 10 |  | Check |  | MAGE_Solar
MAGE Solar | Powertec Plus 230/6PH-US | poly | 230 | 206.2 | +2/-0 | 2 | 0 | 13.1645 | 14.88 | 29.38 | 7.85 | 36.4 | 8.3 | -0.37% | -0.34% | 0.09 | 48 | 15 | yes | tyco | silver | white | 64.41 | 39.06 | 1.77 | 17.4712 | 39.68 | 10 |  | Check |  | MAGE_Solar
MAGE Solar | Powertec Plus 230/6PI | poly | 230 | 205.4 | +2/-0 | 2 | 0 | 13.0531 | 14.36 | 30 | 7.67 | 36 | 8.59 | -0.48% | -0.33% | 0.04 | 45 | 15 | yes | tyco | silver | white | 64.96 | 39.06 | 1.97 | 17.6204 | 43 | 10 |  | Check |  | MAGE_Solar
MAGE Solar | Powertec Plus 240/6MF | mono | 240 | 210.8 | +2/-0 | 2 | 0 | 13.6206 | 14.82 | 30.4 | 7.8 | 36.4 | 8.7 | -0.51% | -0.34% | 0.017 | 50 | 15 | yes | tyco | silver | white | 64.96 | 39.06 | 1.97 | 17.6204 | 43 | 10 |  | Check |  | MAGE_Solar
MAGE Solar | Powertec Plus 245/6MNBS | mono | 245 |  | +5/-0 | 5 | 0 |  | 15.02 | 30.7 | 8 | 37.75 | 8.49 | -0.43% | -0.32% |  |  | 15 | [11 empty] | Check |  | MAGE_Solar
MAGE Solar | Powertec Plus 255/6MNBS |  | 255 |  | +5/-0 | 5 | 0 |  |  | 49.3 | 5.18 | 59.3 | 5.7 | -0.44% | -0.38% |  |  | 15 | [11 empty] | Check | 2015-11-30 | MAGE_Solar
MAGE Solar | Powertec Plus 260/6MNBS |  | 260 |  | +5/-0 | 5 | 0 |  |  | 49.4 | 5.27 | 59.4 | 5.8 | -0.44% | -0.38% |  |  | 15 | [11 empty] | Check | 2015-11-30 | MAGE_Solar
MAGE Solar | Powertec Plus 265/6MNBS |  | 265 |  | +5/-0 | 5 | 0 |  |  | 49.5 | 5.36 | 59.6 | 5.9 | -0.44% | -0.38% |  |  | 15 | [11 empty] | Check | 2015-11-30 | MAGE_Solar
MAGE Solar | Powertec Plus 270/6MNBS |  | 270 |  | +5/-0 | 5 | 0 |  |  | 49.6 | 5.45 | 59.9 | 6 | -0.44% | -0.38% |  |  | 15 | [11 empty] | Check | 2015-11-30 | MAGE_Solar
MAGE Solar | Powertec Plus 250/6MNCS | mono | 250 |  | +5/-0 | 5 | 0 |  | 15.62 | 30 | 8.35 | 37.5 | 8.85 | -0.43% | -0.32% |  |  | 15 | [11 empty] | Check |  | MAGE_Solar
MAGE Solar | Powertec Plus 270/6MNCS | mono | 260 |  | +5/-0 | 5 | 0 |  |  | 49.5 | 5.45 | 5.83 | 61 | -0.45% | -0.33% |  |  | 10 | [11 empty] | Check | 2015-11-30 | MAGE_Solar
MAGE Solar | Powertec Plus 275/MNCS | mono | 275 |  | +5/-0 | 5 | 0 |  |  | 49.7 | 5.53 | 5.87 | 61.2 | -0.45% | -0.33% |  |  | 10 | [11 empty] | Check | 2015-11-30 | MAGE_Solar
MAGE Solar | Powertec Plus 280/MNCS | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 50.4 | 5.56 | 5.91 | 61.6 | -0.45% | -0.33% |  |  | 10 | [11 empty] | Check | 2015-11-30 | MAGE_Solar
MAGE Solar | Powertec Plus 235/6PL | poly | 235 |  | +5/-0 | 5 | 0 |  | 14.4 | 29.69 | 7.92 | 37.03 | 8.55 | -0.43% | -0.32% |  |  | 15 | [11 empty] | Check | 2012-05-24 | MAGE_Solar
MAGE Solar | Powertec Plus 285/6PL | poly | 285 |  | +5/-0 | 5 | 0 |  |  | 36.26 | 7.86 | 44.67 | 8.48 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check |  | MAGE_Solar
MAGE Solar | Powertec Plus 290/6PL | poly | 290 |  | +5/-0 | 5 | 0 |  |  | 35.86 | 8.09 | 44.65 | 8.64 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check |  | MAGE_Solar
MAGE Solar | Powertec Plus 295/6PL | poly | 295 |  | +5/-0 | 5 | 0 |  |  | 37.11 | 7.95 | 44.95 | 8.61 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-03 | MAGE_Solar
MAGE Solar | Powertec Plus 300/6PL | poly | 300 |  | +5/-0 | 5 | 0 |  |  | 37.51 | 8.01 | 45.19 | 8.66 | -0.43% | -0.32% |  |  | 15 | [11 empty] | Check |  | MAGE_Solar
MEMC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | MEMC
MEMC | F310BzC | mono | 310 |  | +5/-0 | 5 | 0 |  |  | 36.2 | 8.57 | 45.3 | 9.16 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | MEMC
MEMC | F315BzC | mono | 315 |  | +5/-0 | 5 | 0 |  |  | 36.6 | 8.63 | 45.7 | 9.23 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | MEMC
MEMC | F320BzC | mono | 320 |  | +5/-0 | 5 | 0 |  |  | 37 | 8.68 | 45.9 | 9.26 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | MEMC
MEMC | F325BzC | mono | 325 |  | +5/-0 | 5 | 0 |  |  | 37.3 | 8.72 | 46 | 9.27 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | MEMC
MEMC | F330BzC | mono | 330 |  | +5/-0 | 5 | 0 |  |  | 37.7 | 8.77 | 46.2 | 9.28 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | MEMC
MEMC | F335BzC | mono | 335 |  | +5/-0 | 5 | 0 |  |  | 37.9 | 8.85 | 46.4 | 9.29 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | MEMC
MEMC | MEMC - M240AMA | mono | 240 |  | +5/-0 | 5 | 0 |  |  | 29.5 | 8.15 | 37.4 | 8.7 | -0.49% | -0.35% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M245AMA | mono | 245 |  | +5/-0 | 5 | 0 |  |  | 29.7 | 8.25 | 37.5 | 8.8 | -0.49% | -0.35% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M250AMA | mono | 250 |  | +5/-0 | 5 | 0 |  |  | 29.9 | 8.36 | 37.6 | 8.9 | -0.49% | -0.35% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M255AMA | mono | 255 |  | +5/-0 | 5 | 0 |  |  | 30 | 8.5 | 37.8 | 9 | -0.49% | -0.35% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M245AMC | mono | 245 |  | +5/-0 | 5 | 0 |  |  | 29.2 | 8.47 | 37.7 | 8.9 | -0.49% | -0.35% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M250AMC | mono | 250 |  | +5/-0 | 5 | 0 |  |  | 29.4 | 8.57 | 37.8 | 9 | -0.49% | -0.35% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M255AMC | mono | 255 |  | +5/-0 | 5 | 0 |  |  | 29.6 | 8.67 | 37.9 | 9.1 | -0.49% | -0.35% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M260AMC | mono | 260 |  | +5/-0 | 5 | 0 |  |  | 29.8 | 8.77 | 40 | 9.2 | -0.49% | -0.35% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P270ACA | multi | 270 |  | +5/-0 | 5 | 0 |  |  | 34.1 | 8 | 43.8 | 8.5 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P275ACA | multi | 275 |  | +5/-0 | 5 | 0 |  |  | 34.6 | 8.05 | 44.1 | 8.56 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P280ACA | multi | 280 |  | +5/-0 | 5 | 0 |  |  | 34.8 | 8.12 | 44.3 | 8.62 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P285ACA | multi | 285 |  | +5/-0 | 5 | 0 |  |  | 35.1 | 8.18 | 44.5 | 8.71 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P290ACA | multi | 290 |  | +5/-0 | 5 | 0 |  |  | 35.4 | 8.2 | 44.7 | 8.78 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P270AMA | multi | 270 |  | +5/-0 | 5 | 0 |  |  | 34.1 | 8 | 43.8 | 8.5 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P275AMA | multi | 275 |  | +5/-0 | 5 | 0 |  |  | 34.6 | 8.05 | 44 | 8.55 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P280AMA | multi | 280 |  | +5/-0 | 5 | 0 |  |  | 34.8 | 8.12 | 44.3 | 8.62 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P285AMA | multi | 285 |  | +5/-0 | 5 | 0 |  |  | 35.1 | 8.18 | 44.5 | 8.71 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P290AMA | multi | 290 |  | +5/-0 | 5 | 0 |  |  | 35.4 | 8.2 | 44.7 | 8.71 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P280ACC | multi | 280 |  | +5/-0 | 5 | 0 |  |  | 34.7 | 8.08 | 44 | 8.6 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P285ACC | multi | 285 |  | +5/-0 | 5 | 0 |  |  | 34.9 | 8.16 | 44.4 | 8.65 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P290ACC | multi | 290 |  | +5/-0 | 5 | 0 |  |  | 35.4 | 8.2 | 44.7 | 8.71 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P295ACC | multi | 295 |  | +5/-0 | 5 | 0 |  |  | 35.7 | 8.26 | 45.1 | 8.95 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P300ACC | multi | 300 |  | +5/-0 | 5 | 0 |  |  | 36 | 8.34 | 45.3 | 9 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P280BMC | multi | 280 |  | +5/-0 | 5 | 0 |  |  | 34.7 | 8.08 | 44 | 8.6 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P285BMC | multi | 285 |  | +5/-0 | 5 | 0 |  |  | 34.9 | 8.16 | 44.4 | 8.65 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P290BMC | multi | 290 |  | +5/-0 | 5 | 0 |  |  | 35.4 | 8.2 | 44.7 | 8.71 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P295BMC | multi | 295 |  | +5/-0 | 5 | 0 |  |  | 35.7 | 8.26 | 45.1 | 8.95 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P300BMC | multi | 300 |  | +5/-0 | 5 | 0 |  |  | 36 | 8.34 | 45.3 | 9 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P305BMC | multi | 305 |  | +5/-0 | 5 | 0 |  |  | 36.3 | 8.41 | 45.4 | 9.05 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P280BCC | multi | 280 |  | +5/-0 | 5 | 0 |  |  | 34.7 | 8.08 | 44 | 8.6 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P285BCC | multi | 285 |  | +5/-0 | 5 | 0 |  |  | 34.9 | 8.16 | 44.4 | 8.65 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P290BCC | multi | 290 |  | +5/-0 | 5 | 0 |  |  | 35.4 | 8.2 | 44.7 | 8.71 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P295BCC | multi | 295 |  | +5/-0 | 5 | 0 |  |  | 35.7 | 8.26 | 45.1 | 8.95 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P300BCC | multi | 300 |  | +5/-0 | 5 | 0 |  |  | 36 | 8.34 | 45.3 | 9 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P305BCC | multi | 305 |  | +5/-0 | 5 | 0 |  |  | 36.3 | 8.41 | 45.4 | 9.05 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P280AMC | multi | 280 |  | +5/-0 | 5 | 0 |  |  | 34.7 | 8.08 | 44 | 8.6 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P285AMC | multi | 285 |  | +5/-0 | 5 | 0 |  |  | 34.9 | 8.16 | 44.4 | 8.65 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P290AMC | multi | 290 |  | +5/-0 | 5 | 0 |  |  | 35.4 | 8.2 | 44.7 | 8.71 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P295AMC | multi | 295 |  | +5/-0 | 5 | 0 |  |  | 35.7 | 8.26 | 45.1 | 8.95 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P300AMC | multi | 300 |  | +5/-0 | 5 | 0 |  |  | 36 | 8.34 | 45.3 | 9 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - P305AMC | multi | 305 |  | +5/-0 | 5 | 0 |  |  | 36.3 | 8.41 | 45.4 | 9.05 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M305ByC | mono | 305 |  | +5/-0 | 5 | 0 |  |  | 36.7 | 8.31 | 45.5 | 9 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M310ByC | mono | 310 |  | +5/-0 | 5 | 0 |  |  | 36.1 | 8.6 | 45.6 | 9.06 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M315ByC | mono | 315 |  | +5/-0 | 5 | 0 |  |  | 36.5 | 8.64 | 45.7 | 9.08 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M320ByC | mono | 320 |  | +5/-0 | 5 | 0 |  |  | 37.1 | 8.65 | 45.9 | 9.1 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M325ByC | mono | 325 |  | +5/-0 | 5 | 0 |  |  | 37.4 | 8.69 | 46 | 9.14 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M330ByC | mono | 330 |  | +5/-0 | 5 | 0 |  |  | 37.6 | 8.78 | 46.2 | 9.18 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M305BMC | mono | 305 |  | +5/-0 | 5 | 0 |  |  | 36.8 | 8.29 | 45.8 | 9 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M310BMC | mono | 310 |  | +5/-0 | 5 | 0 |  |  | 36.9 | 8.4 | 45.9 | 9.02 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M315BMC | mono | 315 |  | +5/-0 | 5 | 0 |  |  | 37 | 8.52 | 46 | 9.05 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M320BMC | mono | 320 |  | +5/-0 | 5 | 0 |  |  | 37.1 | 8.68 | 46.1 | 9.14 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M325BMC | mono | 325 |  | +5/-0 | 5 | 0 |  |  | 37.2 | 8.74 | 46.2 | 9.19 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | MEMC - M330BMC | mono | 330 |  | +5/-0 | 5 | 0 |  |  | 37.3 | 8.85 | 46.3 | 9.24 | -0.46% | -0.34% |  |  | 15 | [11 empty] | Check |  | MEMC
MEMC | F310B(E)zC(D) | mono | 310 |  | +5/-0 | 5 | 0 |  |  | 36.2 | 8.57 | 45.3 | 9.16 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-03 | MEMC
MEMC | F315B(E)zC(D) | mono | 315 |  | +5/-0 | 5 | 0 |  |  | 36.6 | 8.63 | 45.7 | 9.23 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-03 | MEMC
MEMC | F320B(E)zC(D) | mono | 320 |  | +5/-0 | 5 | 0 |  |  | 37 | 8.68 | 45.9 | 9.26 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-03 | MEMC
MEMC | F325B(E)zC(D) | mono | 325 |  | +5/-0 | 5 | 0 |  |  | 37.3 | 8.72 | 46 | 9.27 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-03 | MEMC
MEMC | R(F)330B(E)zC(D) | mono | 330 |  | +5/-5 | 5 | 5 |  |  | 37.7 | 8.77 | 46.2 | 9.28 | -0.44% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-02-19 | MEMC
MEMC | R(F)335B(E)zC(D) | mono | 335 |  | +5/-5 | 5 | 5 |  |  | 37.9 | 8.85 | 46.4 | 9.29 | -0.44% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-02-19 | MEMC
MEMC | R340B(E)zC | mono | 340 |  | +5/-5 | 5 | 5 |  |  | 38 | 8.95 | 46.5 | 9.4 | -0.44% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-02-19 | MEMC
MEMC | R345B(E)zC | mono | 345 |  | +5/-5 | 5 | 5 |  |  | 38.1 | 9.06 | 46.6 | 9.48 | -0.44% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-02-19 | MEMC
MEMC | R350B(E)zC | mono | 350 |  | +5/-5 | 5 | 5 |  |  | 38.2 | 9.16 | 46.7 | 9.56 | -0.44% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-02-19 | MEMC
MEMC | R355B(E)zC | mono | 355 |  | +5/-5 | 5 | 5 |  |  | 38.3 | 9.27 | 46.8 | 9.64 | -0.44% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-02-19 | MEMC
MEMC | SE-H345-4 | mono | 345 |  | +3/-0 | 3 | 0 |  |  | 38.6 | 8.94 | 47.3 | 9.45 | -0.41% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | MEMC
MEMC | SE-H350-4 | mono | 350 |  | +3/-0 | 3 | 0 |  |  | 38.7 | 9.04 | 47.4 | 9.6 | -0.41% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | MEMC
MEMC | SE-H355-4 | mono | 355 |  | +3/-0 | 3 | 0 |  |  | 38.8 | 9.15 | 47.5 | 9.68 | -0.41% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | MEMC
MEMC | SE-H360-4 | mono | 360 |  | +3/-0 | 3 | 0 |  |  | 38.9 | 9.25 | 47.6 | 9.73 | -0.41% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | MEMC
Mitsubishi Electric | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Mitsubishi_Electric
Mitsubishi Electric | PV-MLU250HC | mono | 250 | 225.8 | +/-3 | 3 | -3 | 14.0274 | 15.1 | 31 | 8.08 | 37.6 | 8.79 | -0.45% | -0.35% | 0.15 | 45.7 | 15 | yes | MC4 | black | white | 64 | 40.1 | 1.81 | 17.8222 | 44 | 5 |  | Check |  | Mitsubishi_Electric
Mitsubishi Electric | PV-MLU255HC | mono | 255 | 230.5 | +/-3 | 3 | -3 | 14.308 | 15.4 | 31.2 | 8.18 | 37.8 | 8.89 | -0.45% | -0.35% | 0.15 | 45.7 | 15 | yes | MC4 | black | white | 64 | 40.1 | 1.81 | 17.8222 | 44 | 5 |  | Check |  | Mitsubishi_Electric
Mitsubishi Electric | PV-UD175MF5 | poly | 175 | 157 | +/-3 | 3 | -3 | 11.7656 | 12.7 | 23.9 | 7.32 | 30.2 | 7.93 | -0.45% | -0.33% | 0.05 | 47.5 | 15 | yes | MC4 | black | white | 65.3 | 32.8 | 1.81 | 14.8739 | 37 | 5 |  | Check |  | Mitsubishi_Electric
Mitsubishi Electric | PV-UD180MF5 | poly | 180 | 161.6 | +/-3 | 3 | -3 | 12.1017 | 13 | 24.2 | 7.45 | 30.4 | 8.03 | -0.45% | -0.33% | 0.05 | 47.5 | 15 | yes | MC4 | black | white | 65.3 | 32.8 | 1.81 | 14.8739 | 37 | 5 |  | Check |  | Mitsubishi_Electric
Mitsubishi Electric | PV-UD185MF5 | poly | 185 | 166.2 | +/-3 | 3 | -3 | 12.4379 | 13.4 | 24.4 | 7.58 | 30.6 | 8.13 | -0.45% | -0.33% | 0.05 | 47.5 | 15 | yes | MC4 | black | white | 65.3 | 32.8 | 1.81 | 14.8739 | 37 | 5 |  | Check |  | Mitsubishi_Electric
Mitsubishi Electric | PV-UD190MF5 | poly | 190 | 169.8 | +/-3 | 3 | -3 | 12.7741 | 13.7 | 24.7 | 7.71 | 30.8 | 8.23 | -0.45% | -0.33% | 0.05 | 47.5 | 15 | yes | MC4 | black | white | 65.3 | 32.8 | 1.81 | 14.8739 | 37 | 5 |  | Check |  | Mitsubishi_Electric
Mitsubishi Electric | PV-UE115MF5N | poly | 115 |  | +10/-5 | 10 | -5 | 10.6096 | 11.4 | 17.1 | 6.75 | 21.5 | 7.6 | -0.452% | -34% |  |  | 15 |  | MC |  |  | 58.9 | 26.5 | 1.81 | 10.8392 | 29.8 | 1.25 |  | Check |  | Mitsubishi_Electric
Mitsubishi Electric | PV-UE120MF5N | poly | 120 |  | +10/-5 | 10 | -5 | 11.0709 | 11.9 | 17.2 | 6.99 | 21.6 | 7.75 | -0.452% | -34% |  |  | 15 |  | MC |  |  | 58.9 | 26.5 | 1.81 | 10.8392 | 29.8 | 1.25 |  | Check |  | Mitsubishi_Electric
Mitsubishi Electric | PV-UE125MF5N | poly | 125 |  | +10/-5 | 10 | -5 | 11.5322 | 12.4 | 17.3 | 7.23 | 21.8 | 7.9 | -0.452% | -34% |  |  | 15 |  | MC |  |  | 58.9 | 26.5 | 1.81 | 10.8392 | 29.8 | 1.25 |  | Check |  | Mitsubishi_Electric
Mitsubishi Electric | PV-UE130MF5N | poly | 130 |  | +10/-5 | 10 | -5 | 11.9935 | 12.9 | 17.4 | 7.47 | 21.9 | 8.05 | -0.452% | -34% |  |  | 15 |  | MC |  |  | 58.9 | 26.5 | 1.81 | 10.8392 | 29.8 | 1.25 |  | Check |  | Mitsubishi_Electric
Mitsubishi Electric | PV-UJ212G6 | poly | 212 | 194.5 | +/-3 | 3 | -3 | 11.9566 | 12.9 | 29 | 7.31 | 36.1 | 8.13 | -0.37% | -0.3% | 0.13 | 47.5 | 15 | yes | MC4 | silver | white | 65.3 | 39.1 | 1.81 | 17.7308 | 44 | 5 |  | Check |  | Mitsubishi_Electric
Mitsubishi Electric | PV-UJ218G6 | poly | 218 | 200.1 | +/-3 | 3 | -3 | 12.295 | 13.2 | 29.3 | 7.44 | 36.3 | 8.25 | -0.37% | -0.3% | 0.13 | 47.5 | 15 | yes | MC4 | silver | white | 65.3 | 39.1 | 1.81 | 17.7308 | 44 | 5 |  | Check |  | Mitsubishi_Electric
Mitsubishi Electric | PV-UJ225GA6 | poly | 225 | 203.2 | +/-3 | 3 | -3 | 12.6898 | 13.7 | 30 | 7.5 | 36.4 | 8.3 | -0.41% | -0.32% | 0.15 | 47 | 15 | yes | MC4 | silver | white | 65.3 | 39.1 | 1.81 | 17.7308 | 44 | 5 |  | Check |  | Mitsubishi_Electric
Mitsubishi Electric | PV-UJ230GA6 | poly | 230 | 207.8 | +/-3 | 3 | -3 | 12.9718 | 14 | 30.2 | 7.62 | 36.6 | 8.39 | -0.41% | -0.32% | 0.15 | 47 | 15 | yes | MC4 | silver | white | 65.3 | 39.1 | 1.81 | 17.7308 | 44 | 5 |  | Check |  | Mitsubishi_Electric
Mitsubishi Electric | PV-UJ235GA6 | poly | 235 | 212.4 | +/-3 | 3 | -3 | 13.2538 | 14.3 | 30.5 | 7.71 | 36.8 | 8.49 | -0.41% | -0.32% | 0.15 | 47 | 15 | yes | MC4 | silver | white | 65.3 | 39.1 | 1.81 | 17.7308 | 44 | 5 |  | Check |  | Mitsubishi_Electric
Mitsubishi Electric | PV-MJE265FB | mono | 265 |  | +5/-0 | 5 | 0 |  |  | 30.9 | 8.59 | 38 | 9.1 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Mitsubishi_Electric
Mitsubishi Electric | PV-MLE265HD2 | mono | 265 |  | +5/-0 | 5 | 0 |  |  | 31.7 | 8.38 | 38.2 | 9.08 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Mitsubishi_Electric
Mitsubishi Electric | PV-MLE270HD | mono | 270 |  | +5/-0 | 5 | 0 |  |  | 31.2 | 8.18 | 37.8 | 8.89 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Mitsubishi_Electric
Mitsubishi Electric | PV-MLE270HD2 | mono | 270 |  | +5/-0 | 5 | 0 |  |  | 31.4 | 8.29 | 38 | 8.98 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Mitsubishi_Electric
Mitsubishi Electric | PV-MLE275HD2 | mono | 275 |  | +5/-0 | 5 | 0 |  |  | 31.7 | 8.38 | 38.2 | 9.08 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Mitsubishi_Electric
Motech Americas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Motech_North_America
Motech Americas | GEPVp-205-MSA | poly | 205 | 183.5 | +5/-3 | 5 | -3 | 13.0729 | 14.31 | 27.2 | 7.6 | 33 | 8.2 | -0.5% | -0.12% | 0.07 | 50 | 15 | yes | tyco | clear | white | 58.5 | 38.6 | 1.4 | 15.6813 | 39 | 5 |  | Check |  | Motech_North_America
Motech Americas | GEPVp-205-MSB | poly | 205 | 183.1 | +5/-3 | 5 | -3 | 13.0729 | 14.31 | 27.2 | 7.6 | 33 | 8.2 | -0.5% | -0.12% | 0.07 | 50 | 15 | yes | tyco | black | black | 58.5 | 38.6 | 1.4 | 15.6813 | 39 | 5 |  | Check |  | Motech_North_America
Motech Americas | GEPVp-210-MSA | poly | 210 | 188.1 | +5/-3 | 5 | -3 | 13.3918 | 14.5 | 27.3 | 7.7 | 33 | 8.3 | -0.5% | -0.12% | 0.07 | 50 | 15 | yes | tyco | clear | white | 58.5 | 38.6 | 1.4 | 15.6813 | 39 | 5 |  | Check |  | Motech_North_America
Motech Americas | GEPVp-210-MSB | poly | 210 | 187.7 | +5/-3 | 5 | -3 | 13.3918 | 14.5 | 27.3 | 7.7 | 33 | 8.3 | -0.5% | -0.12% | 0.07 | 50 | 15 | yes | tyco | black | black | 58.5 | 38.6 | 1.4 | 15.6813 | 39 | 5 |  | Check |  | Motech_North_America
Motech Americas | MTPVp-230-MSB | poly | 230 | 203.4 | +5/-3 | 5 | -3 | 13.0317 | 14.28 | 29.1 | 7.9 | 36.8 | 8.4 | -0.46% | -0.34% | 0.07 | 48 | 15 | yes | tyco | black | black | 65 | 39.1 | 1.97 | 17.6493 | 43.7 | 5 |  | Check |  | Motech_North_America
Motech Americas | MTPVp-230-MSC/D | poly | 230 | 205.4 | +5/-3 | 5 | -3 | 13.0317 | 14.28 | 29.1 | 7.9 | 36.8 | 8.4 | -0.46% | -0.34% | 0.07 | 48 | 15 | yes | tyco | clear/black | white | 65 | 39.1 | 1.97 | 17.6493 | 43.7 | 5 |  | Check |  | Motech_North_America
Motech Americas | MTPVp-235-MSB | poly | 235 | 208 | +5/-3 | 5 | -3 | 13.315 | 14.59 | 29.4 | 8 | 37.1 | 8.5 | -0.46% | -0.34% | 0.07 | 48 | 15 | yes | tyco | black | black | 65 | 39.1 | 1.97 | 17.6493 | 43.7 | 5 |  | Check |  | Motech_North_America
Motech Americas | MTPVp-235-MSC/D | poly | 235 | 210 | +5/-3 | 5 | -3 | 13.315 | 14.59 | 29.4 | 8 | 37.1 | 8.5 | -0.46% | -0.34% | 0.07 | 48 | 15 | yes | tyco | clear/black | white | 65 | 39.1 | 1.97 | 17.6493 | 43.7 | 5 |  | Check |  | Motech_North_America
Motech Americas | MTPVp-240-MSB | poly | 240 | 212.6 | +5/-3 | 5 | -3 | 13.5983 | 14.9 | 29.8 | 8.1 | 37.3 | 8.6 | -0.46% | -0.34% | 0.07 | 48 | 15 | yes | tyco | black | black | 65 | 39.1 | 1.97 | 17.6493 | 43.7 | 5 |  | Check |  | Motech_North_America
Motech Americas | MTPVp-240-MSC/D | poly | 240 | 214.6 | +5/-3 | 5 | -3 | 13.5983 | 14.9 | 29.8 | 8.1 | 37.3 | 8.6 | -0.46% | -0.34% | 0.07 | 48 | 15 | yes | tyco | clear/black | white | 65 | 39.1 | 1.97 | 17.6493 | 43.7 | 5 |  | Check |  | Motech_North_America
Motech Americas | MTPVp-245-MSB | poly | 245 | 217.1 | +5/-3 | 5 | -3 | 13.8816 | 15.21 | 29.9 | 8.2 | 37.4 | 8.7 | -0.46% | -0.34% | 0.07 | 48 | 15 | yes | tyco | black | black | 65 | 39.1 | 1.97 | 17.6493 | 43.7 | 5 |  | Check |  | Motech_North_America
Motech Americas | MTPVp-245-MSC/D | poly | 245 | 219.2 | +5/-3 | 5 | -3 | 13.8816 | 15.21 | 29.9 | 8.2 | 37.4 | 8.7 | -0.46% | -0.34% | 0.07 | 48 | 15 | yes | tyco | clear/black | white | 65 | 39.1 | 1.97 | 17.6493 | 43.7 | 5 |  | Check |  | Motech_North_America
Motech Americas | XS60C3-260-G | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 29.89 | 8.7 | 37.42 | 9.13 | -0.46% | -0.33% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | XS60C3-265-G | mono | 265 |  | +3/-0 | 3 | 0 |  |  | 30.05 | 8.82 | 37.49 | 9.24 | -0.46% | -0.33% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | XS60C3-270-G | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 30.2 | 8.94 | 37.59 | 9.34 | -0.46% | -0.33% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | XS60C3-275-G | mono | 275 |  | +3/-0 | 3 | 0 |  |  | 30.35 | 9.06 | 37.83 | 9.44 | -0.46% | -0.33% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | XS60C3-280-G | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 30.5 | 9.18 | 38.08 | 9.55 | -0.46% | -0.33% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | XS72C3-310-G | mono | 310 |  | +3/-0 | 3 | 0 |  |  | 35.71 | 8.68 | 45.22 | 9.08 | -0.47% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | XS72C3-315-G | mono | 315 |  | +3/-0 | 3 | 0 |  |  | 35.84 | 8.79 | 45.27 | 9.18 | -0.47% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | XS72C3-320-G | mono | 320 |  | +3/-0 | 3 | 0 |  |  | 35.91 | 8.91 | 45.31 | 9.28 | -0.47% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | XS72C3-325-G | mono | 325 |  | +3/-0 | 3 | 0 |  |  | 35.99 | 9.03 | 45.48 | 9.39 | -0.47% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | XS72C3-330-G | mono | 330 |  | +3/-0 | 3 | 0 |  |  | 36.26 | 9.1 | 45.68 | 9.48 | -0.47% | -0.34% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | IM60(C)(B)(D)3-250-G | multi | 250 |  | +3/-0 | 3 | 0 |  |  | 29.68 | 8.41 | 37.43 | 8.78 | -0.46% | -0.33% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | IM60(C)(B)(D)3-255-G | multi | 255 |  | +3/-0 | 3 | 0 |  |  | 29.86 | 8.54 | 37.6 | 8.9 | -0.46% | -0.33% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | IM60(C)(D)3-260-G | multi | 260 |  | +3/-0 | 3 | 0 |  |  | 30.02 | 8.66 | 37.78 | 9.02 | -0.46% | -0.33% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | IM72B3-285-G | multi | 285 |  | +3/-0 | 3 | 0 |  |  | 35.1 | 8.12 | 44.53 | 8.51 | -0.46% | -0.33% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | IM72B3-290-G | multi | 290 |  | +3/-0 | 3 | 0 |  |  | 35.2 | 8.24 | 44.61 | 8.62 | -0.46% | -0.33% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | IM72B3-295-G | multi | 295 |  | +3/-0 | 3 | 0 |  |  | 35.37 | 8.34 | 44.69 | 8.72 | -0.46% | -0.33% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | IM72C(B)3-300-G | multi | 300 |  | +3/-0 | 3 | 0 |  |  | 35.5 | 8.45 | 44.78 | 8.83 | -0.46% | -0.33% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | IM72C(B)3-305-G | multi | 305 |  | +3/-0 | 3 | 0 |  |  | 35.59 | 8.57 | 44.88 | 8.95 | -0.46% | -0.33% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | IM72C(B)3-310-G | multi | 310 |  | +3/-0 | 3 | 0 |  |  | 35.76 | 8.67 | 44.97 | 9.05 | -0.46% | -0.33% |  |  | 12 | [11 empty] | Check | 2015-11-30 | Motech_North_America
Motech Americas | MTPVp-280-MSC | poly | 280 | 249.9 | +5/-3 | 5 | -3 | 13.323 | 14.65 | 35.2 | 8 | 44.3 | 8.4 | -0.46% | -0.34% | 0.07 | 48 | 15 | yes | tyco | clear | white | 77.4 | 39.1 | 1.97 | 21.0162 | 59.5 | 5 |  | Check |  | Motech_North_America
Motech Americas | MTPVp-285-MSC | poly | 285 | 254.5 | +5/-3 | 5 | -3 | 13.5609 | 14.91 | 35.6 | 8.1 | 44.6 | 8.6 | -0.46% | -0.34% | 0.07 | 48 | 15 | yes | tyco | clear | white | 77.4 | 39.1 | 1.97 | 21.0162 | 59.5 | 5 |  | Check |  | Motech_North_America
Motech Americas | MTPVp-290-MSC | poly | 290 | 259.1 | +5/-3 | 5 | -3 | 13.7988 | 15.18 | 31.6 | 8.1 | 44.8 | 8.6 | -0.46% | -0.34% | 0.07 | 48 | 15 | yes | tyco | clear | white | 77.4 | 39.1 | 1.97 | 21.0162 | 59.5 | 5 |  | Check |  | Motech_North_America
Nexus Energy Solutions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Nexus_Energy_Solutions
Nexus Energy Solutions | DJ-165D |  | 165 |  | +3/-0 | 3 | 0 |  |  | 35.4 | 4.66 | 43.6 | 5.08 | -0.37% | -0.34% |  |  | 10 | [7 empty] | 0 |  |  |  | Check |  | Nexus_Energy_Solutions
Nexus Energy Solutions | DJ-170D |  | 170 |  | +3/-0 | 3 | 0 |  |  | 35 | 4.78 | 44.2 | 5.15 | -0.37% | -0.34% |  |  | 10 | [7 empty] | 0 |  |  |  | Check |  | Nexus_Energy_Solutions
Nexus Energy Solutions | DJ-175D |  | 175 |  | +3/-0 | 3 | 0 |  |  | 35.8 | 4.89 | 44.2 | 5.25 | -0.37% | -0.34% |  |  | 10 | [7 empty] | 0 |  |  |  | Check |  | Nexus_Energy_Solutions
Nexus Energy Solutions | DJ-180D |  | 180 |  | +3/-0 | 3 | 0 |  |  | 36.2 | 4.97 | 44.2 | 5.36 | -0.37% | -0.34% |  |  | 10 | [7 empty] | 0 |  |  |  | Check |  | Nexus_Energy_Solutions
Nexus Energy Solutions | DJ-200P |  | 200 |  | +3/-0 | 3 | 0 |  |  | 29.1 | 6.87 | 34.92 | 7.85 | -0.45% | -0.35% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | Nexus_Energy_Solutions
Nexus Energy Solutions | DJ-210P |  | 210 |  | +3/-0 | 3 | 0 |  |  | 29.3 | 7.173 | 35.4 | 8.12 | -0.45% | -0.35% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | Nexus_Energy_Solutions
Nexus Energy Solutions | DJ-220P |  | 220 |  | +3/-0 | 3 | 0 |  |  | 29.4 | 7.48 | 35.87 | 8.4 | -0.45% | -0.35% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | Nexus_Energy_Solutions
Nexus Energy Solutions | DJ-230P |  | 230 |  | +3/-0 | 3 | 0 |  |  | 30.73 | 7.81 | 37.48 | 8.78 | -0.45% | -0.35% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | Nexus_Energy_Solutions
Nexus Energy Solutions | DJ-240P |  | 240 |  | +3/-0 | 3 | 0 |  |  | 34.21 | 7.18 | 39.64 | 8.32 | -0.45% | -0.35% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | Nexus_Energy_Solutions
Nexus Energy Solutions | DJ-250P |  | 250 |  | +3/-0 | 3 | 0 |  |  | 34.6 | 7.23 | 40.9 | 8.57 | -0.45% | -0.35% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | Nexus_Energy_Solutions
Nexus Energy Solutions | DJ-260P |  | 260 |  | +3/-0 | 3 | 0 |  |  | 34.9 | 7.45 | 42.26 | 8.59 | -0.45% | -0.35% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | Nexus_Energy_Solutions
Nexus Energy Solutions | DJ-270P |  | 270 |  | +3/-0 | 3 | 0 |  |  | 35.38 | 7.91 | 44.5 | 8.519 | -0.45% | -0.35% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | Nexus_Energy_Solutions
Nexus Energy Solutions | DJ-280P |  | 280 |  | +3/-0 | 3 | 0 |  |  | 36.48 | 7.95 | 45.29 | 8.9 | -0.45% | -0.35% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | Nexus_Energy_Solutions
Panasonic (Sanyo) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Panasonic_Sanyo
Panasonic (Sanyo) | HIP-180DA3 | mono, a-Si | 180 |  | +10/-0 | 10 | 0 | 13.7632 | 14.8 | 54.6 | 4.21 | 67.7 | 4.71 | -0.3% | -0.26% |  |  | 15 |  | MC |  | clear | 53.2 | 35.4 | 2.4 | 13.0783 | 50.7 | 2 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIP-186DA3 | mono, a-Si | 186 |  | +10/-0 | 10 | 0 | 14.222 | 15.3 | 55.1 | 4.32 | 68.2 | 4.78 | -0.3% | -0.25% |  |  | 15 |  | MC |  | clear | 53.2 | 35.4 | 2.4 | 13.0783 | 50.7 | 2 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIP-190DA3 | mono, a-Si | 190 |  | +10/-0 | 10 | 0 | 14.5278 | 15.7 | 55.6 | 4.37 | 68.8 | 4.81 | -0.3% | -0.25% |  |  | 15 |  | MC |  | clear | 53.2 | 35.4 | 2.4 | 13.0783 | 50.7 | 2 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIP-195DA3 | mono, a-Si | 195 |  | +10/-0 | 10 | 0 | 14.9102 | 16.1 | 56.1 | 4.45 | 69.5 | 4.85 | -0.29% | -0.25% |  |  | 15 |  | MC |  | clear | 53.2 | 35.4 | 2.4 | 13.0783 | 50.7 | 2 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIP-200DA3 | mono, a-Si | 200 |  | +10/-0 | 10 | 0 | 15.2925 | 16.5 | 56.5 | 4.52 | 69.6 | 4.88 | -0.29% | -0.25% |  |  | 15 |  | MC |  | clear | 53.2 | 35.4 | 2.4 | 13.0783 | 50.7 | 2 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIT Power 180 or HIP-180BA19 | mono, a-Si | 180 |  | +10/-0 | 10 | 0 | 14.4342 | 15.5 | 54 | 3.33 | 66.4 | 3.65 | -0.33% | -0.25% |  |  | 15 |  | MC4 |  |  | 51.9 | 34.6 | 1.8 | 12.4704 | 33.1 | 5 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIT Power 186 or HIP-186BA19 | mono, a-Si | 186 |  | +10/-0 | 10 | 0 | 14.9153 | 16 | 54.4 | 3.42 | 67 | 3.71 | -0.3% | -0.25% |  |  | 15 |  | MC4 |  |  | 51.9 | 34.6 | 1.8 | 12.4704 | 33.1 | 5 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIT Power 190 or HIP-190BA19 | mono, a-Si | 190 |  | +10/-0 | 10 | 0 | 15.2361 | 16.4 | 54.8 | 3.47 | 67.5 | 3.75 | -0.3% | -0.25% |  |  | 15 |  | MC4 |  |  | 51.9 | 34.6 | 1.8 | 12.4704 | 33.1 | 5 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIT Power 195 or HIP-195BA19 | mono, a-Si | 195 |  | +10/-0 | 10 | 0 | 15.637 | 16.8 | 55.3 | 3.53 | 68.1 | 3.79 | -0.3% | -0.25% |  |  | 15 |  | MC4 |  |  | 51.9 | 34.6 | 1.8 | 12.4704 | 33.1 | 5 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIT Power 200 or HIP-200BA19 | mono, a-Si | 200 |  | +10/-0 | 10 | 0 | 16.038 | 17.2 | 55.8 | 3.59 | 68.7 | 3.83 | -0.29% | -0.25% |  |  | 15 |  | MC4 |  |  | 51.9 | 34.6 | 1.8 | 12.4704 | 33.1 | 5 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIT Power 205 or HIP-205BA19 | mono, a-Si | 205 |  | +10/-0 | 10 | 0 | 16.4389 | 17.7 | 56.7 | 3.62 | 68.8 | 3.84 | -0.29% | -0.25% |  |  | 15 |  | MC4 |  |  | 51.9 | 34.6 | 1.8 | 12.4704 | 33.1 | 5 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIT-195DA3 | mono, a-Si | 195 | 181.1 | +10/-0 | 10 | 0 | 14.9312 | 16.1 | 55.8 | 3.5 | 68.7 | 3.73 | -0.29% | -0.25% | 0.02 | 47 | 15 | no | MC3 | silver | none | 53.2 | 35.35 | 2.36 | 13.0599 | 50.7 | 2 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIT-205NKHA1 | mono, a-Si | 205 | 190.2 | +10/-0 | 10 | 0 | 15.1146 | 16.3 | 40.7 | 5.05 | 50.3 | 5.54 | -0.34% | -0.28% | 0.04 | 46 | 15 | yes | MC4 | black | white | 62.2 | 31.4 | 1.8 | 13.5631 | 35.3 | 5 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIT-210NKHA1 | mono, a-Si | 210 | 194.9 | +10/-0 | 10 | 0 | 15.4832 | 16.7 | 41.3 | 5.09 | 50.9 | 5.57 | -0.34% | -0.28% | 0.04 | 46 | 15 | yes | MC4 | black | white | 62.2 | 31.4 | 1.8 | 13.5631 | 35.3 | 5 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIT-215NKHA1 | mono, a-Si | 215 | 199.6 | +10/-0 | 10 | 0 | 15.8519 | 17.1 | 42 | 5.13 | 51.6 | 5.61 | -0.34% | -0.27% | 0.03 | 46 | 15 | yes | MC4 | black | white | 62.2 | 31.4 | 1.8 | 13.5631 | 35.3 | 5 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIT-N220A01 | mono, a-Si | 220 | 204.4 | +10/-0 | 10 | 0 | 16.2205 | 17.4 | 42.7 | 5.17 | 52.3 | 5.65 | -0.34% | -0.27% | 0.03 | 46 | 15 | yes | MC4 | black | white | 62.2 | 31.4 | 1.8 | 13.5631 | 35.3 | 5 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIT-N225A01 | mono, a-Si | 225 | 209.1 | +10/-0 | 10 | 0 | 16.5892 | 17.8 | 43.4 | 5.21 | 53 | 5.66 | -0.34% | -0.27% | 0.03 | 46 | 15 | yes | MC4 | black | white | 62.2 | 31.4 | 1.8 | 13.5631 | 35.3 | 5 |  | Check |  | Panasonic_Sanyo
Panasonic (Sanyo) | HIT Power 235S | mono, a-Si | 235 |  | +10/-0 | 10 | 0 |  |  | 43 | 5.48 | 51.8 | 5.84 | -0.3% | -0.24% |  |  | 15 | [11 empty] | Check | 2013-09-24 | Panasonic_Sanyo
Panasonic (Sanyo) | HIT Power 240S | mono, a-Si | 240 |  | +10/-0 | 10 | 0 |  |  | 43.7 | 5.51 | 52.4 | 5.85 | -0.3% | -0.24% |  |  | 15 | [11 empty] | Check | 2013-09-24 | Panasonic_Sanyo
Panasonic (Sanyo) | VBMS250AE04 | poly | 250 |  | +10/-5 | 10 | -5 |  |  | 30.2 | 8.3 | 37.4 | 8.86 | -0.45% | -0.13% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Panasonic_Sanyo
Panasonic (Sanyo) | VBMS255AE04 | poly | 255 |  | +10/-5 | 10 | -5 |  |  | 30.5 | 8.42 | 37.6 | 8.95 | -0.45% | -0.13% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Panasonic_Sanyo
Panasonic (Sanyo) | VBMS260AE04 | poly | 260 |  | +10/-5 | 10 | -5 |  |  | 30.7 | 8.5 | 37.8 | 9.01 | -0.45% | -0.13% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Panasonic_Sanyo
Panasonic (Sanyo) | VBHN310KA01 | mono, a-Si | 310 |  | +10/-0 | 10 | 0 |  |  | 58.1 | 5.34 | 69.9 | 5.78 | -0.258% | -0.229% |  |  | 15 | [11 empty] | 600 | 2018-02-09 | Panasonic_Sanyo
Panasonic (Sanyo) | VBHN315KA01 | mono, a-Si | 315 |  | +10/-0 | 10 | 0 |  |  | 58.4 | 5.34 | 70.2 | 5.83 | -0.258% | -0.2279% |  |  | 15 | [11 empty] | 600 | 2018-02-09 | Panasonic_Sanyo
Panasonic (Sanyo) | VBHN320KA01 | mono, a-Si | 320 |  | +10/-0 | 10 | 0 |  |  | 58.7 | 5.46 | 70.5 | 5.89 | -0.258% | -0.227% |  |  | 15 | [11 empty] | 600 | 2018-02-09 | Panasonic_Sanyo
Panasonic (Sanyo) | VBHN325SA16 | mono, a-Si | 325 |  | +10/-0 | 10 | 0 |  |  | 57.6 | 5.65 | 69.6 | 6.03 | -0.258% | -0.235% |  |  | 15 | [11 empty] | 600 | 2018-02-09 | Panasonic_Sanyo
Panasonic (Sanyo) | VBHN330SA16 | mono, a-Si | 330 |  | +10/-0 | 10 | 0 |  |  | 58 | 5.7 | 69.7 | 6.07 | -0.258% | -0.235% |  |  | 15 | [11 empty] | 600 | 2018-02-09 | Panasonic_Sanyo
Peimar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Peimar
Peimar | SG270P | poly | 270 |  | +5/-0 | 5 | 0 |  |  | 30.8 | 8.77 | 37.2 | 9.82 | -0.43% | -0.32% |  |  | 15 |  |  |  |  | 64.5 | 39 | 1.57 |  | 39.7 |  |  | 1000 | 2018-03-09 | Peimar
Peimar | SG280P | poly | 280 |  | +5/-0 | 5 | 0 |  |  | 31.2 | 8.98 | 38 | 9.85 | -0.43% | -0.32% |  |  | 15 |  |  |  |  | 64.5 | 39 | 1.57 |  | 39.7 |  |  | 1000 | 2018-03-09 | Peimar
Peimar | SG290M (FB) | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 31.6 | 9.18 | 39.6 | 9.55 | -0.42% | -0.32% |  |  | 15 |  |  |  |  | 64.5 | 39 | 1.57 |  | 39.7 |  |  | 1000 | 2018-03-09 | Peimar
Peimar | SG300M | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 32 | 9.4 | 39.6 | 9.93 | -0.43% | -0.32% |  |  | 15 |  |  |  |  | 64.5 | 39 | 1.57 |  | 39.7 |  |  | 1000 | 2018-03-09 | Peimar
Peimar | SG300M (BF) | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 32 | 9.4 | 39.6 | 9.93 | -0.4% | -0.32% |  |  | 15 |  |  |  |  | 64.5 | 39 | 1.57 |  | 39.7 |  |  | 1000 | 2018-03-09 | Peimar
Peimar | SG310M (BF) | mono | 310 |  | +5/-0 | 5 | 0 |  |  | 32.6 | 9.51 | 40.55 | 10.09 | -0.4% | -0.32% |  |  | 15 |  |  |  |  | 64.5 | 39 | 1.57 |  | 39.7 |  |  | 1000 | 2018-03-09 | Peimar
Peimar | SG325P | poly | 325 |  | +5/-0 | 5 | 0 |  |  | 36.3 | 9.03 | 44.6 | 9.74 | -0.43% | -0.32% |  |  | 15 |  |  |  |  | 77 | 39 | 1.57 |  | 49.6 |  |  | 1000 | 2018-03-09 | Peimar
Peimar | SG330P | poly | 330 |  | +5/-0 | 5 | 0 |  |  | 36.4 | 9.07 | 45.1 | 9.78 | -0.43% | -0.32% |  |  | 15 |  |  |  |  | 77 | 39 | 1.57 |  | 49.6 |  |  | 1000 | 2018-03-09 | Peimar
Perlight Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Perlight_Solar
Perlight Solar | PLM-175M-72 (PLM-5B-175M) | mono | 175 | 149.8 | +5/-0 | 5 | 0 | 12.7199 | 13.7079 | 36.4 | 4.81 | 44.2 | 5.22 | -0.459% | -0.333% | 0.03 | 47 | DNR | yes | MC4 | black/silver | black/white | 62.3 | 31.8 | 1.6 | 13.7579 | 34 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-185M-72 (PLM-5B-185M) | mono | 185 | 161.5 | +5/-0 | 5 | 0 | 13.4468 | 14.4912 | 36.8 | 5.03 | 44.6 | 5.46 | -0.459% | -0.333% | 0.03 | 47 | DNR | yes | MC4 | black/silver | black/white | 62.3 | 31.8 | 1.6 | 13.7579 | 34 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-205P-60 (PLM-6B-205P) | poly | 205 | 176.2 | +5/-0 | 5 | 0 | 11.6152 | 12.5244 | 28.9 | 7.09 | 36.4 | 7.79 | -0.45% | -0.35% | 0.05 | 47 | DNR | yes | MC4 | black/silver | black/white | 65 | 39.1 | 1.8 | 17.6493 | 46 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-210P-60 (PLM-6B-210P) | poly | 210 | 181.7 | +5/-0 | 5 | 0 | 11.8985 | 12.8299 | 29.2 | 7.19 | 36.4 | 7.86 | -0.45% | -0.35% | 0.05 | 47 | DNR | yes | MC4 | black/silver | black/white | 65 | 39.1 | 1.8 | 17.6493 | 46 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-215P-60 (PLM-6B-215P) | poly | 215 | 187.3 | +5/-0 | 5 | 0 | 12.1818 | 13.1354 | 29.5 | 7.29 | 36.6 | 7.93 | -0.45% | -0.35% | 0.05 | 47 | DNR | yes | MC4 | black/silver | black/white | 65 | 39.1 | 1.8 | 17.6493 | 46 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-220P-60 (PLM-6B-220P) | poly | 220 | 190.7 | +5/-0 | 5 | 0 | 12.4651 | 13.4409 | 29.82 | 7.39 | 36.8 | 8 | -0.45% | -0.35% | 0.05 | 47 | DNR | yes | MC4 | black/silver | black/white | 65 | 39.1 | 1.8 | 17.6493 | 46 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-225P-60 (PLM-6B-225P) | poly | 225 | 197.4 | +5/-0 | 5 | 0 | 12.7484 | 13.7463 | 30.2 | 7.45 | 36.8 | 8.29 | -0.45% | -0.35% | 0.05 | 47 | DNR | yes | MC4 | black/silver | black/white | 65 | 39.1 | 1.8 | 17.6493 | 46 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-230P-60 (PLM-6B-230P) | poly | 230 | 206.4 | +5/-0 | 5 | 0 | 13.0317 | 14.0518 | 30.5 | 7.55 | 36.8 | 8.57 | -0.45% | -0.35% | 0.05 | 47 | DNR | yes | MC4 | black/silver | black/white | 65 | 39.1 | 1.8 | 17.6493 | 46 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-235P-60 (PLM-6B-235P) | poly | 235 | 210.9 | +5/-0 | 5 | 0 | 13.315 | 14.3573 | 30.6 | 7.68 | 36.9 | 8.65 | -0.45% | -0.35% | 0.05 | 47 | DNR | yes | MC4 | black/silver | black/white | 65 | 39.1 | 1.8 | 17.6493 | 46 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-240M-60 | mono | 240 | 212.9 | +5/-0 | 5 | 0 | 13.5983 | 14.6628 | 30.7 | 7.81 | 36.9 | 8.73 | -0.46% | -0.31% | 0.03 | 47 | DNR | yes | MC4 | black/silver | black/white | 65 | 39.1 | 1.8 | 17.6493 | 46 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-240P-60 (PLM-6B-240P) | poly | 240 | 214.6 | +5/-0 | 5 | 0 | 13.5983 | 14.6628 | 30.7 | 7.81 | 35.9 | 8.73 | -0.45% | -0.35% | 0.05 | 47 | DNR | yes | MC4 | black/silver | black/white | 65 | 39.1 | 1.8 | 17.6493 | 46 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-245M-60 | mono | 245 | 217.5 | +5/-0 | 5 | 0 | 13.8816 | 14.9682 | 31 | 7.9 | 37 | 8.82 | -0.46% | -0.31% | 0.03 | 47 | DNR | yes | MC4 | black/silver | black/white | 65 | 39.1 | 1.8 | 17.6493 | 46 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-250M-60 | mono | 250 | 222.1 | +5/-0 | 5 | 0 | 14.1649 | 15.2737 | 31.1 | 8.03 | 37.1 | 8.97 | -0.46% | -0.31% | 0.03 | 47 | DNR | yes | MC4 | black/silver | black/white | 65 | 39.1 | 1.8 | 17.6493 | 46 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-255M-60 | mono | 255 | 226.7 | +5/-0 | 5 | 0 | 14.4482 | 15.5792 | 31.2 | 8.16 | 37.2 | 9.05 | -0.46% | -0.31% | 0.03 | 47 | DNR | yes | MC4 | black/silver | black/white | 65 | 39.1 | 1.8 | 17.6493 | 46 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-270M-66 | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 34.1 | 7.92 | 40.7 | 8.85 | -0.46% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-275M-66 | mono | 275 |  | +3/-0 | 3 | 0 |  |  | 34.21 | 8.04 | 40.81 | 8.98 | -0.46% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-280M-66 | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 34.32 | 8.16 | 40.9 | 9.12 | -0.46% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-285M-66 | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 34.43 | 8.28 | 40.99 | 9.26 | -0.46% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-270P-66 | poly | 270 |  | +3/-0 | 3 | 0 |  |  | 34.5 | 7.83 | 41.16 | 8.48 | -0.46% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-275P-66 | poly | 275 |  | +3/-0 | 3 | 0 |  |  | 34.9 | 7.88 | 41.34 | 8.51 | -0.46% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-285P-66 | poly | 285 |  | +3/-0 | 3 | 0 |  |  | 35.29 | 8.08 | 41.71 | 8.67 | -0.46% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-270P-72 | poly | 270 | 240.1 | +3/-0 | 3 | 0 | 12.8972 | 13.8442 | 35.81 | 7.54 | 44.14 | 8.29 | -0.45% | -0.34% | 0.05 | 47 | DNR | yes | MC4 | black/silver | black/white | 77.1 | 39.1 | 2 | 20.9348 | 59.5 | 7 |  | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-275P-72 | poly | 275 | 244.7 | +3/-0 | 3 | 0 | 13.136 | 14.1006 | 36.14 | 7.61 | 44.37 | 8.3 | -0.45% | -0.34% | 0.05 | 47 | DNR | yes | MC4 | black/silver | black/white | 77.1 | 39.1 | 2 | 20.9348 | 59.5 | 7 |  | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-280P-72 | poly | 280 | 249.3 | +3/-0 | 3 | 0 | 13.3749 | 14.357 | 36.56 | 7.66 | 44.57 | 8.33 | -0.45% | -0.34% | 0.05 | 47 | DNR | yes | MC4 | black/silver | black/white | 77.1 | 39.1 | 2 | 20.9348 | 59.5 | 7 |  | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-285P-72 | poly | 285 | 253.8 | +3/-0 | 3 | 0 | 13.6137 | 14.6133 | 36.97 | 7.71 | 44.65 | 8.36 | -0.45% | -0.34% | 0.05 | 47 | DNR | yes | MC4 | black/silver | black/white | 77.1 | 39.1 | 2 | 20.9348 | 59.5 | 7 |  | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-290M-72 | mono | 290 | 256.1 | +5/-0 | 5 | 0 | 13.8525 | 14.8697 | 36.9 | 7.86 | 44.8 | 8.42 | -0.46% | -0.31% | 0.03 | 47 | DNR | yes | MC4 | black/silver | black/white | 77.1 | 39.1 | 2 | 20.9348 | 59.5 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-290P-72 | poly | 290 | 258.4 | +3/-0 | 3 | 0 | 13.8525 | 14.8697 | 37.14 | 7.81 | 44.84 | 8.38 | -0.45% | -0.34% | 0.05 | 47 | 15 | yes | MC4 | black/silver | black/white | 77.1 | 39.1 | 2 | 20.9348 | 59.5 | 7 |  | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-295P-72 | mono | 295 |  | +3/-0 | 3 | 0 |  |  | 37.58 | 7.85 | 44.92 | 8.47 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-295M-72 | mono | 295 | 260.7 | +5/-0 | 5 | 0 | 14.0914 | 15.1261 | 37.2 | 7.93 | 45 | 8.48 | -0.46% | -0.31% | 0.03 | 47 | DNR | yes | MC4 | black/silver | black/white | 77.1 | 39.1 | 2 | 20.9348 | 59.5 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-300P-72 | poly | 300 |  | +3/-0 | 3 | 0 |  |  | 38.08 | 7.88 | 45.1 | 8.49 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-305P-72 | poly | 305 |  | +3/-0 | 3 | 0 |  |  | 38.82 | 7.96 | 45.3 | 8.52 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-310P-72 | poly | 310 |  | +3/-0 | 3 | 0 |  |  | 38.47 | 8.06 | 45.47 | 8.6 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-300M-72 | mono | 300 | 265.3 | +5/-0 | 5 | 0 | 14.3302 | 15.3825 | 37.6 | 7.98 | 45.3 | 8.52 | -0.46% | -0.31% | 0.03 | 47 | DNR | yes | MC4 | black/silver | black/white | 77.1 | 39.1 | 2 | 20.9348 | 59.5 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-305M-72 | mono | 305 | 269.8 | +5/-0 | 5 | 0 | 14.569 | 15.6388 | 37.8 | 8.07 | 45.5 | 8.58 | -0.46% | -0.31% | 0.03 | 47 | DNR | yes | MC4 | black/silver | black/white | 77.1 | 39.1 | 2 | 20.9348 | 59.5 | 7 |  | Check |  | Perlight_Solar
Perlight Solar | PLM-310M-72 | mono | 310 |  | +3/-0 | 3 | 0 |  |  | 37.31 | 8.31 | 45.81 | 8.87 | -0.45% | -0.34% |  |  | DNR | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-315M-72 | mono | 315 |  | +3/-0 | 3 | 0 |  |  | 37.64 | 8.37 | 45.91 | 8.94 | -0.45% | -0.34% |  |  | DNR | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-320M-72 | mono | 320 |  | +3/-0 | 3 | 0 |  |  | 37.79 | 8.47 | 46.01 | 8.97 | -0.45% | -0.34% |  |  | DNR | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-340M-84 | mono | 340 |  | +3/-0 | 3 | 0 |  |  | 43.32 | 7.85 | 51.62 | 8.54 | -0.46% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-345M-84 | mono | 345 |  | +3/-0 | 3 | 0 |  |  | 43.41 | 7.95 | 51.79 | 8.61 | -0.46% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-350M-84 | mono | 350 |  | +3/-0 | 3 | 0 |  |  | 43.54 | 8.04 | 51.94 | 8.97 | -0.46% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-340P-84 | poly | 340 |  | +3/-0 | 3 | 0 |  |  | 43.59 | 7.8 | 52.34 | 8.34 | -0.46% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-345P-84 | poly | 345 |  | +3/-0 | 3 | 0 |  |  | 43.62 | 7.91 | 52.44 | 8.41 | -0.46% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-350P-84 | poly | 350 |  | +3/-0 | 3 | 0 |  |  | 43.7 | 8.01 | 52.51 | 8.49 | -0.46% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
Perlight Solar | PLM-355P-84 | poly | 355 |  | +3/-0 | 3 | 0 |  |  | 43.83 | 8.1 | 52.62 | 8.61 | -0.46% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Perlight_Solar
REC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | REC
REC | REC215AE |  | 215 |  | +5/-0 | 5 | 0 |  |  | 28.2 | 7.7 | 36.3 | 8.3 | -0.46% | -0.34% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | REC
REC | REC220AE |  | 220 |  | +5/-0 | 5 | 0 |  |  | 25.5 | 7.8 | 36.5 | 8.4 | -0.46% | -0.34% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | REC
REC | REC225AE |  | 225 |  | +5/-0 | 5 | 0 |  |  | 28.7 | 7.9 | 36.7 | 8.5 | -0.46% | -0.34% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | REC
REC | REC230AE |  | 230 |  | +5/-0 | 5 | 0 |  |  | 29 | 8 | 36.9 | 8.6 | -0.46% | -0.34% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | REC
REC | REC235AE |  | 235 |  | +5/-0 | 5 | 0 |  |  | 29.3 | 8.1 | 37.1 | 8.6 | -0.46% | -0.34% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | REC
REC | REC240AE |  | 240 |  | +5/-0 | 5 | 0 |  |  | 29.6 | 8.2 | 37.4 | 8.7 | -0.46% | -0.34% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | REC
REC | SCM210 | poly | 210 |  | +3/-3 | 3 | -3 | 11.8243 | 12.7 | 28.2 | 7.5 | 36.1 | 8.1 | -0.452% | -0.29% |  |  | 15 |  | MC |  |  | 65.55 | 39.02 | 1.69 | 17.7622 | 48.5 | 5.25 |  | Check |  | REC
REC | SCM215 | poly | 215 |  | +3/-3 | 3 | -3 | 12.1059 | 13 | 28.3 | 7.6 | 36.3 | 8.1 | -0.452% | -0.29% |  |  | 15 |  | MC |  |  | 65.55 | 39.02 | 1.69 | 17.7622 | 48.5 | 5.25 |  | Check |  | REC
REC | REC220PE | poly | 220 | 195.2 | +2/-0 | 2 | 0 | 12.3858 | 13.3 | 28.7 | 7.7 | 36.6 | 8.2 | -0.46% | -0.32% | 0.011 | 47.9 | 15 | yes | Radox | black | white | 65.55 | 39.02 | 1.5 | 17.7622 | 39.6 | 5.25 |  | Check |  | REC
REC | REC225PE | poly | 225 | 199.7 | +5/-0 | 5 | 0 | 12.6673 | 13.6 | 28.9 | 7.8 | 36.2 | 8.3 | -0.43% | -0.33% | 0.011 | 47.9 | 15 | yes | Radox | black | white | 65.55 | 39.02 | 1.5 | 17.7622 | 39.6 | 5.25 |  | Check | 2012-03-28 | REC
REC | REC230PE | poly | 230 | 204.3 | +5/-0 | 5 | 0 | 12.9488 | 13.9 | 29.2 | 7.9 | 36.5 | 8.4 | -0.43% | -0.33% | 0.011 | 47.9 | 15 | yes | Radox | black | white | 65.55 | 39.02 | 1.5 | 17.7622 | 39.6 | 5.25 |  | Check | 2012-03-28 | REC
REC | REC235PE | poly | 235 | 208.8 | +5/-0 | 5 | 0 | 13.2303 | 14.2 | 29.6 | 8 | 36.7 | 8.5 | -0.43% | -0.33% | 0.011 | 47.9 | 15 | yes | Radox | black | white | 65.55 | 39.02 | 1.5 | 17.7622 | 39.6 | 5.25 |  | Check | 2012-03-28 | REC
REC | REC240PE | poly | 240 | 213.4 | +5/-0 | 5 | 0 | 13.5118 | 14.5 | 29.7 | 8.17 | 36.8 | 8.75 | -0.43% | -0.33% | 0.011 | 47.9 | 25 | yes | Radox | black | white | 65.55 | 39.02 | 1.5 | 17.7622 | 39.6 | 5.25 |  | Check | 2014-05-23 | REC
REC | REC245PE | poly | 245 | 217.3 | +5/-0 | 5 | 0 | 13.7933 | 14.8 | 30.1 | 8.23 | 37.1 | 8.8 | -0.43% | -0.33% | 0.011 | 47.9 | 25 | yes | Radox | black | white | 65.55 | 39.02 | 1.5 | 17.7622 | 39.6 | 5.25 |  | Check | 2014-05-23 | REC
REC | REC250PE | poly | 250 | 221.9 | +5/-0 | 5 | 0 | 14.0748 | 15.1 | 30.2 | 8.3 | 37.4 | 8.86 | -0.43% | -0.33% | 0.011 | 47.9 | 25 | yes | Radox | black | white | 65.55 | 39.02 | 1.5 | 17.7622 | 39.6 | 5.25 |  | Check | 2014-05-23 | REC
REC | REC255PE | poly | 255 |  | +5/-0 | 5 | 0 |  |  | 30.5 | 8.42 | 37.6 | 8.95 | -0.4% | -0.27% |  |  | 25 | [11 empty] | 1000 | 2014-05-23 | REC
REC | REC260PE | poly | 260 |  | +5/-0 | 5 | 0 |  |  | 30.7 | 8.5 | 37.8 | 9.01 | -0.4% | -0.27% |  |  | 25 | [11 empty] | 1000 | 2014-05-23 | REC
REC | REC265PE | poly | 265 |  | +5/-0 | 5 | 0 |  |  | 30.9 | 8.58 | 38.1 | 9.08 | -0.4% | -0.27% |  |  | 25 | [11 empty] | 1000 | 2014-05-23 | REC
REC | REC270PE | poly | 270 |  | +5/-0 | 5 | 0 |  |  | 31.2 | 8.66 | 38.4 | 9.18 | -0.4% | -0.27% |  |  | 25 | [11 empty] | 1000 | 2017-10-12 | REC
REC | REC275PE | poly | 275 |  | +5/-0 | 5 | 0 |  |  | 31.5 | 8.74 | 38.7 | 9.25 | -0.4% | -0.27% |  |  | 25 | [11 empty] | 1000 | 2017-10-12 | REC
REC | REC295PE72 | multi | 295 |  | +5-0 | 5 | 0 |  |  | 36.1 | 8.23 | 44.5 | 8.8 | -0.4% | -0.27% |  |  | 20 | [11 empty] | Check | 2015-11-25 | REC
REC | REC300PE72 | multi | 300 |  | +5/-0 | 5 | 0 |  |  | 36.4 | 8.33 | 44.9 | 8.86 | -0.4% | -0.27% |  |  | 20 | [11 empty] | Check | 2015-11-25 | REC
REC | REC305PE72 | multi | 305 |  | +5/-0 | 5 | 0 |  |  | 36.6 | 8.42 | 45.1 | 8.95 | -0.4% | -0.27% |  |  | 20 | [11 empty] | Check | 2015-11-25 | REC
REC | REC310PE72 | multi | 310 |  | +5/-0 | 5 | 0 |  |  | 36.7 | 8.53 | 45.3 | 9.02 | -0.4% | -0.27% |  |  | 20 | [11 empty] | Check | 2015-11-25 | REC
REC | REC315PE72 | multi | 315 |  | +5/-0 | 5 | 0 |  |  | 36.8 | 8.62 | 45.5 | 9.09 | -0.4% | -0.27% |  |  | 20 | [11 empty] | Check | 2015-11-25 | REC
REC | REC295PE72 XV | multi | 295 |  | +5/-0 | 5 | 0 |  |  | 36.1 | 8.23 | 44.5 | 8.8 | -0.4% | -0.27% |  |  | 20 | [11 empty] | Check | 2015-12-03 | REC
REC | REC300PE72 XV | multi | 300 |  | +5/-0 | 5 | 0 |  |  | 36.4 | 8.33 | 44.9 | 8.86 | -0.4% | -0.27% |  |  | 20 | [11 empty] | Check | 2015-12-03 | REC
REC | REC305PE72 XV | multi | 305 |  | +5/-0 | 5 | 0 |  |  | 36.6 | 8.42 | 45.1 | 8.95 | -0.4% | -0.27% |  |  | 20 | [11 empty] | Check | 2015-12-03 | REC
REC | REC310PE72 XV | multi | 310 |  | +5/-0 | 5 | 0 |  |  | 36.7 | 8.53 | 45.3 | 9.02 | -0.4% | -0.27% |  |  | 20 | [11 empty] | Check | 2015-12-03 | REC
REC | REC315PE72 XV | multi | 315 |  | +5/-0 | 5 | 0 |  |  | 36.8 | 8.62 | 45.5 | 9.09 | -0.4% | -0.27% |  |  | 20 | [11 empty] | Check | 2015-12-03 | REC
REC | REC320PE72 XV | multi | 320 |  | +5/-0 | 5 | 0 |  |  | 36.9 | 8.68 | 45.7 | 9.17 | -0.4% | -0.27% |  |  | 20 | [11 empty] | Check | 2015-12-03 | REC
REC | REC325PE72 XV | multi | 325 |  | +5/-0 | 5 | 0 |  |  | 37.1 | 8.77 | 45.9 | 9.23 | -0.4% | -0.27% |  |  | 20 | [11 empty] | Check | 2015-12-03 | REC
REC | REC330TP72 | multi | 330 |  | +5/-0 | 5 | 0 |  |  | 38.1 | 8.67 | 46 | 9.22 | -0.36% | -0.3% |  |  | 25 | [11 empty] | 1500 | 2017-10-12 | REC
REC | REC335TP72 | multi | 335 |  | +5/-0 | 5 | 0 |  |  | 38.3 | 8.75 | 46.2 | 9.27 | -0.36% | -0.3% |  |  | 25 | [11 empty] | 1500 | 2017-10-12 | REC
REC | REC340TP72 | multi | 340 |  | +5/-0 | 5 | 0 |  |  | 38.5 | 8.84 | 46.3 | 9.32 | -0.36% | -0.3% |  |  | 25 | [11 empty] | 1500 | 2017-10-12 | REC
REC | REC345TP72 | multi | 345 |  | +5/-0 | 5 | 0 |  |  | 38.7 | 8.92 | 46.5 | 9.36 | -0.36% | -0.3% |  |  | 25 | [11 empty] | 1500 | 2017-10-12 | REC
REC | REC330TP2S 72 | multi | 330 |  | +5/-0 | 5 | 0 |  |  | 38.1 | 8.67 | 46 | 9.22 | -0.36% | -0.3% |  |  | 25 | [11 empty] | 1500 | 2017-10-12 | REC
REC | REC335TP2S 72 | multi | 335 |  | +5/-0 | 5 | 0 |  |  | 38.3 | 8.75 | 46.2 | 9.52 | -0.36% | -0.3% |  |  | 25 | [11 empty] | 1500 | 2017-10-12 | REC
REC | REC340TP2S 72 | multi | 340 |  | +5/-0 | 5 | 0 |  |  | 38.5 | 8.84 | 46.3 | 9.58 | -0.36% | -0.3% |  |  | 25 | [11 empty] | 1500 | 2017-10-12 | REC
REC | REC345TP2S 72 | multi | 345 |  | +5/-0 | 5 | 0 |  |  | 38.7 | 8.92 | 46.5 | 9.64 | -0.36% | -0.3% |  |  | 25 | [11 empty] | 1500 | 2017-10-12 | REC
REC | REC350TP2S 72 | multi | 350 |  | +5/-0 | 5 | 0 |  |  | 38.9 | 9 | 46.7 | 9.72 | -0.36% | -0.3% |  |  | 25 | [11 empty] | 1500 | 2017-10-12 | REC
REC | REC355TP2S 72 | multi | 355 | 323.4 | +5/-0 | 5 | 0 |  |  | 39.1 | 9.09 | 46.8 | 9.78 | -0.36% | -0.3% |  |  | 25 | [11 empty] | 1500 | 2017-10-12 | REC
REC | REC275TP2 | multi | 275 |  | +5/-0 | 5 | 0 |  |  | 31.5 | 8.74 | 38.2 | 9.52 | -0.36% | -0.3% |  |  | 25 |  |  |  |  | 65.94 | 39.25 | 1.5 |  | 40.8 |  |  | 1000 | 2018-06-01 | REC
REC | REC280TP2 | multi | 280 |  | +5/-0 | 5 | 0 |  |  | 31.7 | 8.84 | 38.4 | 9.61 | -0.36% | -0.3% |  |  | 25 |  |  |  |  | 65.94 | 39.25 | 1.5 |  | 40.8 |  |  | 1000 | 2018-06-01 | REC
REC | REC285TP2 | multi | 285 |  | +5/-0 | 5 | 0 |  |  | 31.9 | 8.95 | 38.6 | 9.66 | -0.36% | -0.3% |  |  | 25 |  |  |  |  | 65.94 | 39.25 | 1.5 |  | 40.8 |  |  | 1000 | 2018-06-01 | REC
REC | REC290TP2 | multi | 290 |  | +5/-0 | 5 | 0 |  |  | 32.1 | 9.05 | 38.8 | 9.71 | -0.36% | -0.3% |  |  | 25 |  |  |  |  | 65.94 | 39.25 | 1.5 |  | 40.8 |  |  | 1000 | 2018-06-01 | REC
REC | REC295TP2 | multi | 295 |  | +5/-0 | 5 | 0 |  |  | 32.3 | 9.14 | 39 | 9.76 | -0.36% | -0.3% |  |  | 25 |  |  |  |  | 65.94 | 39.25 | 1.5 |  | 40.8 |  |  | 1000 | 2018-06-01 | REC
REC | REC300TP2 | multi | 300 |  | +5/-0 | 5 | 0 |  |  | 32.5 | 9.24 | 39.2 | 9.82 | -0.36% | -0.3% |  |  | 25 |  |  |  |  | 65.94 | 39.25 | 1.5 |  | 40.8 |  |  | 1000 | 2018-06-01 | REC
REC | REC275TP2 BLK2 | multi | 275 |  | +5/-0 | 5 | 0 |  |  | 31.6 | 8.71 | 38.2 | 9.28 | -0.36% | -0.3% |  |  | 25 |  |  |  |  | 65.94 | 39.25 | 1.5 |  | 40.8 |  |  | 1000 | 2018-06-01 | REC
REC | REC280TP2 BLK2 | multi | 280 |  | +5/-0 | 5 | 0 |  |  | 31.8 | 8.82 | 38.4 | 9.39 | -0.36% | -0.3% |  |  | 25 |  |  |  |  | 65.94 | 39.25 | 1.5 |  | 40.8 |  |  | 1000 | 2018-06-01 | REC
REC | REC285TP2 BLK2 | multi | 285 |  | +5/-0 | 5 | 0 |  |  | 32 | 8.92 | 38.6 | 9.49 | -0.36% | -0.3% |  |  | 25 |  |  |  |  | 65.94 | 39.25 | 1.5 |  | 40.8 |  |  | 1000 | 2018-06-01 | REC
REC | REC265TP | multi | 265 |  | +5/-0 | 5 | 0 |  |  | 31.1 | 8.53 | 38.3 | 9.21 | -0.36% | -0.3% |  |  | 25 |  |  |  |  | 65.5 | 39 | 1.5 |  | 39.5 |  |  | 1000 | 2018-06-01 | REC
REC | REC270TP | multi | 270 |  | +5/-0 | 5 | 0 |  |  | 31.2 | 8.66 | 38.6 | 9.29 | -0.36% | -0.3% |  |  | 25 |  |  |  |  | 65.5 | 39 | 1.5 |  | 39.5 |  |  | 1000 | 2018-06-01 | REC
REC | REC275TP | multi | 275 |  | +5/-0 | 5 | 0 |  |  | 31.4 | 8.76 | 38.8 | 9.4 | -0.36% | -0.3% |  |  | 25 |  |  |  |  | 65.5 | 39 | 1.5 |  | 39.5 |  |  | 1000 | 2018-06-01 | REC
REC | REC280TP | multi | 280 |  | +5/-0 | 5 | 0 |  |  | 31.9 | 8.78 | 39.2 | 9.44 | -0.36% | -0.3% |  |  | 25 |  |  |  |  | 65.5 | 39 | 1.5 |  | 39.5 |  |  | 1000 | 2018-06-01 | REC
REC | REC285TP | multi | 285 |  | +5/-0 | 5 | 0 |  |  | 32.1 | 8.9 | 39.5 | 9.54 | -0.36% | -0.3% |  |  | 25 |  |  |  |  | 65.5 | 39 | 1.5 |  | 39.5 |  |  | 1000 | 2018-06-01 | REC
ReneSola | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | ReneSola
ReneSola | JC195F-24/Db | mono | 195 |  | +5/-0 | 5 | 0 |  |  | 36.7 | 5.32 | 45 | 5.61 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2013-10-01 | ReneSola
ReneSola | JC200F-24/Db | mono | 200 |  | +5/-0 | 5 | 0 |  |  | 37.1 | 5.41 | 45.3 | 5.7 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2013-10-01 | ReneSola
ReneSola | JC205F-24/Db | mono | 205 |  | +5/-0 | 5 | 0 |  |  | 37.2 | 5.51 | 45.4 | 5.79 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2013-10-01 | ReneSola
ReneSola | JC210F-24/Db | mono | 210 |  | +5/-0 | 5 | 0 |  |  | 37.4 | 5.62 | 45.6 | 5.88 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2013-10-01 | ReneSola
ReneSola | JC190S-24/Db | mono | 190 |  | +5/-0 | 5 | 0 |  |  | 36.6 | 5.19 | 44.9 | 5.49 | -0.43% | -0.31% |  |  | 15 | -0.0019 | -0.0007 |  |  | 16 | 0.0005 | 0.0017 |  |  | 17 |  | Check | 2013-08-27 | ReneSola
ReneSola | JC195S-24/Db | mono | 195 |  | +5/-0 | 5 | 0 |  |  | 36.7 | 5.32 | 45 | 5.61 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2013-08-27 | ReneSola
ReneSola | JC200S-24/Db | mono | 200 |  | +5/-0 | 5 | 0 |  |  | 37.1 | 5.41 | 45.3 | 5.7 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2013-08-27 | ReneSola
ReneSola | JC205S-24/Db | mono | 205 |  | +5/-0 | 5 | 0 |  |  | 37.2 | 5.51 | 45.4 | 5.79 | -0.43% | -0.31% |  |  | 15 | [11 empty] | Check | 2013-08-27 | ReneSola
ReneSola | JC250M-24/Bb(h) | poly | 250 |  | +5/-0 | 5 | 0 |  |  | 30.1 | 8.31 | 37.4 | 8.83 | -0.4% | -0.3% |  |  | 20 | [11 empty] | Check | 2013-08-27 | ReneSola
ReneSola | JC255M-24/Bb(h) | poly | 255 |  | +5/-0 | 5 | 0 |  |  | 30.4 | 8.39 | 37.5 | 8.86 | -0.4% | -0.3% |  |  | 20 | [11 empty] | Check | 2013-08-27 | ReneSola
ReneSola | JC260M-24/Bb(h)(s) | poly | 260 |  | +5/-0 | 5 | 0 |  |  | 30.5 | 8.53 | 37.6 | 8.95 | -0.4% | -0.3% |  |  | 20 | [11 empty] | Check | 2013-08-27 | ReneSola
ReneSola | JC265M-24/Bbs | poly | 265 |  | +5/-0 | 5 | 0 |  |  | 30.6 | 8.66 | 37.7 | 9.03 | -0.4% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | ReneSola
ReneSola | JC270M-24/Bbs | poly | 270 |  | +5/-0 | 5 | 0 |  |  | 31 | 8.71 | 38.1 | 9.1 | -0.4% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | ReneSola
ReneSola | JC260S-24/Bb | mono | 260 |  | +5/-0 | 5 | 0 |  |  | 30.4 | 8.55 | 37.7 | 9.1 | -0.43% | -0.31% |  |  | 20 | [11 empty] | Check | 2013-08-27 | ReneSola
ReneSola | JC265S-24/Bb | mono | 265 |  | +5/-0 | 5 | 0 |  |  | 30.6 | 8.66 | 37.9 | 9.19 | -0.43% | -0.31% |  |  | 20 | [11 empty] | Check | 2013-08-27 | ReneSola
ReneSola | JC270S-24/Bb | mono | 270 |  | +5/-0 | 5 | 0 |  |  | 30.8 | 8.77 | 38.1 | 9.28 | -0.43% | -0.31% |  |  | 20 | [11 empty] | Check | 2013-08-27 | ReneSola
ReneSola | JC295M-24/Ab | poly | 295 |  | +5/-0 | 5 | 0 |  |  | 36.3 | 8.13 | 44.7 | 8.62 | -0.4% | -0.3% |  |  | 20 | [11 empty] | Check | 2014-03-05 | ReneSola
ReneSola | JC300M-24/Ab(h) | poly | 300 |  | +5/-0 | 5 | 0 |  |  | 36.6 | 8.2 | 44.8 | 8.69 | -0.4% | -0.3% |  |  | 20 | [11 empty] | Check | 2013-08-27 | ReneSola
ReneSola | JC305M-24/Ab(h) | poly | 305 |  | +5/-0 | 5 | 0 |  |  | 36.6 | 8.33 | 44.9 | 8.73 | -0.4% | -0.3% |  |  | 20 | [11 empty] | Check | 2013-08-27 | ReneSola
ReneSola | JC310M-24/Ab(h) | poly | 310 |  | +5/-0 | 5 | 0 |  |  | 37 | 8.38 | 45 | 8.8 | -0.4% | -0.3% |  |  | 20 | [11 empty] | Check | 2013-08-27 | ReneSola
ReneSola | JC290M-24/Abh | poly | 290 |  | +5/-0 | 5 | 0 |  |  | 35.9 | 8.08 | 44.6 | 8.56 | -0.39% | -0.29% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ReneSola
ReneSola | JC295M-24/Abh | poly | 295 |  | +5/-0 | 5 | 0 |  |  | 36.3 | 8.13 | 44.7 | 8.62 | -0.39% | -0.29% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ReneSola
ReneSola | JC300M-24/Abh | poly | 300 |  | +5/-0 | 5 | 0 |  |  | 36.6 | 8.2 | 44.8 | 8.69 | -0.39% | -0.29% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ReneSola
ReneSola | JC305M-24/Abh | poly | 305 |  | +5/-0 | 5 | 0 |  |  | 36.6 | 8.33 | 44.9 | 8.73 | -0.39% | -0.29% |  |  | 20 | [11 empty] | Check | 2014-05-23 | ReneSola
ReneSola | JC310M-24/Abs | poly | 310 |  | +5/-0 | 5 | 0 |  |  | 37 | 8.38 | 45 | 8.8 | -0.4% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | ReneSola
ReneSola | JC315M-24/Abs | poly | 315 |  | +5/-0 | 5 | 0 |  |  | 37.3 | 8.45 | 45.4 | 8.88 | -0.4% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | ReneSola
ReneSola | JC320M-24/Abs | poly | 320 |  | +5/-0 | 5 | 0 |  |  | 37.4 | 8.56 | 45.6 | 9 | -0.4% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | ReneSola
Renogy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Renogy
Renogy | RNG-230P | poly | 230 | 206.9 | +3/-0 | 3 | 0 | 13.0651 | 14.08 | 30.36 | 7.58 | 36.36 | 7.9 | -0.44% | -0.3% | 0.04 | 47 | 14 | yes | MC4 | silver | white | 65 | 39 | 2 | 17.6042 | 41.9 | 10 |  | Check |  | Renogy
Renogy | RNG-235P | poly | 235 | 211.5 | +3/-0 | 3 | 0 | 13.3491 | 14.39 | 30.68 | 7.66 | 37.08 | 8.34 | -0.44% | -0.3% | 0.04 | 47 | 14 | yes | MC4 | silver | white | 65 | 39 | 2 | 17.6042 | 41.9 | 10 |  | Check |  | Renogy
Renogy | RNG 240P | poly | 240 |  | +3/-0 | 3 | 0 |  |  | 29.8 | 8.05 | 37 | 8.69 | -0.44% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Renogy
Renogy | RNG 245P | poly | 245 |  | +3/-0 | 3 | 0 |  |  | 29.9 | 8.19 | 37.1 | 8.74 | -0.44% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Renogy
Renogy | RNG 250P | poly | 250 |  | +3/-0 | 3 | 0 |  |  | 30.2 | 8.29 | 37.3 | 8.84 | -0.44% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Renogy
Renogy | RNG 255P | poly | 255 |  | +3/-0 | 3 | 0 |  |  | 30.3 | 8.43 | 37.4 | 8.98 | -0.44% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Renogy
Renogy | RNG 260P | poly | 260 |  | +3/-0 | 3 | 0 |  |  | 30.4 | 8.56 | 37.6 | 9.09 | -0.44% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Renogy
Renogy | RNG-240D | mono | 240 | 213 | +3/-0 | 3 | 0 | 13.6331 | 14.69 | 30.81 | 7.79 | 37.36 | 8.45 | -0.44% | -0.3% | 0.04 | 47 | 14 | yes | MC4 | silver | white | 65 | 39 | 2 | 17.6042 | 41.9 | 10 |  | Check |  | Renogy
Renogy | RNG-270P | poly | 270 | 246.4 | +3/-0 | 3 | 0 | 12.9639 | 13.96 | 36.29 | 7.44 | 43.63 | 7.86 | -0.44% | -0.3% | 0.04 | 47 | 14 | yes | MC4 | silver | white | 76.9 | 39 | 2 | 20.8271 | 50.6 | 10 |  | Check |  | Renogy
Renogy | RNG-280D | mono | 280 | 248.4 | +3/-0 | 3 | 0 | 13.444 | 14.47 | 37.01 | 7.57 | 43.99 | 8.14 | -0.44% | -0.3% | 0.04 | 47 | 14 | yes | MC4 | silver | white | 76.9 | 39 | 2 | 20.8271 | 50.6 | 10 |  | Check |  | Renogy
Renogy | RNG-290P | poly | 290 |  | +3/-0 | 3 | 0 |  |  | 37.23 | 7.79 | 44.72 | 8.45 | -0.44% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Renogy
Renogy | RNG-295P | poly | 295 |  | +3/-0 | 3 | 0 |  |  | 37.25 | 7.92 | 45.62 | 8.51 | -0.44% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Renogy
Renogy | RNG-300P | poly | 300 |  | +3/-0 | 3 | 0 |  |  | 37.46 | 8.01 | 46.12 | 8.56 | -0.44% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Renogy
Renogy | RNG-305P | poly | 305 |  | +3/-0 | 3 | 0 |  |  | 37.63 | 8.1 | 46.33 | 8.62 | -0.44% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Renogy
Renogy | RNG-310P | poly | 310 |  | +3/-0 | 3 | 0 |  |  | 37.7 | 8.2 | 46.46 | 8.7 | -0.44% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Renogy
Ritek | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Ritek
Ritek | MM300T | mono | 300 | 269.7 | +/-3 | 3 | -3 | 14.2893 | 15.39 | 35.4 | 8.42 | 44.5 | 8.87 | -0.46% | -0.34% | 0.05 | 46.5 | 15 | yes | tyco | silver | white | 77.4 | 39.06 | 1.65 | 20.9948 | 57 | 2 |  | Check |  | Ritek
Ritek | PM200 | poly | 200 | 177.7 | +/-3 | 3 | -3 | 11.199 | 12.06 | 27.64 | 7.25 | 35.92 | 7.9 | -0.52% | -0.37% | 0.07 | 44.2 | 15 | yes | tyco | silver | white | 65.32 | 39.37 | 1.65 | 17.8587 | 46 | 2 |  | Check |  | Ritek
Ritek | PM205 | poly | 205 | 182.3 | +/-3 | 3 | -3 | 11.479 | 12.36 | 27.81 | 7.3 | 36.03 | 7.94 | -0.52% | -0.37% | 0.07 | 44.2 | 15 | yes | tyco | silver | white | 65.32 | 39.37 | 1.65 | 17.8587 | 46 | 2 |  | Check |  | Ritek
Ritek | PM210 | poly | 210 | 186.3 | +/-3 | 3 | -3 | 11.759 | 12.83 | 27.98 | 7.54 | 36.03 | 8.1 | -0.376% | -0.3% | 0.123 | 49.1 | 15 | yes | tyco | silver | white | 65.32 | 39.37 | 1.65 | 17.8587 | 46 | 2 |  | Check |  | Ritek
Ritek | PM215 | poly | 215 | 190.9 | +/-3 | 3 | -3 | 12.039 | 13.14 | 28.21 | 7.7 | 36.21 | 8.25 | -0.376% | -0.3% | 0.123 | 49.1 | 15 | yes | tyco | silver | white | 65.32 | 39.37 | 1.65 | 17.8587 | 46 | 2 |  | Check |  | Ritek
Ritek | PM220 | poly | 220 | 195.4 | +/-3 | 3 | -3 | 12.3189 | 13.44 | 28.38 | 7.76 | 36.33 | 8.31 | -0.376% | -0.3% | 0.123 | 49.1 | 15 | yes | tyco | silver | white | 65.32 | 39.37 | 1.65 | 17.8587 | 46 | 2 |  | Check |  | Ritek
Ritek | PM225 | poly | 225 | 200 | +/-3 | 3 | -3 | 12.5989 | 13.75 | 28.66 | 7.86 | 36.69 | 8.43 | -0.376% | -0.3% | 0.123 | 49.1 | 15 | yes | tyco | silver | white | 65.32 | 39.37 | 1.65 | 17.8587 | 46 | 2 |  | Check |  | Ritek
Ritek | PM230 | poly | 230 | 205.4 | +/-3 | 3 | -3 | 12.8789 | 14.05 | 29 | 7.98 | 36.99 | 8.53 | -0.376% | -0.3% | 0.123 | 49.1 | 15 | yes | tyco/MC4 | silver/black | white | 65.32 | 39.37 | 1.65 | 17.8587 | 46 | 2 |  | Check |  | Ritek
Ritek | PM235 | poly | 235 | 209.9 | +/-3 | 3 | -3 | 13.1589 | 14.36 | 29.29 | 8.07 | 37.28 | 8.61 | -0.376% | -0.3% | 0.123 | 49.1 | 15 | yes | tyco | silver | white | 65.32 | 39.37 | 1.65 | 17.8587 | 46 | 2 |  | Check |  | Ritek
Ritek | PM240 | poly | 240 | 214.5 | +/-3 | 3 | -3 | 13.4389 | 14.66 | 29.29 | 8.23 | 37.16 | 8.79 | -0.376% | -0.3% | 0.123 | 49.1 | 15 | yes | tyco | silver | white | 65.32 | 39.37 | 1.65 | 17.8587 | 46 | 2 |  | Check |  | Ritek
Ritek | PM280 | poly | 280 | 250.2 | +/-3 | 3 | -3 | 13.3367 | 14.36 | 34.8 | 7.98 | 44.38 | 8.53 | -0.376% | -0.3% | 0.123 | 49.1 | 15 | yes | tyco | silver | white | 77.4 | 39.06 | 1.65 | 20.9948 | 57 | 2 |  | Check |  | Ritek
Ritek | PM60-6RT-250 | poly | 250 |  | +5/-0 | 5 | 0 |  |  | 30.69 | 8.15 | 38.12 | 8.63 | -0.38% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | PM60-6RT-255 | poly | 255 |  | +5/-0 | 5 | 0 |  |  | 30.88 | 8.32 | 38.7 | 8.94 | -0.38% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | PM60-6RT-260 | poly | 260 |  | +5/-0 | 5 | 0 |  |  | 31.21 | 8.36 | 38.85 | 9.01 | -0.38% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | PM60-6RT-265 | poly | 265 |  | +5/-0 | 5 | 0 |  |  | 31.47 | 8.46 | 39.13 | 9.06 | -0.38% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | PM60-6RT-270 | poly | 270 |  | +5/-0 | 5 | 0 |  |  | 31.74 | 8.55 | 39.41 | 9.15 | -0.38% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | PM72-6RT-285 | poly | 285 |  | +5/-0 | 5 | 0 |  |  | 35.94 | 7.95 | 45.09 | 8.52 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | MM60-6RT-260 | mono | 260 |  | +5/-0 | 5 | 0 |  |  | 30.12 | 8.74 | 37.87 | 9.1 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | MM60-6RT-265 | mono | 265 |  | +5/-0 | 5 | 0 |  |  | 30.28 | 8.78 | 38.06 | 9.15 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | MM60-6RT-270 | mono | 270 |  | +5/-0 | 5 | 0 |  |  | 30.58 | 8.87 | 38.44 | 9.24 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | MM60-6RT-275 | mono | 275 |  | +5/-0 | 5 | 0 |  |  | 30.84 | 8.97 | 38.75 | 9.33 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | MM60-6RT-280 | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 31.1 | 9.06 | 39.08 | 9.41 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | MM60-6RT-285 | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 31.37 | 9.16 | 39.4 | 9.49 | -0.4% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | MM72-6RT-300 | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 35.7 | 8.5 | 44.62 | 8.91 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | MM72-6RT-305 | mono | 305 |  | +5/-0 | 5 | 0 |  |  | 35.61 | 8.61 | 44.76 | 8.97 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | MM72-6RT-310 | mono | 310 |  | +5/-0 | 5 | 0 |  |  | 36.06 | 8.72 | 45.33 | 9.08 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | MM72-6RT-315 | mono | 315 |  | +5/-0 | 5 | 0 |  |  | 36.15 | 8.74 | 45.45 | 9.11 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | MM72-6RT-320 | mono | 320 |  | +5/-0 | 5 | 0 |  |  | 36.6 | 8.85 | 46.01 | 9.22 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | MM72-6RT-325 | mono | 325 |  | +5/-0 | 5 | 0 |  |  | 36.69 | 8.87 | 46.13 | 9.24 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | MM72-6RT-330 | mono | 330 |  | +5/-0 | 5 | 0 |  |  | 37.01 | 8.97 | 46.52 | 9.33 | -0.45% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Ritek
Ritek | MM72-6RT-335 | mono | 335 |  | +5/-0 | 5 | 0 |  |  | 37.28 | 9.04 | 46.86 | 9.4 | -0.45% | -0.34% |  |  | 15 | [11 empty] | 1000 | 2015-12-03 | Ritek
Samsung Electronics | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Samsung_Electronics
Samsung Electronics | LPC235SM-02 | mono | 235 | 207.8 | +1.3/-0 | 1.3 | 0 | 13.6202 | DNR | 29.9 | 7.88 | 37.2 | 8.47 | -0.519% | -0.00341% | 0.025 | 45 | 15 | DNR | MC4 | silver | white | 64.2 | 38.7 | 1.81 | 17.2538 | 44.09 | 5 |  | Check |  | Samsung_Electronics
Samsung Electronics | LPC238SM-02 | mono | 238 | 210.6 | +1.3/-0 | 1.3 | 0 | 13.7941 | DNR | 30 | 7.94 | 37.3 | 8.51 | -0.519% | -0.00341% | 0.025 | 45 | 15 | DNR | MC4 | silver | white | 64.2 | 38.7 | 1.81 | 17.2538 | 44.09 | 5 |  | Check |  | Samsung_Electronics
Samsung Electronics | LPC241SM-02 | mono | 241 | 213.3 | +1.2/-0 | 1.2 | 0 | 13.968 | DNR | 30.1 | 8.01 | 37.4 | 8.54 | -0.519% | -0.00341% | 0.025 | 45 | 15 | DNR | MC4 | silver | white | 64.2 | 38.7 | 1.81 | 17.2538 | 44.09 | 5 |  | Check |  | Samsung_Electronics
Samsung Electronics | LPC244SM | mono | 244 |  | +3/-3 | 3 | -3 | 14.1631 |  | 30.3 | 8.07 | 37.5 | 8.58 | -0.48% | -0.35% |  |  | 15 |  | Tyco |  |  | 64.17 | 38.66 | 1.81 | 17.2279 | 41 | 5 |  | Check |  | Samsung_Electronics
Samsung Electronics | LPC247SM | mono | 247 |  | +3/-3 | 3 | -3 | 14.3372 |  | 30.4 | 8.14 | 37.6 | 8.62 | -0.48% | -0.35% |  |  | 15 |  | Tyco |  |  | 64.17 | 38.66 | 1.81 | 17.2279 | 41 | 5 |  | Check |  | Samsung_Electronics
Samsung Electronics | LPC250SM | mono | 250 |  | +3/-3 | 3 | -3 | 14.5114 |  | 30.5 | 8.2 | 37.6 | 8.66 | -0.48% | -0.35% |  |  | 15 |  | Tyco |  |  | 64.17 | 38.66 | 1.81 | 17.2279 | 41 | 5 |  | Check |  | Samsung_Electronics
Samsung Electronics | PV-MBA1BG247 | mono | 247 |  | +2/-0 | 2 | 0 |  |  | 30.5 | 8.11 | 37.6 | 8.64 | -0.438% | -0.325% |  |  | 15 | [11 empty] | Check | 2012-07-24 | Samsung_Electronics
Samsung Electronics | PV-MBA1CG247 | mono | 247 |  | +2/-0 | 2 | 0 |  |  | 30.5 | 8.11 | 37.6 | 8.64 | -0.438% | -0.325% |  |  | 15 | [11 empty] | Check | 2012-07-24 | Samsung_Electronics
Samsung Electronics | PV-MBA1BG250 | mono | 250 |  | +2/-0 | 2 | 0 |  |  | 30.7 | 8.15 | 37.8 | 8.68 | -0.438% | -0.325% |  |  | 15 | [11 empty] | Check | 2012-07-24 | Samsung_Electronics
Samsung Electronics | PV-MBA1CG250 | mono | 250 |  | +2/-0 | 2 | 0 |  |  | 30.7 | 8.15 | 37.8 | 8.68 | -0.438% | -0.325% |  |  | 15 | [11 empty] | Check | 2012-07-24 | Samsung_Electronics
Samsung Electronics | PV-MBA1BG255 | mono | 255 |  | +2/-0 | 2 | 0 |  |  | 31.1 | 8.21 | 38.1 | 8.75 | -0.438% | -0.325% |  |  | 15 | [11 empty] | Check | 2012-07-24 | Samsung_Electronics
Samsung Electronics | PV-MBA1CG255 | mono | 255 |  | +2/-0 | 2 | 0 |  |  | 31.1 | 8.21 | 38.1 | 8.75 | -0.438% | -0.325% |  |  | 15 | [11 empty] | Check | 2012-07-24 | Samsung_Electronics
Sainty Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Sainty_Solar
Sainty Solar | GES-6M235 | mono | 235 |  | +5/-0 | +5 | 0 |  |  | 29.5 | 7.98 | 36.9 | 8.51 | -0.44% | -0.32% |  |  | 13 | [11 empty] | Check | 2013-12-20 | Sainty_Solar
Sainty Solar | GES-6M240 | mono | 240 |  | +5/-0 | +5 | 0 |  |  | 29.6 | 8.11 | 37 | 8.65 | -0.44% | -0.32% |  |  | 13 | [11 empty] | Check | 2013-12-20 | Sainty_Solar
Sainty Solar | GES-6M245 | mono | 245 |  | +5/-0 | +5 | 0 |  |  | 29.8 | 8.24 | 37.2 | 8.97 | -0.44% | -0.32% |  |  | 13 | [11 empty] | Check | 2013-12-20 | Sainty_Solar
Sainty Solar | GES-6M250 | mono | 250 |  | +5/-0 | +5 | 0 |  |  | 29.9 | 8.36 | 37.3 | 8.94 | -0.44% | -0.32% |  |  | 13 | [11 empty] | Check | 2013-12-20 | Sainty_Solar
Sainty Solar | GES-6M255 | mono | 255 |  | +5/-0 | +5 | 0 |  |  | 30 | 8.5 | 37.4 | 9.09 | -0.44% | -0.32% |  |  | 13 | [11 empty] | Check | 2013-12-20 | Sainty_Solar
Sainty Solar | GES-6P280 | poly | 280 |  | +1.5/-0 | 1.5 | 0 |  |  | 35.9 | 7.8 | 44.3 | 8.41 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Sainty_Solar
Sainty Solar | GES-6P285 | poly | 285 |  | +1.5/-0 | 1.5 | 0 |  |  | 36 | 7.91 | 44.5 | 8.47 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Sainty_Solar
Sainty Solar | GES-6P290 | poly | 290 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.2 | 8.01 | 44.7 | 8.54 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Sainty_Solar
Sainty Solar | GES-6P295 | poly | 295 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.4 | 8.11 | 44.9 | 8.61 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Sainty_Solar
Sainty Solar | GES-6P300 | poly | 300 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.5 | 8.21 | 45.1 | 8.67 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Sainty_Solar
Sainty Solar | GES-6P305 | poly | 305 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.7 | 8.31 | 45.3 | 8.74 | -0.42% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Sainty_Solar
Sainty Solar | GES-6M290 | mono | 290 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.8 | 7.89 | 45.4 | 8.58 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Sainty_Solar
Sainty Solar | GES-6M295 | mono | 295 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.8 | 8.02 | 45.4 | 8.66 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Sainty_Solar
Sainty Solar | GES-6M300 | mono | 300 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.8 | 8.16 | 45.4 | 8.72 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Sainty_Solar
Sainty Solar | GES-6M305 | mono | 305 |  | +1.5/-0 | 1.5 | 0 |  |  | 37.3 | 8.19 | 46 | 8.83 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Sainty_Solar
Sainty Solar | GES-6M310 | mono | 310 |  | +1.5/-0 | 1.5 | 0 |  |  | 37.4 | 8.28 | 46.2 | 8.87 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Sainty_Solar
Sainty Solar | GES-6M315 | mono | 315 |  | +1.5/-0 | 1.5 | 0 |  |  | 37.5 | 8.4 | 45.3 | 8.95 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-03 | Sainty_Solar
Scheuten Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Scheuten_Solar
Scheuten Solar | P6-54 190W | poly | 190 | 170.5 | +10/-0 | 10 | 0 | 11.7668 | 12.6667 | 25.5 | 7.43 | 32.6 | 7.98 | -0.48% | -0.34% | 0.07 | 44 | 15 | yes | MC4 | silver/black | black | 59.06 | 39.37 | 1.65 | 16.1472 | 44.09 | 10 |  | Check |  | Scheuten_Solar
Scheuten Solar | P6-54 195W | poly | 195 | 175.1 | +10/-0 | 10 | 0 | 12.0764 | 13 | 25.7 | 7.57 | 32.8 | 8.1 | -0.48% | -0.34% | 0.07 | 44 | 15 | yes | MC4 | silver/black | black | 59.06 | 39.37 | 1.65 | 16.1472 | 44.09 | 10 |  | Check |  | Scheuten_Solar
Scheuten Solar | P6-54 200W | poly | 200 | 179.7 | +10/-0 | 10 | 0 | 12.3861 | 13.3333 | 25.9 | 7.71 | 33 | 8.22 | -0.48% | -0.34% | 0.07 | 44 | 15 | yes | MC4 | silver/black | black | 59.06 | 39.37 | 1.65 | 16.1472 | 44.09 | 10 |  | Check |  | Scheuten_Solar
Scheuten Solar | P6-54 205W | poly | 205 | 184.3 | +10/-0 | 10 | 0 | 12.6957 | 13.6667 | 26.1 | 7.85 | 33.1 | 8.33 | -0.48% | -0.34% | 0.07 | 44 | 15 | yes | MC4 | silver/black | black | 59.06 | 39.37 | 1.65 | 16.1472 | 44.09 | 10 |  | Check |  | Scheuten_Solar
Scheuten Solar | STP6-280/72 | poly | 280 |  | +5/-0 | 5 | 0 |  |  | 35.6 | 7.89 | 44.1 | 8.41 | -0.47% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Scheuten_Solar
Scheuten Solar | STP6-285/72 | poly | 285 |  | +5/-0 | 5 | 0 |  |  | 35.7 | 7.99 | 44.2 | 8.53 | -0.47% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Scheuten_Solar
Scheuten Solar | STP6-290/72 | poly | 290 |  | +5/-0 | 5 | 0 |  |  | 35.8 | 8.1 | 44.3 | 8.65 | -0.47% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Scheuten_Solar
Scheuten Solar | STP6-295/72 | poly | 295 |  | +5/-0 | 5 | 0 |  |  | 35.9 | 8.22 | 44.4 | 8.78 | -0.47% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Scheuten_Solar
Scheuten Solar | STP6-300/72 | poly | 300 |  | +/-3 | 3 | -3 |  |  | 35.9 | 8.35 | 44.5 | 8.92 | -0.47% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Scheuten_Solar
Scheuten Solar | STM6-285/72 | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 35.68 | 7.99 | 44.35 | 8.52 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Scheuten_Solar
Scheuten Solar | STM6-290/72 | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 35.72 | 8.12 | 44.5 | 8.61 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Scheuten_Solar
Scheuten Solar | STM6-295/72 | mono | 295 |  | +5/-0 | 5 | 0 |  |  | 35.78 | 8.25 | 44.8 | 8.72 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Scheuten_Solar
Scheuten Solar | STM6-300/72 | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 36.24 | 8.28 | 44.92 | 8.81 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Scheuten_Solar
Scheuten Solar | STM6-305/72 | mono | 305 |  | +/-3 | 3 | -3 |  |  | 36.75 | 8.3 | 45.12 | 8.88 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-30 | Scheuten_Solar
SCHOTT Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | SCHOTT_Solar
SCHOTT Solar | ASE 250 | ribbon | 250 |  | +2/-2 | 2 | -2 | 9.6 | 10.3 | 48.5 | 5.15 | 60 | 5.9 | -0.47% | -0.35% |  |  | 10 |  | MC |  |  | 74.5 | 50.5 | 2 | 26.1267 | 107 | 1 |  | Check |  | SCHOTT_Solar
SCHOTT Solar | ASE 260 | ribbon | 260 |  | +2/-2 | 2 | -2 | 10 | 10.7 | 48.7 | 5.5 | 60 | 5.9 | -0.47% | -0.35% |  |  | 10 |  | MC |  |  | 74.5 | 50.5 | 2 | 26.1267 | 107 | 1 |  | Check |  | SCHOTT_Solar
SCHOTT Solar | ASE 270 | ribbon | 270 |  | +2/-2 | 2 | -2 | 10.3 | 11.1 | 49.1 | 5.5 | 60 | 6.05 | -0.47% | -0.35% |  |  | 10 |  | MC |  |  | 74.5 | 50.5 | 2 | 26.1267 | 107 | 1 |  | Check |  | SCHOTT_Solar
SCHOTT Solar | ASE 280 | ribbon | 280 |  | +4/-4 | 4 | -4 | 10.7 | 11.5 | 49.6 | 5.65 | 61.9 | 6.2 | -0.47% | -0.35% |  |  | 12 |  | MC |  |  | 74.5 | 50.5 | 2 | 26.1267 | 107 | 1 |  | Check |  | SCHOTT_Solar
SCHOTT Solar | ASE 290 | ribbon | 290 |  | +4/-4 | 4 | -4 | 11.1 | 11.9 | 50.1 | 5.8 | 62.5 | 6.4 | -0.47% | -0.35% |  |  | 12 |  | MC |  |  | 74.5 | 50.5 | 2 | 26.1267 | 107 | 1 |  | Check |  | SCHOTT_Solar
SCHOTT Solar | ASE 300 | ribbon | 300 |  | +4/-4 | 4 | -4 | 11.5 | 12.4 | 50.6 | 5.9 | 63.2 | 6.5 | -0.47% | -0.35% |  |  | 12 |  | MC |  |  | 74.5 | 50.5 | 2 | 26.1267 | 107 | 1 |  | Check |  | SCHOTT_Solar
SCHOTT Solar | ASE 310 | ribbon | 310 |  | +4/-4 | 4 | -4 | 11.9 | 12.8 | 51.1 | 6.1 | 63.8 | 6.5 | -0.47% | -0.35% |  |  | 12 |  | MC |  |  | 74.5 | 50.5 | 2 | 26.1267 | 107 | 1 |  | Check |  | SCHOTT_Solar
SCHOTT Solar | ASITHRU-1-L |  | 35 | [5 empty] | 6.2 | 68 | 0.37 | 93 | 0.49 | -0.2% | -0.31% |  |  | NA |  |  |  |  | 38.4 | 22.7 |  | 6.0533 |  |  |  | Check |  | SCHOTT_Solar
SCHOTT Solar | POLY 220 | poly | 220 | 198.5 | +2/-0 | 2 | 0 | 12.2164 | 13.15 | 29.7 | 7.41 | 36.5 | 8.15 | -0.44% | -0.32% | 0.04 | 45.5 | 15 | yes | tyco | silver | white | 66.34 | 39.09 | 1.97 | 18.0085 | 41.5 | 5 |  | Check |  | SCHOTT_Solar
SCHOTT Solar | POLY 225 | poly | 225 | 203.1 | +2/-0 | 2 | 0 | 12.4941 | 13.4489 | 29.8 | 7.55 | 36.7 | 8.24 | -0.44% | -0.32% | 0.04 | 45.5 | 15 | yes | tyco | silver | white | 66.34 | 39.09 | 1.97 | 18.0085 | 41.5 | 5 |  | Check |  | SCHOTT_Solar
SCHOTT Solar | POLY 230 | poly | 230 | 207.7 | +2/-0 | 2 | 0 | 12.7717 | 13.7478 | 30 | 7.66 | 36.9 | 8.33 | -0.44% | -0.32% | 0.04 | 45.5 | 15 | yes | tyco | silver | white | 66.34 | 39.09 | 1.97 | 18.0085 | 41.5 | 5 |  | Check |  | SCHOTT_Solar
SCHOTT Solar | POLY 235 | poly | 235 | 212.4 | +2/-0 | 2 | 0 | 13.0494 | 14.0466 | 30.2 | 7.78 | 37.1 | 8.42 | -0.44% | -0.32% | 0.04 | 45.5 | 15 | yes | tyco | silver | white | 66.34 | 39.09 | 1.97 | 18.0085 | 41.5 | 5 |  | Check |  | SCHOTT_Solar
SCHOTT Solar | POLY 240 | poly | 240 | 217 | +2/-0 | 2 | 0 | 13.327 | 14.3455 | 30.4 | 7.9 | 37.3 | 8.52 | -0.44% | -0.32% | 0.04 | 45.5 | 15 | yes | tyco | silver | white | 66.34 | 39.09 | 1.97 | 18.0085 | 41.5 | 5 |  | Check |  | SCHOTT_Solar
Schüco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Schüco
Schüco | 232 923 | poly | 165 |  | +5/-5 | 5 | -5 | 11.1 | 11.9 | 23.4 | 7.06 | 29.7 | 7.73 | -0.45% | -0.34% |  |  | 15 |  | MC |  |  | 65.28 | 32.83 | 1.81 | 14.8829 | 37.5 | 5 |  | Check |  | Schüco
Schüco | 232 924 | poly | 170 |  | +5/-5 | 5 | -5 | 11.4 | 12.3 | 23.7 | 7.19 | 29.9 | 7.83 | -0.45% | -0.34% |  |  | 15 |  | MC |  |  | 65.28 | 32.83 | 1.81 | 14.8829 | 37.5 | 5 |  | Check |  | Schüco
Schüco | 256 186 | poly | 180 |  | +5/-5 | 5 | -5 | 12.1 | 13 | 24.2 | 7.45 | 30.4 | 8.03 | -0.45% | -0.34% |  |  | 15 |  | MC |  |  | 65.28 | 32.83 | 1.81 | 14.8829 | 37.5 | 5 |  | Check |  | Schüco
Schüco | 256 695 | poly | 175 |  | +5/-5 | 5 | -5 | 11.8 | 12.7 | 23.9 | 7.32 | 30.2 | 7.93 | -0.45% | -0.34% |  |  | 15 |  | MC |  |  | 65.28 | 32.83 | 1.81 | 14.8829 | 37.5 | 5 |  | Check |  | Schüco
Schüco | MPE 170 MS 05 | mono | 170 |  | +5/-0 | 5 | 0 | 12.4 | 13.3 | 35.9 | 4.74 | 44.5 | 5.12 | -0.4% | -0.38% |  |  | 10 |  | MC |  |  | 62.2 | 31.81 | 1.57 | 13.7402 | 33.1 | 5 |  | Check |  | Schüco
Schüco | MPE 175 MS 05 | mono | 175 |  | +5/-0 | 5 | 0 | 12.7 | 13.7 | 36 | 4.86 | 44.8 | 5.17 | -0.4% | -0.38% |  |  | 10 |  | MC |  |  | 62.2 | 31.81 | 1.57 | 13.7402 | 33.1 | 5 |  | Check |  | Schüco
Schüco | MPE 180 MS 05 | mono | 180 |  | +5/-0 | 5 | 0 | 13.1 | 14.1 | 36 | 5 | 45 | 5.2 | -0.4% | -0.38% |  |  | 10 |  | MC |  |  | 62.2 | 31.81 | 1.57 | 13.7402 | 33.1 | 5 |  | Check |  | Schüco
Schüco | MPE 185 MS 05 |  | 185 |  | +5/-0 | 5 | 0 |  |  | 36.5 | 5.09 | 44.8 | 5.47 | -0.33% | -0.33% |  |  | 10 | [7 empty] | 0 |  |  |  | Check |  | Schüco
Schüco | MPE 240 MS 08 | mono | 240 |  | +5/-0 | 5 | 0 |  | 14.7 | 30.7 | 7.96 | 37.7 | 8.54 | -0.48% | -0.36% |  |  | 15 | [11 empty] | Check |  | Schüco
Schüco | MPE 245 MS 08 | mono | 245 |  | +5/-0 | 5 | 0 |  | 15 | 30.7 | 8.09 | 37.8 | 8.6 | -0.48% | -0.36% |  |  | 15 | [11 empty] | Check |  | Schüco
Schüco | MPE 250 MS 08 | mono | 250 |  | +5/-0 | 5 | 0 |  | 15.3 | 30.8 | 8.22 | 37.9 | 8.66 | -0.48% | -0.36% |  |  | 15 | [11 empty] | Check |  | Schüco
Schüco | MPE 255 MS 08 | mono | 255 |  | +5/-0 | 5 | 0 |  | 15.6 | 30.9 | 8.34 | 37.9 | 8.72 | -0.48% | -0.36% |  |  | 15 | [11 empty] | Check |  | Schüco
Schüco | MPE 260 MS 08 | mono | 260 |  | +5/-0 | 5 | 0 |  | 15.9 | 30.9 | 8.47 | 37.9 | 8.78 | -0.48% | -0.36% |  |  | 15 | [11 empty] | Check |  | Schüco
Schüco | MPE 210 PS 04 | poly | 210 | 192.3 | +5/-0 | 5 | 0 | 11.876 | 13.1 | 28.9 | 7.26 | 36.2 | 7.91 | -0.35% | -0.35% | 0.06 | 45 | 15 | no | MC4 | silver | white | 65.04 | 39.15 | 1.77 | 17.6828 | 44.1 | 5 |  | Check |  | Schüco
Schüco | MPE 215 PS 04 | poly | 215 | 197 | +5/-0 | 5 | 0 | 12.1587 | 13.4 | 29 | 7.43 | 36.5 | 8.01 | -0.35% | -0.35% | 0.06 | 45 | 15 | no | MC4 | silver | white | 65.04 | 39.15 | 1.77 | 17.6828 | 44.1 | 5 |  | Check |  | Schüco
Schüco | MPE 220 PS 04 | poly | 220 |  | +5/-0 | 5 | 0 | 12.7 |  | 29.3 | 7.52 | 36.6 | 8.09 | -0.45% | -0.35% |  |  | 15 |  | MC4 |  |  | 64.49 | 38.66 | 1.57 | 17.3138 | 44.1 | 5 |  | Check |  | Schüco
Schüco | MPE 220 PS 09 | poly | 220 | 199.5 | +5/-0 | 5 | 0 | 12.4415 | 13.4 | 29.7 | 7.38 | 36.8 | 8.12 | -0.46% | -0.35% | 0.05 | 43 | 15 | no | MC4 | silver | white | 65.04 | 39.15 | 1.77 | 17.6828 | 44.1 | 5 |  | Check |  | Schüco
Schüco | MPE 225 PS 04 | poly | 225 |  | +5/-0 | 5 | 0 | 13 |  | 29.5 | 7.63 | 36.7 | 8.19 | -0.45% | -0.35% |  |  | 15 |  | MC4 |  |  | 64.49 | 38.66 | 1.57 | 17.3138 | 44.1 | 5 |  | Check |  | Schüco
Schüco | MPE 225 PS 09 | poly | 225 | 204.1 | +5/-0 | 5 | 0 | 12.7243 | 13.7 | 29.8 | 7.55 | 36.9 | 8.27 | -0.46% | -0.35% | 0.05 | 43 | 15 | no | MC4 | silver | white | 65.04 | 39.15 | 1.77 | 17.6828 | 44.1 | 5 |  | Check |  | Schüco
Schüco | MPE 230 PS 04 | poly | 230 |  | +5/-0 | 5 | 0 | 13.3 |  | 29.8 | 7.71 | 36.8 | 8.34 | -0.45% | -0.35% |  |  | 15 |  | MC4 |  |  | 64.49 | 38.66 | 1.57 | 17.3138 | 44.1 | 5 |  | Check |  | Schüco
Schüco | MPE 230 PS 09 | poly | 230 | 208.8 | +5/-0 | 5 | 0 | 13.007 | 14 | 29.8 | 7.69 | 37 | 8.43 | -0.46% | -0.35% | 0.05 | 43 | 15 | no | MC4 | silver | white | 65.04 | 39.15 | 1.77 | 17.6828 | 44.1 | 5 |  | Check |  | Schüco
Schüco | MPE 235 PS 09 |  | 235 |  | +5/-0 | 5 | 0 |  |  | 29.85 | 7.84 | 37.11 | 8.58 | -0.46% | -0.35% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | Schüco
Schüco | MPE 230 PS 08 | poly | 230 |  | +5/-0 | 5 | 0 |  | 13.8 | 29.04 | 8.04 | 36.89 | 8.6 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2012-05-24 | Schüco
Schüco | MPE 235 PS 08 | poly | 235 |  | +5/-0 | 5 | 0 |  | 14.1 | 29.35 | 8.09 | 37.19 | 8.67 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2012-05-24 | Schüco
Schüco | MPE 240 PS 08 | poly | 240 |  | +5/-0 | 5 | 0 |  | 14.4 | 29.65 | 8.11 | 37.44 | 8.68 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2012-05-24 | Schüco
Schüco | MPE 245 PS 08 | poly | 245 |  | +5/-0 | 5 | 0 |  | 14.7 | 30.05 | 8.17 | 37.7 | 8.74 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2012-05-24 | Schüco
Schüco | MPE 310 MP 02 | mono | 310 | 274.9 | +/-3 | 3 | -3 | 10.69 | 11.5 | 72.3 | 4.3 | 88.1 | 4.65 | -0.37% | -0.34% | 0.09 | 46 | 10 | no | MC4 | bronze | black | 84.72 | 49.29 | 3.66 | 28.9989 | 108.03 | 5 |  | Check |  | Schüco
Schüco | MPE 320 MP 02 | mono | 320 | 284 | +/-3 | 3 | -3 | 11.0349 | 11.9 | 72.3 | 4.4 | 88.1 | 4.75 | -0.37% | -0.34% | 0.09 | 46 | 10 | no | MC4 | bronze | black | 84.72 | 49.29 | 3.66 | 28.9989 | 108.03 | 5 |  | Check |  | Schüco
Schüco | S 330-PMU-2 | mono | 330 |  | +3/-3 | 3 | -3 | 11.4 | 12.2 | 72.4 | 4.5 | 88.6 | 4.8 | -0.37% | -0.34% |  |  | 10 |  | MC |  |  | 84.72 | 49.29 | 3.66 | 28.9989 | 108.03 | 5 |  | Check |  | Schüco
Schüco | SPV 200 SMAU-1 | mono | 200 | 179 | +/-3 | 3 | -3 | 12.6839 | 13.7 | 25.4 | 7.89 | 33.5 | 8.24 | -0.5% | -0.33% | 0.03 | 43 | 15 | no | Tyco | black | white | 58.31 | 38.94 | 1.87 | 15.768 | 37.92 | 5 |  | Check |  | Schüco
Schüco | SPV 210 SMAU-1 | mono | 210 | 188.2 | +/-3 | 3 | -3 | 13.3181 | 14.3 | 26.3 | 7.98 | 33.7 | 8.35 | -0.5% | -0.33% | 0.03 | 43 | 15 | no | Tyco | black | white | 58.31 | 38.94 | 1.87 | 15.768 | 37.92 | 5 |  | Check |  | Schüco
Schuco | MPE 340 AL 01 | amorphous | 340 |  | +5/-0 | 5 | 0 |  |  | 151.2 | 2.25 | 191 | 2.88 | -0.12% | -0.2% |  |  | 6 | [11 empty] | Check | 2015-12-04 | Schüco
Schuco | MPE 350 AL 01 | amorphous | 350 |  | +5/-0 | 5 | 0 |  |  | 153.5 | 2.28 | 193 | 2.92 | -0.12% | -0.2% |  |  | 6 | [11 empty] | Check | 2015-12-04 | Schüco
Schuco | MPE 360 AL 01 | amorphous | 360 |  | +5/-0 | 5 | 0 |  |  | 155 | 2.32 | 196 | 2.98 | -0.12% | -0.2% |  |  | 6 | [11 empty] | Check | 2015-12-04 | Schüco
Schuco | MPE 370 AL 01 | amorphous | 370 |  | +5/-0 | 5 | 0 |  |  | 156.7 | 2.36 | 199 | 3.03 | -0.12% | -0.2% |  |  | 6 | [11 empty] | Check | 2015-12-04 | Schüco
Schuco | MPE 380 AL 01 | amorphous | 380 |  | +5/-0 | 5 | 0 |  |  | 158.1 | 2.4 | 201 | 3.08 | -0.12% | -0.2% |  |  | 6 | [11 empty] | Check | 2015-12-04 | Schüco
SET-Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | SET_Solar
SET-Solar | SETA-125-175W-72M | mono | 175 | 154.6 | +/-3 | 3 | -3 | 12.7404 | 13.71 | 35.2 | 4.95 | 44.4 | 5.2 | -0.576% | -0.44% | 0.072 | 50 | 12 | DNR | MC4 | silver | white | 62.2 | 31.8 | 1.57 | 13.7358 | 35.3 | 5 |  | Check |  | SET_Solar
SET-Solar | SETA-125-180W-72M | mono | 180 | 159.2 | +/-3 | 3 | -3 | 13.1044 | 14.1 | 35.6 | 5 | 44.6 | 5.3 | -0.576% | -0.44% | 0.072 | 50 | 12 | DNR | MC4 | silver | white | 62.2 | 31.8 | 1.57 | 13.7358 | 35.3 | 5 |  | Check |  | SET_Solar
SET-Solar | SETA-125-185W-72M | mono | 185 | 163.7 | +/-3 | 3 | -3 | 13.4684 | 14.49 | 36 | 5.05 | 44.8 | 5.35 | -0.576% | -0.44% | 0.072 | 50 | 12 | DNR | MC4 | silver | white | 62.2 | 31.8 | 1.57 | 13.7358 | 35.3 | 5 |  | Check |  | SET_Solar
SET-Solar | M3000P-250 | multi | 250 |  | +/-5 | 5 | -5 |  |  | 34.1 | 7.33 | 40.9 | 8.06 | -0.46% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | SET_Solar
SET-Solar | M3000P-255 | multi | 255 |  | +/-5 | 5 | -5 |  |  | 34.3 | 7.43 | 41.1 | 8.18 | -0.46% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | SET_Solar
SET-Solar | M3000P-260 | multi | 260 |  | +/-5 | 5 | -5 |  |  | 34.4 | 7.56 | 41.2 | 8.31 | -0.46% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | SET_Solar
SET-Solar | M3000P-265 | multi | 265 |  | +/-5 | 5 | -5 |  |  | 34.5 | 7.68 | 41.4 | 8.45 | -0.46% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | SET_Solar
SET-Solar | M3000P-270 | multi | 270 |  | +/-5 | 5 | -5 |  |  | 34.7 | 7.78 | 41.6 | 8.56 | -0.46% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | SET_Solar
SET-Solar | M3000P-275 | multi | 275 |  | +/-5 | 5 | -5 |  |  | 34.9 | 7.88 | 41.8 | 8.67 | -0.46% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | SET_Solar
SET-Solar | M3000P-280 | multi | 280 |  | +/-5 | 5 | -5 |  |  | 35.1 | 7.98 | 42.1 | 8.77 | -0.46% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | SET_Solar
Sharp | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Sharp
Sharp | ND-130UJF | poly | 130 |  | +10/-5 | 10 | -5 | 12.1566 | 13.1 | 17.4 | 7.5 | 21.9 | 8.2 | -0.485% | -0.3288% |  |  | 15 |  | J-Box |  |  | 59 | 26.1 | 1.8 | 10.6938 | 30.86 | 1 |  | Check |  | Sharp
Sharp | ND-162U1F | poly | 162 |  | +10/-5 | 10 | -5 | 11.4956 | 12.4 | 22.76 | 7.12 | 28.83 | 7.95 | -0.485% | -0.333% |  |  | 15 |  | MC |  |  | 51.9 | 39.1 | 1.81 | 14.0923 | 36.4 | 1 |  | Check |  | Sharp
Sharp | ND-167U1F | poly | 167 |  | +10/-5 | 10 | -5 | 11.8505 | 12.7 | 22.97 | 7.27 | 29.04 | 8.02 | -0.485% | -0.3306% |  |  | 15 |  | MC |  |  | 51.9 | 39.1 | 1.81 | 14.0923 | 36.4 | 1 |  | Check |  | Sharp
Sharp | ND-176U1Y | poly | 176 |  | +10/-5 | 10 | -5 | 12.3936 | 13.3 | 23.42 | 7.52 | 29.28 | 8.22 | -0.485% | -0.3279% |  |  | 15 |  | MC |  |  | 52.3 | 39.1 | 2.3 | 14.2009 | 36.4 | 1 |  | Check |  | Sharp
Sharp | ND-181U1F | poly | 181 |  | +10/-5 | 10 | -5 | 11.4339 | 12.3 | 25.8 | 7.04 | 32.4 | 7.9 | -0.485% | -0.3333% |  |  | 15 |  | MC |  |  | 58.3 | 39.1 | 2.26 | 15.8301 | 39.6 | 1 |  | Check |  | Sharp
Sharp | ND-187U1F | poly | 187 |  | +10/-5 | 10 | -5 | 11.7325 | 12.7 | 25.8 | 7.25 | 32.7 | 7.99 | -0.485% | -0.3303% |  |  | 15 |  | MC |  |  | 58.7 | 39.1 | 2.26 | 15.9387 | 39.6 | 1 |  | Check |  | Sharp
Sharp | ND-198U1F | poly | 198 |  | +10/-5 | 10 | -5 | 12.4226 | 13.4 | 26.3 | 7.52 | 32.9 | 8.23 | -0.485% | -0.3283% |  |  | 15 |  | MC |  |  | 58.7 | 39.1 | 2.3 | 15.9387 | 39.6 | 1 |  | Check |  | Sharp
Sharp | ND-200U1F | poly | 200 |  | +10/-5 | 10 | -5 | 11.4021 | 12.3 | 28.42 | 7.04 | 36.01 | 7.9 | -0.485% | -0.3332% |  |  | 15 |  | MC |  |  | 64.6 | 39.1 | 1.81 | 17.5407 | 46.3 | 1 |  | Check |  | Sharp
Sharp | ND-208U1F | poly | 208 |  | +10/-5 | 10 | -5 | 11.8581 | 12.8 | 28.71 | 7.25 | 36.3 | 7.99 | -0.485% | -0.3306% |  |  | 15 |  | MC |  |  | 64.6 | 39.1 | 1.81 | 17.5407 | 46.3 | 1 |  | Check |  | Sharp
Sharp | ND-216QCJ | poly | 216 | 190.6 | +10/-5 | 10 | -5 | 12.3142 | 13.3 | 28.9 | 7.48 | 36.5 | 8.1 | -0.485% | -0.36% | 0.053 | 47.5 | 15 | yes | MC4 | silver | white | 64.6 | 39.1 | 1.8 | 17.5407 | 44.1 | 5 |  | Check |  | Sharp
Sharp | ND-216U2 | poly | 216 |  | +10/-5 | 10 | -5 | 12.3142 | 13.3 | 28.7 | 7.53 | 36.3 | 8.35 | -0.485% | -0.3609% |  |  | 15 |  | MC |  |  | 64.6 | 39.1 | 1.8 | 17.5407 | 44.1 | 1 |  | Check |  | Sharp
Sharp | ND-220U1F | poly | 220 |  | +10/-5 | 10 | -5 | 12.5423 | 13.5 | 29.19 | 7.54 | 36.5 | 8.24 | -0.485% | -0.3288% |  |  | 15 |  | MC |  |  | 64.6 | 39.1 | 1.8 | 17.5407 | 44.1 | 1 |  | Check |  | Sharp
Sharp | ND-224QCJ | poly | 224 | 201.8 | +10/-5 | 10 | -5 | 12.7703 | 13.7 | 29.28 | 7.66 | 36.6 | 8.33 | -0.485% | -0.36% | 0.053 | 47.5 | 15 | yes | MC4 | silver | white | 64.6 | 39.1 | 1.8 | 17.5407 | 44.1 | 5 |  | Check |  | Sharp
Sharp | ND-224U2 | poly | 224 |  | +10/-5 | 10 | -5 | 12.7703 | 13.74 | 29.28 | 7.66 | 36.6 | 8.33 | -0.485% | -0.3279% |  |  | 15 |  | MC |  |  | 64.6 | 39.1 | 1.8 | 17.5407 | 44.1 | 1 |  | Check |  | Sharp
Sharp | ND-230QCJ | poly | 230 | 207.4 | +10/-5 | 10 | -5 | 13.1124 | 14.1 | 30.3 | 7.6 | 37 | 8.24 | -0.485% | -0.36% | 0.053 | 47.5 | 15 | yes | MC4 | silver | white | 64.6 | 39.1 | 1.8 | 17.5407 | 44 | 5 |  | Check |  | Sharp
Sharp | ND-H240Q2/ND-Q240Q2 | poly | 240 | 216.6 | +10/-5 | 10 | -5 | 13.6825 | 14.706 | 30.2 | 7.95 | 37.5 | 8.61 | -0.485% | -0.36% | 0.053 | 47.5 | 15 | yes | MC4 | silver | white | 64.6 | 39.1 | 1.8 | 17.5407 | 41.9 | 5 |  | Check |  | Sharp
Sharp | ND-H245Q2/ND-Q245Q2 | poly | 245 | 221.2 | +10/-5 | 10 | -5 | 13.9675 | 15 | 30.4 | 8.06 | 37.6 | 8.63 | -0.485% | -0.36% | 0.053 | 47.5 | 15 | yes | MC4 | silver | white | 64.6 | 39.1 | 1.8 | 17.5407 | 41.9 | 5 |  | Check |  | Sharp
Sharp | ND-L3EJEA | poly | 123 |  | +10/-5 | 10 | -5 | 11.5158 | 12.39 | 17.2 | 7.16 | 21.3 | 8.04 | -0.485% | -0.338% |  |  | 15 |  | J-Box |  |  | 59.02 | 26.06 | 1.81 | 10.681 | 30.86 | 1 |  | Check |  | Sharp
Sharp | ND-L5E1U | poly | 125 |  | +10/-5 | 10 | -5 | 11.703 | 12.6 | 17.2 | 7.3 | 21.7 | 8.14 | -0.485% | -0.3318% |  |  | 15 |  | MC |  |  | 59.02 | 26.06 | 1.81 | 10.681 | 30.86 | 1 |  | Check |  | Sharp
Sharp | ND-N2ECU | poly | 142 |  | +10/-5 | 10 | -5 | 11.4362 | 12.31 | 20 | 7.11 | 24.9 | 7.92 | -0.485% | -0.3373% |  |  | 15 |  | MC |  |  | 45.87 | 38.98 | 1.81 | 12.4168 | 31.96 | 1 |  | Check |  | Sharp
Sharp | ND-Q230Q2^3^ | poly | 230 | 207.4 | +10/-5 | 10 | -5 | 13.1124 | 14.1 | 30 | 7.67 | 37.1 | 8.48 | -0.485% | -0.36% | 0.053 | 47.5 | 15 | yes | MC4 | silver | white | 64.6 | 39.1 | 1.8 | 17.5407 | 41.9 | 5 |  | Check |  | Sharp
Sharp | ND-Q235Q2^2^ | poly | 235 | 212 | +10/-5 | 10 | -5 | 13.3974 | 14.4 | 30.1 | 7.81 | 37.2 | 8.59 | -0.485% | -0.36% | 0.053 | 47.5 | 15 | yes | MC4 | silver | white | 64.6 | 39.1 | 1.8 | 17.5407 | 41.9 | 5 |  | Check |  | Sharp
Sharp | NE-170U1 | poly | 170 |  | +10/-5 | 10 | -5 | 12.1395 | 13.1 | 34.8 | 4.9 | 43.2 | 5.47 | -0.485% | -0.3333% |  |  | 10 |  | MC |  |  | 62.01 | 32.52 | 1.81 | 14.0039 | 37.485 | 1 |  | Check |  | Sharp
Sharp | NT-175U1 | mono | 175 |  | +10/-5 | 10 | -5 | 12.5062 | 13.45 | 35.4 | 4.95 | 44.4 | 5.4 | -0.485% | -0.3604% |  |  | 10 |  | MC |  |  | 62 | 32.5 | 1.8 | 13.9931 | 35.3 | 1 |  | Check |  | Sharp
Sharp | NT-180U1 | mono | 180 |  | +10/-5 | 10 | -5 | 12.8635 | 13.8 | 35.86 | 5.02 | 44.8 | 5.6 | -0.485% | -0.3214% |  |  | 10 |  | MC |  |  | 62 | 32.5 | 1.81 | 13.9931 | 37.5 | 1 |  | Check |  | Sharp
Sharp | NU-Q230F4 | mono | 230 | 207.3 | +10/-5 | 10 | -5 | 13.1124 | 14.1 | 30 | 7.67 | 37 | 8.4 | -0.485% | -0.351% | 0.053 | 47.5 | 15 | yes | MC4 | black | black | 64.6 | 39.1 | 1.8 | 17.5407 | 41.9 | 5 |  | Check |  | Sharp
Sharp | NU-Q235F2 | mono | 235 | 211.9 | +10/-5 | 10 | -5 | 13.3974 | 14.4 | 30 | 7.84 | 37 | 8.6 | -0.485% | -0.351% | 0.053 | 47.5 | 15 | yes | MC4 | silver | white | 64.6 | 39.1 | 1.8 | 17.5407 | 41.9 | 5 |  | Check |  | Sharp
Sharp | NU-Q235F4 | mono | 235 | 211.9 | +10/-5 | 10 | -5 | 13.3974 | 14.4 | 30.1 | 7.81 | 37 | 8.5 | -0.485% | -0.351% | 0.053 | 47.5 | 15 | yes | MC4 | black | black | 64.6 | 39.1 | 1.8 | 17.5407 | 41.9 | 5 |  | Check |  | Sharp
Sharp | NU-Q240F2 | mono | 240 | 216.5 | +10/-5 | 10 | -5 | 13.6825 | 14.706 | 30.1 | 7.98 | 37.4 | 8.65 | -0.485% | -0.351% | 0.053 | 47.5 | 15 | yes | MC4 | silver | white | 64.6 | 39.1 | 1.8 | 17.5407 | 41.9 | 5 |  | Check |  | Sharp
Sharp | ND-F4Q295 | poly | 295 |  | +5/-0 | 5 | 0 |  |  | 34.94 | 8.45 | 44.7 | 8.87 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Sharp
Sharp | ND-F4Q300 | poly | 300 |  | +5/-0 | 5 | 0 |  |  | 35.2 | 8.52 | 45.1 | 8.94 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Sharp
Silfab Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | Silfab_Solar
Silfab Solar | SLA-M 285 | mono | 285 | 256.4 | +5/-0 | 5 | 0 |  | 17.4 | 32 | 8.91 | 39.1 | 9.47 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 65 | 38.98 | 1.5 |  | 41.89 |  |  | 1000 | 2018-11-12 | Silfab_Solar
Silfab Solar | SLA-M 290 | mono | 290 | 261.1 | +5/-0 | 5 | 0 |  | 17.8 | 32.4 | 8.97 | 39.4 | 9.54 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 65 | 38.98 | 1.5 |  | 41.89 |  |  | 1000 | 2018-11-12 | Silfab_Solar
Silfab Solar | SLA-M 300 | mono | 300 | 270.4 | +5/-0 | 5 | 0 |  | 18.8 | 32.9 | 9.26 | 40.53 | 9.76 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 65 | 38.98 | 1.5 |  | 41.89 |  |  | 1000 | 2018-11-12 | Silfab_Solar
Silfab Solar | SLA-M 310 | mono | 310 | 279.8 | +5/-0 | 5 | 0 |  | 19 | 33.05 | 9.38 | 40.25 | 9.93 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 65 | 38.98 | 1.5 |  | 41.89 |  |  | 1000 | 2018-11-12 | Silfab_Solar
Silfab Solar | SLA-M 315 | mono | 315 |  | +5/-0 | 5 | 0 |  | 19.3 | 33.4 | 9.45 | 40.35 | 9.94 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 65 | 38.98 | 1.5 |  | 41.89 |  |  | 1000 | 2018-11-12 | Silfab_Solar
Silfab Solar | SLA-M 320 | mono | 320 |  | +5/-0 | 5 | 0 |  | 19.6 | 33.7 | 9.5 | 40.45 | 9.96 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 65 | 38.98 | 1.5 |  | 41.89 |  |  | 1000 | 2018-11-12 | Silfab_Solar
Silfab Solar | SLA-M-HC 320 | mono | 320 |  | +5/-0 | 5 | 0 |  | 20 | 33.7 | 9.5 | 40.45 | 9.96 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 65.55 | 39.13 | 1.37 |  | 43 |  |  | 1000 | 2018-11-12 | Silfab_Solar
Silfab Solar | SLA-MWT 320 | mono | 320 |  | +5/-0 | 5 | 0 |  | 20 | 33.95 | 9.43 | 40.5 | 9.99 | -0.38% | -0.29% |  |  | 20 |  |  |  |  | 63.78 | 38.66 | 1.37 |  | 39.68 |  |  | 1000 | 2018-11-12 | Silfab_Solar
Silfab Solar | SLG345M | mono | 345 |  | +5/-0 | 5 | 0 |  | 17.7 | 38.7 | 8.93 | 47.3 | 9.52 | -0.38% | -0.3% |  |  | 15 | [11 empty] | Check | 2017-08-18 | Silfab_Solar
Silfab Solar | SLG360M | mono | 360 |  | +5/-0 | 5 | 0 |  | 18.5 | 39.3 | 9.2 | 47.9 | 9.71 | -0.38% | -0.3% |  |  | 15 | [11 empty] | Check | 2017-08-18 | Silfab_Solar
Silfab Solar | SLG-M 345 | mono | 345 | 306.5 | +5/-0 | 5 | 0 |  | 17.7 | 38.7 | 8.93 | 47.3 | 9.52 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 77.56 | 38.98 | 1.5 |  | 50.7 |  |  | 1000 | 2018-11-12 | Silfab_Solar
Silfab Solar | SLG-M 350 | mono | 350 | 311.1 | +5/-0 | 5 | 0 |  | 17.9 | 38.9 | 9.02 | 47.5 | 9.61 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 77.56 | 38.98 | 1.5 |  | 50.7 |  |  | 1000 | 2018-11-12 | Silfab_Solar
Silfab Solar | SLG-M 360 | mono | 360 | 320.4 | +5/-0 | 5 | 0 |  | 18.5 | 39.3 | 9.2 | 47.9 | 9.71 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 77.56 | 38.98 | 1.5 |  | 50.7 |  |  | 1000 | 2018-11-12 | Silfab_Solar
Silfab Solar | SLG-M 370 | mono | 370 | 329.7 | +5/-0 | 5 | 0 |  | 19 | 39.6 | 9.35 | 48.2 | 9.93 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 77.56 | 38.98 | 1.5 |  | 50.7 |  |  | 1000 | 2018-11-12 | Silfab_Solar
Silfab Solar | SLG-M 380 | mono | 380 |  | +5/-0 | 5 | 0 |  | 19.2 | 39.9 | 9.54 | 48.4 | 9.98 | -0.38% | -0.3% |  |  | 20 |  |  |  |  | 78.4 | 39.13 | 1.5 |  | 51.8 |  |  | 1500 | 2018-11-12 | Silfab_Solar
Silicon Energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Silicon_Energy
Silicon Energy | SiE160 | poly | 160 |  | n/a |  |  |  | n/a | 24.7 | 6.5 | 29.9 | 7.6 | -0.566% | -0.389% |  |  | 15 | [11 empty] | Check |  | Silicon_Energy
Silicon Energy | Sie165 | poly | 165 |  | n/a |  |  |  | n/a | 24.8 | 6.7 | 30 | 7.7 | -0.566% | -0.389% |  |  | 15 | [11 empty] | Check |  | Silicon_Energy
Silicon Energy | Sie170 | poly | 170 |  | n/a |  |  |  | n/a | 24.8 | 6.9 | 30 | 7.8 | -0.566% | -0.389% |  |  | 15 | [11 empty] | Check |  | Silicon_Energy
Silicon Energy | SiE175 | poly | 175 | 151.7 | +/-3 | 3 | -3 | 11.877 | 12.8 | 24.9 | 7.03 | 30.1 | 7.8 | -0.566% | -0.389% | 0.109 | 45 | 15 | no | tyco | any | none | 46 | 46.125 | 0.6 | 14.7344 | 58 | 5 |  | Check |  | Silicon_Energy
Silicon Energy | SiE180 | poly | 180 | 156.2 | +/-3 | 3 | -3 | 12.2163 | 13.2 | 25 | 7.2 | 30.2 | 7.9 | -0.566% | -0.389% | 0.109 | 45 | 15 | no | tyco | any | none | 46 | 46.125 | 0.6 | 14.7344 | 58 | 5 |  | Check |  | Silicon_Energy
Silicon Energy | SiE185 | poly | 185 | 159.9 | +/-3 | 3 | -3 | 12.5557 | 13.6 | 25.1 | 7.37 | 30.3 | 7.9 | -0.566% | -0.389% | 0.109 | 45 | 15 | no | tyco | any | none | 46 | 46.125 | 0.6 | 14.7344 | 58 | 5 |  | Check |  | Silicon_Energy
Silicon Energy | SiE190 | poly | 190 | 164.4 | +/-3 | 3 | -3 | 12.895 | 13.9 | 25.3 | 7.51 | 30.5 | 8 | -0.566% | -0.389% | 0.109 | 45 | 15 | no | tyco | any | none | 46 | 46.125 | 0.6 | 14.7344 | 58 | 5 |  | Check |  | Silicon_Energy
Silicon Energy | SiE195 | poly | 195 | 168.9 | +/-3 | 3 | -3 | 13.2344 | 14.3 | 25.5 | 7.65 | 30.5 | 8.2 | -0.566% | -0.389% | 0.109 | 45 | 15 | no | tyco | any | none | 46 | 46.125 | 0.6 | 14.7344 | 58 | 5 |  | Check |  | Silicon_Energy
Silicon Energy | SiE200 | poly | 200 | 173.4 | +/-3 | 3 | -3 | 13.5737 | 14.7 | 25.6 | 7.8 | 30.6 | 8.4 | -0.566% | -0.389% | 0.109 | 45 | 15 | no | tyco | any | none | 46 | 46.125 | 0.6 | 14.7344 | 58 | 5 |  | Check |  | Silicon_Energy
Silicon Energy | SiE-V-275 | mono | 275 |  | +/-3 | 3 | -3 |  |  | 31 | 8.94 | 39.4 | 9.58 | -0.45% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Silicon_Energy
Silicon Energy | SiE-V-280 | mono | 280 |  | +/-3 | 3 | -3 |  |  | 31.2 | 9.07 | 39.5 | 9.71 | -0.45% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Silicon_Energy
Silicon Energy | SiE-V-285 | mono | 285 |  | +/-3 | 3 | -3 |  |  | 31.3 | 9.2 | 39.7 | 9.84 | -0.45% | -0.3% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Silicon_Energy
Siliken | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Siliken
Siliken | SLK60P6L BLK/BLK 225 | poly | 225 | 199.8 | +3/-0 | 3 | 0 | 12.8602 | 13.8528 | 29.3 | 7.68 | 36.8 | 8.2 | -0.43% | -0.356% | 0.062 | 47 | 15 | yes | MC4 | black | black | 64.6 | 39 | 1.57 | 17.4958 | 41.9 | 10 |  | Check |  | Siliken
Siliken | SLK60P6L BLK/BLK 230 | poly | 230 | 205.1 | +3/-0 | 3 | 0 | 13.146 | 14.1606 | 29.5 | 7.79 | 36.9 | 8.32 | -0.43% | -0.356% | 0.062 | 47 | 15 | yes | MC4 | black | black | 64.6 | 39 | 1.57 | 17.4958 | 41.9 | 10 |  | Check |  | Siliken
Siliken | SLK60P6L BLK/BLK 235 | poly | 235 | 209.7 | +3/-0 | 3 | 0 | 13.4318 | 14.4685 | 29.5 | 7.97 | 36.9 | 8.47 | -0.43% | -0.356% | 0.062 | 47 | 15 | yes | MC4 | black | black | 64.6 | 39 | 1.57 | 17.4958 | 41.9 | 10 |  | Check |  | Siliken
Siliken | SLK60P6L BLK/BLK 240 | poly | 240 | 214.3 | +3/-0 | 3 | 0 | 13.7176 | 14.7763 | 29.6 | 8.12 | 37 | 8.61 | -0.43% | -0.356% | 0.062 | 47 | 15 | yes | MC4 | black | black | 64.6 | 39 | 1.57 | 17.4958 | 41.9 | 10 |  | Check |  | Siliken
Siliken | SLK60P6L BLK/BLK 245 | poly | 245 | 218.9 | +3/-0 | 3 | 0 | 14.0033 | 15.0842 | 29.6 | 8.27 | 37 | 8.75 | -0.43% | -0.356% | 0.062 | 47 | 15 | yes | MC4 | black | black | 64.6 | 39 | 1.57 | 17.4958 | 41.9 | 10 |  | Check |  | Siliken
Siliken | SLK60P6L BLK/BLK 250 | poly | 250 | 223.5 | +3/-0 | 3 | 0 | 14.2891 | 15.392 | 29.8 | 8.39 | 37.1 | 8.91 | -0.43% | -0.356% | 0.062 | 47 | 15 | yes | MC4 | black | black | 64.6 | 39 | 1.57 | 17.4958 | 41.9 | 10 |  | Check |  | Siliken
Siliken | SLK60P6L BLK/WHT 225 | poly | 225 | 200.9 | +3/-0 | 3 | 0 | 12.8602 | 13.8528 | 29.3 | 7.68 | 36.8 | 8.2 | -0.43% | -0.356% | 0.062 | 46 | 15 | yes | MC4 | black | white | 64.6 | 39 | 1.57 | 17.4958 | 41.9 | 10 |  | Check |  | Siliken
Siliken | SLK60P6L BLK/WHT(BLK) 220 | poly | 220 | 196.4 | +3/-0 | 3 | 0 | 12.5744 | 13.545 | 29.2 | 7.54 | 36.7 | 8.1 | -0.43% | -0.356% | 0.062 | 46 | 15 | yes | MC4 | black | white/black | 64.6 | 39 | 1.57 | 17.4958 | 41.9 | 10 |  | Check |  | Siliken
Siliken | SLK60P6L SLV(BLK)/WHT 230 | poly | 230 | 205.9 | +3/-0 | 3 | 0 | 13.146 | 14.1606 | 29.5 | 7.79 | 36.9 | 8.32 | -0.43% | -0.356% | 0.062 | 46 | 15 | yes | MC4 | silver/black | white | 64.6 | 39 | 1.57 | 17.4958 | 41.9 | 10 |  | Check |  | Siliken
Siliken | SLK60P6L SLV(BLK)/WHT 235 | poly | 235 | 210.5 | +3/-0 | 3 | 0 | 13.4318 | 14.4685 | 29.5 | 7.97 | 36.9 | 8.47 | -0.43% | -0.356% | 0.062 | 46 | 15 | yes | MC4 | silver/black | white | 64.6 | 39 | 1.57 | 17.4958 | 41.9 | 10 |  | Check |  | Siliken
Siliken | SLK60P6L SLV(BLK)/WHT 240 | poly | 240 | 215.1 | +3/-0 | 3 | 0 | 13.7176 | 14.7763 | 29.6 | 8.12 | 37 | 8.61 | -0.43% | -0.356% | 0.062 | 46 | 15 | yes | MC4 | silver/black | white | 64.6 | 39 | 1.57 | 17.4958 | 41.9 | 10 |  | Check |  | Siliken
Siliken | SLK60P6L SLV(BLK)/WHT 245 | poly | 245 | 219.8 | +3/-0 | 3 | 0 | 14.0033 | 15.0842 | 29.6 | 8.27 | 37 | 8.75 | -0.43% | -0.356% | 0.062 | 46 | 15 | yes | MC4 | silver/black | white | 64.6 | 39 | 1.57 | 17.4958 | 41.9 | 10 |  | Check |  | Siliken
Siliken | SLK60P6L SLV(BLK)/WHT 250 | poly | 250 | 224.4 | +3/-0 | 3 | 0 | 14.2891 | 15.392 | 29.8 | 8.39 | 37.1 | 8.91 | -0.43% | -0.356% | 0.062 | 46 | 15 | yes | MC4 | silver/black | white | 64.6 | 39 | 1.57 | 17.4958 | 41.9 | 10 |  | Check |  | Siliken
Siliken | SLK60P6L SLV(BLK)/WHT 255 | poly | 255 | 227.6 | +3/-0 | 3 | 0 | 14.5749 | 15.6998 | 29.8 | 8.56 | 37.1 | 9.02 | -0.43% | -0.356% | 0.062 | 46 | 15 | yes | MC4 | silver/black | white | 64.6 | 39 | 1.57 | 17.4958 | 41.9 | 10 |  | Check |  | Siliken
Siliken | SLK60P6L SLV/WHT 220 | poly | 220 | 197 | +3/-0 | 3 | 0 | 12.5744 | 13.545 | 29.2 | 7.54 | 36.7 | 8.1 | -0.43% | -0.356% | 0.062 | 46 | 15 | yes | MC4 | silver | white | 64.6 | 39 | 1.57 | 17.4958 | 41.9 | 10 |  | Check |  | Siliken
Siliken | SLK60P6L SLV/WHT 225 | poly | 225 | 201.5 | +3/-0 | 3 | 0 | 12.8602 | 13.8528 | 29.3 | 7.68 | 36.8 | 8.2 | -0.43% | -0.356% | 0.062 | 46 | 15 | yes | MC4 | silver | white | 64.6 | 39 | 1.57 | 17.4958 | 41.9 | 10 |  | Check |  | Siliken
Siliken | SLK72P6L BLK(SLV)/WHT 270 | poly | 270 |  | +3/-0 | 3 | 0 |  |  | 35.61 | 7.58 | 44.1 | 8.02 | -0.45% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Siliken
Siliken | SLK72P6L BLK(SLV)/WHT 275 | poly | 275 |  | +3/-0 | 3 | 0 |  |  | 35.64 | 7.72 | 44.1 | 8.17 | -0.45% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Siliken
Siliken | SLK72P6L BLK(SLV)/WHT 280 | poly | 280 |  | +3/-0 | 3 | 0 |  |  | 35.67 | 7.85 | 44.2 | 8.32 | -0.45% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Siliken
Siliken | SLK72P6L BLK(SLV)/WHT 285 | poly | 285 |  | +3/-0 | 3 | 0 |  |  | 35.7 | 7.98 | 44.2 | 8.47 | -0.45% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Siliken
Siliken | SLK72P6L BLK(SLV)/WHT 290 | poly | 290 |  | +3/-0 | 3 | 0 |  |  | 35.73 | 8.12 | 44.4 | 8.61 | -0.45% | -0.36% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Siliken
Siliken | SLK72P6L BLK(SLV)/WHT 295 | poly | 295 |  | +3/-0 | 3 | 0 |  |  | 35.76 | 8.25 | 44.4 | 8.75 | -0.46% | -0.36% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Siliken
Siliken | SLK72P6L BLK(SLV)/WHT 300 | poly | 300 |  | +3/-0 | 3 | 0 |  |  | 35.79 | 8.38 | 44.4 | 8.91 | -0.46% | -0.36% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Siliken
Siliken | SLK72P6L BLK(SLV)/WHT 305 | poly | 305 |  | +3/-0 | 3 | 0 |  |  | 35.82 | 8.51 | 44.5 | 9.02 | -0.46% | -0.36% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Siliken
SolarCity | [31 empty] | SolarCity
SolarCity | SC320 | mono | 320 | 301.7 | +5/-0 | 5 | 0 |  |  | 57.3 | 5.59 | 69.4 | 5.98 | -0.29% | -0.25% |  |  | 15 | [11 empty] | 600 | 2018-02-01 | SolarCity
SolarCity | SC325 | mono | 325 | 306.5 | +5/-0 | 5 | 0 |  |  | 57.6 | 5.65 | 69.6 | 6.03 | -0.29% | -0.25% |  |  | 15 | [11 empty] | 600 | 2018-02-01 | SolarCity
SolarCity | SC330 | mono | 330 | 311.3 | +5/-0 | 5 | 0 |  |  | 58 | 5.7 | 69.7 | 6.07 | -0.29% | -0.25% |  |  | 15 | [11 empty] | 600 | 2018-02-01 | SolarCity
Solar Frontier | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Solar_Frontier
Solar Frontier | SF130-L | cis | 130 |  | +10/-5 | 10 | -5 |  |  | 74 | 1.77 | 106 | 2.1 | -0.31% | -0.3% |  |  | n/a | [11 empty] | Check | 2013-09-24 | Solar_Frontier
Solar Frontier | SF140-L | cis | 140 |  | +10/-5 | 10 | -5 |  |  | 77 | 1.82 | 109 | 2.1 | -0.31% | -0.3% |  |  | n/a | [11 empty] | Check | 2013-09-24 | Solar_Frontier
Solar Frontier | SF145-L | cis | 145 |  | +10/-5 | 10 | -5 |  |  | 78 | 1.86 | 110 | 2.1 | -0.31% | -0.3% |  |  | n/a | [11 empty] | Check | 2013-09-24 | Solar_Frontier
Solar Frontier | SF150-L | cis | 150 |  | +10/-5 | 10 | -5 |  |  | 79 | 1.9 | 110 | 2.1 | -0.31% | -0.3% |  |  | n/a | [11 empty] | Check | 2013-09-24 | Solar_Frontier
Solar Frontier | SF140-S | cis | 140 |  | +10/-0 | 10 | 0 |  |  | 80.5 | 1.74 | 107 | 2.1 | -0.31% | -0.3% |  |  | n/a | [11 empty] | Check | 2013-09-24 | Solar_Frontier
Solar Frontier | SF145-S | cis | 145 |  | +10/-0 | 10 | 0 |  |  | 81 | 1.8 | 107 | 2.2 | -0.31% | -0.3% |  |  | n/a | [11 empty] | Check | 2013-09-24 | Solar_Frontier
Solar Frontier | SF150-S | cis | 150 |  | +10/-0 | 10 | 0 |  |  | 81.5 | 1.85 | 108 | 2.2 | -0.31% | -0.3% |  |  | n/a | [11 empty] | Check | 2013-09-24 | Solar_Frontier
Solar Frontier | SF155-S | cis | 155 |  | +10/-0 | 10 | 0 |  |  | 82.5 | 1.88 | 109 | 2.2 | -0.31% | -0.3% |  |  | n/a | [11 empty] | Check | 2013-09-24 | Solar_Frontier
Solar Frontier | SF160-S | cis | 160 |  | +10/-0 | 10 | 0 |  |  | 84 | 1.91 | 110 | 2.2 | -0.31% | -0.3% |  |  | n/a | [11 empty] | Check | 2013-09-24 | Solar_Frontier
Solar Frontier | SF165-S | cis | 165 |  | +10/-0 | 10 | 0 |  |  | 85.5 | 1.93 | 110 | 2.2 | -0.31% | -0.3% |  |  | n/a | [11 empty] | Check | 2013-09-24 | Solar_Frontier
Solar Frontier | SF170-S | cis | 170 |  | +5/-0 | 5 | 0 |  |  | 87.5 | 1.95 | 112 | 2.2 | -0.31% | -0.3% |  |  | n/a | [11 empty] | Check | 2015-12-04 | Solar_Frontier
Solar Frontier | SF175-S | cis | 175 |  | +5/-0 | 5 | 0 |  |  | 89.5 | 1.96 | 114 | 2.2 | -0.35% | -0.28% |  |  | n/a | [11 empty] | Check | 2015-12-04 | Solar_Frontier
Solaria | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Solaria
Solaria | Solaria 270 |  | 270 |  | +3/-2 | 3 | -2 |  |  | 35.14 | 7.69 | 44.18 | 8.04 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check |  | Solaria
Solaria | Solaria 275 |  | 275 |  | +3/-2 | 3 | -2 |  |  | 35.57 | 7.73 | 44.39 | 8.15 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check |  | Solaria
Solaria | Solaria 280 |  | 280 |  | +3/-2 | 3 | -2 |  |  | 35.92 | 7.8 | 44.57 | 8.27 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check |  | Solaria
Solaria | Solaria 285 | poly | 285 |  | +3/-2 | 3 | -2 |  |  | 37.11 | 7.68 | 45.36 | 8.17 | -0.44% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Solaria
Solar Power Inc | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Solar_Power_Inc
Solar Power Inc | SP175FM52 |  | 175 |  | +3/-3 | 3 | -3 | 12.4861 | 13.4 | 35.21 | 4.97 | 43.4 | 5.38 | -0.5% | -0.356% |  |  | 10 |  |  |  |  | 62.1 | 32.5 | 1.8 | 14.0156 | 35 |  |  | Check |  | Solar_Power_Inc
Solar Power Inc | SP200F-P12/P52/M52 |  | 200 |  | +3/-3 | 3 | -3 | 12.6671 | 13.6 | 25.41 | 7.87 | 32.3 | 8.4 | -0.5% | -0.354% |  |  | 15 |  |  |  |  | 58 | 39.2 | 1.8 | 15.7889 | 37.8 |  |  | Check |  | Solar_Power_Inc
Solar Power Inc | SP205F-P12/P52/M52 |  | 205 |  | +3/-3 | 3 | -3 | 12.9838 | 14 | 25.8 | 7.95 | 32.6 | 8.48 | -0.5% | -0.35% |  |  | 15 |  |  |  |  | 58 | 39.2 | 1.8 | 15.7889 | 37.8 |  |  | Check |  | Solar_Power_Inc
Solartech | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Solartech
Solartech | STR 220W |  | 220 |  | N/A | N/A | N/A |  |  | 29.3 | 7.51 | 36.6 | 7.85 | -0.54% | -0.38% |  |  | 15 | [11 empty] | Check | 2013-12-19 | Solartech
Solartech | STR 230W |  | 230 |  | N/A | N/A | N/A |  |  | 30.6 | 7.52 | 37.3 | 8.13 | -0.54% | -0.38% |  |  | 15 | [11 empty] | Check | 2013-12-19 | Solartech
Solartech | STR 240W |  | 240 |  | N/A | N/A | N/A |  |  | 31.8 | 7.55 | 37.9 | 8.28 | -0.54% | -0.38% |  |  | 15 | [11 empty] | Check | 2013-12-19 | Solartech
Solartech | STR 250W |  | 250 |  | N/A | N/A | N/A |  |  | 33 | 7.57 | 38.5 | 8.44 | -0.54% | -0.38% |  |  | 15 | [11 empty] | Check | 2013-12-19 | Solartech
SolarWorld | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | SolarWorld
SolarWorld | SWA 285 - BLK | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 32 | 9 | 39.2 | 9.52 | -0.39% | -0.29% |  |  | 25 | [11 empty] | 1000 | 2017-11-13 | SolarWorld
SolarWorld | SWA 290 - BLK | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 32.2 | 9.12 | 39.5 | 9.6 | -0.39% | -0.29% |  |  | 25 | [11 empty] | 1000 | 2017-11-13 | SolarWorld
SolarWorld | SWA 290 | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 31.9 | 9.2 | 39.6 | 9.75 | -0.39% | -0.29% |  |  | 25 | [11 empty] | 1000 | 2017-11-13 | SolarWorld
SolarWorld | SWA 295 | mono | 295 |  | +5/-0 | 5 | 0 |  |  | 32.3 | 9.25 | 39.8 | 9.78 | -0.39% | -0.29% |  |  | 25 | [11 empty] | 1000 | 2017-11-13 | SolarWorld
SolarWorld | SWA 300 | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 32.6 | 9.31 | 40 | 9.83 | -0.39% | -0.29% |  |  | 25 | [11 empty] | 1000 | 2017-11-13 | SolarWorld
SolarWorld | SWA 340 XL Mono | mono | 340 |  | +5/-0 | 5 | 0 |  |  | 37.1 | 9.26 | 47 | 9.81 | -0.42% | -0.29% |  |  | 25 | [11 empty] | 1500 | 2017-11-13 | SolarWorld
SolarWorld | SWA 345 XL Mono | mono | 345 |  | +5/-0 | 5 | 0 |  |  | 37.5 | 9.28 | 47.2 | 9.82 | -0.42% | -0.29% |  |  | 25 | [11 empty] | 1500 | 2017-11-13 | SolarWorld
SolarWorld | SWA 350 XL Mono | mono | 350 |  | +5/-0 | 5 | 0 |  |  | 37.8 | 9.29 | 47.3 | 9.82 | -0.42% | -0.29% |  |  | 25 | [11 empty] | 1500 | 2017-11-13 | SolarWorld
SolarWorld | SW 155 mono | mono | 155 |  | +3/-3 | 3 | -3 | 11.0413 | 11.9 | 34.8 | 4.46 | 43.6 | 4.9 | -0.47% | -0.33% |  |  | 16 |  | MC |  |  | 63.39 | 31.89 | 1.34 | 14.0382 | 33 | 2 |  | Check |  | SolarWorld
SolarWorld | SW 165 mono | mono | 165 |  | +3/-3 | 3 | -3 | 11.7536 | 12.7 | 35.3 | 4.68 | 44 | 5.1 | -0.47% | -0.33% |  |  | 16 |  | MC |  |  | 63.39 | 31.89 | 1.34 | 14.0382 | 33 | 2 |  | Check |  | SolarWorld
SolarWorld | SW 175 mono | mono | 175 |  | +3/-3 | 3 | -3 | 12.4659 | 13.4 | 35.8 | 4.89 | 44.4 | 5.3 | -0.47% | -0.33% |  |  | 16 |  | MC |  |  | 63.39 | 31.89 | 1.34 | 14.0382 | 33 | 2 |  | Check |  | SolarWorld
SolarWorld | SW 225 mono | mono | 225 | 201.2 | +5/-0 | 5 | 0 | 12.4678 | 13.4 | 29.7 | 7.59 | 37.3 | 8.13 | -0.45% | -0.3% | 0.042 | 47 | 16 | yes | MC4 | silver | white | 65.94 | 39.41 | 1.22 | 18.0465 | 46.7 | 10 |  | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 230 mono | mono | 230 | 205.8 | +5/-0 | 5 | 0 | 12.7449 | 13.7 | 30 | 7.68 | 37.4 | 8.16 | -0.45% | -0.3% | 0.042 | 47 | 16 | yes | MC4 | silver | white | 65.94 | 39.41 | 1.22 | 18.0465 | 46.7 | 10 |  | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 235 mono | mono | 235 | 210.4 | +5/-0 | 5 | 0 | 13.0219 | 14 | 30.3 | 7.77 | 37.5 | 8.19 | -0.45% | -0.3% | 0.042 | 47 | 16 | yes | MC4 | silver | white | 65.94 | 39.41 | 1.22 | 18.0465 | 46.7 | 10 |  | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 235 mono black | mono | 235 | 209.8 | +5/-0 | 5 | 0 | 13.0219 | 14 | 30.3 | 7.77 | 37.5 | 8.19 | -0.45% | -0.3% | 0.042 | 47 | 16 | yes | MC4 | black | black | 65.94 | 39.41 | 1.22 | 18.0465 | 46.7 | 10 |  | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 240 mono | mono | 240 | 215 | +5/-0 | 5 | 0 | 13.299 | 14.3 | 30.6 | 7.87 | 37.6 | 8.22 | -0.45% | -0.3% | 0.042 | 47 | 16 | yes | MC4 | silver | white | 65.94 | 39.41 | 1.22 | 18.0465 | 46.7 | 10 |  | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 240 mono black | mono | 240 | 214.4 | +5/-0 | 5 | 0 | 13.299 | 14.3 | 30.6 | 7.87 | 37.6 | 8.22 | -0.45% | -0.3% | 0.042 | 47 | 16 | yes | MC4 | black | black | 65.94 | 39.41 | 1.22 | 18.0465 | 46.7 | 10 |  | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 245 mono | mono | 245 | 219.6 | +5/-0 | 5 | 0 | 13.576 | 14.6 | 30.8 | 7.96 | 37.7 | 8.25 | -0.45% | -0.3% | 0.042 | 47 | 16 | yes | MC4 | silver | white | 65.94 | 39.41 | 1.22 | 18.0465 | 46.7 | 10 |  | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 245 mono black | mono | 245 |  | +5/-0 | 5 | 0 |  | 14.6 | 30.8 | 7.96 | 37.7 | 8.25 | -0.45% | -0.3% |  |  | 16 | [11 empty] | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 250 mono | mono | 250 | 222.3 | +5/-0 | 5 | 0 | 13.8531 | 14.9 | 31.1 | 8.05 | 37.8 | 8.28 | -0.45% | -0.3% | 0.042 | 47 | 16 | yes | MC4 | silver | white | 65.94 | 39.41 | 1.22 | 18.0465 | 46.7 | 10 |  | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 250 mono black | mono | 250 |  | +5/-0 | 5 | 0 |  | 14.9 | 31.1 | 8.05 | 37.8 | 8.28 | -0.45% | -0.3% |  |  | 16 | [11 empty] | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 255 mono | mono | 255 |  | +5/-0 | 5 | 0 | 14.1302 |  | 31.4 | 8.15 | 37.8 | 8.66 | -0.45% | -0.3% |  |  | 16 | yes | MC5 | silver | white | 65.94 | 39.41 | 1.22 | 18.0465 | 46.7 | 11 |  | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 260 mono | mono | 260 |  | +5/-0 | 5 | 0 |  | 15.51 | 31.6 | 8.24 | 37.9 | 8.73 | -0.45% | -0.3% |  |  | 16 | [11 empty] | Check | 2012-07-25 | SolarWorld
SolarWorld | SW 265 mono | mono | 265 |  | +5/-0 | 5 | 0 |  | 15.81 | 31.9 | 8.33 | 38.1 | 8.82 | -0.45% | -0.3% |  |  | 16 | [11 empty] | Check | 2012-12-13 | SolarWorld
SolarWorld | SW 270 mono | mono | 270 |  | +5/-0 | 5 | 0 |  | 16.1 | 32.1 | 8.42 | 38.3 | 8.9 | -0.45% | -0.3% |  |  | 16 | [11 empty] | Check | 2012-12-13 | SolarWorld
SolarWorld | SW 275 mono | mono | 275 |  | +5/-0 | 5 | 0 |  |  | 31 | 8.94 | 39.4 | 9.58 | -0.45% | -0.3% |  |  | 16 | [11 empty] | Check | 2014-07-21 | SolarWorld
SolarWorld | SW 290 mono | mono | 290 | 266.1 | +5/-0 | 5 | 0 |  | 17.3 | 31.9 | 9.2 | 39.6 | 9.75 | -0.39% | -0.29% |  |  | 25 |  |  |  |  | 65.95 | 39.4 | 1.3 |  | 39.7 |  |  | 1000 | 2018-10-24 | SolarWorld
SolarWorld | SW 295 mono | mono | 295 | 268.7 | +5/-0 | 5 | 0 |  | 17.59 | 32.3 | 9.25 | 39.8 | 9.78 | -0.39% | -0.29% |  |  | 25 |  |  |  |  | 65.95 | 39.4 | 1.3 |  | 39.7 |  |  | 1000 | 2018-10-24 | SolarWorld
SolarWorld | SW 300 mono | mono | 300 | 271.4 | +5/-0 | 5 | 0 |  | 17.89 | 32.6 | 9.31 | 40 | 9.83 | -0.39% | -0.29% |  |  | 25 |  |  |  |  | 65.95 | 39.4 | 1.3 |  | 39.7 |  |  | 1000 | 2017-12-29 | SolarWorld
SolarWorld | SW 305 mono | mono | 305 |  | +5/-0 | 5 | 0 |  |  | 36.3 | 8.49 | 45.6 | 9.02 | -0.41% | -0.3% |  |  | 16 | [11 empty] | Check | 2014-07-21 | SolarWorld
SolarWorld | SW 310 mono | mono | 310 |  | +5/-0 | 5 | 0 |  |  | 36.6 | 8.56 | 45.8 | 9.09 | -0.41% | -0.3% |  |  | 16 | [11 empty] | Check | 2014-07-21 | SolarWorld
SolarWorld | SW 315 XL mono | mono | 315 |  | +5/-0 | 5 | 0 |  |  | 36.5 | 8.71 | 45.6 | 9.35 | -0.43% | -0.3% |  |  | 25 | [11 empty] | Check | 8/13/15 RM | SolarWorld
SolarWorld | SW 320 XL mono | mono | 320 |  | +5/-0 | 5 | 0 |  |  | 36.7 | 8.78 | 45.9 | 9.41 | -0.43% | -0.3% |  |  | 25 | [11 empty] | Check | 8/13/15 RM | SolarWorld
SolarWorld | SW 325 XL mono | mono | 325 |  | +5/-0 | 5 | 0 |  |  | 37 | 8.84 | 46.1 | 9.48 | -0.43% | -0.3% |  |  | 25 | [11 empty] | Check | 8/13/15 RM | SolarWorld
SolarWorld | SW 340 XL mono | mono | 340 |  | +5/-0 | 5 | 0 |  |  | 38 | 9.01 | 47.6 | 9.69 | -0.43% | -0.304% |  |  | 25 | [11 empty] | Check | 2015-11-25 | SolarWorld
SolarWorld | SW 345 XL mono | mono | 345 |  | +5/-0 | 5 | 0 |  |  | 38.2 | 9.1 | 47.8 | 9.75 | -0.43% | -0.304% |  |  | 25 | [11 empty] | Check | 2015-11-25 | SolarWorld
SolarWorld | SW350 XL mono | mono | 350 |  | +5/-0 | 5 | 0 |  |  | 38.4 | 9.17 | 48 | 9.82 | -0.43% | -0.304% |  |  | 25 | [11 empty] | Check | 2015-11-25 | SolarWorld
SolarWorld | Sunmodule Protect SW275 | mono | 275 |  | +5/-0 | 5 | 0 |  |  | 31 | 8.94 | 39.4 | 9.58 | -0.43% | -0.31% |  |  | 25 | [11 empty] | Check | 2015-11-25 | SolarWorld
SolarWorld | Sunmodule Protect SW280 | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 31.2 | 9.07 | 39.5 | 9.71 | -0.43% | -0.31% |  |  | 25 | [11 empty] | Check | 2015-11-25 | SolarWorld
SolarWorld | SW 280 mono black (5-busbar) | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 31.2 | 9.07 | 39.5 | 9.71 | -0.43% | -0.31% |  |  | 25 |  |  |  |  | 65.95 | 39.4 | 1.3 |  | 39.7 |  |  | 1000 | 2016-07-29 | SolarWorld
SolarWorld | SW 285 mono black (5-busbar) | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 31.3 | 9.2 | 39.7 | 9.84 | -0.41% | -0.3% |  |  | 25 |  |  |  |  | 65.95 | 39.4 | 1.3 |  | 39.7 |  |  | 1000 | 2018-06-01 | SolarWorld
SolarWorld | SW 290 mono black (5-busbar) | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 31.4 | 9.33 | 39.9 | 9.97 | -0.41% | -0.3% |  |  | 25 |  |  |  |  | 65.95 | 39.4 | 1.3 |  | 39.7 |  |  | 1000 | 2018-06-01 | SolarWorld
SolarWorld | SW 295 mono black (5-busbar) | mono | 295 |  | +5/-0 | 5 | 0 |  |  | 31.5 | 9.45 | 40 | 10.1 | -0.41% | -0.3% |  |  | 25 |  |  |  |  | 65.95 | 39.4 | 1.3 |  | 39.7 |  |  | 1000 | 2018-06-01 | SolarWorld
SolarWorld | SW 300 mono black (5-busbar) | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 31.6 | 9.57 | 40.1 | 10.23 | -0.41% | -0.3% |  |  | 25 |  |  |  |  | 65.95 | 39.4 | 1.3 |  | 39.7 |  |  | 1000 | 2018-06-01 | SolarWorld
SolarWorld | SW 220 poly | poly | 220 | 194.7 | +5/-0 | 5 | 0 | 12.1907 | 13.1 | 29.2 | 7.54 | 36.6 | 8.08 | -0.45% | -0.37% | 0.034 | 46 | 16 | yes | MC4 | silver | white | 65.94 | 39.41 | 1.22 | 18.0465 | 46.7 | 10 |  | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 225 poly | poly | 225 | 200.7 | +5/-0 | 5 | 0 | 12.4678 | 13.4 | 29.5 | 7.63 | 36.8 | 8.17 | -0.45% | -0.37% | 0.034 | 46 | 16 | yes | MC4 | silver | white | 65.94 | 39.41 | 1.22 | 18.0465 | 46.7 | 10 |  | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 230 poly | poly | 230 | 205.2 | +5/-0 | 5 | 0 | 12.7449 | 13.7 | 29.8 | 7.72 | 36.9 | 8.25 | -0.45% | -0.37% | 0.034 | 46 | 16 | yes | MC4 | silver | white | 65.94 | 39.41 | 1.22 | 18.0465 | 46.7 | 10 |  | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 235 poly | poly | 235 | 209.8 | +5/-0 | 5 | 0 | 13.0219 | 14 | 30 | 7.85 | 37 | 8.35 | -0.45% | -0.37% | 0.034 | 46 | 16 | yes | MC4 | silver | white | 65.94 | 39.41 | 1.22 | 18.0465 | 46.7 | 10 |  | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 240 poly | poly | 240 | 214.4 | +5/-0 | 5 | 0 | 13.299 | 14.3 | 30.2 | 7.96 | 37.2 | 8.44 | -0.45% | -0.37% | 0.034 | 46 | 16 | yes | MC4 | silver | white | 65.94 | 39.41 | 1.22 | 18.0465 | 46.7 | 10 |  | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 245 poly | poly | 245 |  | +5/-0 | 5 | 0 |  | 14.6 | 30.8 | 7.96 | 37.5 | 8.49 | -0.45% | -0.37% |  |  | 16 | [7 empty] | 0 |  |  |  | Check | 2012-04-02 | SolarWorld
SolarWorld | SW 245 poly Pro | poly | 245 |  | +5/-0 | 5 | 0 |  |  | 30.1 | 8.22 | 37.3 | 8.75 | -0.45% | -0.37% |  |  | 16 | [11 empty] | Check | 2015-11-25 | SolarWorld
SolarWorld | SW 250 poly | poly | 250 |  | +5/-0 | 5 | 0 |  |  | 30.5 | 8.27 | 37.6 | 8.81 | -0.41% | -0.31% |  |  | 25 | [11 empty] | Check | 2015-11-25 | SolarWorld
SolarWorld | SW 255 poly | poly | 255 |  | +5/-0 | 5 | 0 |  |  | 30.9 | 8.32 | 38 | 8.88 | -0.41% | -0.31% |  |  | 25 | [11 empty] | Check | 2015-11-25 | SolarWorld
SolarWorld | SW 260 poly | poly | 260 |  | +5/-0 | 5 | 0 |  |  | 31.4 | 8.37 | 38.4 | 8.94 | -0.41% | -0.31% |  |  | 25 | [11 empty] | Check | 2015-11-25 | SolarWorld
Solon | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Solon
Solon | 220/01 220W | poly | 220 |  | +3/-3 | 3 | -3 | 12.462 | 14.02 | 28.8 | 7.65 | 36.4 | 8.3 | -0.44% | -0.35% |  |  | 15 |  | Tyco |  |  | 64.57 | 39.37 | 1.65 | 17.6536 | 51.81 | 2 |  | Check |  | Solon
Solon | 220/01 225W | poly | 225 |  | +3/-3 | 3 | -3 | 12.7453 | 14.02 | 28.9 | 7.8 | 36.6 | 8.4 | -0.44% | -0.35% |  |  | 15 |  | Tyco |  |  | 64.57 | 39.37 | 1.65 | 17.6536 | 51.81 | 2 |  | Check |  | Solon
Solon | 220/01 230W | poly | 230 |  | +3/-3 | 3 | -3 | 13.0285 | 14.02 | 29 | 7.95 | 36.7 | 8.55 | -0.44% | -0.35% |  |  | 15 |  | Tyco |  |  | 64.57 | 39.37 | 1.65 | 17.6536 | 51.81 | 2 |  | Check |  | Solon
Solon | 220/01 235W | poly | 235 |  | +3/-3 | 3 | -3 | 13.3117 |  | 29.2 | 8.05 | 36.9 | 8.65 | -0.44% | -0.35% |  |  | 15 |  | Tyco |  |  | 64.57 | 39.37 | 1.65 | 17.6536 | 51.81 | 2 |  | Check |  | Solon
Solon | 220/01 240W | poly | 240 |  | +3/-3 | 3 | -3 | 13.5949 |  | 29.4 | 8.1 | 40 | 8.7 | -0.44% | -0.35% |  |  | 15 |  | Tyco |  |  | 64.57 | 39.37 | 1.65 | 17.6536 | 51.81 | 2 |  | Check |  | Solon
Solon | SOLON Black 230 | mono | 230 | 203.7 | +5/-0 | 5 | 0 | 13.0285 | 14.02 | 29.2 | 7.88 | 36.22 | 8.38 | -0.47% | -0.36% | 0.04 | 48 | 15 | yes | tyco | silver | white | 64.57 | 39.37 | 1.65 | 17.6536 | 51.8 | 10 |  | Check |  | Solon
Solon | SOLON Black 235 | mono | 235 | 208.2 | +5/-0 | 5 | 0 | 13.3117 | 14.33 | 29.41 | 7.99 | 36.48 | 8.47 | -0.47% | -0.36% | 0.04 | 48 | 15 | yes | tyco | silver | white | 64.57 | 39.37 | 1.65 | 17.6536 | 51.8 | 10 |  | Check |  | Solon
Solon | SOLON Black 240 | mono | 240 | 212.8 | +5/-0 | 5 | 0 | 13.5949 | 14.63 | 29.62 | 8.11 | 36.75 | 8.56 | -0.47% | -0.36% | 0.04 | 48 | 15 | yes | tyco | silver | white | 64.57 | 39.37 | 1.65 | 17.6536 | 51.8 | 10 |  | Check |  | Solon
Solon | SOLON Black 245 | mono | 245 | 217.4 | +5/-0 | 5 | 0 | 13.8782 | 14.94 | 29.82 | 8.22 | 37.01 | 8.65 | -0.47% | -0.36% | 0.04 | 48 | 15 | yes | tyco | silver | white | 64.57 | 39.37 | 1.65 | 17.6536 | 51.8 | 10 |  | Check |  | Solon
Solon | SOLON Black XT 280 | mono | 280 | 246.2 | +5/-0 | 5 | 0 | 13.1383 | 14.14 | 35.2 | 7.96 | 43.69 | 8.44 | -0.47% | -0.36% | 0.04 | 48 | 15 | yes | tyco | silver | white | 77.95 | 39.37 | 1.65 | 21.3117 | 66.1 | 10 |  | Check |  | Solon
Solon | SOLON Black XT 285 | mono | 285 | 250.8 | +5/-0 | 5 | 0 | 13.3729 | 14.39 | 35.4 | 8.06 | 43.96 | 8.51 | -0.47% | -0.36% | 0.04 | 48 | 15 | yes | tyco | silver | white | 77.95 | 39.37 | 1.65 | 21.3117 | 66.1 | 10 |  | Check |  | Solon
Solon | SOLON Black XT 290 | mono | 290 | 255.3 | +5/-0 | 5 | 0 | 13.6075 | 14.65 | 35.6 | 8.16 | 44.23 | 8.59 | -0.47% | -0.36% | 0.04 | 48 | 15 | yes | tyco | silver | white | 77.95 | 39.37 | 1.65 | 21.3117 | 66.1 | 10 |  | Check |  | Solon
Solon | SOLON Black XT 295 | mono | 295 | 259.9 | +5/-0 | 5 | 0 | 13.8421 | 14.9 | 35.8 | 8.26 | 44.5 | 8.66 | -0.47% | -0.36% | 0.04 | 48 | 15 | yes | tyco | silver | white | 77.95 | 39.37 | 1.65 | 21.3117 | 66.1 | 10 |  | Check |  | Solon
Solon | SOLON Blue 220 | poly | 220 | 196.8 | +5/-0 | 5 | 0 | 12.462 | 13.41 | 29.23 | 7.53 | 36.35 | 8 | -0.45% | -0.35% | 0.07 | 46 | 15 | yes | tyco | silver | white | 64.57 | 39.37 | 1.65 | 17.6536 | 51.8 | 10 |  | Check |  | Solon
Solon | SOLON Blue 225 | poly | 225 | 201.4 | +5/-0 | 5 | 0 | 12.7453 | 13.72 | 29.4 | 7.65 | 36.52 | 8.12 | -0.45% | -0.35% | 0.07 | 46 | 15 | yes | tyco | silver | white | 64.57 | 39.37 | 1.65 | 17.6536 | 51.8 | 10 |  | Check |  | Solon
Solon | SOLON Blue 230 | poly | 230 | 206 | +5/-0 | 5 | 0 | 13.0285 | 14.02 | 29.58 | 7.78 | 36.69 | 8.24 | -0.45% | -0.35% | 0.07 | 46 | 15 | yes | tyco | silver | white | 64.57 | 39.37 | 1.65 | 17.6536 | 51.8 | 10 |  | Check |  | Solon
Solon | SOLON Blue 235 | poly | 235 | 210.6 | +5/-0 | 5 | 0 | 13.3117 | 14.33 | 29.76 | 7.9 | 36.86 | 8.36 | -0.45% | -0.35% | 0.07 | 46 | 15 | yes | tyco | silver | white | 64.57 | 39.37 | 1.65 | 17.6536 | 51.8 | 10 |  | Check |  | Solon
Solon | SOLON Blue XT 270 | poly | 270 | 241.1 | +5/-0 | 5 | 0 | 12.6691 | 13.64 | 35.45 | 7.61 | 43.62 | 8.08 | -0.45% | -0.35% | 0.07 | 46 | 15 | yes | tyco | silver | white | 77.95 | 39.37 | 1.65 | 21.3117 | 66.1 | 10 |  | Check |  | Solon
Solon | SOLON Blue XT 275 | poly | 275 | 245.7 | +5/-0 | 5 | 0 | 12.9037 | 13.88 | 35.7 | 7.7 | 43.85 | 8.14 | -0.45% | -0.35% | 0.07 | 46 | 15 | yes | tyco | silver | white | 77.95 | 39.37 | 1.65 | 21.3117 | 66.1 | 10 |  | Check |  | Solon
Solon | SOLON Blue XT 280 | poly | 280 | 250.3 | +5/-0 | 5 | 0 | 13.1383 | 14.14 | 35.95 | 7.78 | 44.08 | 8.2 | -0.45% | -0.35% | 0.07 | 46 | 15 | yes | tyco | silver | white | 77.95 | 39.37 | 1.65 | 21.3117 | 66.1 | 10 |  | Check |  | Solon
Solon | SOLON Blue XT 285 | poly | 285 | 254.9 | +5/-0 | 5 | 0 | 13.3729 | 14.39 | 36.25 | 7.86 | 44.3 | 8.27 | -0.45% | -0.35% | 0.07 | 46 | 15 | yes | tyco | silver | white | 77.95 | 39.37 | 1.65 | 21.3117 | 66.1 | 10 |  | Check |  | Solon
Solon | SOLON Corvus 225 | mono | 225 | 196.4 | +5/-0 | 5 | 0 | 12.7453 | 13.72 | 29 | 7.76 | 35.96 | 8.2 | -0.47% | -0.36% | 0.04 | 48 | 15 | yes | tyco | black | black | 64.57 | 39.37 | 1.65 | 17.6536 | 51.8 | 10 |  | Check |  | Solon
Solon | SOLON Corvus 230 | mono | 230 | 200.9 | +5/-0 | 5 | 0 | 13.0285 | 14.02 | 29.2 | 7.88 | 36.22 | 8.38 | -0.47% | -0.36% | 0.04 | 48 | 15 | yes | tyco | black | black | 64.57 | 39.37 | 1.65 | 17.6536 | 51.8 | 10 |  | Check |  | Solon
Solon | SOLON Corvus 235 | mono | 235 | 205.5 | +5/-0 | 5 | 0 | 13.3117 | 14.33 | 29.41 | 7.99 | 36.48 | 8.47 | -0.47% | -0.36% | 0.04 | 48 | 15 | yes | tyco | black | black | 64.57 | 39.37 | 1.65 | 17.6536 | 51.8 | 10 |  | Check |  | Solon
Solon | SOLON Corvus 240 | mono | 240 | 210 | +5/-0 | 5 | 0 | 13.5949 | 14.63 | 29.62 | 8.11 | 36.75 | 8.56 | -0.47% | -0.36% | 0.04 | 48 | 15 | yes | tyco | black | black | 64.57 | 39.37 | 1.65 | 17.6536 | 51.8 | 10 |  | Check |  | Solon
Solon | SOLquick Black XT 290 | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 35.6 | 8.16 | 44.23 | 8.59 | -0.43% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Solon
Solon | SOLquick Black XT 295 | mono | 295 |  | +5/-0 | 5 | 0 |  |  | 35.8 | 8.26 | 44.55 | 8.66 | -0.43% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Solon
Solon | SOLquick Black XT 300 | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 36 | 8.36 | 44.77 | 8.74 | -0.43% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Solon
Solon | SOLquick Blue XT-H 280 | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 36.1 | 7.76 | 44.3 | 8.4 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Solon
Solon | SOLquick Blue XT 280 | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 35.95 | 7.78 | 44.08 | 8.2 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Solon
Solon | SOLquick Blue XT 285 | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 36.25 | 7.86 | 44.5 | 8.27 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Solon
Solopower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Solopower
Solopower | SFX1-i210 |  | 210 |  | +5/-3 | 5 | -3 |  |  | 64 | 3.3 | 93 | 4 | -0.43% | -0.35% | [10 empty] | 0 |  |  |  | Check |  | Solopower
Solopower | SFX1-i220 |  | 220 |  | +5/-3 | 5 | -3 |  |  | 66 | 3.3 | 95 | 4 | -0.43% | -0.35% | [10 empty] | 0 |  |  |  | Check |  | Solopower
Solopower | SFX1-i230 |  | 230 |  | +5/-3 | 5 | -3 |  |  | 68 | 3.4 | 96 | 4 | -0.43% | -0.35% | [10 empty] | 0 |  |  |  | Check |  | Solopower
Solopower | SFX1-i240 |  | 240 |  | +5/-3 | 5 | -3 |  |  | 69 | 3.5 | 98 | 4.1 | -0.43% | -0.35% | [10 empty] | 0 |  |  |  | Check |  | Solopower
Solopower | SFX1-i250 |  | 250 |  | +5/-3 | 5 | -3 |  |  | 71 | 3.5 | 99 | 4.1 | -0.43% | -0.35% | [10 empty] | 0 |  |  |  | Check |  | Solopower
Solopower | SFX1-i260 |  | 260 |  | +5/-3 | 5 | -3 |  |  | 73 | 3.6 | 101 | 4.1 | -0.43% | -0.35% | [10 empty] | 0 |  |  |  | Check |  | Solopower
Solopower | SFX1-i65 |  | 65 |  | +5/-3 | 5 | -3 |  |  | 20 | 3.3 | 29 | 4 | -0.43% | -0.35% | [10 empty] | 0 |  |  |  | Check |  | Solopower
Solopower | SFX1-i70 |  | 70 |  | +5/-3 | 5 | -3 |  |  | 21 | 3.3 | 30 | 4 | -0.43% | -0.35% | [10 empty] | 0 |  |  |  | Check |  | Solopower
Solopower | SFX1-i75 |  | 75 |  | +5/-3 | 5 | -3 |  |  | 22 | 3.3 | 32 | 4 | -0.43% | -0.35% | [10 empty] | 0 |  |  |  | Check |  | Solopower
Solopower | SFX1-i80 |  | 80 |  | +5/-3 | 5 | -3 |  |  | 24 | 3.4 | 33 | 4 | -0.43% | -0.35% | [10 empty] | 0 |  |  |  | Check |  | Solopower
Solopower | SFX1-i85 |  | 85 |  | +5/-3 | 5 | -3 |  |  | 25 | 3.4 | 35 | 4.1 | -0.43% | -0.35% | [10 empty] | 0 |  |  |  | Check |  | Solopower
Solopower | SP3L 220 | cis | 220 |  | +5/-3 | 5 | -3 |  |  | 65.1 | 3.4 | 91.8 | 4.4 | -0.48% | -0.36% | [14 empty] | Check | 2015-12-04 | Solopower
Solopower | SP3L 240 | cis | 240 |  | +5/-3 | 5 | -3 |  |  | 68.2 | 3.5 | 95.4 | 4.3 | -0.48% | -0.36% | [14 empty] | Check | 2015-12-04 | Solopower
Solopower | SP3L 260 | cis | 260 |  | +5/-3 | 5 | -3 |  |  | 70.8 | 3.7 | 97.2 | 4.4 | -0.48% | -0.36% | [14 empty] | Check | 2015-12-04 | Solopower
Solopower | SP3L 280 | cis | 280 |  | +5/-3 | 5 | -3 |  |  | 77.1 | 3.6 | 102.6 | 4.2 | -0.48% | -0.36% | [14 empty] | Check | 2015-12-04 | Solopower
Solopower | SP3L 300 | cis | 300 |  | +5/-3 | 5 | -3 |  |  | 83.6 | 3.6 | 108 | 4.2 | -0.48% | -0.36% | [14 empty] | Check | 2015-12-04 | Solopower
SolTech |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | SolTech
SolTech | 1 STH-230 | mono | 230 |  | +/-3 | 3 | -3 |  |  | 28.8 | 8 | 36.9 | 8.5 | -0.48% | -0.37% |  |  | N/A | [11 empty] | Check |  | SolTech
SolTech | 1 STH-235 | mono | 235 |  | +/-3 | 3 | -3 |  |  | 29.3 | 8.02 | 37 | 8.54 | -0.48% | -0.37% |  |  | N/A | [11 empty] | Check |  | SolTech
SolTech | 1 STH-240 | mono | 240 |  | +/-3 | 3 | -3 |  |  | 29.7 | 8.07 | 37.1 | 8.58 | -0.48% | -0.37% |  |  | N/A | [11 empty] | Check |  | SolTech
SolTech | 1 STH-245 | mono | 245 |  | +/-3 | 3 | -3 |  |  | 30.2 | 8.1 | 37.2 | 8.62 | -0.48% | -0.37% |  |  | N/A | [11 empty] | Check |  | SolTech
SolTech | 1 STH-250 | mono | 250 |  | +/-3 | 3 | -3 |  |  | 30.7 | 8.15 | 37.3 | 8.66 | -0.48% | -0.37% |  |  | N/A | [11 empty] | Check |  | SolTech
SolTech | 1 STH-255 | mono | 255 |  | +/-3 | 3 | -3 |  |  | 31.1 | 8.2 | 37.4 | 8.7 | -0.48% | -0.37% |  |  | N/A | [11 empty] | Check |  | SolTech
SolTech | 1 STH-260 | mono | 260 |  | +/-3 | 3 | -3 |  |  | 31.5 | 8.25 | 37.5 | 8.74 | -0.48% | -0.37% |  |  | N/A | [11 empty] | Check |  | SolTech
SolTech | 1STH-335-WH | mono | 335 |  | +/-3 | 3 | -3 |  |  | 41.5 | 8.06 | 50 | 8.8 | -0.48% | -0.19% |  |  | 15 | [11 empty] | Check | 2015-12-04 | SolTech
SolTech | 1STH-340-WH | mono | 340 |  | +/-3 | 3 | -3 |  |  | 42 | 8.09 | 50.45 | 8.85 | -0.48% | -0.19% |  |  | 15 | [11 empty] | Check | 2015-12-04 | SolTech
SolTech | 1STH-345-WH | mono | 345 |  | +/-3 | 3 | -3 |  |  | 42.49 | 8.11 | 50.96 | 8.89 | -0.48% | -0.19% |  |  | 15 | [11 empty] | Check | 2015-12-04 | SolTech
SolTech | 1STH-350-WH | mono | 350 |  | +/-3 | 3 | -3 |  |  | 42.98 | 8.13 | 51.47 | 8.93 | -0.48% | -0.19% |  |  | 15 | [11 empty] | Check | 2015-12-04 | SolTech
Stion | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Stion
Stion | STN-125 | cigs | 125 |  | +10/-0 | 10 | -10 |  |  | 42.2 | 3 | 58 | 3.45 | -0.34% | -0.28% |  |  | 6 | [11 empty] | Check |  | Stion
Stion | STN-130 | cigs | 130 |  | +10/-0 | 10 | -10 |  |  | 43 | 3.02 | 58.3 | 3.45 | -0.34% | -0.28% |  |  | 6 | [11 empty] | Check |  | Stion
Stion | STN-135 | cigs | 135 |  | +10/-0 | 10 | -10 |  |  | 44.3 | 3.05 | 58.7 | 3.45 | -0.34% | -0.28% |  |  | 6 | [11 empty] | Check |  | Stion
Stion | STN-140 | cigs | 140 |  | +10/-0 | 10 | -10 |  |  | 45.5 | 3.08 | 59.5 | 3.45 | -0.34% | -0.28% |  |  | 6 | [11 empty] | Check |  | Stion
Stion | STN-145 | cigs | 145 |  | +10/-0 | 10 | -10 |  |  | 46.3 | 3.1 | 60.9 | 3.45 | -0.34% | -0.28% |  |  | 6 | [11 empty] | Check |  | Stion
Stion | STN-150 | cigs | 150 |  | +10/-0 | 10 | -10 |  |  | 47.9 | 3.13 | 62.1 | 3.45 | -0.34% | -0.28% |  |  | 6 | [11 empty] | Check |  | Stion
Stion | STO-135 | cigs | 135 |  | +10/-0 | 10 | -10 |  |  | 58.2 | 2.32 | 77.4 | 2.62 | -0.26% | -0.24% |  |  | 7 | [11 empty] | Check |  | Stion
Stion | STO-140 | cigs | 140 |  | +10/-0 | 10 | -10 |  |  | 59.8 | 2.34 | 78.8 | 2.62 | -0.26% | -0.24% |  |  | 7 | [11 empty] | Check |  | Stion
Stion | STO-145 | cigs | 145 |  | +10/-0 | 10 | -10 |  |  | 61 | 2.38 | 79.6 | 80.2 | -0.26% | -0.24% |  |  | 7 | [11 empty] | Check |  | Stion
Stion | STO-150 | cigs | 150 |  | +10/-0 | 10 | -10 |  |  | 62.7 | 2.39 | 80.8 | 2.72 | -0.26% | -0.24% |  |  | 7 | [11 empty] | Check |  | Stion
Stion | STO-155 | cigs | 155 |  | +/-10 | 10 | -10 |  |  | 63.4 | 2.45 | 2.75 | 82 | -0.26% | -0.24% |  |  | 7 | [11 empty] | Check | 2015-12-04 | Stion
Stion | STO-160 | cigs | 160 |  | +/-10 | 10 | -10 |  |  | 64.1 | 2.5 | 83.2 | 2.78 | -0.26% | -0.24% |  |  | 7 | [11 empty] | Check | 2015-12-04 | Stion
Stion | STL-135 | cigs | 135 |  | +10/-0 | 10 | -10 |  |  | 58.2 | 2.32 | 77.4 | 2.62 | -0.26% | -0.24% |  |  | 7 | [11 empty] | Check |  | Stion
Stion | STL-140 | cigs | 140 |  | +10/-0 | 10 | -10 |  |  | 59.8 | 2.34 | 78.8 | 2.65 | -0.26% | -0.24% |  |  | 7 | [11 empty] | Check |  | Stion
Stion | STL-145 | cigs | 145 |  | +10/-0 | 10 | -10 |  |  | 61 | 2.38 | 79.6 | 2.68 | -0.26% | -0.24% |  |  | 7 | [11 empty] | Check |  | Stion
Stion | STL-150 | cigs | 150 |  | +10/-0 | 10 | -10 |  |  | 62.7 | 2.39 | 80.8 | 2.72 | -0.26% | -0.24% |  |  | 7 | [11 empty] | Check |  | Stion
Stion | STL-155 | cigs | 155 |  | +/-10 | 10 | -10 |  |  | 63.4 | 2.45 | 82 | 2.75 | -0.26% | -0.24% |  |  | 7 | [11 empty] | Check | 2015-12-04 | Stion
Stion | STL-160 | cigs | 160 |  | +/-10 | 10 | -10 |  |  | 64.1 | 2.5 | 83.2 | 2.75 | -0.26% | -0.24% |  |  | 7 | [11 empty] | Check | 2015-12-04 | Stion
Sun Earth Solar Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Sun_Earth_Solar_Power
Sun Earth Solar Power | TDB125x125-72-P 185W | mono | 185 | 165.1 | +/-3 | 3 | -3 | 13.4684 | 14.5 | 36.6 | 5.06 | 44.8 | 5.35 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 62.2 | 31.8 | 1.8 | 13.7358 | 35.27 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TDB125x125-72-P 190W | mono | 190 | 169.7 | +/-3 | 3 | -3 | 13.8324 | 14.9 | 36.8 | 5.17 | 45 | 5.42 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 62.2 | 31.8 | 1.8 | 13.7358 | 35.27 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TDB156x156-60-P 215W | poly | 215 | 193 | +/-3 | 3 | -3 | 12.2603 | 13 | 36.8 | 7.24 | 29.7 | 7.92 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TDB156x156-60-P 220W | poly | 220 | 197.6 | +/-3 | 3 | -3 | 12.5454 | 13.3 | 36.9 | 7.39 | 29.8 | 8.03 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TDB156x156-60-P 225W | poly | 225 | 202.2 | +/-3 | 3 | -3 | 12.8305 | 13.6 | 37 | 7.53 | 29.9 | 8.14 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TDB156x156-60-P 230W | poly | 230 | 206.8 | +/-3 | 3 | -3 | 13.1156 | 13.9 | 37.1 | 7.67 | 30 | 8.25 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TDB156x156-60-P 235W | poly | 235 | 211.4 | +/-3 | 3 | -3 | 13.4008 | 14.3 | 37.2 | 7.81 | 30.1 | 8.36 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TDB156x156-60-P 240W | poly | 240 | 216 | +/-3 | 3 | -3 | 13.6859 | 14.5 | 37.3 | 7.95 | 30.2 | 8.47 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TDB156x156-60-P 245W | poly | 245 | 220.6 | +/-3 | 3 | -3 | 13.971 | 14.8 | 37.4 | 8.09 | 30.3 | 8.58 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TDB156x156-72-P 280W | poly | 280 | 251.8 | +/-3 | 3 | -3 | 13.3903 | 14.4156 | 44.6 | 7.78 | 36 | 8.32 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 77.09 | 39.06 | 1.8 | 20.9107 | 59.47 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TDB156x156-72-P 285W | poly | 285 | 256.4 | +/-3 | 3 | -3 | 13.6294 | 14.6 | 44.7 | 7.9 | 36.1 | 8.41 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 77.09 | 39.06 | 1.8 | 20.9107 | 59.47 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TDB156x156-72-P 290W | poly | 290 | 261 | +/-3 | 3 | -3 | 13.8685 | 14.9 | 44.8 | 8.01 | 36.2 | 8.5 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 77.09 | 39.06 | 1.8 | 20.9107 | 59.47 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TDB156x156-72-P 295W | poly | 295 | 265.6 | +/-3 | 3 | -3 | 14.1076 | 15.1 | 44.9 | 8.13 | 36.3 | 8.59 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 77.09 | 39.06 | 1.8 | 20.9107 | 59.47 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB125x125-72-P 185W | poly | 185 | 167.5 | +/-3 | 3 | -3 | 13.4684 | 14.5 | 36.5 | 5.07 | 44.7 | 5.38 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 62.2 | 31.8 | 1.8 | 13.7358 | 35.27 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB125x125-72-P 190W | poly | 190 | 172.1 | +/-3 | 3 | -3 | 13.8324 | 14.9 | 36.7 | 5.18 | 44.9 | 5.45 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 62.2 | 31.8 | 1.8 | 13.7358 | 35.27 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB125x125-96-P 200W | poly | 200 | 181.1 | +/-3 | 3 | -3 | 10.932 | 11.8 | 47 | 4.26 | 57.9 | 4.86 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 62.83 | 41.93 | 1.8 | 18.2949 | 47.36 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB125x125-96-P 205W | poly | 205 | 185.6 | +/-3 | 3 | -3 | 11.2053 | 12.1 | 47.2 | 4.35 | 58.1 | 4.91 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 62.83 | 41.93 | 1.8 | 18.2949 | 47.36 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB125x125-96-P 210W | poly | 210 | 190.2 | +/-3 | 3 | -3 | 11.4786 | 12.4 | 47.4 | 4.43 | 58.3 | 4.96 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 62.83 | 41.93 | 1.8 | 18.2949 | 47.36 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB125x125-96-P 215W | poly | 215 | 194.7 | +/-3 | 3 | -3 | 11.7519 | 12.7 | 47.6 | 4.52 | 58.5 | 5.01 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 62.83 | 41.93 | 1.8 | 18.2949 | 47.36 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB125x125-96-P 220W | poly | 220 | 199.2 | +/-3 | 3 | -3 | 12.0252 | 13 | 47.8 | 4.61 | 58.7 | 5.07 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 62.83 | 41.93 | 1.8 | 18.2949 | 47.36 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB125x125-96-P 225W | poly | 225 | 201.7 | +/-3 | 3 | -3 | 12.2985 | 13.3 | 48 | 4.69 | 58.9 | 5.12 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 62.83 | 41.93 | 1.8 | 18.2949 | 47.36 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB125x125-96-P 230W | poly | 230 | 206.2 | +/-3 | 3 | -3 | 12.5718 | 13.6 | 48.2 | 4.77 | 59.1 | 5.17 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 62.83 | 41.93 | 1.8 | 18.2949 | 47.36 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB125x125-96-P 235W | poly | 235 | 210.7 | +/-3 | 3 | -3 | 12.8451 | 13.9 | 48.4 | 4.86 | 59.3 | 5.22 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 62.83 | 41.93 | 1.8 | 18.2949 | 47.36 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB125x125-96-P 240W | poly | 240 | 215.2 | +/-3 | 3 | -3 | 13.1184 | 14.2 | 48.6 | 4.95 | 59.5 | 5.28 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 62.83 | 41.93 | 1.8 | 18.2949 | 47.36 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-54-P 190W | poly | 190 | 172.6 | +/-3 | 3 | -3 | 12.0045 | 12.7 | 32.6 | 7.34 | 25.9 | 7.95 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 58.35 | 39.06 | 1.8 | 15.8274 | 37.44 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-54-P 195W | poly | 195 | 177.1 | +/-3 | 3 | -3 | 12.3204 | 13.1 | 32.7 | 7.59 | 26 | 8.07 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 58.35 | 39.06 | 1.8 | 15.8274 | 37.44 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-54-P 200W | poly | 200 | 181.7 | +/-3 | 3 | -3 | 12.6363 | 13.4 | 32.8 | 7.67 | 26.1 | 8.2 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 58.35 | 39.06 | 1.8 | 15.8274 | 37.44 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-54-P 205W | poly | 205 | 186.2 | +/-3 | 3 | -3 | 12.9522 | 13.7 | 32.9 | 7.83 | 26.2 | 8.31 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 58.35 | 39.06 | 1.8 | 15.8274 | 37.44 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-54-P 210W | poly | 210 | 188.1 | +/-3 | 3 | -3 | 13.2681 | 14 | 33 | 7.99 | 26.3 | 8.42 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 58.35 | 39.06 | 1.8 | 15.8274 | 37.44 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-54-P 215W | poly | 215 | 192.7 | +/-3 | 3 | -3 | 13.584 | 14.3 | 33.1 | 8.15 | 26.4 | 8.54 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 58.35 | 39.06 | 1.8 | 15.8274 | 37.44 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-54-P 220W | poly | 220 | 197.3 | +/-3 | 3 | -3 | 13.8999 | 14.7 | 33.2 | 8.3 | 26.5 | 8.66 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 58.35 | 39.06 | 1.8 | 15.8274 | 37.44 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-60-P 200W | poly | 200 | 184.7 | +/-3 | 3 | -3 | 11.4049 | 12.1 | 36 | 7.02 | 28.5 | 7.7 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-60-P 205W | poly | 205 | 189.4 | +/-3 | 3 | -3 | 11.69 | 12.4 | 36.1 | 7.17 | 28.6 | 7.81 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-60-P 210W | poly | 210 | 193.9 | +/-3 | 3 | -3 | 11.9752 | 12.7 | 36.2 | 7.32 | 28.7 | 7.92 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-60-P 215W | poly | 215 | 198.6 | +/-3 | 3 | -3 | 12.2603 | 13 | 36.3 | 7.47 | 28.8 | 8.04 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-60-P 220W | poly | 220 | 202.9 | +/-3 | 3 | -3 | 12.5454 | 13.3 | 36.4 | 7.62 | 28.9 | 8.16 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-60-P 225W | poly | 225 | 207.5 | +/-3 | 3 | -3 | 12.8305 | 13.6 | 36.5 | 7.76 | 29 | 8.26 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-60-P 230W | poly | 230 | 212.1 | +/-3 | 3 | -3 | 13.1156 | 13.9 | 36.6 | 7.91 | 29.1 | 8.73 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-60-P 235W | poly | 235 | 210.6 | +/-3 | 3 | -3 | 13.4008 | 14.3 | 36.7 | 8.05 | 29.2 | 8.47 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-60-P 240W | poly | 240 | 215.2 | +/-3 | 3 | -3 | 13.6859 | 14.5 | 36.8 | 8.19 | 29.3 | 8.58 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-60-P 245W | poly | 245 | 219.8 | +/-3 | 3 | -3 | 13.971 | 14.8 | 36.9 | 8.34 | 29.4 | 8.68 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 64.65 | 39.06 | 1.8 | 17.5363 | 44.05 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-72-P 285W | poly | 285 | 255.5 | +/-3 | 3 | -3 | 13.6294 | 14.6 | 44.2 | 8.12 | 35.2 | 8.51 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 77.09 | 39.06 | 1.8 | 20.9107 | 59.47 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-72-P 290W | poly | 290 | 260.2 | +/-3 | 3 | -3 | 13.8685 | 14.9 | 44.4 | 8.24 | 35.4 | 8.59 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 77.09 | 39.06 | 1.8 | 20.9107 | 59.47 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-72-P 295W | poly | 295 | 264.8 | +/-3 | 3 | -3 | 14.1076 | 15.1 | 44.6 | 8.36 | 35.6 | 8.67 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 77.09 | 39.06 | 1.8 | 20.9107 | 59.47 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-72-P 230W | poly | 230 | 208.1 | +/-3 | 3 | -3 | 10.9992 | 11.8 | 43 | 6.77 | 34 | 7.5 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 77.09 | 39.06 | 1.8 | 20.9107 | 59.47 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-72-P 240W | poly | 240 | 218.8 | +/-3 | 3 | -3 | 11.4774 | 12.4 | 43.2 | 7.02 | 34.2 | 7.7 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 77.09 | 39.06 | 1.8 | 20.9107 | 59.47 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-72-P 250W | poly | 250 | 227.9 | +/-3 | 3 | -3 | 11.9556 | 12.9 | 43.4 | 7.27 | 34.4 | 7.89 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 77.09 | 39.06 | 1.8 | 20.9107 | 59.47 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-72-P 255W | poly | 255 | 230.9 | +/-3 | 3 | -3 | 12.1947 | 13.1285 | 43.5 | 7.39 | 34.5 | 7.98 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 77.09 | 39.06 | 1.8 | 20.9107 | 59.47 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-72-P 260W | poly | 260 | 235.4 | +/-3 | 3 | -3 | 12.4338 | 13.4 | 43.6 | 7.52 | 34.6 | 8.07 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 77.09 | 39.06 | 1.8 | 20.9107 | 59.47 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-72-P 270W | poly | 270 | 244.4 | +/-3 | 3 | -3 | 12.9121 | 13.9008 | 43.8 | 7.76 | 34.8 | 8.26 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 77.09 | 39.06 | 1.8 | 20.9107 | 59.47 | 5 |  | Check |  | Sun_Earth_Solar_Power
Sun Earth Solar Power | TPB156x156-72-P 280W | poly | 280 | 253.5 | +/-3 | 3 | -3 | 13.3903 | 14.4156 | 44 | 8 | 35 | 8.43 | -0.4% | -0.35% | 0.03 | 47 | 10 | yes | MC4 | silver | white | 77.09 | 39.06 | 1.8 | 20.9107 | 59.47 | 5 |  | Check |  | Sun_Earth_Solar_Power
SunPower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | SunPower
SunPower | SER-228P | poly | 228 | 202 | +5/-3 | 5 | -3 | 12.8887 | 13.9 | 29.6 | 7.7 | 37.8 | 8.3 | -0.45% | -0.35% | 0.05 | 45 | 15 | yes | MC3 | silver | white | 65.35 | 38.98 | 1.65 | 17.6899 | 42.1 | 10 |  | Check |  | SunPower
SunPower | SER-235P | poly | 235 | 212 | +5/-3 | 5 | -3 | 13.2844 | 14.3 | 29.7 | 7.91 | 36.8 | 8.45 | -0.45% | -0.35% | 0.05 | 45 | 15 | yes | MC3 | silver | white | 65.35 | 38.98 | 1.65 | 17.6899 | 42.1 | 10 |  | Check |  | SunPower
SunPower | SPR-225E-BLK | mono | 225 | 204.9 | +5/-3 | 5 | -3 | 16.7974 | 18.1 | 41 | 5.49 | 48.5 | 5.87 | -0.38% | -0.27% | 0.03 | 46 | 20 | yes | MC4 | black | black | 61.39 | 31.42 | 1.81 | 13.395 | 33.1 | 10 |  | Check |  | SunPower
SunPower | SPR-230E-WHT | mono | 230 | 209.5 | +5/-3 | 5 | -3 | 17.1706 | 18.5 | 41 | 5.61 | 48.7 | 5.99 | -0.38% | -0.27% | 0.03 | 45 | 20 | yes | MC4 | black | white | 61.39 | 31.42 | 1.81 | 13.395 | 33.1 | 10 |  | Check |  | SunPower
SunPower | SPR-305E-WHT | mono | 305 | 280.6 | +5/-3 | 5 | -3 | 17.3731 | 18.7 | 54.7 | 5.58 | 64.2 | 5.96 | -0.38% | -0.28% | 0.03 | 45 | 20 | yes | MC4 | black | white | 61.39 | 41.18 | 1.81 | 17.5558 | 41 | 10 |  | Check |  | SunPower
SunPower | SPR-308E-WHT-D | mono | 308 | 283.4 | +5/-3 | 5 | -3 | 17.544 | 18.9 | 54.7 | 5.64 | 64.3 | 6.02 | -0.38% | -0.2747% | 0.03 | 45 | 20 | yes | MC4 | black | white | 61.39 | 41.18 | 1.81 | 17.5558 | 41 | 10 |  | Check |  | SunPower
SunPower | SPR-310E-WHT | mono | 310 | 285.3 | +5/-3 | 5 | -3 | 17.6579 | 19 | 54.7 | 5.67 | 64.2 | 6.05 | -0.38% | -0.28% | 0.03 | 45 | 20 | yes | MC4 | black | white | 61.39 | 41.18 | 1.81 | 17.5558 | 41 | 10 |  | Check |  | SunPower
SunPower | SPR-315E-WHT | mono | 315 | 290 | +5/-3 | 5 | -3 | 17.9428 | 19.3 | 54.7 | 5.76 | 64.2 | 6.14 | -0.38% | -0.28% | 0.03 | 45 | 20 | yes | MC4 | black | white | 61.39 | 41.18 | 1.81 | 17.5558 | 41 | 10 |  | Check |  | SunPower
SunPower | SPR-318E-WHT-D | mono | 318 | 292.9 | +5/-3 | 5 | -3 | 18.1136 | 19.5 | 54.7 | 5.82 | 64.7 | 6.2 | -0.38% | -0.28% | 0.03 | 45 | 20 | yes | MC4 | black | white | 61.39 | 41.18 | 1.81 | 17.5558 | 41 | 10 |  | Check |  | SunPower
SunPower | SPR-320E-WHT-D | mono | 320 |  | +5/-3 | 5 | -3 |  | 19.6 | 54.7 | 5.86 | 64.6 | 6.24 | -0.38% | -0.27% | 0.03 | 45 | 20 | [11 empty] | Check | 2012-12-24 | SunPower
SunPower | SPR-327NE-WHT-D | n/a | 327 |  | +5/-3 | 5 | -3 |  | 20.1 | 54.7 | 5.98 | 64.9 | 6.46 | -0.38% | -0.27% | 0.03 | 45 | 20 | [11 empty] | Check | 2012-12-24 | SunPower
SunPower | SPR-X21-335 | mono | 335 |  | +5/-0 | 5 | 0 |  |  | 57.3 | 5.85 | 67.9 | 6.23 | -0.3% | -0.24% |  |  | 15 | [11 empty] | Check | 2015-11-25 | SunPower
SunPower | SPR-X21-345 | mono | 345 |  | +5/-0 | 5 | 0 |  |  | 57.3 | 6.02 | 68.2 | 6.39 | -0.3% | -0.24% |  |  | 15 | [11 empty] | Check | 2015-11-25 | SunPower
SunPower | SPR-435E-WHT-D | mono | 435 |  | +5/-0 | 5 | 0 |  |  | 72.9 | 5.97 | 85.6 | 6.43 | -0.42% | -0.32% |  |  | 20 | [11 empty] | Check | 2015-12-04 | SunPower
SunPower | SPR-440NE-WHT-D | mono | 440 |  | +5/-0 | 5 | 0 |  |  | 72.9 | 6.04 | 86.5 | 6.5 | -0.42% | -0.32% |  |  | 20 | [11 empty] | Check | 2015-12-04 | SunPower
SunPower | SPR-445(N)J(X)-WHT-D | mono | 445 |  | +5/-0 | 5 | 0 |  |  | 76.7 | 5.8 | 90.5 | 6.21 | -0.39% | -0.29% |  |  | 20 | [11 empty] | Check | 2015-12-04 | SunPower
SunPower | SPR-X22-360 | mono | 360 |  | +5/-0 | 5 | 0 |  |  | 59.1 | 6.09 | 69.5 | 6.48 | -0.29% | -0.24% |  |  | 15 | [11 empty] | 600 | 2018-01-02 | SunPower
SunPower | SPR-390E-WHT-D | mono | 390 |  | +5/-0 | 5 | 0 |  |  | 72.9 | 5.35 | 85.3 | 5.72 | -0.35% | -0.23% |  |  | 20 | [11 empty] | Check | 2015-12-04 | SunPower
SunPower | SPR-400E-WHT-D | mono | 400 |  | +5/-0 | 5 | 0 |  |  | 72.9 | 5.49 | 85.3 | 5.87 | -0.35% | -0.23% |  |  | 20 | [11 empty] | Check | 2015-12-04 | SunPower
SunPower | SPR-410NE-WHT-D | mono | 410 |  | +5/-0 | 5 | 0 |  |  | 72.9 | 5.62 | 85.3 | 6.01 | -0.35% | -0.27% |  |  | 20 | [11 empty] | Check | 2015-12-04 | SunPower
SunPower | SPR-415E-WHT-D | mono | 415 |  | +5/-0 | 5 | 0 |  |  | 72.9 | 5.69 | 85.3 | 6.09 | -0.35% | -0.23% |  |  | 20 | [11 empty] | Check | 2015-12-04 | SunPower
SunPower | SPR-425E-WHT-D | mono | 425 |  | +5/-0 | 5 | 0 |  |  | 72.9 | 5.83 | 85.6 | 6.18 | -0.42% | -0.32% |  |  | 20 | [11 empty] | Check | 2015-12-04 | SunPower
SunPower | SPR-E19-320 | mono | 320 |  | +5/-0 | 5 | 0 |  |  | 54.7 | 5.86 | 64.8 | 6.24 | -0.35% | -0.27% |  |  | 15 | [11 empty] | 600 | 2018-02-09 | SunPower
SunPower | SPR-E20-327 | mono | 327 |  | +5/-0 | 5 | 0 |  |  | 54.7 | 5.98 | 64.9 | 6.46 | -0.35% | -0.27% |  |  | 15 | [11 empty] | 600 | 2018-02-09 | SunPower
SunPower | SPR-X22-360-COM | mono | 360 | 334.4 | +5/-0 | 5 | 0 |  |  | 59.1 | 6.09 | 69.5 | 6.48 | -0.29% | -0.24% |  |  | 15 |  |  |  |  | 61.4 | 41.2 | 1.8 |  | 41 |  |  | 1000 | 2018-06-07 | SunPower
SunPower | SPR-P17-330-COM-1000V | mono | 330 |  | +5/-0 | 5 | 0 |  |  | 41.9 | 7.88 | 50.9 | 8.47 | -0.37% | -0.34% |  |  | 15 | [11 empty] | 1000 | 2018-02-09 | SunPower
SunPower | SPR-P17-335-COM-1000V | mono | 335 |  | +5/-0 | 5 | 0 |  |  | 42.2 | 7.94 | 51.1 | 8.51 | -0.37% | -0.34% |  |  | 15 | [11 empty] | 1000 | 2018-02-09 | SunPower
SunPower | SPR-P17-340-COM-1000V | mono | 340 |  | +5/-0 | 5 | 0 |  |  | 42.5 | 8 | 51.3 | 8.52 | -0.37% | -0.34% |  |  | 15 | [11 empty] | 1000 | 2018-02-09 | SunPower
SunPower | SPR-P17-345-COM-1000V | mono | 345 |  | +5/-0 | 5 | 0 |  |  | 42.8 | 8.06 | 51.5 | 8.57 | -0.37% | -0.34% |  |  | 15 | [11 empty] | 1000 | 2018-02-09 | SunPower
SunPower | SPR-P17-350-COM-1000V | mono | 350 |  | +5/-0 | 5 | 0 |  |  | 43.1 | 8.12 | 51.7 | 8.65 | -0.37% | -0.34% |  |  | 15 | [11 empty] | 1000 | 2018-02-09 | SunPower
SunPower | SPR-P17-335-COM-1500V | mono | 335 |  | +5/-0 | 5 | 0 |  |  | 42.2 | 7.94 | 51.1 | 8.51 | -0.37% | -0.34% |  |  | 15 | [11 empty] | 1500 | 2018-02-09 | SunPower
SunPower | SPR-P17-340-COM-1500V | mono | 340 |  | +5/-0 | 5 | 0 |  |  | 42.5 | 8 | 51.3 | 8.52 | -0.37% | -0.34% |  |  | 15 | [11 empty] | 1500 | 2018-02-09 | SunPower
SunPower | SPR-P17-345-COM-1500V | mono | 345 |  | +5/-0 | 5 | 0 |  |  | 42.8 | 8.06 | 51.5 | 8.57 | -0.37% | -0.34% |  |  | 15 | [11 empty] | 1500 | 2018-02-09 | SunPower
SunPower | SPR-P17-350-COM-1500V | mono | 350 |  | +5/-0 | 5 | 0 |  |  | 43.1 | 8.12 | 51.7 | 8.65 | -0.37% | -0.34% |  |  | 15 | [11 empty] | 1500 | 2018-02-09 | SunPower
SunPower | SPR-P17-350-COM-1500V | mono | 350 |  | +5/-0 | 5 | 0 |  |  | 43.4 | 8.18 | 51.9 | 8.68 | -0.37% | -0.34% |  |  | 15 | [11 empty] | 1500 | 2018-02-09 | SunPower
SunPower | SPR-E20-320-C-AC @ 208 | mono | 320 |  | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [8 empty] | 61.3 | 41.2 | [5 empty] | Check | 2018-06-12 | SunPower |  | Yes | 320 | 320 | 240 | 1.54 | 96 | 10 | 20 | 208 | 1
SunPower | SPR-E20-320-C-AC @ 240 | mono | 320 |  | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [8 empty] | 61.3 | 41.2 | [5 empty] | Check | 2018-06-12 | SunPower |  | Yes | 320 | 320 | 240 | 1.33 | 96 | 12 | 20 | 240 | 1
SunPower | SPR-E20-327-C-AC @ 208 | mono | 327 | 301.4 | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [8 empty] | 61.3 | 41.2 | [5 empty] | Check | 2018-06-12 | SunPower |  | Yes | 320 | 320 | 240 | 1.54 | 96 | 10 | 20 | 208 | 1
SunPower | SPR-E20-327-C-AC @ 240 | mono | 327 | 301.4 | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [8 empty] | 61.3 | 41.2 | [5 empty] | Check | 2018-06-12 | SunPower |  | Yes | 320 | 320 | 240 | 1.33 | 96 | 12 | 20 | 240 | 1
SunPower | SPR-X20-327BLK-D-AC @ 208 | mono | 327 |  | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [8 empty] | 61.3 | 41.2 | [5 empty] | Check | 2018-06-12 | SunPower |  | Yes | 320 | 320 | 240 | 1.54 | 95.5 | 10 | 20 | 208 | 1
SunPower | SPR-X20-327BLK-D-AC @ 240 | mono | 327 |  | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [8 empty] | 61.3 | 41.2 | [5 empty] | Check | 2018-06-12 | SunPower |  | Yes | 320 | 320 | 240 | 1.33 | 96 | 12 | 20 | 240 | 1
SunPower | SPR-X21-335-C-AC @ 208 | mono | 335 |  | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [15 empty] | Check | 2017-08-15 | SunPower |  | Yes | 320 | 320 | 208 | 1.54 | 95.5 | 10 | 20 | 208 | 1
SunPower | SPR-X21-335-C-AC @ 240 | mono | 335 |  | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [15 empty] | Check | 2017-08-15 | SunPower |  | Yes | 320 | 320 | 240 | 1.33 | 96 | 12 | 20 | 240 | 1
SunPower | SPR-X21-345-C-AC @ 208 | mono | 345 | 323.3 | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [15 empty] | Check | 2017-08-15 | SunPower |  | Yes | 320 | 320 | 208 | 1.54 | 95.5 | 10 | 20 | 208 | 1
SunPower | SPR-X21-345-C-AC @ 240 | mono | 345 | 323.3 | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [15 empty] | Check | 2017-08-15 | SunPower |  | Yes | 320 | 320 | 240 | 1.33 | 96 | 12 | 20 | 240 | 1
SunPower | SPR-X21-350BLK-D-AC @ 208 | mono | 350 |  | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [15 empty] | Check | 2018-06-12 | SunPower |  | Yes | 320 | 320 | 240 | 1.54 | 95.5 | 10 | 20 | 208 | 1
SunPower | SPR-X21-350BLK-D-AC @ 240 | mono | 350 |  | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [15 empty] | Check | 2018-06-12 | SunPower |  | Yes | 320 | 320 | 240 | 1.33 | 96 | 12 | 20 | 240 | 1
SunPower | SPR-X22-360-C-AC @ 208 | mono | 360 |  | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [15 empty] | Check | 2017-08-15 | SunPower |  | Yes | 320 | 320 | 208 | 1.54 | 96 | 10 | 20 | 208 | 1
SunPower | SPR-X22-360-C-AC @ 240 | mono | 360 |  | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [15 empty] | Check | 2017-08-15 | SunPower |  | Yes | 320 | 320 | 240 | 1.33 | 96 | 12 | 20 | 240 | 1
SunPower | SPR-X22-360-D-AC @ 208 | mono | 360 |  | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [15 empty] | Check | 2017-08-15 | SunPower |  | Yes | 320 | 320 | 208 | 1.54 | 96 | 10 | 20 | 240 | 1
SunPower | SPR-X22-360-D-AC @ 240 | mono | 360 |  | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [15 empty] | Check | 2017-08-15 | SunPower |  | Yes | 320 | 320 | 240 | 1.33 | 96 | 12 | 20 | 240 | 1
SunPower | SPR-X22-370-D-AC @ 208 | mono | 370 |  | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [15 empty] | Check | 2017-08-15 | SunPower |  | Yes | 320 | 320 | 208 | 1.54 | 96 | 10 | 20 | 240 | 1
SunPower | SPR-X22-370-D-AC @ 240 | mono | 370 |  | +5/-0 | 5 | 0 | [6 empty] | -0.29% | [15 empty] | Check | 2017-08-15 | SunPower |  | Yes | 320 | 320 | 240 | 1.33 | 96 | 12 | 20 | 240 | 1
Sunpreme | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Sunpreme
Sunpreme | G60-02-180 |  | 180 |  | +3/-0 | 3 | -0 |  |  | 29.1 | 6.2 | 36.6 | 6.9 | -0.39% | -0.3% |  |  | 15 | [11 empty] | Check | 2013-11-27 | Sunpreme
Sunpreme | G60-02-185 |  | 185 |  | +3/-0 | 3 | -0 |  |  | 29.4 | 6.3 | 36.9 | 7 | -0.39% | -0.3% |  |  | 15 | [11 empty] | Check | 2013-11-27 | Sunpreme
Sunpreme | G60-02-190 |  | 190 |  | +3/-0 | 3 | -0 |  |  | 29.7 | 6.4 | 37.1 | 7.1 | -0.39% | -0.3% |  |  | 15 | [11 empty] | Check | 2013-11-27 | Sunpreme
Sunpreme | G60-02-195 |  | 195 |  | +3/-0 | 3 | -0 |  |  | 30.1 | 6.5 | 37.6 | 7.2 | -0.39% | -0.3% |  |  | 15 | [11 empty] | Check | 2013-11-27 | Sunpreme
Sunpreme | G60-02-200 |  | 200 |  | +3/-0 | 3 | -0 |  |  | 30.4 | 6.6 | 37.9 | 7.3 | -0.39% | -0.3% |  |  | 15 | [11 empty] | Check | 2013-11-27 | Sunpreme
Sunpreme | G60-02-205 |  | 205 |  | +3/-0 | 3 | -0 |  |  | 30.7 | 6.7 | 38.3 | 7.4 | -0.39% | -0.3% |  |  | 15 | [11 empty] | Check | 2013-11-27 | Sunpreme
Sunpreme | G60-02-210 |  | 210 |  | +3/-0 | 3 | -0 |  |  | 31 | 6.8 | 38.7 | 7.5 | -0.39% | -0.3% |  |  | 15 | [11 empty] | Check | 2013-11-27 | Sunpreme
Sunpreme | GX-230 |  | 230 |  | +3/-0 | 3 | -0 |  |  | 32.9 | 7 | 47.4 | 7.6 | -0.39% | -0.34% |  |  | 15 | [11 empty] | Check | 2013-11-27 | Sunpreme
Sunpreme | GX-235 |  | 235 |  | +3/-0 | 3 | -0 |  |  | 33.1 | 7.1 | 47.7 | 7.7 | -0.39% | -0.34% |  |  | 15 | [11 empty] | Check | 2013-11-27 | Sunpreme
Sunpreme | GX-240 |  | 240 |  | +3/-0 | 3 | -0 |  |  | 33.3 | 7.2 | 42 | 7.8 | -0.39% | -0.34% |  |  | 15 | [11 empty] | Check | 2013-11-27 | Sunpreme
Sunpreme | GX-280 |  | 280 |  | +3/-0 | 3 | -0 |  |  | 37.2 | 7.5 | 48.2 | 8 | -0.35% | -0.2% |  |  | 15 | [11 empty] | Check | 2013-11-27 | Sunpreme
Sunpreme | GX-290 |  | 290 |  | +3/-0 | 3 | -0 |  |  | 37.9 | 7.7 | 49 | 8.2 | -0.35% | -0.2% |  |  | 15 | [11 empty] | Check | 2013-11-27 | Sunpreme
Sunpreme | GX-300 |  | 300 |  | +3/-0 | 3 | -0 |  |  | 38.5 | 7.8 | 49.7 | 8.5 | -0.35% | -0.2% |  |  | 15 | [11 empty] | Check | 2013-11-27 | Sunpreme
Sunpreme | GxB-290 | mono | 290 |  | +5/-3 | 5 | -3 |  |  | 33.7 | 8.6 | 43.9 | 9.2 | -0.28% | -0.21% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Sunpreme
Sunpreme | GxB-300 | mono | 300 |  | +5/-3 | 5 | -3 |  |  | 34.5 | 8.7 | 44.9 | 9.3 | -0.28% | -0.21% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Sunpreme
Sunpreme | GxB-310 | mono | 310 |  | +5/-3 | 5 | -3 |  |  | 35.2 | 8.8 | 45.9 | 9.4 | -0.28% | -0.21% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Sunpreme
Sunpreme | GxB-290-SL | mono | 290 |  | +5/-3 | 5 | -3 |  |  | 33.7 | 8.6 | 43.9 | 9.2 | -0.28% | -0.21% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Sunpreme
Sunpreme | GxB-300-SL | mono | 300 |  | +5/-3 | 5 | -3 |  |  | 34.5 | 8.7 | 44.9 | 9.3 | -0.28% | -0.21% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Sunpreme
Sunpreme | GxB -310-SL | mono | 310 |  | +5/-3 | 5 | -3 |  |  | 35.6 | 8.7 | 45.1 | 9.3 | -0.28% | -0.21% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Sunpreme
Sunpreme | GxB-350 | mono | 350 |  | +5/-3 | 5 | -3 |  |  | 41.2 | 8.5 | 53 | 9 | -0.28% | -0.23% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Sunpreme
Sunpreme | GxB-360 | mono | 360 |  | +5/-3 | 5 | -3 |  |  | 41.9 | 8.6 | 53.9 | 9.1 | -0.28% | -0.23% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Sunpreme
Sunpreme | GxB-370 | mono | 370 |  | +5/-3 | 5 | -3 |  |  | 42.5 | 8.7 | 54.7 | 9.2 | -0.28% | -0.23% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Sunpreme
Suntech | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Suntech
Suntech | PLUTO240-Wde | poly | 240 | 217.4 | +5/-0 | 5 | 0 | 13.5084 | 14.8 | 29.6 | 8.11 | 36.9 | 8.46 | -0.4% | -0.314% | 0.051 | 45 | 20 | yes | H4 | black | white | 65.6 | 39 | 2 | 17.7667 | 43.7 | 10 |  | Check |  | Suntech
Suntech | PLUTO245-Wde | poly | 245 | 222 | +5/-0 | 5 | 0 | 13.7899 | 14.8 | 29.8 | 8.23 | 37.2 | 8.65 | -0.4% | -0.314% | 0.051 | 45 | 20 | yes | H4 | black | white | 65.6 | 39 | 2 | 17.7667 | 43.7 | 10 |  | Check |  | Suntech
Suntech | STP160-24/Ab-1 | poly | 160 |  | +3/-3 | 3 | -3 | 11.6 | 12.5 | 34.4 | 4.65 | 43.2 | 5 | -0.47% | -0.34% |  |  | 15 |  | MC |  |  | 62.2 | 31.8 | 1.38 | 13.7358 | 34.17 | 5 |  | Check |  | Suntech
Suntech | STP160S-24/Ab-1 | mono | 160 |  | +3/-3 | 3 | -3 | 11.6 | 12.5 | 34.4 | 4.65 | 43.2 | 5 | -0.48% | -0.34% |  |  | 15 |  | MC |  |  | 62.2 | 31.8 | 1.38 | 13.7358 | 34.17 | 5 |  | Check |  | Suntech
Suntech | STP165-24/Ab-1 | poly | 165 |  | +3/-3 | 3 | -3 | 12 | 12.9 | 34.8 | 4.74 | 43.6 | 5.04 | -0.47% | -0.34% |  |  | 15 |  | MC |  |  | 62.2 | 31.8 | 1.38 | 13.7358 | 34.17 | 5 |  | Check |  | Suntech
Suntech | STP165S-24/Ab-1 | mono | 165 |  | +3/-3 | 3 | -3 | 12 | 12.9 | 34.8 | 4.74 | 43.6 | 5.04 | -0.48% | -0.34% |  |  | 15 |  | MC |  |  | 62.2 | 31.8 | 1.38 | 13.7358 | 34.17 | 5 |  | Check |  | Suntech
Suntech | STP170-24/Ab-1 | poly | 170 |  | +3/-3 | 3 | -3 | 12.4 | 13.3 | 35.2 | 4.83 | 43.8 | 5.14 | -0.47% | -0.34% |  |  | 15 |  | MC |  |  | 62.2 | 31.8 | 1.38 | 13.7358 | 34.17 | 5 |  | Check |  | Suntech
Suntech | STP170S-24/Ab-1 | mono | 170 |  | +3/-3 | 3 | -3 | 12.4 | 13.3 | 35.2 | 4.83 | 43.8 | 5.14 | -0.48% | -0.34% |  |  | 15 |  | MC |  |  | 62.2 | 31.8 | 1.38 | 13.7358 | 34.17 | 5 |  | Check |  | Suntech
Suntech | STP175-24/Ab-1 | poly | 175 |  | +3/-3 | 3 | -3 | 12.7 | 13.7 | 35.2 | 4.95 | 44.2 | 5.2 | -0.47% | -0.34% |  |  | 15 |  | MC |  |  | 62.2 | 31.8 | 1.38 | 13.7358 | 34.17 | 5 |  | Check |  | Suntech
Suntech | STP175S-24/Ab-1 | mono | 175 |  | +3/-3 | 3 | -3 | 12.7 | 13.7 | 35.2 | 4.95 | 44.2 | 5.2 | -0.48% | -0.34% |  |  | 15 |  | MC |  |  | 62.2 | 31.8 | 1.38 | 13.7358 | 34.17 | 5 |  | Check |  | Suntech
Suntech | STP180-24/Ab-1 | poly | 180 |  | +3/-3 | 3 | -3 | 13.1 | 14.1 | 35.6 | 5.05 | 44.4 | 5.4 | -0.47% | -0.34% |  |  | 15 |  | MC |  |  | 62.2 | 31.8 | 1.38 | 13.7358 | 34.17 | 5 |  | Check |  | Suntech
Suntech | STP180S-24/Ab-1 | mono | 180 |  | +3/-3 | 3 | -3 | 13.1 | 14.1 | 35.6 | 5.05 | 44.4 | 5.4 | -0.48% | -0.34% |  |  | 15 |  | MC |  |  | 62.2 | 31.8 | 1.38 | 13.7358 | 34.17 | 5 |  | Check |  | Suntech
Suntech | STP190-18/Ub-1 | poly | 190 |  | +3/-3 | 3 | -3 | 12 | 12.9 | 26 | 7.31 | 33 | 7.89 | -0.48% | -0.34% |  |  | 20 |  | MC |  |  | 58.3 | 39.1 | 1.38 | 15.8301 | 37.04 | 5 |  | Check |  | Suntech
Suntech | STP190S - 24/Ad(b)+ | mono | 190 | 171.5 | +5/-0 | 5 | 0 | 13.8324 | 14.9 | 36.6 | 5.2 | 45.2 | 5.62 | -0.45% | -0.34% | 0.05 | 45 | 15 | yes | H4 | silver/black | white/black | 62.2 | 31.8 | 1.4 | 13.7358 | 34.1 | 10 |  | Check |  | Suntech
Suntech | STP190S-18/Ub-1 | mono | 190 |  | +3/-3 | 3 | -3 | 12 | 12.9 | 26.2 | 7.25 | 33.2 | 7.84 | -0.48% | -0.34% |  |  | 20 |  | MC |  |  | 58.3 | 39.1 | 1.38 | 15.8301 | 37.04 | 5 |  | Check |  | Suntech
Suntech | STP200-18/Ub-1 | poly | 200 |  | +3/-3 | 3 | -3 | 12.6 | 13.6 | 26.2 | 7.63 | 33.4 | 8.12 | -0.48% | -0.34% |  |  | 20 |  | MC |  |  | 58.3 | 39.1 | 1.38 | 15.8301 | 37.04 | 5 |  | Check |  | Suntech
Suntech | STP200S-18/Ub-1 | mono | 200 |  | +3/-3 | 3 | -3 | 12.6 | 13.6 | 26.2 | 7.63 | 33.6 | 8.1 | -0.48% | -0.34% |  |  | 20 |  | MC |  |  | 58.3 | 39.1 | 1.38 | 15.8301 | 37.04 | 5 |  | Check |  | Suntech
Suntech | STP205-18/Ud |  | 205 |  | +5/-0 | 5 | 0 |  |  | 26.3 | 7.8 | 33.5 | 8.23 | -0.44% | -0.33% |  |  | 20 | [7 empty] | 0 |  |  |  | Check |  | Suntech
Suntech | STP210-18/Ub-1 | poly | 210 |  | +3/-3 | 3 | -3 | 13.3 | 14.3 | 26.4 | 7.95 | 33.6 | 8.33 | -0.48% | -0.34% |  |  | 20 |  | MC |  |  | 58.3 | 39.1 | 1.38 | 15.8301 | 37.04 | 5 |  | Check |  | Suntech
Suntech | STP210S-18/Ub-1 | mono | 210 |  | +3/-3 | 3 | -3 | 13.3 | 14.3 | 26.4 | 7.95 | 33.6 | 8.33 | -0.48% | -0.34% |  |  | 20 |  | MC |  |  | 58.3 | 39.1 | 1.38 | 15.8301 | 37.04 | 5 |  | Check |  | Suntech
Suntech | STP225 - 20/Wd | poly | 225 | 203.9 | +5/-0 | 5 | 0 | 12.6642 | 13.6 | 29.6 | 7.61 | 36.7 | 8.15 | -0.44% | -0.33% | 0.055 | 45 | 15 | yes | H4 | silver | white | 65.6 | 39 | 2 | 17.7667 | 43.7 | 10 |  | Check |  | Suntech
Suntech | STP230 - 20/Wd | poly | 230 | 208.6 | +5/-0 | 5 | 0 | 12.9456 | 13.9 | 29.8 | 7.72 | 36.8 | 8.25 | -0.44% | -0.33% | 0.055 | 45 | 20 | yes | H4 | silver | white | 65.6 | 39 | 2 | 17.7667 | 43.7 | 10 |  | Check |  | Suntech
Suntech | STP235 - 20/Wd | poly | 235 |  | +5/-0 | 5 | 0 |  |  | 30.2 | 7.79 | 37 | 8.35 | -0.44% | -0.33% | 0.055 | 45 | 20 | [11 empty] | Check | 2013-12-20 | Suntech
Suntech | STP240 - 20/Wd | poly | 240 |  | +5/-0 | 5 | 0 |  |  | 30.2 | 7.95 | 37.2 | 8.43 | -0.44% | -0.33% | 0.055 | 45 | 20 | [11 empty] | Check | 2013-12-20 | Suntech
Suntech | STP250S-20/Wdb | mono | 250 |  | +5/-0 | 5 | 0 |  |  | 30.7 | 8.15 | 37.4 | 8.63 | -0.44% | -0.34% |  |  | 20 | [11 empty] | Check | 2014-05-23 | Suntech
Suntech | STP255S-20/Wdb | mono | 255 |  | +5/-0 | 5 | 0 |  |  | 30.8 | 8.28 | 37.6 | 8.76 | -0.44% | -0.34% |  |  | 20 | [11 empty] | Check | 2014-05-23 | Suntech
Suntech | STP255-20/Wem | poly | 255 |  | +5/-0 | 5 | 0 |  |  | 30.8 | 8.28 | 37.6 | 8.76 | -0.42% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP260-20/Wem | poly | 260 |  | +5/-0 | 5 | 0 |  |  | 30.9 | 8.42 | 37.7 | 8.89 | -0.42% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP265-20/Wem | poly | 265 |  | +5/-0 | 5 | 0 |  |  | 31 | 8.56 | 37.8 | 9.02 | -0.42% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP265S-20/Wem | mono | 265 |  | +5/-0 | 5 | 0 |  |  | 30.5 | 8.69 | 38.1 | 9.22 | -0.42% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP270S-20/Wem | mono | 270 |  | +5/-0 | 5 | 0 |  |  | 30.8 | 8.77 | 38.3 | 9.28 | -0.42% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP275S-20/Wem | mono | 275 |  | +5/-0 | 5 | 0 |  |  | 31.1 | 8.85 | 38.5 | 9.34 | -0.42% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP260S-20/Web | mono | 260 |  | +5/-0 | 5 | 0 |  |  | 30.2 | 8.61 | 37.9 | 9.17 | -0.42% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP265S-20/Web | mono | 265 |  | +5/-0 | 5 | 0 |  |  | 30.5 | 8.69 | 38.1 | 9.22 | -0.42% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP270S-20/Web | mono | 270 |  | +5/-0 | 5 | 0 |  |  | 30.8 | 8.77 | 38.3 | 9.28 | -0.42% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP280S-20/Web | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 31.5 | 8.89 | 39.4 | 9.41 | -0.4% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP285S-20/Web | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 31.6 | 9.02 | 39.6 | 9.48 | -0.4% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP265S-20/Wew | mono | 265 |  | +5/-0 | 5 | 0 |  |  | 30.5 | 8.69 | 38.1 | 9.22 | -0.42% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP270S-20/Wew | mono | 270 |  | +5/-0 | 5 | 0 |  |  | 30.8 | 8.77 | 38.3 | 9.28 | -0.42% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP275S-20/Wew | mono | 275 |  | +5/-0 | 5 | 0 |  |  | 31.1 | 8.85 | 38.5 | 9.34 | -0.42% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP280S-20/Wew | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 31.5 | 8.89 | 39.4 | 9.41 | -0.4% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP285S-20/Wew | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 31.6 | 9.02 | 39.6 | 9.48 | -0.4% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP290S-20/Wew | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 31.7 | 9.15 | 39.8 | 9.55 | -0.4% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP260-24/Vb -1 |  | 260 |  | +3/-3 | 3 | -3 | 12.4 | 13.4 | 34.2 | 7.47 | 44 | 8.09 | -0.47% | -0.34% |  |  | 20 |  | MC |  |  | 77 | 39.1 | 2 | 20.9076 | 59.5 |  |  | Check |  | Suntech
Suntech | STP270-24/Vb -1 |  | 270 |  | +3/-3 | 3 | -3 | 12.9 | 13.9 | 35 | 7.71 | 44.5 | 8.2 | -0.47% | -0.34% |  |  | 20 |  | MC |  |  | 77 | 39.1 | 2 | 20.9076 | 59.5 |  |  | Check |  | Suntech
Suntech | STP275 - 24/Vd | poly | 275 | 249.3 | +5/-0 | 5 | 0 | 13.1531 | 14.4 | 35.1 | 7.84 | 44.7 | 8.26 | -0.44% | -0.33% | 0.055 | 45 | 15 | yes | H4 | silver | white | 77 | 39.1 | 2 | 20.9076 | 59.5 | 10 |  | Check |  | Suntech
Suntech | STP275 - VRM - 1 | poly | 275 | 249.3 | +5/-0 | 5 | 0 | 12.2158 | 14.4 | 35.1 | 7.84 | 44.7 | 8.26 | -0.44% | -0.33% | 0.055 | 45 | 20 | yes | H4 | silver | white | 77 | 42.1 | 2.5 | 22.5118 | 64 | 10 |  | Check |  | Suntech
Suntech | STP280 - 24/Vd | poly | 280 | 254 | +5/-0 | 5 | 0 | 13.3922 | 14.4 | 35.2 | 7.95 | 44.8 | 8.33 | -0.44% | -0.33% | 0.055 | 45 | 15 | yes | H4 | silver | white | 77 | 39.1 | 2 | 20.9076 | 59.5 | 10 |  | Check |  | Suntech
Suntech | STP280 - VRM - 1 | poly | 280 | 254 | +5/-0 | 5 | 0 | 12.4379 | 14.4 | 35.2 | 7.95 | 44.8 | 8.33 | -0.44% | -0.33% | 0.055 | 45 | 20 | yes | H4 | silver | white | 77 | 42.1 | 2.5 | 22.5118 | 64 | 10 |  | Check |  | Suntech
Suntech | STP280-24/Vb -1 |  | 280 |  | +3/-3 | 3 | -3 | 13.4 | 14.4 | 35.2 | 7.95 | 44.8 | 8.33 | -0.47% | -0.34% |  |  | 20 |  | MC |  |  | 77 | 39.1 | 2 | 20.9076 | 59.5 |  |  | Check |  | Suntech
Suntech | STP285 - 24/Vd | poly | 285 | 258.6 | +5/-0 | 5 | 0 | 13.6314 | 14.9 | 35.4 | 8.06 | 44.9 | 8.37 | -0.44% | -0.33% | 0.055 | 45 | 20 | yes | H4 | silver | white | 77 | 39.1 | 2 | 20.9076 | 59.5 | 10 |  | Check |  | Suntech
Suntech | STP290 - 24/Vd | poly | 290 | 263.3 | +5/-0 | 5 | 0 | 13.8705 | 14.9 | 35.6 | 8.15 | 45 | 8.42 | -0.44% | -0.33% | 0.055 | 45 | 20 | yes | H4 | silver | white | 77 | 39.1 | 2 | 20.9076 | 59.5 | 10 |  | Check |  | Suntech
Suntech | STP295 - 24/Ve | poly | 295 |  | +5/-0 | 5 | 0 |  |  | 35.6 | 8.29 | 44.3 | 8.74 | -0.43% | -0.33% |  |  | 20 | [11 empty] | Check |  | Suntech
Suntech | STP300 - 24/Ve | poly | 300 |  | +5/-0 | 5 | 0 |  |  | 35.9 | 8.36 | 44.5 | 8.83 | -0.43% | -0.33% |  |  | 20 | [11 empty] | Check |  | Suntech
Suntech | STP305 - 24/Ve | poly | 305 |  | +5/-0 | 5 | 0 |  |  | 36.2 | 8.43 | 44.7 | 8.89 | -0.43% | -0.33% |  |  | 20 | [11 empty] | Check |  | Suntech
Suntech | STP305-24/Vem | poly | 305 |  | +5/-0 | 5 | 0 |  |  | 36.2 | 8.43 | 44.7 | 8.89 | -0.42% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP310-24/Vem | poly | 310 |  | +5/-0 | 5 | 0 |  |  | 36.5 | 8.5 | 44.9 | 8.96 | -0.42% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP315-24/Vem | poly | 315 |  | +5/-0 | 5 | 0 |  |  | 36.8 | 8.56 | 45.1 | 9.02 | -0.42% | -0.33% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP320S-24/Vem | mono | 320 |  | +5/-0 | 5 | 0 |  |  | 36.9 | 8.69 | 45.6 | 9.21 | -0.42% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Suntech | STP325S-24/Vem | mono | 325 |  | +5/-0 | 5 | 0 |  |  | 37.1 | 8.77 | 45.8 | 9.28 | -0.42% | -0.34% |  |  | 20 | [11 empty] | Check | 2015-11-25 | Suntech
Sunwize | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Sunwize
Sunwize | SW100C | mono | 100 |  | +5/-5 | 5 | -5 | 9.9466 | 15 | 23 | 4.4 | 28.5 | 5 | -0.5% | -0.5% |  |  | 10 |  | J-Box |  |  | 56.93 | 25.43 | 1.34 | 10.0537 | 26 | 1 |  | Check |  | Sunwize
Sunwize | SW115 | mono | 115 |  | +5/-5 | 5 | -5 | 11.4386 | 15 | 16.7 | 6.89 | 21 | 7.7 | -0.5% | -0.5% |  |  | 12 |  | J-Box |  |  | 56.93 | 25.43 | 1.34 | 10.0537 | 26 | 1 |  | Check |  | Sunwize
Sunwize | SW120 | mono | 120 |  | +5/-5 | 5 | -5 | 11.9359 | 15 | 16.7 | 7.18 | 21 | 8 | -0.5% | -0.5% |  |  | 13 |  | J-Box |  |  | 56.93 | 25.43 | 1.34 | 10.0537 | 26 | 1 |  | Check |  | Sunwize
Sunwize | SW150 | mono | 150 |  | +5/-5 | 5 | -5 | 10.7128 | 15 | 33.4 | 4.5 | 42 | 5.11 | -0.5% | -0.29% |  |  | 15 |  | MC |  |  | 66.61 | 30.27 | 1.65 | 14.002 | 44 | 1 |  | Check |  | Sunwize
Sunwize | SW155 | mono | 155 |  | +5/-5 | 5 | -5 | 11.0699 | 15 | 33.4 | 4.65 | 42 | 5.28 | -0.5% | -0.29% |  |  | 15 |  | MC |  |  | 66.61 | 30.27 | 1.65 | 14.002 | 44 | 1 |  | Check |  | Sunwize
Sunwize | SW160 | mono | 160 |  | +5/-5 | 5 | -5 | 11.427 | 15 | 33.4 | 4.79 | 42 | 5.43 | -0.5% | -0.29% |  |  | 15 |  | MC |  |  | 66.61 | 30.27 | 1.65 | 14.002 | 44 | 1 |  | Check |  | Sunwize
Sunwize | SW165-L |  | 165 | [6 empty] | 33.4 | 4.95 | 42 | 5.62 | -0.5% | -0.29% | [14 empty] | Check |  | Sunwize
Talesun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Talesun
Talesun | TP660P 235 | poly | 235 |  | +5/-0 | 5 | 0 |  |  | 29.5 | 7.97 | 36.8 | 8.59 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2013-12-20 | Talesun
Talesun | TP660P 240 | poly | 240 |  | +5/-0 | 5 | 0 |  |  | 29.7 | 8.08 | 36.9 | 8.62 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2013-12-21 | Talesun
Talesun | TP660P 245 | poly | 245 |  | +5/-0 | 5 | 0 |  |  | 30.1 | 8.14 | 37.1 | 8.65 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2013-12-22 | Talesun
Talesun | TP660P 250 | poly | 250 |  | +5/-0 | 5 | 0 |  |  | 30.3 | 8.25 | 37.3 | 8.69 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2013-12-23 | Talesun
Talesun | TP660P 255 | poly | 255 |  | +5/-0 | 5 | 0 |  |  | 30.4 | 8.39 | 37.5 | 8.73 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2013-12-24 | Talesun
Talesun | TP672P 285 | poly | 285 |  | +5/-0 | 5 | 0 |  |  | 35.8 | 7.97 | 44.6 | 8.65 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2014-05-23 | Talesun
Talesun | TP672P 290 | poly | 290 |  | +5/-0 | 5 | 0 |  |  | 35.9 | 8.09 | 44.7 | 8.72 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2014-05-23 | Talesun
Talesun | TP672P 295 | poly | 295 |  | +5/-0 | 5 | 0 |  |  | 36 | 8.22 | 44.9 | 8.8 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2014-05-23 | Talesun
Talesun | TP672P 300 | poly | 300 |  | +5/-0 | 5 | 0 |  |  | 36.1 | 8.33 | 45 | 8.88 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2014-05-23 | Talesun
Talesun | TP672P 305 | poly | 305 |  | +5/-0 | 5 | 0 |  |  | 36.2 | 8.43 | 45.1 | 8.97 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2014-05-23 | Talesun
Talesun | TP672P 310 | poly | 310 |  | +5/-0 | 5 | 0 |  |  | 36.3 | 8.55 | 45.2 | 9.07 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2014-05-23 | Talesun
Talesun | TP672P-B-270 | poly | 270 |  | +3/-0 | 3 | 0 |  |  | 35.4 | 7.64 | 44.3 | 8.4 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Talesun | TP672P-B-275 | poly | 275 |  | +3/-0 | 3 | 0 |  |  | 35.5 | 7.76 | 44.4 | 8.49 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Talesun | TP672P-B-280 | poly | 280 |  | +3/-0 | 3 | 0 |  |  | 35.7 | 7.86 | 44.5 | 8.56 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Talesun | TP672P-B-285 | poly | 285 |  | +3/-0 | 3 | 0 |  |  | 35.8 | 7.97 | 44.6 | 8.65 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Talesun | TP672P-B-290 | poly | 290 |  | +3/-0 | 3 | 0 |  |  | 35.9 | 8.09 | 44.7 | 8.72 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Talesun | TP672P-B-295 | poly | 295 |  | +3/-0 | 3 | 0 |  |  | 36 | 8.22 | 44.9 | 8.8 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Talesun | TP672P-B-300 | poly | 300 |  | +3/-0 | 3 | 0 |  |  | 36.1 | 8.33 | 45 | 8.88 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Talesun | TP672M-270 | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 35.1 | 7.7 | 43.9 | 8.39 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Talesun | TP672M-275 | mono | 275 |  | +3/-0 | 3 | 0 |  |  | 35.3 | 7.8 | 44.1 | 8.46 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Talesun | TP672M-280 | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 35.5 | 7.89 | 44.3 | 8.53 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Talesun | TP672M-285 | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 35.7 | 7.99 | 44.5 | 8.59 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Talesun | TP672M-290 | mono | 290 |  | +3/-0 | 3 | 0 |  |  | 35.8 | 8.11 | 44.7 | 8.65 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Talesun | TP672M-B-295 | mono | 295 |  | +3/-0 | 3 | 0 |  |  | 36.5 | 8.1 | 45.4 | 8.73 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Talesun | TP672M-B-300 | mono | 300 |  | +3/-0 | 3 | 0 |  |  | 36.5 | 8.22 | 45.5 | 8.81 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Talesun | TP672M-B-305 | mono | 305 |  | +3/-0 | 3 | 0 |  |  | 36.7 | 8.33 | 45.6 | 8.9 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Talesun | TP672M-B-310 | mono | 310 |  | +3/-0 | 3 | 0 |  |  | 36.7 | 8.45 | 45.7 | 8.98 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Talesun | TP672M-B-315 | mono | 315 |  | +3/-0 | 3 | 0 |  |  | 36.8 | 8.56 | 45.8 | 9.04 | -0.45% | -0.35% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Talesun
Tianwei New Energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Tianwei_New_Energy
Tianwei New Energy | TW175(35)D-1 | mono | 175 | 153 | +3/-0 | 3 | 0 | 12.7346 | 13.71 | 35.5 | 4.93 | 42.6 | 5.52 | -0.43% | -0.34% | 0.05 | 47 | 15 | yes | MC4 comp. | silver | white | 62.2 | 31.81 | 1.57 | 13.7402 | 34.17 | 5 |  | Check |  | Tianwei_New_Energy
Tianwei New Energy | TW180(35)D-1 | mono | 180 | 155.6 | +3/-0 | 3 | 0 | 13.0984 | 14.1 | 36 | 5 | 43.2 | 5.6 | -0.43% | -0.34% | 0.05 | 47 | 15 | yes | MC4 comp. | silver | white | 62.2 | 31.81 | 1.57 | 13.7402 | 34.17 | 5 |  | Check |  | Tianwei_New_Energy
Tianwei New Energy | TW185(35)D-1 | mono | 185 | 162.1 | +3/-0 | 3 | 0 | 13.4623 | 14.49 | 36.7 | 5.04 | 43.8 | 5.62 | -0.43% | -0.34% | 0.05 | 47 | 15 | yes | MC4 comp. | silver | white | 62.2 | 31.81 | 1.57 | 13.7402 | 34.17 | 5 |  | Check |  | Tianwei_New_Energy
Tianwei New Energy | TW225(28)P | poly | 225 | 195.8 | +3/-0 | 3 | 0 | 12.7087 | 13.68 | 29.3 | 7.68 | 36.65 | 8.6 | -0.44% | -0.34% | 0.06 | 47 | 15 | yes | MC4 comp. | silver | white | 65.07 | 39.17 | 1.77 | 17.6999 | 44.09 | 5 |  | Check |  | Tianwei_New_Energy
Tianwei New Energy | TW230(28)P | poly | 230 | 200.3 | +3/-0 | 3 | 0 | 12.9912 | 13.98 | 29.7 | 7.74 | 36.7 | 8.72 | -0.44% | -0.34% | 0.06 | 47 | 15 | yes | MC4 comp. | silver | white | 65.07 | 39.17 | 1.77 | 17.6999 | 44.09 | 5 |  | Check |  | Tianwei_New_Energy
Tianwei New Energy | TW235(28)P | poly | 235 | 204.8 | +3/-0 | 3 | 0 | 13.2736 | 14.29 | 30.1 | 7.81 | 36.7 | 8.86 | -0.44% | -0.34% | 0.06 | 47 | 15 | yes | MC4 comp. | silver | white | 65.07 | 39.17 | 1.77 | 17.6999 | 44.09 | 5 |  | Check |  | Tianwei_New_Energy
Tianwei New Energy | TW250B60-PA | poly | 250 |  | +2/-0 | 2 | 0 |  |  | 30.4 | 8.26 | 37.3 | 8.91 | -0.47% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Tianwei_New_Energy
Tianwei New Energy | TW255B60-PA | poly | 255 |  | +2/-0 | 2 | 0 |  |  | 30.6 | 8.37 | 37.5 | 9 | -0.47% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Tianwei_New_Energy
Tianwei New Energy | TW260B60-PA | poly | 260 |  | +2/-0 | 2 | 0 |  |  | 30.8 | 8.47 | 37.7 | 9.08 | -0.47% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Tianwei_New_Energy
Tianwei New Energy | TW265B60-PA | poly | 265 |  | +2/-0 | 2 | 0 |  |  | 31 | 8.58 | 37.8 | 9.17 | -0.47% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Tianwei_New_Energy
Tianwei New Energy | TW270B60-PA | poly | 270 |  | +2/-0 | 2 | 0 |  |  | 31.1 | 8.69 | 38 | 9.25 | -0.47% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Tianwei_New_Energy
Tianwei New Energy | TW275B60-PA | poly | 275 |  | +2/-0 | 2 | 0 |  |  | 31.2 | 8.82 | 38.2 | 9.33 | -0.47% | -0.37% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Tianwei_New_Energy
Tianwei New Energy | TW275P72-EA | poly | 275 |  | +2/-0 | 2 | 0 |  |  | 35.3 | 7.79 | 44.7 | 8.28 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Tianwei_New_Energy
Tianwei New Energy | TW280P72-EA | poly | 280 |  | +2/-0 | 2 | 0 |  |  | 35.6 | 7.87 | 44.9 | 8.38 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Tianwei_New_Energy
Tianwei New Energy | TW285P72-EA | poly | 285 |  | +2/-0 | 2 | 0 |  |  | 35.8 | 7.96 | 45.2 | 8.47 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Tianwei_New_Energy
Tianwei New Energy | TW290P72-EA | poly | 290 |  | +2/-0 | 2 | 0 |  |  | 36 | 8.06 | 45.3 | 8.53 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Tianwei_New_Energy
Tianwei New Energy | TW295P72-EA | poly | 295 |  | +2/-0 | 2 | 0 |  |  | 36.2 | 8.15 | 45.4 | 8.62 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Tianwei_New_Energy
Tianwei New Energy | TW290L72-EA | mono | 290 |  | +1.5/-0 | 1.5 | 0 |  |  | 35.7 | 8.12 | 44.8 | 8.74 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Tianwei_New_Energy
Tianwei New Energy | TW295L72-EA | mono | 295 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.1 | 8.18 | 45 | 8.86 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Tianwei_New_Energy
Tianwei New Energy | TW300L72-EA | mono | 300 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.5 | 8.22 | 45.5 | 8.89 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Tianwei_New_Energy
Tianwei New Energy | TW305L72-EA | mono | 305 |  | +1.5/-0 | 1.5 | 0 |  |  | 36.9 | 8.27 | 45.7 | 8.91 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Tianwei_New_Energy
Tianwei New Energy | TW310L72-EA | mono | 310 |  | +1.5/-0 | 1.5 | 0 |  |  | 37.3 | 8.32 | 45.9 | 8.93 | -0.44% | -0.34% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Tianwei_New_Energy
Trina Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Trina_Solar
Trina Solar | 165-DC01 | mono | 165 |  | +3/-3 | 3 | -3 | 12 | 12.9 | 35.6 | 4.65 | 43.2 | 5.2 | -0.45% | -0.35% |  |  | 7 |  | MC |  |  | 62.24 | 31.85 | 1.57 | 13.7663 | 34.39 | 5 |  | Check |  | Trina_Solar
Trina Solar | 170-DC01 | mono | 170 |  | +3/-3 | 3 | -3 | 12.3 | 13.3 | 35.8 | 4.76 | 43.6 | 5.25 | -0.45% | -0.35% |  |  | 7 |  | MC |  |  | 62.24 | 31.85 | 1.57 | 13.7663 | 34.39 | 5 |  | Check |  | Trina_Solar
Trina Solar | TSM-PEG40.07 160 |  | 160 |  | +5/-0 | 5 | 0 |  |  | 20 | 8 | 24.9 | 8.58 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-25 | Trina_Solar
Trina Solar | TSM-PEG40.07 165 |  | 165 |  | +5/-0 | 5 | 0 |  |  | 20.2 | 8.17 | 25.1 | 8.72 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-25 | Trina_Solar
Trina Solar | TSM-PEG40.07 170 |  | 170 |  | +5/-0 | 5 | 0 |  |  | 20.4 | 8.33 | 25.3 | 8.86 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-25 | Trina_Solar
Trina Solar | TSM-PEG40.07 175 | multi | 175 |  | +5/-0 | 5 | 0 |  |  | 20.6 | 8.5 | 25.4 | 9 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-25 | Trina_Solar
Trina Solar | TSM-DD05A.05(2) 275 | mono | 275 |  | +5/-0 | 5 | 0 |  |  | 31.4 | 8.76 | 38.4 | 9.24 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD05A.05(2) 280 | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 31.7 | 8.84 | 38.4 | 9.42 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD05A.08(2) 280 | mono | 280 |  | +5/-0 | 5 | 0 |  |  | 31.7 | 8.84 | 38.4 | 9.42 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD05A.05(2) 285 | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 31.8 | 8.97 | 38.5 | 9.51 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD05A.08(2) 285 | mono | 285 |  | +5/-0 | 5 | 0 |  |  | 31.8 | 8.97 | 38.5 | 9.51 | -0.39% | -0.29% |  |  | 15 | [11 empty] | 1000 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD05A.05(2) 290 | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 32.2 | 9.01 | 38.9 | 9.66 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD05A.08(2) 290 | mono | 290 |  | +5/-0 | 5 | 0 |  |  | 32.2 | 9.01 | 38.9 | 9.66 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD05A.05(2) 295 | mono | 295 |  | +5/-0 | 5 | 0 |  |  | 32.5 | 9.08 | 39.6 | 9.68 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD05A.08(2) 295 | mono | 295 |  | +5/-0 | 5 | 0 |  |  | 32.5 | 9.08 | 39.6 | 9.68 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD05A.05(2) 300 | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 32.6 | 9.19 | 39.8 | 9.77 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD05A.08(2) 300 | mono | 300 |  | +5/-0 | 5 | 0 |  |  | 32.6 | 9.19 | 39.8 | 9.77 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD05A.05(2) 305 | mono | 305 |  | +5/-0 | 5 | 0 |  |  | 32.9 | 9.28 | 40 | 9.85 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD05A.08(2) 305 | mono | 305 |  | +5/-0 | 5 | 0 |  |  | 32.9 | 9.28 | 40 | 9.85 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD05A.05(2) 310 | mono | 310 |  | +5/-0 | 5 | 0 |  |  | 33.1 | 9.37 | 40.2 | 9.94 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD05A.08(2) 310 | mono | 310 |  | +5/-0 | 5 | 0 |  |  | 33.1 | 9.37 | 40.2 | 9.94 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD05A.08(2) 315 | mono | 315 |  | +5/-0 | 5 | 0 |  |  | 33.3 | 9.46 | 40.5 | 10 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1000 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD14A(2) STD 340 | mono | 340 |  | +5/-0 | 5 | 0 |  |  | 38.2 | 8.9 | 46.2 | 9.5 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1500 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD14A(2) STD 345 | mono | 345 |  | +5/-0 | 5 | 0 |  |  | 38.5 | 8.96 | 46.7 | 9.55 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1500 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD14A(2) STD 350 | mono | 350 |  | +5/-0 | 5 | 0 |  |  | 38.7 | 9.07 | 47 | 9.6 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1500 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD14A(2) PERC 355 | mono | 355 |  | +5/-0 | 5 | 0 |  |  | 38.8 | 9.14 | 47.1 | 9.65 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1500 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD14A(2) PERC 360 | mono | 360 |  | +5/-0 | 5 | 0 |  |  | 39 | 9.24 | 47.7 | 9.7 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1500 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD14A(2) PERC 365 | mono | 365 |  | +5/-0 | 5 | 0 |  |  | 39.3 | 9.3 | 48 | 9.77 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1500 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD14A(2) PERC 370 | mono | 370 |  | +5/-0 | 5 | 0 |  |  | 39.7 | 9.33 | 48.3 | 9.83 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1500 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DD14A(2) PERC 375 | mono | 375 |  | +5/-0 | 5 | 0 |  |  | 40 | 9.37 | 48.5 | 9.88 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1500 | 2017-10-12 | Trina_Solar
Trina Solar | TSM-DDE14A(2) STD 340 | mono | 340 | 306.2 | +5/-0 | 5 | 0 |  | 17.5 | 38.2 | 8.9 | 46.2 | 9.5 | -0.39% | -0.29% |  |  | 20 |  |  |  |  | 77.2 | 39.1 | 1.57 |  |  |  |  | 1500 | 2018-11-12 | Trina_Solar
Trina Solar | TSM-DDE14A(2) STD 345 | mono | 345 | 310.9 | +5/-0 | 5 | 0 |  | 17.7 | 38.5 | 8.96 | 46.7 | 9.55 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1500 | 2018-11-12 | Trina_Solar
Trina Solar | TSM-DDE14A(2) STD 350 | mono | 350 | 315.5 | +5/-0 | 5 | 0 |  | 18 | 38.7 | 9.07 | 47 | 9.6 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1500 | 2018-11-12 | Trina_Solar
Trina Solar | TSM-DDE14A(2) PERC 355 | mono | 355 | 320.2 | +5/-0 | 5 | 0 |  | 18.3 | 38.8 | 9.14 | 47.1 | 9.65 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1500 | 2018-11-12 | Trina_Solar
Trina Solar | TSM-DDE14A(2) PERC 360 | mono | 360 | 324.9 | +5/-0 | 5 | 0 |  | 18.5 | 39 | 9.24 | 47.7 | 9.7 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1500 | 2018-11-12 | Trina_Solar
Trina Solar | TSM-DDE14A(2) PERC 365 | mono | 365 | 334.8 | +5/-0 | 5 | 0 |  | 18.8 | 39.3 | 9.3 | 48 | 9.77 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1500 | 2018-11-12 | Trina_Solar
Trina Solar | TSM-DDE14A(2) PERC 370 | mono | 370 |  | +5/-0 | 5 | 0 |  | 19 | 39.7 | 9.33 | 48.3 | 9.83 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1500 | 2018-11-12 | Trina_Solar
Trina Solar | TSM-DDE14A(2) PERC 375 | mono | 375 |  | +5/-0 | 5 | 0 |  | 19.3 | 40 | 9.37 | 48.5 | 9.88 | -0.39% | -0.29% |  |  | 20 | [11 empty] | 1500 | 2018-11-12 | Trina_Solar
Trina Solar | TSM-175DA01 | mono | 175 | 158.4 | +3/-0 | 3 | 0 | 12.7122 | 13.7 | 36.2 | 4.85 | 43.9 | 5.3 | -0.45% | -0.35% | 0.05 | 46 | 10 | DNR | tyco/MC | silver | white | 62.24 | 31.85 | 1.57 | 13.7663 | 34.4 | 10 |  | Check |  | Trina_Solar
Trina Solar | TSM-180DA01 | mono | 180 | 163.1 | +3/-0 | 3 | 0 | 13.0754 | 14.1 | 36.8 | 4.9 | 44.2 | 5.35 | -0.45% | -0.35% | 0.05 | 46 | 10 | DNR | tyco/MC | silver | white | 62.24 | 31.85 | 1.57 | 13.7663 | 34.4 | 10 |  | Check |  | Trina_Solar
Trina Solar | TSM-185DA01 | mono | 185 | 164.3 | +3/-0 | 3 | 0 | 13.4386 | 14.5 | 37.5 | 4.95 | 44.5 | 5.4 | -0.45% | -0.35% | 0.05 | 46 | 10 | DNR | tyco/MC | silver | white | 62.24 | 31.85 | 1.57 | 13.7663 | 34.4 | 10 |  | Check |  | Trina_Solar
Trina Solar | TSM-PD14-320 | poly | 320 |  | +5/-0 | 5 | 0 |  |  | 37.1 | 8.63 | 45.5 | 9.15 | -0.41% | -0.32% |  |  | 15 | [11 empty] | 1000 | 3/19/18 | Trina_Solar
Trina Solar | TSM-PD14-325 | poly | 325 |  | +5/-0 | 5 | 0 |  |  | 37.2 | 8.73 | 45.6 | 9.19 | -0.41% | -0.32% |  |  | 15 | [11 empty] | 1000 | 3/19/18 | Trina_Solar
Trina Solar | TSM-PD14-330 | poly | 330 |  | +5/-0 | 5 | 0 |  |  | 37.4 | 8.83 | 45.8 | 9.28 | -0.41% | -0.32% |  |  | 15 | [11 empty] | 1000 | 3/19/18 | Trina_Solar
Trina Solar | TSM-PD14-335 | poly | 335 |  | +5/-0 | 5 | 0 |  |  | 37.6 | 8.91 | 46 | 9.35 | -0.41% | -0.32% |  |  | 15 | [11 empty] | 1000 | 3/19/18 | Trina_Solar
Trina Solar | TSM-PD14-340 | poly | 340 |  | +5/-0 | 5 | 0 |  |  | 37.8 | 8.99 | 46.2 | 9.42 | -0.41% | -0.32% |  |  | 15 | [11 empty] | 1000 | 3/19/18 | Trina_Solar
Trina Solar | TSM-PE14A-320 | multi | 320 |  | +5/-0 | 5 | 0 |  |  | 37.1 | 8.63 | 45.5 | 9.15 | -0.41% | -0.32% |  |  | 15 |  |  |  |  | 77.2 | 39.1 | 1.57 |  | 49.6 |  |  | 1500 | 6/1/18 | Trina_Solar
Trina Solar | TSM-PE14A-325 | multi | 325 |  | +5/-0 | 5 | 0 |  |  | 37.2 | 8.73 | 45.6 | 9.19 | -0.41% | -0.32% |  |  | 15 |  |  |  |  | 77.2 | 39.1 | 1.57 |  | 49.6 |  |  | 1500 | 6/1/18 | Trina_Solar
Trina Solar | TSM-PE14A-330 | multi | 330 |  | +5/-0 | 5 | 0 |  |  | 37.4 | 8.83 | 45.8 | 9.28 | -0.41% | -0.32% |  |  | 15 |  |  |  |  | 77.2 | 39.1 | 1.57 |  | 49.6 |  |  | 1500 | 6/1/18 | Trina_Solar
Trina Solar | TSM-PE14A-335 | multi | 335 |  | +5/-0 | 5 | 0 |  |  | 37.6 | 8.91 | 46 | 9.35 | -0.41% | -0.32% |  |  | 15 |  |  |  |  | 77.2 | 39.1 | 1.57 |  | 49.6 |  |  | 1500 | 6/1/18 | Trina_Solar
Trina Solar | TSM-PE14A-340 | multi | 340 |  | +5/-0 | 5 | 0 |  |  | 37.8 | 8.99 | 46.2 | 9.42 | -0.41% | -0.32% |  |  | 15 |  |  |  |  | 77.2 | 39.1 | 1.57 |  | 49.6 |  |  | 1500 | 6/1/18 | Trina_Solar
Trina Solar | TSM-225PA05 | poly | 225 | 200.7 | +3/-0 | 3 | 0 | 12.7745 | 13.7 | 29.4 | 7.66 | 36.9 | 8.2 | -0.45% | -0.35% | 0.05 | 46 | 15 | DNR | tyco/MC | silver | white | 64.95 | 39.05 | 1.57 | 17.6132 | 43 | 10 |  | Check |  | Trina_Solar
Trina Solar | TSM-230PA05 | poly | 230 | 205.2 | +3/-0 | 3 | 0 | 13.0584 | 14.1 | 29.8 | 7.72 | 37 | 8.26 | -0.45% | -0.35% | 0.05 | 46 | 15 | DNR | tyco/MC | silver | white | 64.95 | 39.05 | 1.57 | 17.6132 | 43 | 10 |  | Check |  | Trina_Solar
Trina Solar | TSM-235PA05 | poly | 235 | 209.8 | +3/-0 | 3 | 0 | 13.3423 | 14.4 | 30.1 | 7.81 | 37.1 | 8.31 | -0.45% | -0.35% | 0.05 | 46 | 15 | DNR | tyco/MC | silver | white | 64.95 | 39.05 | 1.57 | 17.6132 | 43 | 10 |  | Check |  | Trina_Solar
Trina Solar | TSM-240PA05 | poly | 240 | 211 | +3/-0 | 3 | 0 | 13.6262 | 14.7 | 30.4 | 7.89 | 37.2 | 8.37 | -0.45% | -0.35% | 0.05 | 46 | 15 | DNR | tyco/MC | silver | white | 64.95 | 39.05 | 1.57 | 17.6132 | 43 | 10 |  | Check |  | Trina_Solar
Trina Solar | TSM-270PA14 | poly | 270 | 241.6 | +3/-0 | 3 | 0 | 12.9305 | 13.9 | 35.5 | 7.6 | 44.3 | 8.29 | -0.45% | -0.35% | 0.05 | 46 | 15 | DNR | tyco/MC | silver | white | 77 | 39.05 | 1.81 | 20.8809 | 61.7 | 10 |  | Check |  | Trina_Solar
Trina Solar | TSM-275PA14 | poly | 275 | 246.2 | +3/-0 | 3 | 0 | 13.1699 | 14.2 | 35.9 | 7.68 | 44.4 | 8.39 | -0.45% | -0.35% | 0.05 | 46 | 15 | DNR | tyco/MC | silver | white | 77 | 39.05 | 1.81 | 20.8809 | 61.7 | 10 |  | Check |  | Trina_Solar
Trina Solar | TSM-280 PA14 | multi | 280 |  | +3/-0 | 3 | 0 |  |  | 35.4 | 7.91 | 44.4 | 8.41 | -0.44% | -0.33% |  |  | 15 | [11 empty] | Check |  | Trina_Solar
Trina Solar | TSM-285 PA14 | multi | 285 |  | +3/-0 | 3 | 0 |  |  | 35.6 | 8.02 | 44.7 | 8.5 | -0.44% | -0.33% |  |  | 15 | [11 empty] | Check |  | Trina_Solar
Trina Solar | TSM-290 PA14 | multi | 290 |  | +3/-0 | 3 | 0 |  |  | 36.1 | 8.04 | 44.9 | 8.53 | -0.44% | -0.33% |  |  | 15 | [11 empty] | Check |  | Trina_Solar
Trina Solar | TSM-295 PA14 | multi | 295 |  | +3/-0 | 3 | 0 |  |  | 36.6 | 8.07 | 45.2 | 8.55 | -0.44% | -0.33% |  |  | 15 | [11 empty] | Check |  | Trina_Solar
Trina Solar | TSM-300 PA14 | multi | 300 |  | +3/-0 | 3 | 0 |  |  | 36.9 | 8.13 | 45.3 | 8.6 | -0.44% | -0.33% |  |  | 15 | [11 empty] | Check |  | Trina_Solar
Trina Solar | TSM-305 PA14 | multi | 305 |  | +3/-0 | 3 | 0 |  |  | 37 | 8.25 | 45.4 | 8.75 | -0.44% | -0.33% |  |  | 15 | [11 empty] | Check |  | Trina_Solar
Trina Solar | TSM-PA05 220 | poly | 220 |  | +3/-3 | 3 | -3 | 12.5 | 13.4 | 29.8 | 7.39 | 36.8 | 8 | -0.45% | -0.35% |  |  | 14 |  | Tyco |  |  | 64.96 | 39.05 | 1.81 | 17.6159 | 43 | 5 |  | Check |  | Trina_Solar
Trina Solar | TSM-PA05 230 | poly | 230 |  | +3/-3 | 3 | -3 | 13.1 | 14.1 | 30 | 7.66 | 37 | 8.18 | -0.45% | -0.35% |  |  | 14 |  | Tyco |  |  | 64.96 | 39.05 | 1.81 | 17.6159 | 43 | 5 |  | Check |  | Trina_Solar
Trina Solar | TSM-PA05 240 | poly | 240 |  | +3/-3 | 3 | -3 | 13.6 | 14.7 | 30.6 | 7.84 | 37.5 | 8.38 | -0.45% | -0.35% |  |  | 14 |  | Tyco |  |  | 64.96 | 39.05 | 1.81 | 17.6159 | 43 | 5 |  | Check |  | Trina_Solar
Trina Solar | TSM-PA05.08 240 | multi | 240 |  | +3/-0 | 3 | 0 |  |  | 29.7 | 8.1 | 37.3 | 8.62 | -0.43% | -0.32% |  |  | 15 | [11 empty] | Check | 2013-12-20 | Trina_Solar
Trina Solar | TSM-PA05.08 245 | multi | 245 |  | +3/-0 | 3 | 0 |  |  | 30.2 | 8.13 | 37.5 | 8.68 | -0.43% | -0.32% |  |  | 15 | [11 empty] | Check | 2013-12-20 | Trina_Solar
Trina Solar | TSM-PA05.08 250 | multi | 250 |  | +3/-0 | 3 | 0 |  |  | 30.3 | 8.27 | 37.6 | 8.85 | -0.43% | -0.32% |  |  | 15 | [11 empty] | Check | 2013-12-20 | Trina_Solar
Trina Solar | TSM-PA05.08 255 | multi | 255 |  | +3/-0 | 3 | 0 |  |  | 30.5 | 8.36 | 37.7 | 8.92 | -0.43% | -0.32% |  |  | 15 | [11 empty] | Check | 2013-12-20 | Trina_Solar
Trina Solar | TSM-PA05.08 260 | multi | 260 |  | +3/-0 | 3 | 0 |  |  | 30.7 | 8.47 | 37.9 | 9 | -0.43% | -0.32% |  |  | 15 | [11 empty] | Check | 2013-12-20 | Trina_Solar
Trina Solar | TSM-PD05.05 245 | multi | 245 |  | +3/-0 | 3 | 0 |  |  | 29.9 | 8.2 | 37.8 | 8.75 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
Trina Solar | TSM-PD05.05 250 | multi | 250 |  | +5/-0 | 5 | 0 |  |  | 30.3 | 8.27 | 38 | 8.79 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
Trina Solar | TSM-PD05.05/08 255 | multi | 255 |  | +5/-0 | 5 | 0 |  |  | 30.5 | 8.37 | 38.1 | 8.88 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
Trina Solar | TSM-PD05.05/08 260 | multi | 260 |  | +5/-0 | 5 | 0 |  |  | 30.6 | 8.5 | 38.2 | 9 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
Trina Solar | TSM-PD05.08 265 | multi | 265 |  | +5/-0 | 5 | 0 |  |  | 30.8 | 8.61 | 38.3 | 9.1 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
Trina Solar | TSM-PEG5.07 250 | multi | 250 |  | +5/-0 | 5 | 0 |  |  | 30 | 8.34 | 37.5 | 8.97 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-25 | Trina_Solar
Trina Solar | TSM-PEG5(.07) 255 | multi | 255 |  | +5/-0 | 5 | 0 |  |  | 30.3 | 8.42 | 37.5 | 9.01 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-25 | Trina_Solar
Trina Solar | TSM-PEG5(.07) 260 | multi | 260 |  | +5/-0 | 5 | 0 |  |  | 30.5 | 8.52 | 37.6 | 9.1 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-25 | Trina_Solar
Trina Solar | TSM-PEG5 265 | multi | 265 |  | +5/-0 | 5 | 0 |  |  | 30.8 | 8.6 | 37.6 | 9.2 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-25 | Trina_Solar
Trina Solar | TSM-PD14 300 | multi | 300 |  | +3/-0 | 3 | 0 |  |  | 36.2 | 8.28 | 45.4 | 8.77 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
Trina Solar | TSM-PD14 305 | multi | 305 |  | +5/-0 | 5 | 0 |  |  | 36.6 | 8.33 | 45.5 | 8.81 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
Trina Solar | TSM-PD14 310 | multi | 310 |  | +5/-0 | 5 | 0 |  |  | 37 | 8.38 | 45.5 | 8.85 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
Trina Solar | TSM-PD14 315 | multi | 315 |  | +5/-0 | 5 | 0 |  |  | 37.1 | 8.51 | 45.6 | 9 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
Trina Solar | TSM-PD14 320 | multi | 320 |  | +5/-0 | 5 | 0 |  |  | 37.1 | 8.63 | 45.8 | 9.1 | -0.41% | -0.32% |  |  | 15 | [11 empty] | 1000 | 2018-05-22 | Trina_Solar
Trina Solar | TSM-260-DC05A.08(5) | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 30.7 | 8.49 | 38.5 | 9.01 | -0.4% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Trina_Solar
Trina Solar | TSM-265-DC05A.08(5) | mono | 265 |  | +3/-0 | 3 | 0 |  |  | 30.7 | 8.63 | 38.5 | 9.1 | -0.4% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Trina_Solar
Trina Solar | TSM-270-DC05A.08(5) | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 30.8 | 8.77 | 38.6 | 9.23 | -0.4% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Trina_Solar
Trina Solar | TSM-275-DC05A.08 | mono | 275 |  | +3/-0 | 3 | 0 |  |  | 31.2 | 8.82 | 38.7 | 9.26 | -0.4% | -0.31% |  |  | 15 | [11 empty] | Check | 2015-12-04 | Trina_Solar
Trina Solar | TSM-PDG5 250 | multi | 250 |  | +3/-0 | 3 | 0 |  |  | 30 | 8.34 | 37.5 | 8.97 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
Trina Solar | TSM-PDG5 255 | multi | 255 |  | +3/-0 | 3 | 0 |  |  | 30.3 | 8.42 | 37.5 | 9.01 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
Trina Solar | TSM-PDG5 260 | multi | 260 |  | +3/-0 | 3 | 0 |  |  | 30.5 | 8.52 | 37.6 | 9.1 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
Trina Solar | TSM-PDG5 265 | multi | 265 |  | +3/-0 | 3 | 0 |  |  | 30.8 | 8.6 | 37.6 | 9.2 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
Trina Solar | TSM-295-PC14 | poly | 295 |  | +3/-0 | 3 | 0 |  |  | 35.8 | 8.25 | 45.1 | 8.72 | -0.41% | -0.32% |  |  | 12 | [11 empty] | Check | 2015-12-04 | Trina_Solar
Trina Solar | TSM-300-PC14 | poly | 300 |  | +3/-0 | 3 | 0 |  |  | 36.2 | 8.28 | 45.4 | 8.77 | -0.41% | -0.32% |  |  | 12 | [11 empty] | Check | 2015-12-04 | Trina_Solar
Trina Solar | TSM-305-PC14 | poly | 305 |  | +3/-0 | 3 | 0 |  |  | 36.6 | 8.33 | 45.5 | 8.81 | -0.41% | -0.32% |  |  | 12 | [11 empty] | Check | 2015-12-04 | Trina_Solar
Trina Solar | TSM-310-PC14 | poly | 310 |  | +3/-0 | 3 | 0 |  |  | 37 | 8.38 | 45.5 | 8.85 | -0.41% | -0.32% |  |  | 12 | [11 empty] | Check | 2015-12-04 | Trina_Solar
Trina Solar | TSM-PEG14 300 | multi | 300 |  | +3/-0 | 3 | 0 |  |  | 36.4 | 8.24 | 45.2 | 8.74 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
Trina Solar | TSM-PEG14 305 | multi | 305 |  | +5/-0 | 5 | 0 |  |  | 36.6 | 8.33 | 45.4 | 8.82 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
Trina Solar | TSM-PEG14 310 | multi | 310 |  | +5/-0 | 5 | 0 |  |  | 36.8 | 8.42 | 45.6 | 8.91 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
Trina Solar | TSM-PEG14 315 | multi | 315 |  | +5/-0 | 5 | 0 |  |  | 37 | 8.51 | 45.7 | 8.99 | -0.41% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Trina_Solar
UniSolar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | UniSolar
UniSolar | PVL-124 | amorphous | 124 |  | +5/-5 | 5 | -5 | 5.8 | 6.3 | 30 | 4.1 | 42 | 5.1 | -0.21% | -0.38% |  |  | 8 |  | MC |  |  | 197.1 | 15.5 | 0.6 | 21.2156 | 7 | none |  | Check |  | UniSolar
UniSolar | PVL-136 | amorphous | 136 |  | +5/-5 | 5 | -5 | 5.8 | 6.3 | 33 | 4.1 | 46.2 | 5.1 | -0.21% | -0.38% |  |  | 8 |  | MC |  |  | 216 | 15.5 | 0.6 | 23.25 | 7.7 | none |  | Check |  | UniSolar
UniSolar | PVL-144 | amorphous | 144 |  | +5/-5 | 5 | -5 |  |  | 33 | 4.36 | 46.2 | 5.3 | -0.21% | -0.38% |  |  | 10 | [7 empty] | 0 |  |  |  | Check |  | UniSolar
UniSolar | PVL-68 | amorphous | 68 |  | +5/-5 | 5 | -5 | 5.6 | 6.1 | 16.5 | 4.1 | 23.1 | 5.1 | -0.21% | -0.38% |  |  | 8 |  | MC |  |  | 112.1 | 15.5 | 0.6 | 12.0663 | 8.7 | none |  | Check |  | UniSolar
Upsolar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Upsolar
Upsolar | UP-M185M | mono | 185 | 164 | +/-3 | 3 | -3 | 13.4642 | 14.5 | 35.8 | 5.03 | 44.6 | 5.38 | -0.43% | -0.32% | 0.05 | 45 | 15 | yes | MC4 | silver | white | 62.2 | 31.81 | 1.57 | 13.7402 | 34 | 5 |  | Check |  | Upsolar
Upsolar | UP-M190M | mono | 190 | 168.5 | +/-3 | 3 | -3 | 13.8281 | 14.9 | 36.3 | 5.23 | 45.1 | 5.55 | -0.43% | -0.32% | 0.05 | 45 | 15 | yes | MC4 | silver | white | 62.2 | 31.81 | 1.57 | 13.7402 | 34 | 5 |  | Check |  | Upsolar
Upsolar | UP-M200P | poly | 200 | 173.4 | +/-3 | 3 | -3 | 12.6395 | 13.6 | 26 | 7.51 | 32.8 | 8.1 | -0.43% | -0.32% | 0.05 | 45 | 20 | yes | MC4 | silver | white | 58.35 | 39.05 | 1.57 | 15.8234 | 38.6 | 5 |  | Check |  | Upsolar
Upsolar | UP-M210P | poly | 210 | 182.4 | +/-3 | 3 | -3 | 13.2715 | 14.3 | 26.8 | 7.84 | 33.3 | 8.4 | -0.43% | -0.32% | 0.05 | 45 | 20 | yes | MC4 | silver | white | 58.35 | 39.05 | 1.57 | 15.8234 | 38.6 | 5 |  | Check |  | Upsolar
Upsolar | UP-M230P | poly | 230 | 204 | +/-3 | 3 | -3 | 13.1319 | 14.1 | 29.7 | 7.75 | 37.2 | 8.3 | -0.43% | -0.32% | 0.05 | 45 | 20 | yes | MC4 | silver | white | 64.57 | 39.06 | 1.57 | 17.5146 | 41.9 | 5 |  | Check |  | Upsolar
Upsolar | UP-M245P-B | poly | 245 |  | +3/-0 | 3 | 0 |  |  | 30.6 | 8 | 38 | 8.4 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M250P-B | poly | 250 |  | +3/-0 | 3 | 0 |  |  | 30.9 | 8.1 | 38.2 | 8.45 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M255P-B | poly | 255 |  | +3/-0 | 3 | 0 |  |  | 31.1 | 8.2 | 38.4 | 8.5 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M260P-B | poly | 260 |  | +3/-0 | 3 | 0 |  |  | 31.3 | 8.3 | 38.6 | 8.6 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M265P-B | poly | 265 |  | +3/-0 | 3 | 0 |  |  | 31.6 | 8.4 | 38.8 | 8.7 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M240P | poly | 240 | 213.2 | +/-3 | 3 | -3 | 13.7028 | 14.8 | 30.2 | 7.95 | 37.6 | 8.4 | -0.43% | -0.32% | 0.05 | 45 | 20 | yes | MC4 | silver | white | 64.57 | 39.06 | 1.57 | 17.5146 | 41.9 | 5 |  | Check |  | Upsolar
Upsolar | UP-M250P | poly | 250 |  | +3/-0 | 3 | 0 |  |  | 30.6 | 8.17 | 38 | 8.5 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M255P | poly | 255 |  | +3/-0 | 3 | 0 |  |  | 30.8 | 8.28 | 38.2 | 8.55 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M260P | poly | 260 |  | +3/-0 | 3 | 0 |  |  | 31 | 8.39 | 38.4 | 8.7 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M265P | poly | 270 |  | +3/-0 | 3 | 0 |  |  | 31.2 | 8.49 | 38.5 | 8.78 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M270P | poly | 270 | 240.7 | +3/-0 | 3 | 0 | 12.9272 | 13.9 | 31.4 | 8.6 | 38.6 | 8.88 | -0.43% | -0.3% | 0.05 | 45 | 20 | yes | MC4 | silver | white | 77 | 39.06 | 1.97 | 20.8863 | 59.52 | 5 |  | Check | 2015-11-30 | Upsolar
Upsolar | UP-M280P | poly | 280 | 248.5 | +/-3 | 3 | -3 | 13.4059 | 14.4 | 35.2 | 7.95 | 44.8 | 8.35 | -0.43% | -0.32% | 0.05 | 45 | 20 | yes | MC4 | silver | white | 77 | 39.06 | 1.97 | 20.8863 | 59.52 | 5 |  | Check |  | Upsolar
Upsolar | UP-M290P | poly | 290 |  | +3/-0 | 3 | -0 |  |  | 35.5 | 8.17 | 45.2 | 8.5 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check |  | Upsolar
Upsolar | UP-M295P | poly | 295 |  | +3/-0 | 3 | -0 |  |  | 35.7 | 8.26 | 45.4 | 8.58 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check |  | Upsolar
Upsolar | UP-M300P | poly | 300 |  | +3/-0 | 3 | -0 |  |  | 35.9 | 8.36 | 45.6 | 8.66 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check |  | Upsolar
Upsolar | UP-M305P | poly | 305 |  | +3/-0 | 3 | -0 |  |  | 36.1 | 8.45 | 45.8 | 8.74 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check |  | Upsolar
Upsolar | UP-M310P | poly | 310 |  | +3/-0 | 3 | -0 |  |  | 36.3 | 8.54 | 46 | 8.82 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check |  | Upsolar
Upsolar | UP-M315P | poly | 315 |  | +3/-0 | 3 | 0 |  |  | 36.5 | 8.63 | 46.2 | 8.9 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M255M | mono | 255 |  | +3/-0 | 3 | 0 |  |  | 30.2 | 8.44 | 38 | 8.88 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M260M | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 30.4 | 8.55 | 38.3 | 8.96 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M265M | mono | 265 |  | +3/-0 | 3 | 0 |  |  | 30.6 | 8.66 | 38.6 | 9.04 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M270M | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 30.8 | 8.77 | 38.9 | 9.12 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M275M | mono | 275 |  | +3/-0 | 3 | 0 |  |  | 31 | 8.87 | 39.2 | 9.2 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M290M | mono | 290 |  | +3/-0 | 3 | 0 |  |  | 31.6 | 9.18 | 40.1 | 9.44 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M295M | mono | 295 |  | +3/-0 | 3 | 0 |  |  | 31.8 | 9.28 | 40.4 | 9.52 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M300M | mono | 300 |  | +3/-0 | 3 | 0 |  |  | 32 | 9.38 | 40.7 | 9.6 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M305M | mono | 305 |  | +3/-0 | 3 | 0 |  |  | 32.2 | 9.47 | 41 | 9.7 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M310M | mono | 310 |  | +3/-0 | 3 | 0 |  |  | 32.4 | 9.57 | 41.3 | 9.8 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M315M | mono | 315 |  | +3/-0 | 3 | 0 |  |  | 32.6 | 9.66 | 41.6 | 9.9 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M320M | mono | 320 |  | +3/-0 | 3 | 0 |  |  | 36.8 | 8.7 | 46.4 | 9.12 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M325M | mono | 325 |  | +3/-0 | 3 | 0 |  |  | 37 | 8.78 | 46.7 | 9.2 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M340M | mono | 340 |  | +3/-0 | 3 | 0 |  |  | 37.6 | 9.04 | 47.6 | 9.44 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M345M | mono | 345 |  | +3/-0 | 3 | 0 |  |  | 37.8 | 9.16 | 47.9 | 9.52 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M350M | mono | 350 |  | +3/-0 | 3 | 0 |  |  | 38 | 9.21 | 48.2 | 9.59 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M355M | mono | 355 |  | +3/-0 | 3 | 0 |  |  | 38.2 | 9.29 | 48.5 | 9.67 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M360M | mono | 360 |  | +3/-0 | 3 | 0 |  |  | 38.4 | 9.38 | 48.8 | 9.75 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M365M | mono | 365 |  | +3/-0 | 3 | 0 |  |  | 38.6 | 9.46 | 49 | 9.83 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M250-M-B | mono | 250 |  | +3/-0 | 3 | 0 |  |  | 30.3 | 8.24 | 38 | 8.7 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M255M-B | mono | 255 |  | +3/-0 | 3 | 0 |  |  | 30.5 | 8.36 | 38.3 | 8.8 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M260M-B | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 30.7 | 8.48 | 38.6 | 8.9 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M265M-B | mono | 265 |  | +3/-0 | 3 | 0 |  |  | 30.9 | 8.6 | 38.9 | 9 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M270M-B | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 31 | 8.72 | 39.2 | 9.1 | -0.43% | -0.3% |  |  | 20 | [11 empty] | Check | 2015-11-30 | Upsolar
Upsolar | UP-M285M-B | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 31.6 | 9.02 | 40.1 | 9.4 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M290M-B | mono | 290 |  | +3/-0 | 3 | 0 |  |  | 31.8 | 9.12 | 40.4 | 9.5 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M295M-B | mono | 295 |  | +3/-0 | 3 | 0 |  |  | 32 | 9.22 | 40.7 | 9.58 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M300M-B | mono | 300 |  | +3/-0 | 3 | 0 |  |  | 32.2 | 9.32 | 41 | 9.67 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M305M-B | mono | 305 |  | +3/-0 | 3 | 0 |  |  | 32.4 | 9.41 | 41.3 | 9.76 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Upsolar | UP-M310M-B | mono | 310 |  | +3/-0 | 3 | 0 |  |  | 32.6 | 9.51 | 41.6 | 9.85 | -0.42% | -0.3% |  |  | 20 | [11 empty] | 1500 | 2018-02-09 | Upsolar
Westinghouse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Westinghouse
Westinghouse | ST175-1 |  | 175 |  | +3/-3 | 3 | -3 |  |  | 35.2 | 4.92 | 44.2 | 5.2 | -0.5% | -0.35% |  |  | 15 | [7 empty] | 0 |  |  |  | Check |  | Westinghouse
XC3 International | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | XC3_International
XC3 International | XC1300 - 130 | poly | 130 |  | +5/-5 | 5 | -5 | 12.5 | 13.4 | 17.76 | 7.38 | 22.3 | 7.79 | -0.51% | -0.35% |  |  | 10 |  | J-box |  |  | 57.76 | 26 | 1.5 | 10.4289 | 26 | 5 |  | Check |  | XC3_International
XC3 International | XC2300 - 220 | poly | 220 |  | +5/-5 | 5 | -5 | 12.7 | 13.7 | 30.2 | 7.32 | 36.9 | 7.85 | -0.51% | -0.35% |  |  | 10 |  | MC |  |  | 64.02 | 38.98 | 1.5 | 17.3299 | 53.57 | 5 |  | Check |  | XC3_International
Yingli Green Energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Yingli_Green_Energy
Yingli Green Energy | YL 120 (17) | poly | 120 |  | +5/-5 | 5 | -5 | 12.4234 | 12 | 17.5 | 6.9 | 22 | 7.6 | -0.45% | -0.37% |  |  | NA |  | J-Box |  |  | 51.9 | 26.8 | 1.45 | 9.6592 | 26.4 | 2 |  | Check |  | Yingli_Green_Energy
Yingli Green Energy | YL 210 P-29b |  | 210 |  | +3/-3 | 3 | -3 |  |  | 28.5 | 7.37 | 36 | 7.95 | -0.45% | -0.37% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | Yingli_Green_Energy
Yingli Green Energy | YL 215 P-29b |  | 215 |  | +3/-3 | 3 | -3 |  |  | 29 | 7.41 | 36 | 8.1 | -0.45% | -0.37% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | Yingli_Green_Energy
Yingli Green Energy | YL 220 P-29b |  | 220 |  | +3/-3 | 3 | -3 |  |  | 29 | 7.59 | 36.5 | 8.15 | -0.45% | -0.37% |  |  | NA | [7 empty] | 0 |  |  |  | Check |  | Yingli_Green_Energy
Yingli Green Energy | YL175Wp | poly | 175 |  | +3/-3 | 3 | -3 | 12.3 | 13.2 | 23.5 | 7.5 | 29.5 | 8 | -0.45% | -0.37% |  |  | NA |  | J-box |  |  | 52.56 | 38.98 | 1.97 | 14.2277 | 34.6 | 2 |  | Check |  | Yingli_Green_Energy
Yingli Green Energy | YL225P-29b | poly | 225 | 202 | +/-3 | 3 | -3 | 12.7955 | 13.8 | 29.5 | 7.63 | 36.5 | 8.28 | -0.45% | -0.37% | 0.06 | 46 | 15 | yes | H4 | silver/black | white | 64.96 | 38.98 | 1.97 | 17.5843 | 43.65 | 5 |  | Check |  | Yingli_Green_Energy
Yingli Green Energy | YL230P-29b | poly | 230 | 206.6 | +/-3 | 3 | -3 | 13.0798 | 14.1 | 29.5 | 7.8 | 37 | 8.4 | -0.45% | -0.37% | 0.06 | 46 | 15 | yes | H4 | silver/black | white | 64.96 | 38.98 | 1.97 | 17.5843 | 43.65 | 5 |  | Check |  | Yingli_Green_Energy
Yingli Green Energy | YL235P-29b | poly | 235 | 211.2 | +/-3 | 3 | -3 | 13.3642 | 14.4 | 29.5 | 7.97 | 37 | 8.54 | -0.45% | -0.37% | 0.06 | 46 | 15 | yes | H4 | silver/black | white | 64.96 | 38.98 | 1.97 | 17.5843 | 43.65 | 5 |  | Check |  | Yingli_Green_Energy
Yingli Green Energy | YL240P-29b | poly | 240 | 215.9 | +3/-0 | 3 | 0 | 13.6485 | 14.7 | 29.3 | 8.18 | 37.5 | 8.75 | -0.43% | -0.32% | 0.06 | 46 | 15 | yes | H4 | silver/black | white | 64.96 | 38.98 | 1.97 | 17.5843 | 43.65 | 5 |  | Check | 7/13/15 RM | Yingli_Green_Energy
Yingli Green Energy | YL245P-29b | poly | 245 | 215.9 | +3/-0 | 3 | 0 |  |  | 29.6 | 8.28 | 37.5 | 8.83 | -0.43% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Yingli_Green_Energy
Yingli Green Energy | YL250P-29b | poly | 250 | 215.9 | +3/-0 | 3 | 0 |  |  | 29.8 | 8.39 | 37.6 | 8.92 | -0.43% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Yingli_Green_Energy
Yingli Green Energy | YL255P-29b | poly | 255 | 215.9 | +3/-0 | 3 | 0 |  |  | 30 | 8.49 | 37.7 | 9.01 | -0.43% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Yingli_Green_Energy
Yingli Green Energy | YL260P-29b | poly | 260 | 215.9 | +3/-0 | 3 | 0 |  |  | 30.3 | 8.59 | 37.7 | 9.09 | -0.43% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Yingli_Green_Energy
Yingli Green Energy | YL255C-30b | mono | 255 | 221.6 | +/-3 | 3 | -3 | 14.5016 | 15.6 | 30.6 | 8.33 | 38.2 | 8.85 | -0.45% | -0.33% | 0.04 | 46 | 20 | yes | H4 | silver | white | 64.96 | 38.98 | 1.97 | 17.5843 | 43.7 | 5 |  | Check |  | Yingli_Green_Energy
Yingli Green Energy | YL260C-30b | mono | 260 | 226.1 | +/-3 | 3 | -3 | 14.7859 | 15.9 | 30.8 | 8.46 | 38.6 | 8.91 | -0.45% | -0.33% | 0.04 | 46 | 20 | yes | H4 | silver | white | 64.96 | 38.98 | 1.97 | 17.5843 | 43.7 | 5 |  | Check |  | Yingli_Green_Energy
Yingli Green Energy | YL270P-35b | poly | 270 | 241.6 | +/-3 | 3 | -3 | 12.8602 | 13.8 | 35.3 | 7.65 | 44.8 | 8.2 | -0.45% | -0.37% | 0.06 | 46 | 15 | yes | H4 | silver | white | 77.56 | 38.98 | 1.97 | 20.9951 | 57.3 | 5 |  | Check |  | Yingli_Green_Energy
Yingli Green Energy | YL275P-35b | poly | 275 | 246.2 | +/-3 | 3 | -3 | 13.0983 | 14.1 | 35.5 | 7.75 | 45 | 8.3 | -0.45% | -0.37% | 0.06 | 46 | 15 | yes | H4 | silver | white | 77.56 | 38.98 | 1.97 | 20.9951 | 57.3 | 5 |  | Check |  | Yingli_Green_Energy
Yingli Green Energy | YL280P-35b | poly | 280 |  | +5/-0 | 5 | -0 | 13.3365 | 14.4 | 35.5 | 7.89 | 45 | 8.35 | -0.45% | -0.33% | 0.06 | 46 | 15 | yes | H4 | silver | white | 77.56 | 38.98 | 1.97 | 20.9951 | 57.3 | 5 |  | Check | 2015-02-19 | Yingli_Green_Energy
Yingli Green Energy | YL285P-35b | multi | 285 |  | +5/-0 | 5 | -0 |  | 14.6 | 35.5 | 8.02 | 45 | 8.5 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Yingli_Green_Energy
Yingli Green Energy | YL290P-35b | multi | 290 |  | +5/-0 | 5 | -0 |  | 14.9 | 35.8 | 8.29 | 45.3 | 8.62 | -0.45% | -0.33% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Yingli_Green_Energy
Yingli Green Energy | YGE-U YL295P-35b | multi | 295 |  | +3/-0 | 3 | -0 |  | 15.1 | 35.6 | 8.29 | 45 | 8.79 | -0.42% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Yingli_Green_Energy
Yingli Green Energy | YGE-U YL300P-35b | multi | 300 |  | +3/-0 | 3 | -0 |  | 15.4 | 35.8 | 8.37 | 45.2 | 8.86 | -0.42% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Yingli_Green_Energy
Yingli Green Energy | YGE-U YL305P-35b | multi | 305 |  | +3/-0 | 3 | -0 |  |  | 36.1 | 8.45 | 45.4 | 8.93 | -0.42% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Yingli_Green_Energy
Yingli Green Energy | YGE-U YL310P-35b | multi | 310 |  | +3/-0 | 3 | -0 |  |  | 36.3 | 8.53 | 45.6 | 8.99 | -0.42% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Yingli_Green_Energy
Yingli Green Energy | YGE-U YL315P-35b | multi | 315 |  | +3/-0 | 3 | -0 |  |  | 36.8 | 8.56 | 45.7 | 9.12 | -0.42% | -0.32% |  |  | 15 | [11 empty] | Check | 7/13/15 RM | Yingli_Green_Energy
Yingli Green Energy | YGE-U1500 YL315P-35b | multi | 315 |  | +3/-0 | 3 | 0 |  |  | 36.6 | 8.6 | 45.8 | 9.06 | -0.42% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-25 | Yingli_Green_Energy
Yingli Green Energy | YGE-U1500 YL320P-35b | multi | 320 |  | +3/-0 | 3 | 0 |  |  | 36.9 | 8.68 | 46 | 9.12 | -0.42% | -0.32% |  |  | 15 | [11 empty] | Check | 2015-11-25 | Yingli_Green_Energy
Xunlight | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Xunlight
Xunlight | XRU10-71 |  | 71 |  | +5/-5 | 5 | -5 |  |  | 16.7 | 4.24 | 22.5 | 5.4 | -0.23% | -0.38% |  |  | 10 | [11 empty] | Check |  | Xunlight
Xunlight | XRU19-134 |  | 134 |  | +5/-5 | 5 | -5 |  |  | 31.7 | 4.24 | 42 | 5.4 | -0.23% | -0.38% |  |  | 10 | [11 empty] | Check |  | Xunlight
Xunlight | XR12-97 |  | 97 |  | +5/-5 | 5 | -5 |  |  | 19.4 | 5 | 26.5 | 6.35 | -0.243% | -0.394% |  |  | 10 | [11 empty] | Check |  | Xunlight
Xunlight | XR36-291 |  | 291 |  | +5/-5 | 5 | -5 |  |  | 58.2 | 5 | 79.5 | 6.35 | -0.243% | -0.394% |  |  | 10 | [11 empty] | Check |  | Xunlight
Xunlight | XR12-88 |  | 88 |  | +5/-5 | 5 | -5 |  |  | 19.1 | 4.6 | 26 | 5.7 | -0.243% | -0.394% |  |  | 10 | [11 empty] | Check |  | Xunlight
Xunlight | XR36-264 |  | 264 |  | +5/-5 | 5 | -5 |  |  | 57.3 | 4.6 | 78 | 5.7 | -0.243% | -0.394% |  |  | 10 | [11 empty] | Check |  | Xunlight
Xunlight | XR12-100 |  | 100 |  | +5/-5 | 5 | -5 |  |  | 20 | 5 | 27 | 6.35 | -0.23% | -0.38% |  |  | 10 | [11 empty] | Check |  | Xunlight
Xunlight | XR36-300 |  | 300 |  | +5/-5 | 5 | -5 |  |  | 60 | 5 | 81 | 6.35 | -0.23% | -0.38% |  |  | 10 | [11 empty] | Check |  | Xunlight
Xunlight | XRS10-83 |  | 83 |  | +5/-5 | 5 | -5 |  |  | 16.67 | 5 | 22.5 | 6.35 | -0.23% | -0.38% |  |  | 10 | [11 empty] | Check |  | Xunlight
Xunlight | XRS18-150 |  | 150 |  | +5/-5 | 5 | -5 |  |  | 30 | 5 | 40.5 | 6.35 | -0.23% | -0.38% |  |  | 10 | [11 empty] | Check |  | Xunlight
Xunlight | XRS19-158 |  | 158 |  | +5/-5 | 5 | -5 |  |  | 31.67 | 5 | 42.75 | 6.35 | -0.23% | -0.38% |  |  | 10 | [11 empty] | Check |  | Xunlight
Xunlight | XRN10-53 |  | 53 |  | +5/-5 | 5 | -5 |  |  | 16.7 | 3.18 | 22.5 | 4 | -0.23% | -0.38% |  |  | 10 | [11 empty] | Check |  | Xunlight
Xunlight | XRN19-101 |  | 101 |  | +5/-5 | 5 | -5 |  |  | 31.7 | 3.18 | 42 | 4 | -0.23% | -0.38% |  |  | 10 | [11 empty] | Check |  | Xunlight
Xunlight | XLS11-68 |  | 68 |  | +5/-5 | 5 | -5 |  |  | 17.6 | 3.86 | 24.2 | 5.05 | -0.23% | -0.38% |  |  | 8 | [11 empty] | Check |  | Xunlight
Xunlight | XLS22-136 |  | 136 |  | +5/-5 | 5 | -5 |  |  | 35.2 | 3.86 | 48.4 | 5.05 | -0.23% | -0.38% |  |  | 8 | [11 empty] | Check |  | Xunlight
Xunlight | XLS11-72 |  | 72 |  | +5/-5 | 5 | -5 |  |  | 17.6 | 4.09 | 24.2 | 5.1 | -0.23% | -0.38% |  |  | 8 | [11 empty] | Check |  | Xunlight
Xunlight | XLS22-144 |  | 144 |  | +5/-5 | 5 | -5 |  |  | 35.2 | 4.09 | 48.4 | 5.1 | -0.23% | -0.38% |  |  | 8 | [11 empty] | Check |  | Xunlight
Zhejiang Wanxiang Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS180P | poly | 180 | 162.3 | +/-3 | 3 | -3 | 12.7296 | 13.8 | 24.32 | 6.6735 | 29.49 | 8.39 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 52.13 | 39.06 | 1.57 | 14.1403 | 34.1 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS180S | mono | 180 | 162.3 | +/-3 | 3 | -3 | 13.1003 | 14.1 | 36.36 | 4.4637 | 44.19 | 5.6 | -0.45% | -0.33% | 0.02 | 45 | 15 | yes | MC4 | silver/black | white/black | 62.2 | 31.81 | 1.57 | 13.7402 | 33 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS185P | poly | 185 | 167 | +/-3 | 3 | -3 | 13.0832 | 14.2 | 24.52 | 6.8108 | 29.56 | 8.56 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 52.13 | 39.06 | 1.57 | 14.1403 | 34.1 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS185S | mono | 185 | 166.9 | +/-3 | 3 | -3 | 13.4642 | 14.5 | 36.68 | 4.5502 | 44.24 | 5.84 | -0.45% | -0.33% | 0.02 | 45 | 15 | yes | MC4 | silver/black | white/black | 62.2 | 31.81 | 1.57 | 13.7402 | 33 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS190P | poly | 190 | 171.6 | +/-3 | 3 | -3 | 13.4368 | 14.6 | 24.72 | 6.9417 | 29.76 | 8.71 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 52.13 | 39.06 | 1.57 | 14.1403 | 34.1 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS200P | poly | 200 | 179.8 | +/-3 | 3 | -3 | 12.6363 | 12.3 | 27.28 | 6.5909 | 33.16 | 8.33 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 58.35 | 39.06 | 1.57 | 15.8274 | 37.4 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS205P | poly | 205 | 184.4 | +/-3 | 3 | -3 | 12.9522 | 12.6 | 27.32 | 6.7496 | 33.18 | 8.49 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 58.35 | 39.06 | 1.57 | 15.8274 | 37.4 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS210P | poly | 210 | 189 | +/-3 | 3 | -3 | 13.2681 | 12.9 | 27.68 | 6.828 | 33.35 | 8.64 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 58.35 | 39.06 | 1.57 | 15.8274 | 37.4 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS215P | poly | 215 | 193.6 | +/-3 | 3 | -3 | 13.584 | 13.2 | 27.86 | 6.949 | 33.59 | 8.73 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 58.35 | 39.06 | 1.57 | 15.8274 | 37.4 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS220P | poly | 220 | 198.2 | +/-3 | 3 | -3 | 13.8999 | 13.5 | 27.92 | 7.0989 | 33.62 | 8.92 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 58.35 | 39.06 | 1.57 | 15.8274 | 37.4 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS225P | poly | 225 | 202.9 | +/-3 | 3 | -3 | 12.8464 | 13.8 | 30.4 | 6.6743 | 36.86 | 8.39 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 64.57 | 39.06 | 1.57 | 17.5146 | 40.7 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS230P | poly | 230 | 206.5 | +/-3 | 3 | -3 | 13.1319 | 14.1 | 30.6 | 6.7484 | 36.9 | 8.56 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 64.57 | 39.06 | 1.57 | 17.5146 | 40.7 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS235P | poly | 235 | 211.1 | +/-3 | 3 | -3 | 13.4174 | 12.1 | 30.87 | 6.8384 | 37.13 | 8.65 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 64.57 | 39.06 | 1.57 | 17.5146 | 40.7 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS240P | poly | 240 | 215.7 | +/-3 | 3 | -3 | 13.7028 | 12.4 | 30.9 | 6.9806 | 37.2 | 8.82 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 64.57 | 39.06 | 1.57 | 17.5146 | 40.7 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS245P | poly | 245 | 220.3 | +/-3 | 3 | -3 | 13.9883 | 12.6 | 30.93 | 7.1225 | 37.22 | 8.97 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 64.57 | 39.06 | 1.57 | 17.5146 | 40.7 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS250P | poly | 250 | 224.9 | +/-3 | 3 | -3 | 11.968 | 12.9 | 30.93 | 6.94 | 37.22 | 8.97 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 77.01 | 39.06 | 1.57 | 20.889 | 48.4 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS255P | poly | 255 | 229.6 | +/-3 | 3 | -3 | 12.2074 | 13.1 | 36.36 | 7.01 | 44.28 | 8.01 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 77.01 | 39.06 | 1.57 | 20.889 | 48.4 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS260P | poly | 260 | 234.2 | +/-3 | 3 | -3 | 12.4468 | 13.4 | 36.36 | 7.15 | 44.28 | 8.01 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 77.01 | 39.06 | 1.57 | 20.889 | 48.4 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS265P | poly | 265 | 238.8 | +/-3 | 3 | -3 | 12.6861 | 13.7 | 36.36 | 7.29 | 44.28 | 8.3 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 77.01 | 39.06 | 1.57 | 20.889 | 48.4 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS270P | poly | 270 | 243.4 | +/-3 | 3 | -3 | 12.9255 | 13.9 | 36.48 | 7.4 | 44.24 | 8.39 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 77.01 | 39.06 | 1.57 | 20.889 | 48.4 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS275P | poly | 275 | 248.1 | +/-3 | 3 | -3 | 13.1648 | 14.2 | 36.72 | 7.49 | 44.28 | 8.55 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 77.01 | 39.06 | 1.57 | 20.889 | 48.4 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
Zhejiang Wanxiang Solar | WXS280P | poly | 280 | 252.7 | +/-3 | 3 | -3 | 13.4042 | 14.4 | 36.9 | 7.59 | 44.46 | 8.64 | -0.44% | -0.33% | 0.55 | 45 | 15 | yes | MC4 | silver/black | white/black | 77.01 | 39.06 | 1.57 | 20.889 | 48.4 | 5 |  | Check |  | Zhejiang_Wanxiang_Solar
ZNSHINESOLAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Check | 0 | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-72-190/MS | mono | 190 |  | +3/-0 | 3 | 0 |  |  | 36.65 | 5.18 | 45.36 | 5.58 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-72-195/MS | mono | 195 |  | +3/-0 | 3 | 0 |  |  | 36.9 | 5.28 | 45.5 | 5.63 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-72-200/MS | mono | 200 |  | +3/-0 | 3 | 0 |  |  | 37.3 | 5.36 | 45.65 | 5.65 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-72-205/MS | mono | 205 |  | +3/-0 | 3 | 0 |  |  | 37.55 | 5.46 | 45.75 | 5.7 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-72-190/MS(GA) | mono | 190 |  | +3/-0 | 3 | 0 |  |  | 36.65 | 5.18 | 45.36 | 5.58 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-72-195/MS(GA) | mono | 195 |  | +3/-0 | 3 | 0 |  |  | 36.9 | 5.28 | 45.5 | 5.63 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-72-200/MS(GA) | mono | 200 |  | +3/-0 | 3 | 0 |  |  | 37.3 | 5.36 | 45.65 | 5.65 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-72-205/MS(GA) | mono | 205 |  | +3/-0 | 3 | 0 |  |  | 37.55 | 5.46 | 45.75 | 5.7 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-96-250/MS | mono | 250 |  | +3/-0 | 3 | 0 |  |  | 48.7 | 5.14 | 59.6 | 5.49 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-96-255/MS | mono | 255 |  | +3/-0 | 3 | 0 |  |  | 49 | 5.21 | 59.8 | 5.55 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-96-260/MS | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 49.3 | 5.27 | 60 | 5.64 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-96-265/MS | mono | 265 |  | +3/-0 | 3 | 0 |  |  | 49.4 | 5.36 | 60.1 | 5.73 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-96-270/MS | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 49.5 | 5.45 | 60.4 | 5.83 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-96-275/MS | mono | 275 |  | +3/-0 | 3 | 0 |  |  | 49.5 | 5.56 | 60.6 | 5.94 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-96-250/MS(GA) | mono | 250 |  | +3/-0 | 3 | 0 |  |  | 48.7 | 5.14 | 59.6 | 5.49 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-96-255/MS(GA) | mono | 255 |  | +3/-0 | 3 | 0 |  |  | 49 | 5.21 | 59.8 | 5.55 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-96-260/MS(GA) | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 49.3 | 5.27 | 60 | 5.64 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-96-265/MS(GA) | mono | 265 |  | +3/-0 | 3 | 0 |  |  | 49.4 | 5.36 | 60.1 | 5.73 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-96-270/MS(GA) | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 49.5 | 5.45 | 60.4 | 5.83 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM5-96-275/MS(GA) | mono | 275 |  | +3/-0 | 3 | 0 |  |  | 49.5 | 5.56 | 60.6 | 5.94 | -0.42% | -0.29% |  |  | 10 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-60-245/M | mono | 245 |  | +3/-0 | 3 | 0 |  |  | 30.4 | 8.07 | 38.1 | 8.59 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-60-250/M | mono | 250 |  | +3/-0 | 3 | 0 |  |  | 30.5 | 8.2 | 38.2 | 8.71 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-60-255/M | mono | 255 |  | +3/-0 | 3 | 0 |  |  | 30.6 | 8.33 | 38.3 | 8.85 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-60-260/M | mono | 260 |  | +3/-0 | 3 | 0 |  |  | 30.72 | 8.46 | 38.4 | 8.95 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-60-265/M | mono | 265 |  | +3/-0 | 3 | 0 |  |  | 30.94 | 8.59 | 38.5 | 9.07 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-60-270/M | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 30.97 | 8.72 | 38.6 | 9.17 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-11-30 | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-72-305/M | mono | 305 |  | +3/-0 | 3 | 0 |  |  | 37.5 | 8.13 | 46.26 | 8.73 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-11-30 | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-72-310/M | mono | 310 |  | +3/-0 | 3 | 0 |  |  | 37.72 | 8.22 | 46.36 | 8.82 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-11-30 | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-72-315/M | mono | 315 |  | +3/-0 | 3 | 0 |  |  | 37.86 | 8.32 | 46.45 | 8.91 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-11-30 | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-72-320/M | mono | 320 |  | +3/-0 | 3 | 0 |  |  | 37.96 | 8.43 | 46.54 | 8.99 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check | 2015-11-30 | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-96-270/M | mono | 270 |  | +3/-0 | 3 | 0 |  |  | 36 | 7.5 | 44.39 | 8.33 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-96-275/M | mono | 275 |  | +3/-0 | 3 | 0 |  |  | 36.2 | 7.6 | 44.64 | 8.44 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-96-280/M | mono | 280 |  | +3/-0 | 3 | 0 |  |  | 36.5 | 7.67 | 45.01 | 8.52 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-96-285/M | mono | 285 |  | +3/-0 | 3 | 0 |  |  | 36.6 | 7.78 | 45.38 | 8.56 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-96-290/M | mono | 290 |  | +3/-0 | 3 | 0 |  |  | 36.8 | 7.88 | 45.77 | 8.59 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-96-295/M | mono | 295 |  | +3/-0 | 3 | 0 |  |  | 37 | 7.97 | 46 | 8.62 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-96-300/M | mono | 300 |  | +3/-0 | 3 | 0 |  |  | 37.2 | 8.06 | 46.19 | 8.66 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXM6-96-305/M | mono | 305 |  | +3/-0 | 3 | 0 |  |  | 37.5 | 8.13 | 46.26 | 8.73 | -0.42% | -0.29% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-60-220/P | poly | 220 |  | +3/-0 | 3 | 0 |  |  | 28.95 | 7.6 | 36.87 | 8.13 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-60-225/P | poly | 225 |  | +3/-0 | 3 | 0 |  |  | 29.15 | 7.72 | 37.04 | 8.22 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-60-230/P | poly | 230 |  | +3/-0 | 3 | 0 |  |  | 29.35 | 7.84 | 37.21 | 8.31 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-60-235/P | poly | 235 |  | +3/-0 | 3 | 0 |  |  | 29.55 | 7.95 | 37.38 | 8.39 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-60-240/P | poly | 240 |  | +3/-0 | 3 | 0 |  |  | 29.75 | 8.07 | 37.55 | 8.47 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-60-245/P | poly | 245 |  | +3/-0 | 3 | 0 |  |  | 29.95 | 8.18 | 37.72 | 8.53 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-60-250/P | poly | 250 |  | +3/-0 | 3 | 0 |  |  | 30.15 | 8.29 | 37.89 | 8.61 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-D60-245/P | poly | 245 |  | +3/-0 | 3 | 0 |  |  | 29.95 | 8.18 | 37.35 | 8.73 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-D60-250/P | poly | 250 |  | +3/-0 | 3 | 0 |  |  | 30.15 | 8.29 | 37.52 | 8.81 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-D60-255/P | poly | 255 |  | +3/-0 | 3 | 0 |  |  | 30.33 | 8.41 | 37.69 | 8.89 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-D60-260/P | poly | 260 |  | +3/-0 | 3 | 0 |  |  | 30.53 | 8.52 | 37.88 | 8.97 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-D60-265/P | poly | 265 |  | +3/-0 | 3 | 0 |  |  | 30.65 | 8.65 | 38.06 | 9.05 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-72-270/P | poly | 270 |  | +3/-0 | 3 | 0 |  |  | 35.6 | 7.58 | 44.42 | 8.27 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-72-275/P | poly | 275 |  | +3/-0 | 3 | 0 |  |  | 35.9 | 7.66 | 44.45 | 8.37 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-72-280/P | poly | 280 |  | +3/-0 | 3 | 0 |  |  | 36.1 | 7.76 | 44.5 | 8.42 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-72-285/P | poly | 285 |  | +3/-0 | 3 | 0 |  |  | 36.3 | 7.85 | 44.5 | 8.48 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-72-290/P | poly | 290 |  | +3/-0 | 3 | 0 |  |  | 36.5 | 7.95 | 44.6 | 8.52 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-72-295/P | poly | 295 |  | +3/-0 | 3 | 0 |  |  | 36.8 | 8.02 | 44.82 | 8.55 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-72-300/P | poly | 300 |  | +3/-0 | 3 | 0 |  |  | 36.95 | 8.12 | 44.95 | 8.64 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-72-305/P | poly | 305 |  | +3/-0 | 3 | 0 |  |  | 37.1 | 8.22 | 45.3 | 8.78 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check |  | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-72-310/P | poly | 310 |  | +3/-0 | 3 | 0 |  |  | 37.19 | 8.34 | 45.45 | 8.87 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | ZNSHINE_SOLAR
ZNSHINESOLAR | ZXP6-72-315/P | poly | 315 |  | +3/-0 | 3 | 0 |  |  | 37.28 | 8.45 | 45.6 | 8.96 | -0.42% | -0.33% |  |  | 15 | [11 empty] | Check | 2015-11-30 | ZNSHINE_SOLAR

## OCPD Device (hidden)
OCPD Rating
15
20
25
30
35
40
45
50
60
70
80
90
100
110
125
150
175
200
225
250
300
350
400
450
500
600
700
800
1000
1200
1600
2000
2500
3000
4000
5000
6000

## P-Region Factors (hidden)
V4.0.0 | [6 empty] | ` |  | FIXED | [8 empty] | SAT | [8 empty] | ROOF
|  |  |  | x |  | Lat | T(hi) | T(lo) | Irr(POA) |  |  | Irr(3avg) | T(Cell) | P(Array) |  |  | E(Array) | Irr(POA) |  |  | Irr(3avg) | T(Cell) | P(Array) |  |  | E(Array) | Irr(POA) |  |  | Irr(3avg) | T(Cell) | P(Array) |  |  | E(Array)
12 | FL | E | E1 | Orlando | 25 | 28 | 34 | -1 | 1127.258 | 3 | 4% | 1097.4357 | 69.606 | 104512.156 | 2 | 4% | 181.8808 | 1058.907 | 5 | 4% | 1057.07 | 70.912 | 95186.172 | 4 | 4% | 211.3739 | 1072.625 | 5 | 4% | 1046.7443 | 76.048 | 94977.086 | 4 | 4% | 167.8512
14 | GA-n | E | E2 | Atlanta | 30 | 34 | 37 | -7 | 1125.493 | 2 | 16% | 1095.2183 | 72.678 | 104571.563 | 3 | 16% | 172.2008 | 1055.177 | 4 | 4% | 1048.1553 | 71.742 | 98053.711 | 4 | 4% | 194.7922 | 1069.288 | 4 | 4% | 1045.457 | 76.611 | 96177.586 | 4 | 4% | 155.1337
55 | VA | E | E3 | Richmond | 30 | 38 | 39 | -14 | 1117.188 | 3 | 16% | 1087.474 | 73.552 | 102928.422 | 2 | 16% | 166.5889 | 1029.772 | 5 | 4% | 1026.958 | 73.914 | 90152.891 | 4 | 4% | 183.2782 | 1041.451 | 5 | 4% | 1019.737 | 78.248 | 86267.266 | 3 | 4% | 146.693
44 | PA | E | E4 | Harrisburg | 35 | 40 | 34 | -17 | 1132.396 | 3 | 16% | 1100.544 | 69.875 | 105781.625 | 3 | 16% | 158.7944 | 1035.58 | 5 | 4% | 1030.9533 | 68.178 | 93747.672 | 5 | 4% | 173.7258 | 1044.441 | 6 | 4% | 1022.9363 | 73.611 | 90167.992 | 5 | 4% | 138.8123
38 | NY | E | E5 | Albany | 35 | 43 | 30 | -25 | 1141.742 | 3 | 16% | 1108.7237 | 66.04 | 112402.281 | 3 | 16% | 151.9993 | 1019.021 | 6 | 4% | 1010.8847 | 62.641 | 92037.469 | 3 | 16% | 166.2157 | 1022.478 | 6 | 4% | 1003.2257 | 67.955 | 85906.781 | 3 | 16% | 131.9364
49 | TX-s | M | M1 | San Antonio | 25 | 28 | 39 | -7 | 1129.418 | 3 | 4% | 1101.9807 | 71.676 | 103851.648 | 3 | 4% | 178.8737 | 1068.143 | 5 | 4% | 1066.5283 | 72.154 | 92797.5 | 3 | 4% | 207.111 | 1083.409 | 5 | 4% | 1082.3427 | 72.482 | 95619.344 | 3 | 4% | 211.7587
3 | AZ | M | M2 | Phoenix | 30 | 34 | 46 | -2 | 1134.625 | 4 | 4% | 1105.311 | 76.733 | 99489.891 | 2 | 4% | 205.7704 | 1072.804 | 6 | 4% | 1065.048 | 78.336 | 95010.883 | 4 | 4% | 238.8061 | 1080.58 | 4 | 4% | 1077.9253 | 78.755 | 96386.875 | 4 | 4% | 245.2001
32 | NV-s | M | M3 | Denver | 30 | 36 | 36 | -20 | 1143.287 | 4 | 16% | 1117.7737 | 71.452 | 106183.148 | 4 | 16% | 196.6412 | 1060.411 | 6 | 4% | 1055.449 | 69.852 | 97093.836 | 6 | 4% | 216.1023 | 1064.969 | 5 | 4% | 1043.77 | 75.07 | 92417.375 | 6 | 4% | 168.4192
31 | NE | M | M4 | Minneapolis | 35 | 42 | 33 | -31 | 1155.006 | 3 | 16% | 1121.333 | 67.875 | 115787.484 | 3 | 16% | 167.5119 | 1019.841 | 6 | 4% | 1009.3903 | 66.706 | 95663.031 | 3 | 16% | 177.9434 | 1019.356 | 6 | 4% | 1000.0033 | 70.462 | 91160.398 | 3 | 16% | 140.5632
5 | CA-s | W | W1 | Lancaster | 30 | 34 | 43 | -3 | 1125.225 | 4 | 4% | 1098.544 | 74.111 | 106184.836 | 4 | 4% | 218.1322 | 1089.561 | 6 | 4% | 1088.453 | 73.794 | 100299.398 | 4 | 4% | 254.8205 | 1097.17 | 6 | 4% | 1074.8663 | 79.133 | 99086.461 | 4 | 4% | 192.9209
6 | CA-m | W | W2 | Sacremeto | 30 | 37 | 45 | -2 | 1100.036 | 4 | 4% | 1070.5617 | 70.381 | 99643.102 | 3 | 4% | 190.4677 | 1053.88 | 6 | 4% | 1050.9277 | 71.873 | 90949.094 | 6 | 4% | 221.3912 | 1068.131 | 6 | 4% | 1067.483 | 72.278 | 91476.852 | 6 | 4% | 227.1822
56 | WA | W | W3 | Spokane | 35 | 48 | 35 | -13 | 1091.24 | 5 | 4% | 1065.643 | 72.678 | 99595.133 | 5 | 4% | 151.9995 | 1009.576 | 6 | 4% | 1002.8627 | 67.813 | 94637.047 | 5 | 4% | 170.9295 | 1006.278 | 6 | 4% | 988.244 | 73.065 | 90660.594 | 7 | 4% | 131.3708
[9 empty] | MONOFACIAL | [8 empty] | BIFACIAL
[9 empty] | FIXED |  |  | SAT |  |  | ROOF |  |  | FIXED |  |  | SAT |  |  | ROOF
[9 empty] | Fuse | DLR | Isc | Fuse | DLR | Isc | Fuse | DLR | Isc | Fuse | DLR | Isc | Fuse | DLR | Isc | Fuse | DLR | Isc
[9 empty] | F | D | I | F | D | I | F | D | I | F | D | I | F | D | I | F | D | I
[9 empty] | MF | MF | MF | MF | MF | MF | MF | MF | MF | BF | BF | BF | BF | BF | BF | BF | BF | BF
[9 empty] | F | F | F | S | S | S | R | R | R | F | F | F | S | S | S | R | R | R
[9 empty] | FMFF | DMFF | IMFF | FMFS | DMFS | IMFS | FMFR | DMFR | IMFR | FBFF | DBFF | IBFF | FBFS | DBFS | IBFS | FBFR | DBFR | IBFR
[8 empty] | E1 | 1.0974 | 1.0451 | 1.1273 | 1.0571 | 0.95186 | 1.0589 | 1.0467 | 0.94977 | 1.0726 | 1.1374 | 1.0851 | 1.1673 | 1.0971 | 0.99186 | 1.0989 | 1.0867 | 0.98977 | 1.1126
[8 empty] | E2 | 1.0952 | 1.0457 | 1.1255 | 1.0482 | 0.98054 | 1.0552 | 1.0455 | 0.96178 | 1.0693 | 1.2552 | 1.2057 | 1.2855 | 1.0882 | 1.0205 | 1.0952 | 1.0855 | 1.0018 | 1.1093
[8 empty] | E3 | 1.0875 | 1.0293 | 1.1172 | 1.027 | 0.90153 | 1.0298 | 1.0197 | 0.86267 | 1.0415 | 1.2475 | 1.1893 | 1.2772 | 1.067 | 0.94153 | 1.0698 | 1.0597 | 0.90267 | 1.0815
[8 empty] | E4 | 1.1005 | 1.0578 | 1.1324 | 1.031 | 0.93748 | 1.0356 | 1.0229 | 0.90168 | 1.0444 | 1.2605 | 1.2178 | 1.2924 | 1.071 | 0.97748 | 1.0756 | 1.0629 | 0.94168 | 1.0844
[8 empty] | E5 | 1.1087 | 1.124 | 1.1417 | 1.0109 | 0.92037 | 1.019 | 1.0032 | 0.85907 | 1.0225 | 1.2687 | 1.284 | 1.3017 | 1.0509 | 1.0804 | 1.059 | 1.0432 | 1.0191 | 1.0625
[8 empty] | M1 | 1.102 | 1.0385 | 1.1294 | 1.0665 | 0.92797 | 1.0681 | 1.0823 | 0.95619 | 1.0834 | 1.142 | 1.0785 | 1.1694 | 1.1065 | 0.96798 | 1.1081 | 1.1223 | 0.99619 | 1.1234
[8 empty] | M2 | 1.1053 | 0.9949 | 1.1346 | 1.065 | 0.95011 | 1.0728 | 1.0779 | 0.96387 | 1.0806 | 1.1453 | 1.0349 | 1.1746 | 1.105 | 0.99011 | 1.1128 | 1.1179 | 1.0039 | 1.1206
[8 empty] | M3 | 1.1178 | 1.0618 | 1.1433 | 1.0554 | 0.97094 | 1.0604 | 1.0438 | 0.92417 | 1.065 | 1.2778 | 1.2218 | 1.3033 | 1.0954 | 1.0109 | 1.1004 | 1.0838 | 0.96417 | 1.105
[8 empty] | M4 | 1.1213 | 1.1579 | 1.155 | 1.0094 | 0.95663 | 1.0198 | 1 | 0.9116 | 1.0194 | 1.2813 | 1.3179 | 1.315 | 1.0494 | 1.1166 | 1.0598 | 1.04 | 1.0716 | 1.0594
[8 empty] | W1 | 1.0985 | 1.0618 | 1.1252 | 1.0885 | 1.003 | 1.0896 | 1.0749 | 0.99086 | 1.0972 | 1.1385 | 1.1018 | 1.1652 | 1.1285 | 1.043 | 1.1296 | 1.1149 | 1.0309 | 1.1372
[8 empty] | W2 | 1.0706 | 0.99643 | 1.1 | 1.0509 | 0.90949 | 1.0539 | 1.0675 | 0.91477 | 1.0681 | 1.1106 | 1.0364 | 1.14 | 1.0909 | 0.94949 | 1.0939 | 1.1075 | 0.95477 | 1.1081
[8 empty] | W3 | 1.0656 | 0.99595 | 1.0912 | 1.0029 | 0.94637 | 1.0096 | 0.98824 | 0.90661 | 1.0063 | 1.1056 | 1.036 | 1.1312 | 1.0429 | 0.98637 | 1.0496 | 1.0282 | 0.94661 | 1.0463
[5 empty] | F | D | I
MPPT1 | MPPT2 | MPPT3 |  |  | Fuse | DLR | Isc |  | IMFF: MPPT1; FMFS: MPPT2; DMFS: MPPT3
W2 | W2 | W2 |  | REGION | 1.0509 | 0.90949 | 1.0539 | MPPT1 | DMFF: Fuse; IMFF: 1.0509; FMFS: 1.0509; DMFS: 1.0509
S | S | S |  | FIXED/SAT/ROOF | 1.0509 | 0.90949 | 1.0539 | MPPT2 | DMFF: DLR; IMFF: 0.90949; FMFS: 0.90949; DMFS: 0.90949
MF | MF | MF |  | BIFACIAL | 1.0509 | 0.90949 | 1.0539 | MPPT3 | DMFF: Isc; IMFF: 1.0539; FMFS: 1.0539; DMFS: 1.0539

## ASHRAE (hidden)
V4.0.0 |  |  |  |  | Latitude | Longitude | Elevation | Time Zone | Period | WMO# | Extreme Annual Dry Bulb Mean |  | 50yr Min | 50yr Max | 0.4% Dry Bulb | [5 empty] | 2% Dry Bulb
Country | State or Providence |  | Station Name 1 | ASHRAE Name 2 | 3 | 4 | 5 | 6 | 7 | 8 | Min 9 | Min. from Solar ABC's 10 | 11 | 12 | Jun 13 | Jul 14 | Aug 15 | Rounded Avg. 16 | Avg. 17 | .4% From Solar ABC's 18 | Jun 19 | Jul 20 | Aug 21 | Rounded Avg. 22 | Avg. 23 | 2% From Solar ABC's 24 |  | Lookup Index
Canada | Alberta |  | BANFF CS | BANFF CS, AB, Canada | 51.19N | 115.55W | 1397 | -7.00 (NAM) | 94-06 | 711220 | -36.7 |  | -50 | 35.4 | 26.6 | 30.4 | 29.7 | 29 | 28.9 |  | 23 | 28.2 | 27.4 | 26 | 26.2 |  |  | CanadaAlbertaBANFF CS
Canada | Alberta |  | BOW ISLAND | BOW ISLAND, AB, Canada | 49.73N | 111.45W | 817 | -7.00 (NAM) | 94-06 | 712310 | -33.4 |  | -41.6 | 37.1 | 30.9 | 33.1 | 33.6 | 33 | 32.5333 |  | 27.4 | 31.2 | 31.4 | 30 | 30 |  |  | CanadaAlbertaBOW ISLAND
Canada | Alberta |  | BOW VALLEY | BOW VALLEY, AB, Canada | 51.08N | 115.07W | 1298 | -7.00 (NAM) | 94-06 | 712320 | -37.1 |  | -47.7 | 37.3 | 27.4 | 32.3 | 31 | 30 | 30.2333 |  | 24 | 29.3 | 28.6 | 27 | 27.3 |  |  | CanadaAlbertaBOW VALLEY
Canada | Alberta |  | BRETON PLOTS | BRETON PLOTS, AB, Canada | 53.09N | 114.44W | 852 | -7.00 (NAM) | 95-06 | 712330 | N/A |  | N/A | N/A | 30.3 | 32.7 | 31.4 | 31 | 31.4667 |  | 26.7 | 29.6 | 28.4 | 28 | 28.2333 |  |  | CanadaAlbertaBRETON PLOTS
Canada | Alberta |  | BROOKS | BROOKS, AB, Canada | 50.55N | 111.85W | 747 | -7.00 (NAM) | 94-06 | 714570 | -33.8 |  | -43.8 | 38.7 | 30.7 | 34.2 | 34 | 33 | 32.9667 |  | 27.7 | 32 | 31.7 | 30 | 30.4667 |  |  | CanadaAlbertaBROOKS
Canada | Alberta |  | CALGARY INT'L A | CALGARY INT'L A, AB, Canada | 51.11N | 114.02W | 1084 | -7.00 (NAM) | 82-06 | 718770 | -32.4 |  | -42.1 | 36 | 28.3 | 31.1 | 31.1 | 30 | 30.1667 |  | 25.5 | 28.6 | 28.6 | 28 | 27.5667 |  |  | CanadaAlbertaCALGARY INT'L A
Canada | Alberta |  | CAMROSE | CAMROSE, AB, Canada | 53.03N | 112.81W | 739 | -7.00 (NAM) | 94-06 | 712540 | -37.2 |  | -50.3 | 37.1 | 28.7 | 31.6 | 30.6 | 30 | 30.3 |  | 25.9 | 28.2 | 27.9 | 27 | 27.3333 |  |  | CanadaAlbertaCAMROSE
Canada | Alberta |  | CARDSTON | CARDSTON, AB, Canada | 49.20N | 113.29W | 1136 | -7.00 (NAM) | 94-06 | 711530 | -32.4 |  | -42.1 | 38.3 | 28.6 | 33.5 | 33.2 | 32 | 31.7667 |  | 25.9 | 31.2 | 31 | 29 | 29.3667 |  |  | CanadaAlbertaCARDSTON
Canada | Alberta |  | CLARESHOLM | CLARESHOLM, AB, Canada | 50.00N | 113.64W | 1009 | -7.00 (NAM) | 94-06 | 712340 | -34.6 |  | -44 | 37.9 | 28.9 | 33.3 | 33.2 | 32 | 31.8 |  | 26.1 | 31.1 | 31 | 29 | 29.4 |  |  | CanadaAlbertaCLARESHOLM
Canada | Alberta |  | COLD LAKE A | COLD LAKE A, AB, Canada | 54.42N | 110.28W | 541 | -7.00 (NAM) | 82-06 | 711200 | -38.5 |  | -50 | 36.8 | 28.2 | 29.7 | 30.9 | 30 | 29.6 |  | 25.9 | 27.7 | 27.9 | 27 | 27.1667 |  |  | CanadaAlbertaCOLD LAKE A
Canada | Alberta |  | COP UPPER | COP UPPER, AB, Canada | 51.08N | 114.22W | 1235 | -7.00 (NAM) | 94-06 | 712350 | -30.3 |  | -40.3 | 37.2 | 27.1 | 30.9 | 30.7 | 30 | 29.5667 |  | 23.6 | 28.2 | 28.1 | 27 | 26.6333 |  |  | CanadaAlbertaCOP UPPER
Canada | Alberta |  | CORONATION (AUT) | CORONATION (AUT), AB, Canada | 52.08N | 111.45W | 791 | -7.00 (NAM) | 82-03 | 718730 | -37.1 |  | -45 | 38.4 | 29.6 | 32.5 | 32.5 | 32 | 31.5333 |  | 26.4 | 29.5 | 29.9 | 29 | 28.6 |  |  | CanadaAlbertaCORONATION (AUT)
Canada | Alberta |  | CROWSNEST | CROWSNEST, AB, Canada | 49.63N | 114.48W | 1303 | -7.00 (NAM) | 94-06 | 712360 | -34.6 |  | -45.8 | 36 | 27.2 | 31.6 | 30.8 | 30 | 29.8667 |  | 24.2 | 29 | 28.5 | 27 | 27.2333 |  |  | CanadaAlbertaCROWSNEST
Canada | Alberta |  | DRUMHELLER EAST | DRUMHELLER EAST, AB, Canada | 51.43N | 112.67W | 678 | -7.00 (NAM) | 94-06 | 712370 | -36.3 |  | -48 | 39.3 | 30.7 | 33.8 | 34.4 | 33 | 32.9667 |  | 27.9 | 31.4 | 32 | 30 | 30.4333 |  |  | CanadaAlbertaDRUMHELLER EAST
Canada | Alberta |  | EDMONTON CITY CENTRE A | EDMONTON CITY CENTRE A, AB, Canada | 53.57N | 113.52W | 671 | -7.00 (NAM) | 82-04 | 718790 | -31.7 |  | -43.6 | 35.5 | 28.7 | 30.3 | 30.5 | 30 | 29.8333 |  | 25.9 | 27.8 | 27.8 | 27 | 27.1667 |  |  | CanadaAlbertaEDMONTON CITY CENTRE A
Canada | Alberta |  | EDMONTON INT'L A | EDMONTON INT'L A, AB, Canada | 53.32N | 113.58W | 723 | -7.00 (NAM) | 82-06 | 711230 | -36.7 |  | -47.9 | 35.4 | 28.1 | 29.7 | 29.8 | 29 | 29.2 |  | 25.3 | 27 | 27.1 | 26 | 26.4667 |  |  | CanadaAlbertaEDMONTON INT'L A
Canada | Alberta |  | EDMONTON NAMAO A | EDMONTON NAMAO A, AB, Canada | 53.67N | 113.47W | 688 | -7.00 (NAM) | 82-01 | 711210 | -33.2 |  | -44.9 | 34.7 | 27.4 | 28.9 | 29.4 | 29 | 28.5667 |  | 25.1 | 26.8 | 27.1 | 26 | 26.3333 |  |  | CanadaAlbertaEDMONTON NAMAO A
Canada | Alberta |  | EDSON A | EDSON A, AB, Canada | 53.60N | 116.48W | 925 | -7.00 (NAM) | 82-06 | 718810 | -38.2 |  | -51.3 | 33.8 | 27 | 29 | 28.7 | 28 | 28.2333 |  | 24.2 | 26.6 | 26.5 | 26 | 25.7667 |  |  | CanadaAlbertaEDSON A
Canada | Alberta |  | ELK ISLAND NAT PARK | ELK ISLAND NAT PARK, AB, Canada | 53.68N | 112.87W | 716 | -7.00 (NAM) | 94-06 | 712380 | -37.7 |  | -47.8 | 37.4 | 28.5 | 31.7 | 30.4 | 30 | 30.2 |  | 26.1 | 28.2 | 27.9 | 27 | 27.4 |  |  | CanadaAlbertaELK ISLAND NAT PARK
Canada | Alberta |  | ESTHER 1 | ESTHER 1, AB, Canada | 51.67N | 110.21W | 707 | -7.00 (NAM) | 94-06 | 712400 | -35.6 |  | -45.9 | 39.8 | 30.2 | 34.4 | 34.5 | 33 | 33.0333 |  | 27.7 | 31.7 | 32.1 | 31 | 30.5 |  |  | CanadaAlbertaESTHER 1
Canada | Alberta |  | FORT CHIPEWYAN A | FORT CHIPEWYAN A, AB, Canada | 58.77N | 111.12W | 232 | -7.00 (NAM) | 93-06 | 719330 | -43.9 |  | -48.8 | 36.1 | 28.9 | 30.1 | 28.9 | 29 | 29.3 |  | 26.1 | 27.9 | 26.1 | 27 | 26.7 |  |  | CanadaAlbertaFORT CHIPEWYAN A
Canada | Alberta |  | FORT MCMURRAY A | FORT MCMURRAY A, AB, Canada | 56.65N | 111.22W | 369 | -7.00 (NAM) | 82-06 | 719320 | -39.9 |  | -47.2 | 37.7 | 29.4 | 31.2 | 31.9 | 31 | 30.8333 |  | 27 | 28.8 | 28.7 | 28 | 28.1667 |  |  | CanadaAlbertaFORT MCMURRAY A
Canada | Alberta |  | GARDEN RIVER | GARDEN RIVER, AB, Canada | 58.71N | 113.87W | 241 | -7.00 (NAM) | 94-06 | 712530 | -43 |  | -46.5 | 35.4 | 30.5 | 30.6 | 30.2 | 30 | 30.4333 |  | 27.7 | 28.6 | 26.9 | 28 | 27.7333 |  |  | CanadaAlbertaGARDEN RIVER
Canada | Alberta |  | GRANDE PRAIRIE A | GRANDE PRAIRIE A, AB, Canada | 55.18N | 118.88W | 669 | -7.00 (NAM) | 82-06 | 719400 | -40.2 |  | -52.2 | 34.5 | 28.1 | 29.9 | 29.9 | 29 | 29.3 |  | 25.1 | 27.3 | 27.2 | 27 | 26.5333 |  |  | CanadaAlbertaGRANDE PRAIRIE A
Canada | Alberta |  | HIGH LEVEL A | HIGH LEVEL A, AB, Canada | 58.62N | 117.16W | 338 | -7.00 (NAM) | 82-06 | 710660 | -43.1 |  | -51.4 | 33.9 | 28.4 | 30.1 | 29.6 | 29 | 29.3667 |  | 26.3 | 27.8 | 26.9 | 27 | 27 |  |  | CanadaAlbertaHIGH LEVEL A
Canada | Alberta |  | HIGHVALE | HIGHVALE, AB, Canada | 53.45N | 114.47W | 747 | -7.00 (NAM) | 94-06 | 712410 | -33.5 |  | -43.1 | 36 | 28.4 | 30.8 | 30.1 | 30 | 29.7667 |  | 25.3 | 27.8 | 27.1 | 27 | 26.7333 |  |  | CanadaAlbertaHIGHVALE
Canada | Alberta |  | JASPER | JASPER, AB, Canada | 52.88N | 118.07W | 1062 | -7.00 (NAM) | 82-92 | 718880 | -35.1 |  | -47.4 | 32.9 | 27.5 | 29.8 | 28.8 | 29 | 28.7 |  | 24.9 | 27.8 | 26.8 | 27 | 26.5 |  |  | CanadaAlbertaJASPER
Canada | Alberta |  | JASPER WARDEN | JASPER WARDEN, AB, Canada | 52.93N | 118.03W | 1020 | -7.00 (NAM) | 94-06 | 714860 | -36.2 |  | -48.9 | 37.5 | 28.5 | 32.7 | 31.6 | 31 | 30.9333 |  | 25.6 | 29.8 | 29 | 28 | 28.1333 |  |  | CanadaAlbertaJASPER WARDEN
Canada | Alberta |  | LAC LA BICHE (AUT) | LAC LA BICHE (AUT), AB, Canada | 54.77N | 112.02W | 567 | -7.00 (NAM) | 94-04 | 729310 | -38.4 |  | -48.3 | 35.2 | 28.7 | 29.7 | 30.1 | 30 | 29.5 |  | 25.9 | 27.2 | 27.3 | 27 | 26.8 |  |  | CanadaAlbertaLAC LA BICHE (AUT)
Canada | Alberta |  | LACOMBE CDA 2 | LACOMBE CDA 2, AB, Canada | 52.45N | 113.76W | 860 | -7.00 (NAM) | 94-06 | 712420 | -36.6 |  | -49 | 36.6 | 28.2 | 31.1 | 31.1 | 30 | 30.1333 |  | 25.4 | 28.3 | 27.9 | 27 | 27.2 |  |  | CanadaAlbertaLACOMBE CDA 2
Canada | Alberta |  | LETHBRIDGE A | LETHBRIDGE A, AB, Canada | 49.63N | 112.80W | 929 | -7.00 (NAM) | 82-06 | 718740 | -34.3 |  | -44.6 | 39.7 | 30.9 | 33.7 | 34.4 | 33 | 33 |  | 27.9 | 31.3 | 31.5 | 30 | 30.2333 |  |  | CanadaAlbertaLETHBRIDGE A
Canada | Alberta |  | LETHBRIDGE CDA | LETHBRIDGE CDA, AB, Canada | 49.70N | 112.78W | 921 | -7.00 (NAM) | 94-06 | 712430 | -31.9 |  | -43.7 | 39.6 | 30.6 | 34.2 | 34.3 | 33 | 33.0333 |  | 27.2 | 31.8 | 32.1 | 30 | 30.3667 |  |  | CanadaAlbertaLETHBRIDGE CDA
Canada | Alberta |  | LLOYDMINSTER A | LLOYDMINSTER A, AB, Canada | 53.31N | 110.07W | 668 | -7.00 (NAM) | 82-06 | 718710 | -36.2 |  | -46.1 | 38.5 | 29.3 | 30.7 | 31.7 | 31 | 30.5667 |  | 26.3 | 27.7 | 28.6 | 28 | 27.5333 |  |  | CanadaAlbertaLLOYDMINSTER A
Canada | Alberta |  | MEDICINE HAT A | MEDICINE HAT A, AB, Canada | 50.02N | 110.72W | 717 | -7.00 (NAM) | 82-06 | 718720 | -34.3 |  | -44 | 40.2 | 32.6 | 34.5 | 35.6 | 34 | 34.2333 |  | 29.6 | 32.4 | 32.6 | 32 | 31.5333 |  |  | CanadaAlbertaMEDICINE HAT A
Canada | Alberta |  | MILDRED LAKE | MILDRED LAKE, AB, Canada | 57.04N | 111.56W | 310 | -7.00 (NAM) | 94-06 | 712550 | -37.5 |  | -45 | 37.7 | 30.6 | 31.5 | 31.9 | 31 | 31.3333 |  | 27.8 | 29.4 | 28.5 | 29 | 28.5667 |  |  | CanadaAlbertaMILDRED LAKE
Canada | Alberta |  | MILK RIVER | MILK RIVER, AB, Canada | 49.13N | 112.05W | 1050 | -7.00 (NAM) | 94-06 | 712440 | -34.8 |  | -44.1 | 39.2 | 29.9 | 34.2 | 34 | 33 | 32.7 |  | 26.8 | 32 | 31.9 | 30 | 30.2333 |  |  | CanadaAlbertaMILK RIVER
Canada | Alberta |  | NAKISKA RIDGETOP | NAKISKA RIDGETOP, AB, Canada | 50.94N | 115.19W | 2543 | -7.00 (NAM) | 94-06 | 712450 | -32.8 |  | -40.7 | 25.8 | 17.2 | 21.7 | 19.7 | 20 | 19.5333 |  | 14 | 19.2 | 17.5 | 17 | 16.9 |  |  | CanadaAlbertaNAKISKA RIDGETOP
Canada | Alberta |  | ONEFOUR CDA | ONEFOUR CDA, AB, Canada | 49.12N | 110.47W | 935 | -7.00 (NAM) | 94-06 | 711160 | -32.2 |  | -41.8 | 40.3 | 31.8 | 35.5 | 35.7 | 34 | 34.3333 |  | 28.3 | 33.7 | 33.1 | 32 | 31.7 |  |  | CanadaAlbertaONEFOUR CDA
Canada | Alberta |  | PEACE RIVER A | PEACE RIVER A, AB, Canada | 56.23N | 117.45W | 571 | -7.00 (NAM) | 82-06 | 710680 | -38.7 |  | -50.1 | 35.1 | 28.2 | 29.6 | 30.1 | 29 | 29.3 |  | 25.4 | 27.1 | 27.2 | 27 | 26.5667 |  |  | CanadaAlbertaPEACE RIVER A
Canada | Alberta |  | PINCHER CREEK (AUT) | PINCHER CREEK (AUT), AB, Canada | 49.52N | 113.98W | 1190 | -7.00 (NAM) | 94-06 | 718750 | -32.8 |  | -41.8 | 37.3 | 27.9 | 32.4 | 31.9 | 31 | 30.7333 |  | 24.7 | 30 | 29.7 | 28 | 28.1333 |  |  | CanadaAlbertaPINCHER CREEK (AUT)
Canada | Alberta |  | RED DEER A | RED DEER A, AB, Canada | 52.18N | 113.89W | 905 | -7.00 (NAM) | 82-06 | 718780 | -36.6 |  | -47.4 | 35.5 | 27.7 | 30.3 | 30.3 | 29 | 29.4333 |  | 25.3 | 27.6 | 27.8 | 27 | 26.9 |  |  | CanadaAlbertaRED DEER A
Canada | Alberta |  | RED EARTH | RED EARTH, AB, Canada | 56.55N | 115.28W | 546 | -7.00 (NAM) | 94-06 | 712460 | -39.7 |  | -48.9 | 35.3 | 28.7 | 30.2 | 30.6 | 30 | 29.8333 |  | 26.4 | 28.1 | 27.4 | 27 | 27.3 |  |  | CanadaAlbertaRED EARTH
Canada | Alberta |  | ROCKY MTN HOUSE (AUT) | ROCKY MTN HOUSE (AUT), AB, Canada | 52.42N | 114.91W | 988 | -7.00 (NAM) | 82-06 | 719280 | -38.5 |  | -48.9 | 33.8 | 26.5 | 29.2 | 28.7 | 28 | 28.1333 |  | 24 | 26.8 | 26.3 | 26 | 25.7 |  |  | CanadaAlbertaROCKY MTN HOUSE (AUT)
Canada | Alberta |  | SLAVE LAKE A | SLAVE LAKE A, AB, Canada | 55.28N | 114.78W | 583 | -7.00 (NAM) | 82-06 | 710690 | -37.3 |  | -48.4 | 35 | 26.8 | 28.8 | 29.7 | 28 | 28.4333 |  | 24 | 26.1 | 26.2 | 25 | 25.4333 |  |  | CanadaAlbertaSLAVE LAKE A
Canada | Alberta |  | SPRINGBANK A | SPRINGBANK A, AB, Canada | 51.10N | 114.37W | 1201 | -7.00 (NAM) | 88-02 | 718600 | -36.1 |  | -47.5 | 33.7 | 25.5 | 28.5 | 29.5 | 28 | 27.8333 |  | 23.2 | 26.3 | 27.4 | 26 | 25.6333 |  |  | CanadaAlbertaSPRINGBANK A
Canada | Alberta |  | STAVELY AAFC | STAVELY AAFC, AB, Canada | 50.18N | 113.88W | 1364 | -7.00 (NAM) | 96-06 | 715550 | -28.1 |  | -38.5 | 34.2 | 25.2 | 30 | 29.8 | 28 | 28.3333 |  | 22.4 | 27.6 | 27.7 | 26 | 25.9 |  |  | CanadaAlbertaSTAVELY AAFC
Canada | Alberta |  | SUNDRE A | SUNDRE A, AB, Canada | 51.78N | 114.68W | 1114 | -7.00 (NAM) | 94-06 | 712480 | -38.6 |  | -50.7 | 35.1 | 28.2 | 30.3 | 30.5 | 30 | 29.6667 |  | 24.2 | 27.8 | 27.9 | 27 | 26.6333 |  |  | CanadaAlbertaSUNDRE A
Canada | Alberta |  | THREE HILLS | THREE HILLS, AB, Canada | 51.83N | 113.21W | 907 | -7.00 (NAM) | 94-06 | 712490 | -32.9 |  | -42.9 | 38.2 | 28.7 | 32.3 | 32.5 | 31 | 31.1667 |  | 25.7 | 29.4 | 29.8 | 28 | 28.3 |  |  | CanadaAlbertaTHREE HILLS
Canada | Alberta |  | VAUXHALL CDA CS | VAUXHALL CDA CS, AB, Canada | 50.05N | 112.13W | 779 | -7.00 (NAM) | 94-06 | 712510 | -35 |  | -47.6 | 39.5 | 30.4 | 33.8 | 34.5 | 33 | 32.9 |  | 27.5 | 31.8 | 32.1 | 30 | 30.4667 |  |  | CanadaAlbertaVAUXHALL CDA CS
Canada | Alberta |  | VEGREVILLE | VEGREVILLE, AB, Canada | 53.51N | 112.10W | 639 | -7.00 (NAM) | 94-06 | 714580 | -38.6 |  | -51 | 36.7 | 29.5 | 31.7 | 30.5 | 31 | 30.5667 |  | 26 | 28 | 28.1 | 27 | 27.3667 |  |  | CanadaAlbertaVEGREVILLE
Canada | Alberta |  | WAINWRIGHT CFB AIRFIELD 21 | WAINWRIGHT CFB AIRFIELD 21, AB, Canada | 52.83N | 111.10W | 686 | -7.00 (NAM) | 95-06 | 711180 | -36 |  | -46 | 40.7 | 30.3 | 33.5 | 33.7 | 33 | 32.5 |  | 27.2 | 29.9 | 30 | 29 | 29.0333 |  |  | CanadaAlbertaWAINWRIGHT CFB AIRFIELD 21
Canada | Alberta |  | WATERTON PARK GATE | WATERTON PARK GATE, AB, Canada | 49.13N | 113.81W | 1289 | -7.00 (NAM) | 94-06 | 711540 | -36.6 |  | -48.8 | 36 | 28.1 | 32 | 31.2 | 30 | 30.4333 |  | 24.6 | 29.6 | 29.3 | 28 | 27.8333 |  |  | CanadaAlbertaWATERTON PARK GATE
Canada | Alberta |  | WHITECOURT A | WHITECOURT A, AB, Canada | 54.14N | 115.79W | 782 | -7.00 (NAM) | 82-98 | 719300 | -36 |  | -48.7 | 32.6 | 26.7 | 28.3 | 28.5 | 28 | 27.8333 |  | 24.1 | 26.2 | 26.1 | 25 | 25.4667 |  |  | CanadaAlbertaWHITECOURT A
Canada | British Columbia |  | ABBOTSFORD A | ABBOTSFORD A, BC, Canada | 49.03N | 122.36W | 59 | -8.00 (NAP) | 82-06 | 711080 | -10.7 |  | -20.4 | 38.3 | 30.7 | 32.6 | 31.2 | 32 | 31.5 |  | 27.5 | 29.6 | 29.2 | 29 | 28.7667 |  |  | CanadaBritish ColumbiaABBOTSFORD A
Canada | British Columbia |  | AGASSIZ CS | AGASSIZ CS, BC, Canada | 49.25N | 121.77W | 15 | -8.00 (NAP) | 94-06 | 711130 | -8.5 |  | -16.4 | 38.8 | 31.2 | 33.5 | 31.2 | 32 | 31.9667 |  | 27.9 | 30.6 | 29.3 | 29 | 29.2667 |  |  | CanadaBritish ColumbiaAGASSIZ CS
Canada | British Columbia |  | ALERT BAY | ALERT BAY, BC, Canada | 50.58N | 126.93W | 59 | -8.00 (NAP) | 82-94 | 711100 | -6.7 |  | -15.6 | 35 | 19.9 | 22.5 | 22.4 | 22 | 21.6 |  | 17.2 | 19.3 | 19.7 | 19 | 18.7333 |  |  | CanadaBritish ColumbiaALERT BAY
Canada | British Columbia |  | AMPHITRITE POINT | AMPHITRITE POINT, BC, Canada | 48.92N | 125.54W | 27 | -8.00 (NAP) | 82-99 | 711120 | -3.9 |  | -10.5 | 25.7 | 19.9 | 20.2 | 20.7 | 20 | 20.2667 |  | 16.6 | 17.9 | 18.6 | 18 | 17.7 |  |  | CanadaBritish ColumbiaAMPHITRITE POINT
Canada | British Columbia |  | BALLENAS ISLAND | BALLENAS ISLAND, BC, Canada | 49.35N | 124.16W | 13 | -8.00 (NAP) | 94-06 | 717690 | -1.9 |  | -6.9 | 32.6 | 25 | 26.1 | 25.4 | 26 | 25.5 |  | 22.8 | 24.2 | 23.7 | 24 | 23.5667 |  |  | CanadaBritish ColumbiaBALLENAS ISLAND
Canada | British Columbia |  | BLUE RIVER CS | BLUE RIVER CS, BC, Canada | 52.13N | 119.29W | 683 | -8.00 (NAP) | 93-06 | 718830 | -31.6 |  | -47.2 | 38.8 | 30.8 | 33.7 | 33.1 | 33 | 32.5333 |  | 27.6 | 31.2 | 30.4 | 30 | 29.7333 |  |  | CanadaBritish ColumbiaBLUE RIVER CS
Canada | British Columbia |  | BONILLA ISLAND (AUT) | BONILLA ISLAND (AUT), BC, Canada | 53.50N | 130.63W | 15 | -8.00 (NAP) | 94-06 | 714840 | -6.9 |  | -14.5 | 28.3 | 17.6 | 16.7 | 17.4 | 17 | 17.2333 |  | 14.3 | 15.6 | 16.4 | 15 | 15.4333 |  |  | CanadaBritish ColumbiaBONILLA ISLAND (AUT)
Canada | British Columbia |  | BURNS LAKE DECKER LAKE | BURNS LAKE DECKER LAKE, BC, Canada | 54.38N | 125.96W | 713 | -8.00 (NAP) | 94-06 | 719520 | -36.4 |  | -46.5 | 36.1 | 31.6 | 30.9 | 29.3 | 31 | 30.6 |  | 26.9 | 27.4 | 26.5 | 27 | 26.9333 |  |  | CanadaBritish ColumbiaBURNS LAKE DECKER LAKE
Canada | British Columbia |  | CAPE SCOTT | CAPE SCOTT, BC, Canada | 50.78N | 128.43W | 72 | -8.00 (NAP) | 82-01 | 711110 | -3.6 |  | -11.8 | 25.6 | 15.9 | 17.2 | 17.8 | 17 | 16.9667 |  | 14.8 | 16.4 | 16.8 | 16 | 16 |  |  | CanadaBritish ColumbiaCAPE SCOTT
Canada | British Columbia |  | CAPE ST JAMES CS | CAPE ST JAMES CS, BC, Canada | 51.94N | 131.02W | 92 | -8.00 (NAP) | 82-06 | 711070 | -5.7 |  | -14.4 | 27.1 | 20.4 | 20.1 | 21.1 | 21 | 20.5333 |  | 16.7 | 17.8 | 19.1 | 18 | 17.8667 |  |  | CanadaBritish ColumbiaCAPE ST JAMES CS
Canada | British Columbia |  | CATHEDRAL POINT (AUT) | CATHEDRAL POINT (AUT), BC, Canada | 52.19N | 127.47W | 31 | -8.00 (NAP) | 94-06 | 714820 | -8.2 |  | -16.9 | 32.7 | 25.7 | 25.3 | 24.5 | 25 | 25.1667 |  | 21.7 | 23.1 | 22.1 | 22 | 22.3 |  |  | CanadaBritish ColumbiaCATHEDRAL POINT (AUT)
Canada | British Columbia |  | CLINTON (AUT) | CLINTON (AUT), BC, Canada | 51.14N | 121.50W | 1057 | -8.00 (NAP) | 94-06 | 714740 | -30.6 |  | -42.2 | 36.9 | 28.6 | 32.6 | 31.4 | 31 | 30.8667 |  | 25.8 | 29.6 | 28.8 | 28 | 28.0667 |  |  | CanadaBritish ColumbiaCLINTON (AUT)
Canada | British Columbia |  | COMOX A | COMOX A, BC, Canada | 49.72N | 124.90W | 26 | -8.00 (NAP) | 82-06 | 718930 | -7.2 |  | -14.5 | 34.5 | 28.8 | 29.5 | 28.4 | 29 | 28.9 |  | 25.1 | 26.7 | 26.1 | 26 | 25.9667 |  |  | CanadaBritish ColumbiaCOMOX A
Canada | British Columbia |  | CRANBROOK A | CRANBROOK A, BC, Canada | 49.61N | 115.78W | 940 | -7.00 (NAM) | 82-06 | 718800 | -27.8 |  | -40 | 39 | 31.1 | 34.3 | 33 | 33 | 32.8 |  | 28.1 | 32 | 31.1 | 30 | 30.4 |  |  | CanadaBritish ColumbiaCRANBROOK A
Canada | British Columbia |  | CRESTON CAMPBELL SCIENTIFIC | CRESTON CAMPBELL SCIENTIFIC, BC, Canada | 49.08N | 116.50W | 646 | -8.00 (NAP) | 94-06 | 717700 | -16.3 |  | -26.7 | 39.2 | 30.8 | 35.2 | 34.8 | 34 | 33.6 |  | 28.1 | 33 | 32.4 | 31 | 31.1667 |  |  | CanadaBritish ColumbiaCRESTON CAMPBELL SCIENTIFIC
Canada | British Columbia |  | CUMSHEWA ISLAND | CUMSHEWA ISLAND, BC, Canada | 53.03N | 131.60W | 17 | -8.00 (NAP) | 94-06 | 717710 | -5.6 |  | -14.6 | 24.4 | 20.6 | 19.8 | 20.2 | 20 | 20.2 |  | 16.9 | 17.8 | 18.5 | 18 | 17.7333 |  |  | CanadaBritish ColumbiaCUMSHEWA ISLAND
Canada | British Columbia |  | DEASE LAKE | DEASE LAKE, BC, Canada | 58.43N | 130.01W | 807 | -8.00 (NAP) | 83-93 | 719580 | -41.3 |  | -48.6 | 35 | 25.5 | 26.3 | 27.1 | 26 | 26.3 |  | 23.1 | 24.3 | 23.2 | 24 | 23.5333 |  |  | CanadaBritish ColumbiaDEASE LAKE
Canada | British Columbia |  | DISCOVERY ISLAND | DISCOVERY ISLAND, BC, Canada | 48.42N | 123.23W | 15 | -8.00 (NAP) | 97-06 | 710310 | -1.8 |  | -10.6 | 33.3 | 25.8 | 26.2 | 25.3 | 26 | 25.7667 |  | 22.4 | 22.7 | 22.2 | 22 | 22.4333 |  |  | CanadaBritish ColumbiaDISCOVERY ISLAND
Canada | British Columbia |  | ENTRANCE ISLAND CS | ENTRANCE ISLAND CS, BC, Canada | 49.22N | 123.80W | 5 | -8.00 (NAP) | 94-06 | 717720 | -2.6 |  | -8.5 | 34.6 | 25.4 | 26.1 | 26.7 | 26 | 26.0667 |  | 22.2 | 23.7 | 23.7 | 23 | 23.2 |  |  | CanadaBritish ColumbiaENTRANCE ISLAND CS
Canada | British Columbia |  | ESQUIMALT HARBOUR | ESQUIMALT HARBOUR, BC, Canada | 48.43N | 123.44W | 3 | -8.00 (NAP) | 94-06 | 717980 | -3.6 |  | -8.8 | 31.6 | 24.6 | 24.1 | 24.4 | 24 | 24.3667 |  | 21 | 22.2 | 21.9 | 22 | 21.7 |  |  | CanadaBritish ColumbiaESQUIMALT HARBOUR
Canada | British Columbia |  | ESTEVAN POINT CS | ESTEVAN POINT CS, BC, Canada | 49.38N | 126.54W | 7 | -8.00 (NAP) | 94-06 | 718940 | -3.7 |  | -8.9 | 27.4 | 22.5 | 22 | 21.5 | 22 | 22 |  | 18.2 | 19.9 | 19.9 | 19 | 19.3333 |  |  | CanadaBritish ColumbiaESTEVAN POINT CS
Canada | British Columbia |  | FORT NELSON A | FORT NELSON A, BC, Canada | 58.84N | 122.60W | 382 | -8.00 (NAP) | 82-06 | 719450 | -39.5 |  | -48.6 | 35.4 | 28.8 | 30.6 | 30.1 | 30 | 29.8333 |  | 26.7 | 27.8 | 27.3 | 27 | 27.2667 |  |  | CanadaBritish ColumbiaFORT NELSON A
Canada | British Columbia |  | FORT ST JOHN A | FORT ST JOHN A, BC, Canada | 56.24N | 120.74W | 695 | -7.00 (NAD) | 82-06 | 719430 | -36.2 |  | -45.7 | 33.2 | 27 | 28.8 | 28.4 | 28 | 28.0667 |  | 24.2 | 26.1 | 25.9 | 25 | 25.4 |  |  | CanadaBritish ColumbiaFORT ST JOHN A
Canada | British Columbia |  | GREY ISLET (AUT) | GREY ISLET (AUT), BC, Canada | 54.58N | 130.70W | 8 | -8.00 (NAP) | 94-06 | 714760 | -7.3 |  | -13.3 | 26.8 | 21.2 | 20 | 21.1 | 21 | 20.7667 |  | 17.8 | 18.2 | 18.9 | 18 | 18.3 |  |  | CanadaBritish ColumbiaGREY ISLET (AUT)
Canada | British Columbia |  | HERBERT ISLAND (AUT) | HERBERT ISLAND (AUT), BC, Canada | 50.94N | 127.64W | 17 | -8.00 (NAP) | 94-06 | 714850 | -2.5 |  | -8 | 26.9 | 16.2 | 16.7 | 17.8 | 17 | 16.9 |  | 14.8 | 15.7 | 16.3 | 16 | 15.6 |  |  | CanadaBritish ColumbiaHERBERT ISLAND (AUT)
Canada | British Columbia |  | HOLLAND ROCK | HOLLAND ROCK, BC, Canada | 54.17N | 130.36W | 5 | -8.00 (NAP) | 94-06 | 712190 | -7.4 |  | -15.3 | 29.1 | 19 | 17.1 | 19.4 | 19 | 18.5 |  | 15.1 | 15.7 | 17 | 16 | 15.9333 |  |  | CanadaBritish ColumbiaHOLLAND ROCK
Canada | British Columbia |  | HOPE | HOPE, BC, Canada | 49.37N | 121.48W | 39 | -8.00 (NAP) | 82-05 | 711140 | -12.9 |  | -25.1 | 39.6 | 31.1 | 32.9 | 32.1 | 32 | 32.0333 |  | 28.1 | 30.3 | 29.6 | 29 | 29.3333 |  |  | CanadaBritish ColumbiaHOPE
Canada | British Columbia |  | HOWE SOUND - PAM ROCKS | HOWE SOUND - PAM ROCKS, BC, Canada | 49.49N | 123.30W | 5 | -8.00 (NAP) | 94-06 | 712110 | -3.8 |  | -10 | 34 | 25.5 | 27.7 | 28 | 27 | 27.0667 |  | 23 | 25.3 | 24.7 | 24 | 24.3333 |  |  | CanadaBritish ColumbiaHOWE SOUND - PAM ROCKS
Canada | British Columbia |  | KAMLOOPS A | KAMLOOPS A, BC, Canada | 50.70N | 120.44W | 345 | -8.00 (NAP) | 82-06 | 718870 | -22.5 |  | -36 | 40.8 | 34.4 | 36.7 | 35.2 | 35 | 35.4333 |  | 31.2 | 34.3 | 32.9 | 33 | 32.8 |  |  | CanadaBritish ColumbiaKAMLOOPS A
Canada | British Columbia |  | KELOWNA A | KELOWNA A, BC, Canada | 49.96N | 119.38W | 430 | -8.00 (NAP) | 82-04 | 712030 | -22.5 |  | -38 | 40.4 | 33.6 | 36 | 34.4 | 35 | 34.6667 |  | 30.1 | 33.3 | 32.2 | 32 | 31.8667 |  |  | CanadaBritish ColumbiaKELOWNA A
Canada | British Columbia |  | KINDAKUN ROCKS (AUT) | KINDAKUN ROCKS (AUT), BC, Canada | 53.32N | 132.77W | 14 | -8.00 (NAP) | 94-06 | 714720 | -5.2 |  | -10.1 | 31.7 | 17.9 | 16.7 | 18.4 | 18 | 17.6667 |  | 14.2 | 15.4 | 17 | 16 | 15.5333 |  |  | CanadaBritish ColumbiaKINDAKUN ROCKS (AUT)
Canada | British Columbia |  | LANGARA | LANGARA, BC, Canada | 54.26N | 133.06W | 41 | -8.00 (NAP) | 82-01 | 718990 | -5.6 |  | -14.7 | 25.1 | 15.2 | 16.1 | 17.7 | 16 | 16.3333 |  | 13.9 | 15.1 | 16.2 | 15 | 15.0667 |  |  | CanadaBritish ColumbiaLANGARA
Canada | British Columbia |  | LILLOOET | LILLOOET, BC, Canada | 50.68N | 121.93W | 235 | -8.00 (NAP) | 97-06 | 719990 | -17.8 |  | -32.4 | 43.7 | 35.1 | 38.6 | 36.7 | 37 | 36.8 |  | 32.2 | 35.7 | 34.4 | 34 | 34.1 |  |  | CanadaBritish ColumbiaLILLOOET
Canada | British Columbia |  | LUCY ISLAND LIGHTSTATION | LUCY ISLAND LIGHTSTATION, BC, Canada | 54.30N | 130.61W | 26 | -8.00 (NAP) | 94-06 | 712200 | -7.8 |  | -14.3 | 28.8 | 20.9 | 18.6 | 20.1 | 20 | 19.8667 |  | 16.6 | 17 | 17.9 | 17 | 17.1667 |  |  | CanadaBritish ColumbiaLUCY ISLAND LIGHTSTATION
Canada | British Columbia |  | LYTTON | LYTTON, BC, Canada | 50.22N | 121.58W | 225 | -8.00 (NAP) | 82-06 | 718910 | -19 |  | -31.9 | 42.9 | 35.5 | 38.5 | 36.8 | 37 | 36.9333 |  | 32 | 35.3 | 34.2 | 34 | 33.8333 |  |  | CanadaBritish ColumbiaLYTTON
Canada | British Columbia |  | MACKENZIE A | MACKENZIE A, BC, Canada | 55.31N | 123.14W | 690 | -7.00 (NAD) | 94-06 | 719440 | -35.9 |  | -53 | 33.8 | 28.5 | 30.8 | 28.8 | 29 | 29.3667 |  | 26 | 27.5 | 26.5 | 27 | 26.6667 |  |  | CanadaBritish ColumbiaMACKENZIE A
Canada | British Columbia |  | MALAHAT | MALAHAT, BC, Canada | 48.57N | 123.53W | 366 | -8.00 (NAP) | 94-06 | 717740 | -7.1 |  | -15.2 | 36.2 | 29.1 | 31.5 | 28.4 | 30 | 29.6667 |  | 25.4 | 28.4 | 26.6 | 27 | 26.8 |  |  | CanadaBritish ColumbiaMALAHAT
Canada | British Columbia |  | NAKUSP CS | NAKUSP CS, BC, Canada | 50.27N | 117.81W | 512 | -8.00 (NAP) | 94-06 | 712160 | -15.2 |  | -25.3 | 41.6 | 30.7 | 35 | 33.6 | 33 | 33.1 |  | 27.8 | 31.9 | 30.5 | 30 | 30.0667 |  |  | CanadaBritish ColumbiaNAKUSP CS
Canada | British Columbia |  | NELSON CS | NELSON CS, BC, Canada | 49.49N | 117.31W | 535 | -8.00 (NAP) | 94-06 | 717760 | -13.9 |  | -23.8 | 39.5 | 30.3 | 35.2 | 34 | 33 | 33.1667 |  | 27.3 | 32.2 | 31.6 | 30 | 30.3667 |  |  | CanadaBritish ColumbiaNELSON CS
Canada | British Columbia |  | OSOYOOS CS | OSOYOOS CS, BC, Canada | 49.03N | 119.44W | 283 | -8.00 (NAP) | 94-06 | 712150 | -15 |  | -24.7 | 43.1 | 36.4 | 38.5 | 37.4 | 37 | 37.4333 |  | 32.5 | 35.9 | 35 | 34 | 34.4667 |  |  | CanadaBritish ColumbiaOSOYOOS CS
Canada | British Columbia |  | PEMBERTON AIRPORT CS | PEMBERTON AIRPORT CS, BC, Canada | 50.30N | 122.74W | 204 | -8.00 (NAP) | 94-06 | 717770 | -16.6 |  | -25.3 | 42.4 | 34.4 | 37.1 | 34.4 | 35 | 35.3 |  | 30.8 | 34.3 | 32.6 | 33 | 32.5667 |  |  | CanadaBritish ColumbiaPEMBERTON AIRPORT CS
Canada | British Columbia |  | PENTICTON A | PENTICTON A, BC, Canada | 49.46N | 119.60W | 344 | -8.00 (NAP) | 82-06 | 718890 | -15.9 |  | -25.7 | 39.3 | 33.2 | 35.5 | 34.2 | 34 | 34.3 |  | 30 | 33.1 | 31.8 | 32 | 31.6333 |  |  | CanadaBritish ColumbiaPENTICTON A
Canada | British Columbia |  | PITT MEADOWS CS | PITT MEADOWS CS, BC, Canada | 49.21N | 122.69W | 5 | -8.00 (NAP) | 94-06 | 717750 | -10.2 |  | -18.7 | 40.1 | 31.2 | 34.2 | 31.7 | 32 | 32.3667 |  | 28 | 31.4 | 29.8 | 30 | 29.7333 |  |  | CanadaBritish ColumbiaPITT MEADOWS CS
Canada | British Columbia |  | POINT ATKINSON | POINT ATKINSON, BC, Canada | 49.33N | 123.26W | 35 | -8.00 (NAP) | 96-06 | 710370 | N/A |  | N/A | N/A | 26.1 | 27.7 | 26 | 27 | 26.6 |  | 23.3 | 25.4 | 24.5 | 24 | 24.4 |  |  | CanadaBritish ColumbiaPOINT ATKINSON
Canada | British Columbia |  | PORT ALBERNI (AUT) | PORT ALBERNI (AUT), BC, Canada | 49.32N | 124.93W | 76 | -8.00 (NAP) | 94-06 | 714750 | -8.8 |  | -16.8 | 40.3 | 32.7 | 35.1 | 33.1 | 34 | 33.6333 |  | 28.6 | 31.9 | 30.8 | 30 | 30.4333 |  |  | CanadaBritish ColumbiaPORT ALBERNI (AUT)
Canada | British Columbia |  | PORT HARDY A | PORT HARDY A, BC, Canada | 50.68N | 127.37W | 22 | -8.00 (NAP) | 82-06 | 711090 | -6.9 |  | -13.7 | 30.5 | 21.9 | 22.4 | 22.1 | 22 | 22.1333 |  | 18.2 | 19.6 | 19.8 | 19 | 19.2 |  |  | CanadaBritish ColumbiaPORT HARDY A
Canada | British Columbia |  | PRINCE GEORGE A | PRINCE GEORGE A, BC, Canada | 53.89N | 122.68W | 691 | -8.00 (NAP) | 82-06 | 718960 | -34.4 |  | -48.3 | 35 | 28.6 | 30.5 | 29.6 | 30 | 29.5667 |  | 25.9 | 27.7 | 27.2 | 27 | 26.9333 |  |  | CanadaBritish ColumbiaPRINCE GEORGE A
Canada | British Columbia |  | PRINCE RUPERT A | PRINCE RUPERT A, BC, Canada | 54.29N | 130.44W | 35 | -8.00 (NAP) | 82-04 | 718980 | -14.4 |  | -22.8 | 31.6 | 21.4 | 20.5 | 21.9 | 21 | 21.2667 |  | 17.1 | 18.1 | 18.9 | 18 | 18.0333 |  |  | CanadaBritish ColumbiaPRINCE RUPERT A
Canada | British Columbia |  | PRINCETON CS | PRINCETON CS, BC, Canada | 49.47N | 120.51W | 700 | -8.00 (NAP) | 94-06 | 710320 | -26.8 |  | -41.2 | 41.6 | 32.9 | 36.6 | 35.7 | 35 | 35.0667 |  | 29.5 | 33.7 | 32.9 | 32 | 32.0333 |  |  | CanadaBritish ColumbiaPRINCETON CS
Canada | British Columbia |  | PUNTZI MOUNTAIN (AUT) | PUNTZI MOUNTAIN (AUT), BC, Canada | 52.11N | 124.14W | 910 | -8.00 (NAP) | 94-06 | 710500 | -39.5 |  | -56.9 | 36.9 | 29.2 | 32.6 | 31.1 | 31 | 30.9667 |  | 25.9 | 29.4 | 28.6 | 28 | 27.9667 |  |  | CanadaBritish ColumbiaPUNTZI MOUNTAIN (AUT)
Canada | British Columbia |  | QUESNEL A | QUESNEL A, BC, Canada | 53.03N | 122.51W | 545 | -8.00 (NAP) | 82-06 | 711030 | -32 |  | -45.4 | 37.6 | 30.5 | 32.7 | 30.9 | 31 | 31.3667 |  | 27.5 | 29.5 | 28.4 | 28 | 28.4667 |  |  | CanadaBritish ColumbiaQUESNEL A
Canada | British Columbia |  | REVELSTOKE A | REVELSTOKE A, BC, Canada | 50.96N | 118.18W | 445 | -8.00 (NAP) | 82-06 | 718820 | -20.6 |  | -32.2 | 38.7 | 31.2 | 34 | 32.3 | 33 | 32.5 |  | 28.2 | 30.7 | 29.4 | 29 | 29.4333 |  |  | CanadaBritish ColumbiaREVELSTOKE A
Canada | British Columbia |  | ROSE SPIT (AUT) | ROSE SPIT (AUT), BC, Canada | 54.16N | 131.66W | 7 | -8.00 (NAP) | 94-06 | 714770 | -6.4 |  | -11.2 | 24 | 17.6 | 17.1 | 18.3 | 18 | 17.6667 |  | 14.8 | 16.2 | 17.1 | 16 | 16.0333 |  |  | CanadaBritish ColumbiaROSE SPIT (AUT)
Canada | British Columbia |  | SALMON ARM CS | SALMON ARM CS, BC, Canada | 50.70N | 119.29W | 351 | -8.00 (NAP) | 94-06 | 712180 | -19.9 |  | -34.2 | 41 | 32.1 | 35.5 | 34.3 | 34 | 33.9667 |  | 29.4 | 33.1 | 31.4 | 31 | 31.3 |  |  | CanadaBritish ColumbiaSALMON ARM CS
Canada | British Columbia |  | SANDHEADS CS | SANDHEADS CS, BC, Canada | 49.11N | 123.30W | 0 | -8.00 (NAP) | 94-06 | 712090 | -5.5 |  | -11.2 | 27.6 | 22.5 | 24.3 | 23.3 | 23 | 23.3667 |  | 21 | 22.6 | 22 | 22 | 21.8667 |  |  | CanadaBritish ColumbiaSANDHEADS CS
Canada | British Columbia |  | SANDSPIT A | SANDSPIT A, BC, Canada | 53.25N | 131.81W | 6 | -8.00 (NAP) | 82-03 | 711010 | -6.8 |  | -14.7 | 27.3 | 20.1 | 21.9 | 22 | 21 | 21.3333 |  | 17.5 | 19.2 | 20.2 | 19 | 18.9667 |  |  | CanadaBritish ColumbiaSANDSPIT A
Canada | British Columbia |  | SARTINE ISLAND (AUT) | SARTINE ISLAND (AUT), BC, Canada | 50.82N | 128.91W | 112 | -8.00 (NAP) | 94-06 | 714780 | -2.8 |  | -7.9 | 28.5 | 18.6 | 16.1 | 17.1 | 17 | 17.2667 |  | 14.1 | 15.2 | 16.2 | 15 | 15.1667 |  |  | CanadaBritish ColumbiaSARTINE ISLAND (AUT)
Canada | British Columbia |  | SHERINGHAM POINT | SHERINGHAM POINT, BC, Canada | 48.38N | 123.92W | 22 | -8.00 (NAP) | 94-06 | 717800 | -3.3 |  | -11.1 | 33.3 | 25.3 | 25.7 | 24.4 | 25 | 25.1333 |  | 20.2 | 21.8 | 20.5 | 21 | 20.8333 |  |  | CanadaBritish ColumbiaSHERINGHAM POINT
Canada | British Columbia |  | SISTERS ISLAND | SISTERS ISLAND, BC, Canada | 49.49N | 124.43W | 20 | -8.00 (NAP) | 96-06 | 717810 | -2 |  | -6.5 | 30.5 | 24.4 | 25.4 | 24.7 | 25 | 24.8333 |  | 21.9 | 23.5 | 23.1 | 23 | 22.8333 |  |  | CanadaBritish ColumbiaSISTERS ISLAND
Canada | British Columbia |  | SMITHERS A | SMITHERS A, BC, Canada | 54.82N | 127.18W | 522 | -8.00 (NAP) | 82-06 | 719500 | -30.9 |  | -40.8 | 36.5 | 29.3 | 30.4 | 29.4 | 30 | 29.7 |  | 26.2 | 27.1 | 26.2 | 27 | 26.5 |  |  | CanadaBritish ColumbiaSMITHERS A
Canada | British Columbia |  | SOLANDER ISLAND (AUT) | SOLANDER ISLAND (AUT), BC, Canada | 50.11N | 127.94W | 99 | -8.00 (NAP) | 94-06 | 714790 | -1.9 |  | -9.8 | 30.5 | 22.1 | 16.9 | 19.1 | 19 | 19.3667 |  | 14.7 | 15.5 | 16.7 | 16 | 15.6333 |  |  | CanadaBritish ColumbiaSOLANDER ISLAND (AUT)
Canada | British Columbia |  | SPARWOOD CS | SPARWOOD CS, BC, Canada | 49.75N | 114.89W | 1138 | -7.00 (NAM) | 94-06 | 717820 | -31.2 |  | -40.3 | 36.9 | 28.1 | 32.4 | 32 | 31 | 30.8333 |  | 25.3 | 30.1 | 29.6 | 28 | 28.3333 |  |  | CanadaBritish ColumbiaSPARWOOD CS
Canada | British Columbia |  | SQUAMISH | SQUAMISH, BC, Canada | 49.78N | 123.16W | 52 | -8.00 (NAP) | 94-06 | 712070 | -8.7 |  | -15.6 | 37.9 | 31 | 32.7 | 30.4 | 31 | 31.3667 |  | 27.3 | 29.6 | 28.2 | 28 | 28.3667 |  |  | CanadaBritish ColumbiaSQUAMISH
Canada | British Columbia |  | SUMMERLAND CS | SUMMERLAND CS, BC, Canada | 49.56N | 119.64W | 454 | -8.00 (NAP) | 94-06 | 717680 | -16 |  | -24.9 | 39.7 | 32.1 | 36.2 | 34.7 | 34 | 34.3333 |  | 29.5 | 33.8 | 32.4 | 32 | 31.9 |  |  | CanadaBritish ColumbiaSUMMERLAND CS
Canada | British Columbia |  | TERRACE A | TERRACE A, BC, Canada | 54.47N | 128.58W | 217 | -8.00 (NAP) | 82-06 | 719510 | -19.5 |  | -28.5 | 36.8 | 30.2 | 31.2 | 29.9 | 30 | 30.4333 |  | 26.6 | 27.8 | 26.8 | 27 | 27.0667 |  |  | CanadaBritish ColumbiaTERRACE A
Canada | British Columbia |  | VANCOUVER HARBOUR CS | VANCOUVER HARBOUR CS, BC, Canada | 49.30N | 123.12W | 3 | -8.00 (NAP) | 94-06 | 712010 | -4.2 |  | -11.5 | 32.1 | 26.9 | 28.3 | 26.8 | 27 | 27.3333 |  | 24.1 | 25.9 | 25.3 | 25 | 25.1 |  |  | CanadaBritish ColumbiaVANCOUVER HARBOUR CS
Canada | British Columbia |  | VANCOUVER INT'L A | VANCOUVER INT'L A, BC, Canada | 49.20N | 123.18W | 4 | -8.00 (NAP) | 82-06 | 718920 | -9.1 |  | -17.2 | 32.2 | 25.9 | 27.4 | 26.5 | 27 | 26.6 |  | 23.3 | 25.2 | 24.5 | 24 | 24.3333 |  |  | CanadaBritish ColumbiaVANCOUVER INT'L A
Canada | British Columbia |  | VERNON CS | VERNON CS, BC, Canada | 50.22N | 119.19W | 482 | -8.00 (NAP) | 94-06 | 711150 | -19 |  | -34.2 | 42.1 | 32.9 | 36.4 | 34.7 | 35 | 34.6667 |  | 29.7 | 33.9 | 32.5 | 32 | 32.0333 |  |  | CanadaBritish ColumbiaVERNON CS
Canada | British Columbia |  | VICTORIA GONZALES CS | VICTORIA GONZALES CS, BC, Canada | 48.41N | 123.33W | 70 | -8.00 (NAP) | 94-06 | 712000 | -3.9 |  | -10.9 | 36.7 | 28.4 | 27 | 26.3 | 27 | 27.2333 |  | 23.3 | 24.1 | 22.9 | 23 | 23.4333 |  |  | CanadaBritish ColumbiaVICTORIA GONZALES CS
Canada | British Columbia |  | VICTORIA HARTLAND CS | VICTORIA HARTLAND CS, BC, Canada | 48.53N | 123.46W | 154 | -8.00 (NAP) | 94-06 | 710380 | -4.4 |  | -10.6 | 35.9 | 30.1 | 31.7 | 29.7 | 31 | 30.5 |  | 27 | 29.1 | 27.5 | 28 | 27.8667 |  |  | CanadaBritish ColumbiaVICTORIA HARTLAND CS
Canada | British Columbia |  | VICTORIA INT'L A | VICTORIA INT'L A, BC, Canada | 48.65N | 123.43W | 19 | -8.00 (NAP) | 82-06 | 717990 | -6.6 |  | -14 | 34.6 | 28.7 | 29.5 | 28.4 | 29 | 28.8667 |  | 24.8 | 26.5 | 25.8 | 26 | 25.7 |  |  | CanadaBritish ColumbiaVICTORIA INT'L A
Canada | British Columbia |  | VICTORIA MARINE | VICTORIA MARINE, BC, Canada | 48.37N | 123.75W | 32 | -8.00 (NAP) | 82-92 | 712020 | -7.2 |  | -16.6 | 28.4 | 22.4 | 23.8 | 22.3 | 23 | 22.8333 |  | 18.8 | 20.2 | 20.6 | 20 | 19.8667 |  |  | CanadaBritish ColumbiaVICTORIA MARINE
Canada | British Columbia |  | VICTORIA UNIVERSITY CS | VICTORIA UNIVERSITY CS, BC, Canada | 48.46N | 123.30W | 60 | -8.00 (NAP) | 94-06 | 717830 | -4.2 |  | -9.4 | 35.3 | 28.5 | 30.1 | 28.5 | 29 | 29.0333 |  | 24.9 | 27.4 | 26.3 | 26 | 26.2 |  |  | CanadaBritish ColumbiaVICTORIA UNIVERSITY CS
Canada | British Columbia |  | WEST VANCOUVER AUT | WEST VANCOUVER AUT, BC, Canada | 49.35N | 123.19W | 168 | -8.00 (NAP) | 94-06 | 717840 | -6.5 |  | -15.9 | 36.3 | 29.6 | 30.2 | 27.9 | 29 | 29.2333 |  | 26 | 26.8 | 26.1 | 26 | 26.3 |  |  | CanadaBritish ColumbiaWEST VANCOUVER AUT
Canada | British Columbia |  | WHITE ROCK CAMPBELL SCIENTIFI | WHITE ROCK CAMPBELL SCIENTIFI, BC, Canada | 49.02N | 122.78W | 13 | -8.00 (NAP) | 94-06 | 717850 | -6.8 |  | -14.4 | 34.4 | 26.5 | 27.9 | 26.3 | 27 | 26.9 |  | 23.3 | 25 | 24.1 | 24 | 24.1333 |  |  | CanadaBritish ColumbiaWHITE ROCK CAMPBELL SCIENTIFI
Canada | British Columbia |  | WILLIAMS LAKE A | WILLIAMS LAKE A, BC, Canada | 52.18N | 122.05W | 940 | -8.00 (NAP) | 82-06 | 711040 | -32.8 |  | -45.6 | 35.6 | 28.7 | 30.7 | 29.9 | 30 | 29.7667 |  | 25.8 | 28.2 | 27.3 | 27 | 27.1 |  |  | CanadaBritish ColumbiaWILLIAMS LAKE A
Canada | British Columbia |  | YOHO PARK | YOHO PARK, BC, Canada | 51.44N | 116.34W | 1615 | -7.00 (NAM) | 94-06 | 717860 | -35.5 |  | -44.5 | 32.6 | 24.9 | 28.2 | 27.6 | 27 | 26.9 |  | 21.8 | 26.1 | 25.2 | 24 | 24.3667 |  |  | CanadaBritish ColumbiaYOHO PARK
Canada | Manitoba |  | BERENS RIVER CS | BERENS RIVER CS, MB, Canada | 52.36N | 97.02W | 222 | -6.00 (NAC) | 88-06 | 711580 | -38.9 |  | -44.4 | 36 | 30.9 | 29.2 | 29.7 | 30 | 29.9333 |  | 26.7 | 27 | 27.3 | 27 | 27 |  |  | CanadaManitobaBERENS RIVER CS
Canada | Manitoba |  | BRANDON A | BRANDON A, MB, Canada | 49.91N | 99.95W | 409 | -6.00 (NAC) | 82-06 | 711400 | -37.1 |  | -44 | 39.1 | 33.1 | 31.9 | 33.8 | 33 | 32.9333 |  | 28.9 | 29.5 | 30.8 | 30 | 29.7333 |  |  | CanadaManitobaBRANDON A
Canada | Manitoba |  | CARBERRY CS | CARBERRY CS, MB, Canada | 49.91N | 99.36W | 384 | -6.00 (NAC) | 94-06 | 711700 | -37.5 |  | -45.6 | 38.3 | 32.5 | 31.5 | 33.5 | 33 | 32.5 |  | 28.9 | 29.5 | 30.4 | 30 | 29.6 |  |  | CanadaManitobaCARBERRY CS
Canada | Manitoba |  | CARMAN U OF M CS | CARMAN U OF M CS, MB, Canada | 49.50N | 98.03W | 268 | -6.00 (NAC) | 95-06 | 711470 | -35.5 |  | -42.5 | 35.7 | 31.3 | 31.2 | 32.8 | 32 | 31.7667 |  | 29 | 29.6 | 30.4 | 30 | 29.6667 |  |  | CanadaManitobaCARMAN U OF M CS
Canada | Manitoba |  | CHURCHILL A | CHURCHILL A, MB, Canada | 58.74N | 94.06W | 29 | -6.00 (NAC) | 82-06 | 719130 | -39.6 |  | -45.9 | 35.8 | 26.6 | 29 | 28.6 | 28 | 28.0667 |  | 23.3 | 26.2 | 24.7 | 25 | 24.7333 |  |  | CanadaManitobaCHURCHILL A
Canada | Manitoba |  | DAUPHIN A | DAUPHIN A, MB, Canada | 51.10N | 100.05W | 305 | -6.00 (NAC) | 82-06 | 718550 | -36.6 |  | -42.9 | 39.2 | 32.6 | 32.1 | 33.5 | 33 | 32.7333 |  | 28.9 | 29.6 | 30.5 | 30 | 29.6667 |  |  | CanadaManitobaDAUPHIN A
Canada | Manitoba |  | DELTA MARSH CS | DELTA MARSH CS, MB, Canada | 50.18N | 98.38W | 248 | -6.00 (NAC) | 97-06 | 715630 | -35.1 |  | -43.1 | 37.2 | 31 | 31.4 | 31.5 | 31 | 31.3 |  | 28 | 29.3 | 28.8 | 29 | 28.7 |  |  | CanadaManitobaDELTA MARSH CS
Canada | Manitoba |  | EMERSON AUT | EMERSON AUT, MB, Canada | 49.00N | 97.24W | 242 | -6.00 (NAC) | 96-06 | 715600 | -33.6 |  | -43.3 | 35.3 | 30.8 | 32 | 32.7 | 32 | 31.8333 |  | 28.8 | 30.3 | 30.1 | 30 | 29.7333 |  |  | CanadaManitobaEMERSON AUT
Canada | Manitoba |  | FISHER BRANCH (AUT) | FISHER BRANCH (AUT), MB, Canada | 51.08N | 97.55W | 253 | -6.00 (NAC) | 94-06 | 714420 | -37.8 |  | -45.5 | 37.7 | 31.6 | 30.2 | 32.2 | 31 | 31.3333 |  | 27.9 | 28.9 | 29.1 | 29 | 28.6333 |  |  | CanadaManitobaFISHER BRANCH (AUT)
Canada | Manitoba |  | GEORGE ISLAND (AUT) | GEORGE ISLAND (AUT), MB, Canada | 52.82N | 97.62W | 223 | -6.00 (NAC) | 94-06 | 714450 | N/A |  | N/A | N/A | 23.4 | 25.7 | 25.2 | 25 | 24.7667 |  | 21.1 | 24.2 | 23.8 | 23 | 23.0333 |  |  | CanadaManitobaGEORGE ISLAND (AUT)
Canada | Manitoba |  | GILLAM A | GILLAM A, MB, Canada | 56.36N | 94.71W | 145 | -6.00 (NAC) | 82-06 | 719120 | -40.6 |  | -46.8 | 36.4 | 29.5 | 30.1 | 30.7 | 30 | 30.1 |  | 26.1 | 27.5 | 26.7 | 27 | 26.7667 |  |  | CanadaManitobaGILLAM A
Canada | Manitoba |  | GIMLI INDUSTRIAL PARK | GIMLI INDUSTRIAL PARK, MB, Canada | 50.63N | 97.05W | 230 | -6.00 (NAC) | 82-06 | 718560 | -37.2 |  | -44.6 | 38.5 | 31.6 | 30.4 | 31.6 | 31 | 31.2 |  | 27.6 | 28.5 | 28.8 | 28 | 28.3 |  |  | CanadaManitobaGIMLI INDUSTRIAL PARK
Canada | Manitoba |  | GRAND RAPIDS (AUT) | GRAND RAPIDS (AUT), MB, Canada | 53.19N | 99.27W | 223 | -6.00 (NAC) | 94-06 | 718580 | -40.3 |  | -45.3 | 37.3 | 35.1 | 30.8 | 31.6 | 33 | 32.5 |  | 28.8 | 28.4 | 28.3 | 29 | 28.5 |  |  | CanadaManitobaGRAND RAPIDS (AUT)
Canada | Manitoba |  | GRETNA (AUT) | GRETNA (AUT), MB, Canada | 49.03N | 97.56W | 253 | -6.00 (NAC) | 94-06 | 714410 | -35.1 |  | -45.5 | 36.7 | 33.3 | 31.5 | 32.5 | 32 | 32.4333 |  | 29.6 | 29.6 | 30.1 | 30 | 29.7667 |  |  | CanadaManitobaGRETNA (AUT)
Canada | Manitoba |  | HUNTERS POINT MARINE | HUNTERS POINT MARINE, MB, Canada | 53.03N | 100.93W | 256 | -6.00 (NAC) | 94-05 | 711420 | N/A |  | N/A | N/A | 30 | 29.3 | 30 | 30 | 29.7667 |  | 25.4 | 26.9 | 26.3 | 26 | 26.2 |  |  | CanadaManitobaHUNTERS POINT MARINE
Canada | Manitoba |  | ISLAND LAKE A | ISLAND LAKE A, MB, Canada | 53.85N | 94.65W | 236 | -6.00 (NAC) | 86-06 | 711450 | -40.1 |  | -45.5 | 37 | 30.1 | 30.1 | 30.3 | 30 | 30.1667 |  | 27 | 27.6 | 27.5 | 27 | 27.3667 |  |  | CanadaManitobaISLAND LAKE A
Canada | Manitoba |  | LYNN LAKE A | LYNN LAKE A, MB, Canada | 56.86N | 101.08W | 357 | -6.00 (NAC) | 82-05 | 710780 | -42.9 |  | -48.3 | 36.3 | 28.8 | 30.2 | 30.9 | 30 | 29.9667 |  | 26.3 | 27.7 | 27.2 | 27 | 27.0667 |  |  | CanadaManitobaLYNN LAKE A
Canada | Manitoba |  | MELITA | MELITA, MB, Canada | 49.28N | 100.99W | 446 | -6.00 (NAC) | 94-06 | 714470 | -36.6 |  | -44.3 | 38.5 | 31.7 | 31.7 | 33.2 | 32 | 32.2 |  | 28.4 | 29.9 | 30.7 | 30 | 29.6667 |  |  | CanadaManitobaMELITA
Canada | Manitoba |  | NORWAY HOUSE A | NORWAY HOUSE A, MB, Canada | 53.95N | 97.85W | 224 | -6.00 (NAC) | 82-05 | 711410 | -41.3 |  | -47 | 35.4 | 30.2 | 29.9 | 29.6 | 30 | 29.9 |  | 26.4 | 27.6 | 27.5 | 27 | 27.1667 |  |  | CanadaManitobaNORWAY HOUSE A
Canada | Manitoba |  | OAKPOINT MARINE | OAKPOINT MARINE, MB, Canada | 50.50N | 98.04W | 250 | -6.00 (NAC) | 94-06 | 711440 | -35.5 |  | -42.5 | 34 | 28.9 | 29.2 | 29.8 | 29 | 29.3 |  | 26 | 27.3 | 27.6 | 27 | 26.9667 |  |  | CanadaManitobaOAKPOINT MARINE
Canada | Manitoba |  | PILOT MOUND (AUT) | PILOT MOUND (AUT), MB, Canada | 49.19N | 98.90W | 470 | -6.00 (NAC) | 82-06 | 711480 | -35.2 |  | -40.6 | 37.7 | 30 | 30.2 | 32.7 | 31 | 30.9667 |  | 27.1 | 28.6 | 29.7 | 28 | 28.4667 |  |  | CanadaManitobaPILOT MOUND (AUT)
Canada | Manitoba |  | PINAWA | PINAWA, MB, Canada | 50.18N | 96.06W | 268 | -6.00 (NAC) | 94-06 | 714480 | -38.4 |  | -46.3 | 38.1 | 32.2 | 31.2 | 31.4 | 32 | 31.6 |  | 28.5 | 29 | 29 | 29 | 28.8333 |  |  | CanadaManitobaPINAWA
Canada | Manitoba |  | PORTAGE SOUTHPORT A | PORTAGE SOUTHPORT A, MB, Canada | 49.90N | 98.27W | 270 | -6.00 (NAC) | 82-92 | 718510 | -34.7 |  | -39.6 | 41.6 | 34.9 | 33 | 35.4 | 34 | 34.4333 |  | 30.3 | 31.1 | 31.8 | 31 | 31.0667 |  |  | CanadaManitobaPORTAGE SOUTHPORT A
Canada | Manitoba |  | ROBLIN | ROBLIN, MB, Canada | 51.18N | 101.36W | 540 | -6.00 (NAC) | 96-06 | 715530 | -37.6 |  | -44.5 | 37.3 | 28.9 | 30.9 | 32.5 | 31 | 30.7667 |  | 26.5 | 28.7 | 29.2 | 28 | 28.1333 |  |  | CanadaManitobaROBLIN
Canada | Manitoba |  | SHOAL LAKE CS | SHOAL LAKE CS, MB, Canada | 50.45N | 100.60W | 561 | -6.00 (NAC) | 94-06 | 711500 | -38.1 |  | -45.2 | 37.1 | 29.8 | 30.2 | 31.8 | 31 | 30.6 |  | 27.1 | 28.2 | 28.7 | 28 | 28 |  |  | CanadaManitobaSHOAL LAKE CS
Canada | Manitoba |  | SPRAGUE | SPRAGUE, MB, Canada | 49.02N | 95.60W | 329 | -6.00 (NAC) | 94-06 | 714490 | -37.4 |  | -49.8 | 36.6 | 31.2 | 31.4 | 31.2 | 31 | 31.2667 |  | 27.9 | 29.2 | 28.1 | 28 | 28.4 |  |  | CanadaManitobaSPRAGUE
Canada | Manitoba |  | SWAN RIVER RCS | SWAN RIVER RCS, MB, Canada | 52.12N | 101.23W | 335 | -6.00 (NAC) | 94-06 | 714430 | -36.9 |  | -43.3 | 37.1 | 31.9 | 31.7 | 32.3 | 32 | 31.9667 |  | 28.1 | 29.3 | 29.8 | 29 | 29.0667 |  |  | CanadaManitobaSWAN RIVER RCS
Canada | Manitoba |  | THE PAS A | THE PAS A, MB, Canada | 53.97N | 101.10W | 270 | -6.00 (NAC) | 82-06 | 718670 | -38.7 |  | -43.3 | 37.9 | 30.7 | 31.1 | 31.2 | 31 | 31 |  | 27.1 | 28.4 | 28.5 | 28 | 28 |  |  | CanadaManitobaTHE PAS A
Canada | Manitoba |  | THOMPSON A | THOMPSON A, MB, Canada | 55.80N | 97.86W | 223 | -6.00 (NAC) | 82-06 | 710790 | -43.6 |  | -50.3 | 37.5 | 29.8 | 31 | 30.8 | 31 | 30.5333 |  | 26.8 | 28.1 | 27.9 | 28 | 27.6 |  |  | CanadaManitobaTHOMPSON A
Canada | Manitoba |  | VICTORIA BEACH (AUT) | VICTORIA BEACH (AUT), MB, Canada | 50.70N | 96.57W | 220 | -6.00 (NAC) | 96-06 | 715520 | -33.7 |  | -38.8 | 33.5 | 28.3 | 29.6 | 29.8 | 29 | 29.2333 |  | 25.5 | 27.9 | 27.5 | 27 | 26.9667 |  |  | CanadaManitobaVICTORIA BEACH (AUT)
Canada | Manitoba |  | WASAGAMING | WASAGAMING, MB, Canada | 50.66N | 99.94W | 627 | -6.00 (NAC) | 94-06 | 714440 | -40 |  | -49.3 | 36.8 | 29.7 | 30.1 | 31.6 | 30 | 30.4667 |  | 26.6 | 28.2 | 28.5 | 28 | 27.7667 |  |  | CanadaManitobaWASAGAMING
Canada | Manitoba |  | WILSON CREEK WEIR CS | WILSON CREEK WEIR CS, MB, Canada | 50.71N | 99.53W | 351 | -6.00 (NAC) | 97-06 | 711490 | -33.6 |  | -39.7 | 39 | 30.1 | 31.9 | 33 | 32 | 31.6667 |  | 27.2 | 30 | 30 | 29 | 29.0667 |  |  | CanadaManitobaWILSON CREEK WEIR CS
Canada | Manitoba |  | WINNIPEG RICHARDSON INT'L A | WINNIPEG RICHARDSON INT'L A, MB, Canada | 49.92N | 97.23W | 239 | -6.00 (NAC) | 82-06 | 718520 | -35.4 |  | -41.7 | 40 | 33.3 | 31.9 | 33.6 | 33 | 32.9333 |  | 29.4 | 29.9 | 30.7 | 30 | 30 |  |  | CanadaManitobaWINNIPEG RICHARDSON INT'L A
Canada | New Brunswick |  | BAS CARAQUET | BAS CARAQUET, NB, Canada | 47.80N | 64.83W | 5 | -4.00 (NAA) | 94-06 | 715980 | -24.7 |  | -30.8 | 36.8 | 30.2 | 30.2 | 30.8 | 30 | 30.4 |  | 27 | 27.5 | 27.9 | 27 | 27.4667 |  |  | CanadaNew BrunswickBAS CARAQUET
Canada | New Brunswick |  | CHARLO A | CHARLO A, NB, Canada | 47.98N | 66.33W | 40 | -4.00 (NAA) | 82-03 | 717110 | -28.7 |  | -35.9 | 35.2 | 30.5 | 30.6 | 31 | 31 | 30.7 |  | 27.3 | 28.1 | 27.8 | 28 | 27.7333 |  |  | CanadaNew BrunswickCHARLO A
Canada | New Brunswick |  | FREDERICTON A | FREDERICTON A, NB, Canada | 45.87N | 66.53W | 21 | -4.00 (NAA) | 82-06 | 717000 | -28.1 |  | -36.5 | 36.4 | 32 | 31.5 | 32 | 32 | 31.8333 |  | 28.6 | 29.2 | 29.4 | 29 | 29.0667 |  |  | CanadaNew BrunswickFREDERICTON A
Canada | New Brunswick |  | MIRAMICHI A | MIRAMICHI A, NB, Canada | 47.01N | 65.47W | 33 | -4.00 (NAA) | 82-91 | 717170 | -27.9 |  | -34.2 | 36 | 31.5 | 32.7 | 31 | 32 | 31.7333 |  | 28.6 | 30.3 | 29.2 | 29 | 29.3667 |  |  | CanadaNew BrunswickMIRAMICHI A
Canada | New Brunswick |  | MIRAMICHI RCS | MIRAMICHI RCS, NB, Canada | 47.01N | 65.46W | 33 | -4.00 (NAA) | 98-06 | 717440 | -28.2 |  | -35 | 38.6 | 33 | 32 | 32.9 | 33 | 32.6333 |  | 30.1 | 29.9 | 30.1 | 30 | 30.0333 |  |  | CanadaNew BrunswickMIRAMICHI RCS
Canada | New Brunswick |  | MISCOU ISLAND (AUT) | MISCOU ISLAND (AUT), NB, Canada | 48.01N | 64.49W | 4 | -4.00 (NAA) | 87-06 | 717190 | -24 |  | -29.2 | 34.7 | 28 | 28.2 | 28.7 | 28 | 28.3 |  | 24.7 | 25.8 | 25.8 | 25 | 25.4333 |  |  | CanadaNew BrunswickMISCOU ISLAND (AUT)
Canada | New Brunswick |  | MONCTON A | MONCTON A, NB, Canada | 46.10N | 64.69W | 71 | -4.00 (NAA) | 82-06 | 717050 | -26.4 |  | -34.2 | 35.1 | 29.7 | 30.3 | 30.7 | 30 | 30.2333 |  | 27 | 28.2 | 28.1 | 28 | 27.7667 |  |  | CanadaNew BrunswickMONCTON A
Canada | New Brunswick |  | POINT ESCUMINAC (AUT) | POINT ESCUMINAC (AUT), NB, Canada | 47.07N | 64.80W | 4 | -4.00 (NAA) | 87-01 | 714140 | -24.7 |  | -31 | 36.3 | 30.3 | 29.9 | 30.4 | 30 | 30.2 |  | 26.8 | 26.9 | 26.7 | 27 | 26.8 |  |  | CanadaNew BrunswickPOINT ESCUMINAC (AUT)
Canada | New Brunswick |  | POINT LEPREAU CS | POINT LEPREAU CS, NB, Canada | 45.07N | 66.45W | 6 | -4.00 (NAA) | 94-06 | 716990 | -21.7 |  | -28 | 32.6 | 24.6 | 26.5 | 25.9 | 26 | 25.6667 |  | 21.5 | 23 | 23.4 | 23 | 22.6333 |  |  | CanadaNew BrunswickPOINT LEPREAU CS
Canada | New Brunswick |  | SAINT JOHN A | SAINT JOHN A, NB, Canada | 45.32N | 65.89W | 109 | -4.00 (NAA) | 82-06 | 716090 | -26.4 |  | -34.4 | 33.9 | 27.5 | 27.8 | 28.5 | 28 | 27.9333 |  | 24.7 | 25.8 | 25.8 | 25 | 25.4333 |  |  | CanadaNew BrunswickSAINT JOHN A
Canada | New Brunswick |  | ST LEONARD CS | ST LEONARD CS, NB, Canada | 47.16N | 67.83W | 245 | -4.00 (NAA) | 85-06 | 710190 | -30.4 |  | -35.3 | 35.1 | 30.4 | 30.3 | 30.2 | 30 | 30.3 |  | 27.6 | 28 | 27.4 | 28 | 27.6667 |  |  | CanadaNew BrunswickST LEONARD CS
Canada | New Brunswick |  | ST STEPHEN (AUT) | ST STEPHEN (AUT), NB, Canada | 45.22N | 67.25W | 26 | -4.00 (NAA) | 87-06 | 716070 | -29.4 |  | -37.5 | 37.5 | 31.6 | 31.6 | 31.8 | 32 | 31.6667 |  | 28.7 | 28.9 | 29.4 | 29 | 29 |  |  | CanadaNew BrunswickST STEPHEN (AUT)
Canada | Newfoundland and Labrador |  | ARGENTIA (AUT) | ARGENTIA (AUT), NF, Canada | 47.29N | 53.99W | 15 | -3.50 (NAF) | 87-06 | 718070 | -15.1 |  | -21.9 | 26.9 | 18.3 | 21.2 | 22.4 | 21 | 20.6333 |  | 15.9 | 19 | 20.4 | 18 | 18.4333 |  |  | CanadaNewfoundland and LabradorARGENTIA (AUT)
Canada | Newfoundland and Labrador |  | BADGER (AUT) | BADGER (AUT), NF, Canada | 48.97N | 56.07W | 103 | -3.50 (NAF) | 87-06 | 714000 | -32.7 |  | -41.6 | 36.7 | 29.2 | 30.9 | 30.5 | 30 | 30.2 |  | 26.6 | 28.5 | 27.7 | 28 | 27.6 |  |  | CanadaNewfoundland and LabradorBADGER (AUT)
Canada | Newfoundland and Labrador |  | BONAVISTA | BONAVISTA, NF, Canada | 48.67N | 53.11W | 26 | -3.50 (NAF) | 82-06 | 711960 | -18.2 |  | -26.5 | 29.6 | 22.8 | 25.6 | 25.5 | 25 | 24.6333 |  | 20.3 | 23.5 | 23.8 | 23 | 22.5333 |  |  | CanadaNewfoundland and LabradorBONAVISTA
Canada | Newfoundland and Labrador |  | BURGEO 2 | BURGEO 2, NF, Canada | 47.62N | 57.62W | 11 | -3.50 (NAF) | 82-06 | 711940 | -18.5 |  | -25.8 | 29.3 | 19.5 | 22.2 | 23 | 22 | 21.5667 |  | 16.9 | 20 | 21.4 | 19 | 19.4333 |  |  | CanadaNewfoundland and LabradorBURGEO 2
Canada | Newfoundland and Labrador |  | CAPE KAKKIVIAK | CAPE KAKKIVIAK, NF, Canada | 59.98N | 64.16W | 551 | -4.00 (NAA) | 94-06 | 711760 | N/A |  | N/A | N/A | 17.8 | 20.9 | 20.2 | 20 | 19.6333 |  | 13.6 | 18.5 | 17 | 16 | 16.3667 |  |  | CanadaNewfoundland and LabradorCAPE KAKKIVIAK
Canada | Newfoundland and Labrador |  | CAPE RACE (AUT) | CAPE RACE (AUT), NF, Canada | 46.66N | 53.08W | 27 | -3.50 (NAF) | 94-06 | 718000 | -16.1 |  | -22.8 | 30.8 | 17.7 | 20.5 | 22 | 20 | 20.0667 |  | 14.5 | 18 | 19.7 | 17 | 17.4 |  |  | CanadaNewfoundland and LabradorCAPE RACE (AUT)
Canada | Newfoundland and Labrador |  | CARTWRIGHT | CARTWRIGHT, NF, Canada | 53.71N | 57.04W | 14 | -4.00 (NAA) | 82-06 | 718180 | -30.4 |  | -35.1 | 34.7 | 26.2 | 27.1 | 27.7 | 27 | 27 |  | 22 | 23.9 | 23.9 | 23 | 23.2667 |  |  | CanadaNewfoundland and LabradorCARTWRIGHT
Canada | Newfoundland and Labrador |  | CHURCHILL FALLS | CHURCHILL FALLS, NF, Canada | 53.56N | 64.09W | 440 | -4.00 (NAA) | 82-06 | 711820 | -39.1 |  | -43.4 | 33 | 27.6 | 27 | 27 | 27 | 27.2 |  | 23.4 | 24.5 | 23.7 | 24 | 23.8667 |  |  | CanadaNewfoundland and LabradorCHURCHILL FALLS
Canada | Newfoundland and Labrador |  | COMFORT COVE | COMFORT COVE, NF, Canada | 49.27N | 54.88W | 99 | -3.50 (NAF) | 82-96 | 711930 | -24.5 |  | -31.3 | 32.8 | 26.9 | 28.6 | 27.2 | 28 | 27.5667 |  | 23.5 | 26.1 | 25.7 | 25 | 25.1 |  |  | CanadaNewfoundland and LabradorCOMFORT COVE
Canada | Newfoundland and Labrador |  | CORNER BROOK | CORNER BROOK, NF, Canada | 48.93N | 57.92W | 152 | -3.50 (NAF) | 94-06 | 719730 | -22.9 |  | -31.2 | 33.5 | 26.5 | 28 | 28.3 | 28 | 27.6 |  | 24.1 | 26.2 | 26 | 25 | 25.4333 |  |  | CanadaNewfoundland and LabradorCORNER BROOK
Canada | Newfoundland and Labrador |  | DANIELS HARBOUR | DANIELS HARBOUR, NF, Canada | 50.24N | 57.58W | 19 | -3.50 (NAF) | 82-06 | 711850 | -24 |  | -34.1 | 27.2 | 19.7 | 22.6 | 22.5 | 22 | 21.6 |  | 17.8 | 20.5 | 20.9 | 20 | 19.7333 |  |  | CanadaNewfoundland and LabradorDANIELS HARBOUR
Canada | Newfoundland and Labrador |  | DEER LAKE A | DEER LAKE A, NF, Canada | 49.22N | 57.40W | 22 | -3.50 (NAF) | 82-06 | 718090 | -29.9 |  | -39.2 | 34.2 | 27.4 | 29.1 | 29 | 29 | 28.5 |  | 24.8 | 27.1 | 26.6 | 26 | 26.1667 |  |  | CanadaNewfoundland and LabradorDEER LAKE A
Canada | Newfoundland and Labrador |  | ENGLEE (AUT) | ENGLEE (AUT), NF, Canada | 50.72N | 56.11W | 30 | -3.50 (NAF) | 94-06 | 714170 | -22.7 |  | -29.6 | 30.7 | 22.5 | 25 | 25.4 | 24 | 24.3 |  | 19.9 | 22.7 | 23 | 22 | 21.8667 |  |  | CanadaNewfoundland and LabradorENGLEE (AUT)
Canada | Newfoundland and Labrador |  | FEROLLE POINT (AUT) | FEROLLE POINT (AUT), NF, Canada | 51.02N | 57.10W | 6 | -3.50 (NAF) | 94-06 | 714060 | -25 |  | -33.4 | 25.8 | 16.4 | 19.5 | 20.6 | 19 | 18.8333 |  | 14.5 | 18 | 19.2 | 17 | 17.2333 |  |  | CanadaNewfoundland and LabradorFEROLLE POINT (AUT)
Canada | Newfoundland and Labrador |  | GANDER INT'L A | GANDER INT'L A, NF, Canada | 48.95N | 54.58W | 151 | -3.50 (NAF) | 82-06 | 718030 | -22.2 |  | -30 | 32.6 | 26.5 | 28.4 | 27.5 | 27 | 27.4667 |  | 23.9 | 26.2 | 25.7 | 25 | 25.2667 |  |  | CanadaNewfoundland and LabradorGANDER INT'L A
Canada | Newfoundland and Labrador |  | GOOSE A | GOOSE A, NF, Canada | 53.32N | 60.42W | 49 | -4.00 (NAA) | 82-06 | 718160 | -33.4 |  | -37.5 | 37.7 | 30.9 | 30.4 | 31 | 31 | 30.7667 |  | 26.1 | 27.2 | 27.2 | 27 | 26.8333 |  |  | CanadaNewfoundland and LabradorGOOSE A
Canada | Newfoundland and Labrador |  | GRATES COVE | GRATES COVE, NF, Canada | 48.17N | 52.94W | 46 | -3.50 (NAF) | 94-06 | 713360 | N/A |  | N/A | N/A | 22.1 | 24.2 | 24.7 | 24 | 23.6667 |  | 19.8 | 22.8 | 22.7 | 22 | 21.7667 |  |  | CanadaNewfoundland and LabradorGRATES COVE
Canada | Newfoundland and Labrador |  | HOPEDALE (AUT) | HOPEDALE (AUT), NF, Canada | 55.45N | 60.22W | 12 | -4.00 (NAA) | 82-06 | 719000 | -31.1 |  | -35.7 | 31.9 | 23.6 | 24.5 | 27 | 25 | 25.0333 |  | 19.6 | 21.7 | 22.3 | 21 | 21.2 |  |  | CanadaNewfoundland and LabradorHOPEDALE (AUT)
Canada | Newfoundland and Labrador |  | LA SCIE | LA SCIE, NF, Canada | 49.92N | 55.67W | 194 | -3.50 (NAF) | 92-06 | 713370 | -21.5 |  | -27.7 | 33 | 27.7 | 28.7 | 28.1 | 28 | 28.1667 |  | 24.1 | 25.9 | 25.7 | 25 | 25.2333 |  |  | CanadaNewfoundland and LabradorLA SCIE
Canada | Newfoundland and Labrador |  | MARTICOT ISLAND | MARTICOT ISLAND, NF, Canada | 47.33N | 54.59W | 22 | -3.50 (NAF) | 94-06 | 716920 | N/A |  | N/A | N/A | 17.9 | 20.2 | 21.4 | 20 | 19.8333 |  | 15.2 | 18.1 | 19.7 | 18 | 17.6667 |  |  | CanadaNewfoundland and LabradorMARTICOT ISLAND
Canada | Newfoundland and Labrador |  | POOLS ISLAND | POOLS ISLAND, NF, Canada | 49.11N | 53.58W | 19 | -3.50 (NAF) | 94-06 | 719310 | -19.5 |  | -28 | 32.6 | 25.8 | 26.1 | 27.1 | 26 | 26.3333 |  | 21.5 | 23.8 | 23.7 | 23 | 23 |  |  | CanadaNewfoundland and LabradorPOOLS ISLAND
Canada | Newfoundland and Labrador |  | PORT AUX BASQUES | PORT AUX BASQUES, NF, Canada | 47.57N | 59.15W | 40 | -3.50 (NAF) | 82-06 | 711970 | -17.5 |  | -24.6 | 25.8 | 18.8 | 21.1 | 22.3 | 21 | 20.7333 |  | 17 | 19.5 | 20.7 | 19 | 19.0667 |  |  | CanadaNewfoundland and LabradorPORT AUX BASQUES
Canada | Newfoundland and Labrador |  | SAGLEK | SAGLEK, NF, Canada | 58.33N | 62.59W | 501 | -4.00 (NAA) | 89-06 | 713350 | -33.8 |  | -38.8 | 27.7 | 22.3 | 21.9 | 21.6 | 22 | 21.9333 |  | 16.1 | 19.3 | 18.6 | 18 | 18 |  |  | CanadaNewfoundland and LabradorSAGLEK
Canada | Newfoundland and Labrador |  | SAGONA ISLAND | SAGONA ISLAND, NF, Canada | 47.37N | 55.79W | 60 | -3.50 (NAF) | 94-06 | 714080 | -14.7 |  | -22.6 | 26 | 16.7 | 20.1 | 20.7 | 19 | 19.1667 |  | 14.8 | 18.2 | 19.7 | 18 | 17.5667 |  |  | CanadaNewfoundland and LabradorSAGONA ISLAND
Canada | Newfoundland and Labrador |  | ST ANTHONY | ST ANTHONY, NF, Canada | 51.38N | 56.10W | 29 | -3.50 (NAF) | 82-06 | 715580 | -28 |  | -32.8 | 29.2 | 22.8 | 24.6 | 24.6 | 24 | 24 |  | 19.8 | 22.4 | 22.5 | 22 | 21.5667 |  |  | CanadaNewfoundland and LabradorST ANTHONY
Canada | Newfoundland and Labrador |  | ST JOHN'S A | ST JOHN'S A, NF, Canada | 47.62N | 52.74W | 141 | -3.50 (NAF) | 82-06 | 718010 | -18.4 |  | -25.8 | 31.8 | 24 | 26.6 | 26.7 | 26 | 25.7667 |  | 21.8 | 24.7 | 24.6 | 24 | 23.7 |  |  | CanadaNewfoundland and LabradorST JOHN'S A
Canada | Newfoundland and Labrador |  | ST LAWRENCE | ST LAWRENCE, NF, Canada | 46.92N | 55.38W | 49 | -3.50 (NAF) | 82-06 | 718020 | -17.3 |  | -23.7 | 31 | 22.3 | 24.4 | 24.9 | 24 | 23.8667 |  | 18.7 | 22.2 | 22.9 | 21 | 21.2667 |  |  | CanadaNewfoundland and LabradorST LAWRENCE
Canada | Newfoundland and Labrador |  | STEPHENVILLE A | STEPHENVILLE A, NF, Canada | 48.53N | 58.55W | 26 | -3.50 (NAF) | 82-06 | 718150 | -21.4 |  | -29.6 | 30.5 | 23.3 | 25 | 25 | 24 | 24.4333 |  | 20.4 | 23.2 | 23 | 22 | 22.2 |  |  | CanadaNewfoundland and LabradorSTEPHENVILLE A
Canada | Newfoundland and Labrador |  | TWILLINGATE (AUT) | TWILLINGATE (AUT), NF, Canada | 49.68N | 54.80W | 92 | -3.50 (NAF) | 94-06 | 714020 | -16.6 |  | -23.9 | 32.4 | 25.4 | 26.5 | 26.2 | 26 | 26.0333 |  | 22.4 | 24.4 | 23.8 | 24 | 23.5333 |  |  | CanadaNewfoundland and LabradorTWILLINGATE (AUT)
Canada | Newfoundland and Labrador |  | WABUSH LAKE A | WABUSH LAKE A, NF, Canada | 52.93N | 66.87W | 551 | -4.00 (NAA) | 82-06 | 718250 | -40.1 |  | -46.3 | 33.9 | 28.4 | 27.2 | 26.5 | 27 | 27.3667 |  | 23.9 | 24.4 | 23.6 | 24 | 23.9667 |  |  | CanadaNewfoundland and LabradorWABUSH LAKE A
Canada | Northwest Territories |  | AULAVIK NATIONAL PARK | AULAVIK NATIONAL PARK, NT, Canada | 74.14N | 119.99W | 32 | -7.00 (NAM) | 96-06 | 719740 | -44.4 |  | -47.2 | 25.7 | 15 | 19.9 | 17.9 | 18 | 17.6 |  | 12.2 | 16.8 | 13.8 | 14 | 14.2667 |  |  | CanadaNorthwest TerritoriesAULAVIK NATIONAL PARK
Canada | Northwest Territories |  | CAPE PARRY A | CAPE PARRY A, NT, Canada | 70.17N | 124.72W | 87 | -7.00 (NAM) | 82-06 | 719480 | -39.2 |  | -46.6 | 27.1 | 16.1 | 20 | 17.4 | 18 | 17.8333 |  | 12 | 17 | 14.1 | 14 | 14.3667 |  |  | CanadaNorthwest TerritoriesCAPE PARRY A
Canada | Northwest Territories |  | COLVILLE LAKE | COLVILLE LAKE, NT, Canada | 67.04N | 126.08W | 259 | -7.00 (NAM) | 94-06 | 710550 | -45.6 |  | -50.3 | 32.8 | 26.2 | 28.3 | 24.2 | 26 | 26.2333 |  | 22.8 | 25.4 | 21.9 | 23 | 23.3667 |  |  | CanadaNorthwest TerritoriesCOLVILLE LAKE
Canada | Northwest Territories |  | FORT GOOD HOPE CS | FORT GOOD HOPE CS, NT, Canada | 66.24N | 128.64W | 82 | -7.00 (NAM) | 98-06 | 714910 | N/A |  | N/A | N/A | 31.1 | 32.3 | 27.5 | 30 | 30.3 |  | 28.1 | 28.9 | 25.5 | 28 | 27.5 |  |  | CanadaNorthwest TerritoriesFORT GOOD HOPE CS
Canada | Northwest Territories |  | FORT LIARD | FORT LIARD, NT, Canada | 60.23N | 123.47W | 213 | -7.00 (NAM) | 94-06 | 714970 | -41.6 |  | -50.9 | 36 | 30.5 | 31.8 | 30.2 | 31 | 30.8333 |  | 28 | 28.7 | 27.1 | 28 | 27.9333 |  |  | CanadaNorthwest TerritoriesFORT LIARD
Canada | Northwest Territories |  | FORT PROVIDENCE | FORT PROVIDENCE, NT, Canada | 61.32N | 117.60W | 162 | -7.00 (NAM) | 94-06 | 710870 | -42.7 |  | -47.6 | 35.2 | 30.1 | 31.6 | 29.9 | 31 | 30.5333 |  | 27.6 | 28.6 | 27.2 | 28 | 27.8 |  |  | CanadaNorthwest TerritoriesFORT PROVIDENCE
Canada | Northwest Territories |  | FORT RELIANCE | FORT RELIANCE, NT, Canada | 62.72N | 109.17W | 166 | -6.00 (NAS) | 82-91 | 710730 | -45.7 |  | -51.2 | 35.3 | 23.8 | 27.7 | 25.9 | 26 | 25.8 |  | 20.1 | 24.1 | 22.9 | 22 | 22.3667 |  |  | CanadaNorthwest TerritoriesFORT RELIANCE
Canada | Northwest Territories |  | FORT SIMPSON A | FORT SIMPSON A, NT, Canada | 61.76N | 121.24W | 169 | -7.00 (NAM) | 82-06 | 719460 | -42.8 |  | -49.5 | 36 | 30.2 | 31 | 30.4 | 31 | 30.5333 |  | 27.5 | 28.3 | 27.5 | 28 | 27.7667 |  |  | CanadaNorthwest TerritoriesFORT SIMPSON A
Canada | Northwest Territories |  | FORT SMITH A | FORT SMITH A, NT, Canada | 60.02N | 111.96W | 205 | -7.00 (NAM) | 82-06 | 719340 | -41.9 |  | -48.6 | 35.2 | 29.2 | 31.2 | 30.9 | 30 | 30.4333 |  | 27 | 28.4 | 27.6 | 28 | 27.6667 |  |  | CanadaNorthwest TerritoriesFORT SMITH A
Canada | Northwest Territories |  | HANBURY RIVER | HANBURY RIVER, NT, Canada | 63.60N | 105.13W | 317 | -7.00 (NAM) | 94-06 | 719630 | -42.8 |  | -48.1 | 31.2 | 24.3 | 26.9 | 25 | 25 | 25.4 |  | 21.8 | 24.7 | 21.8 | 23 | 22.7667 |  |  | CanadaNorthwest TerritoriesHANBURY RIVER
Canada | Northwest Territories |  | HAY RIVER A | HAY RIVER A, NT, Canada | 60.84N | 115.78W | 165 | -7.00 (NAM) | 82-06 | 719350 | -40.3 |  | -45.6 | 35.2 | 28.7 | 30.6 | 29 | 29 | 29.4333 |  | 25.5 | 27.4 | 26.5 | 26 | 26.4667 |  |  | CanadaNorthwest TerritoriesHAY RIVER A
Canada | Northwest Territories |  | INNER WHALEBACKS | INNER WHALEBACKS, NT, Canada | 61.92N | 113.73W | 165 | -7.00 (NAM) | 94-06 | 711620 | N/A |  | N/A | N/A | 18.1 | 24 | 20.9 | 21 | 21 |  | 15.1 | 21.3 | 19.1 | 19 | 18.5 |  |  | CanadaNorthwest TerritoriesINNER WHALEBACKS
Canada | Northwest Territories |  | INUVIK A | INUVIK A, NT, Canada | 68.30N | 133.48W | 68 | -7.00 (NAM) | 82-06 | 719570 | -44.2 |  | -52.1 | 33.7 | 27.8 | 28.5 | 27.1 | 28 | 27.8 |  | 25 | 26.5 | 23.3 | 25 | 24.9333 |  |  | CanadaNorthwest TerritoriesINUVIK A
Canada | Northwest Territories |  | LAC LA MARTRE | LAC LA MARTRE, NT, Canada | 63.13N | 117.25W | 271 | -7.00 (NAM) | 95-06 | 711630 | N/A |  | N/A | N/A | 30.9 | 30.4 | 28.1 | 30 | 29.8 |  | 27 | 27.4 | 25.3 | 27 | 26.5667 |  |  | CanadaNorthwest TerritoriesLAC LA MARTRE
Canada | Northwest Territories |  | LINDBURG LANDING | LINDBURG LANDING, NT, Canada | 61.12N | 122.85W | 183 | -7.00 (NAM) | 98-06 | 716820 | -42.9 |  | -49.1 | 35.6 | 30.2 | 30.3 | 29.8 | 30 | 30.1 |  | 27.6 | 28.1 | 26.5 | 27 | 27.4 |  |  | CanadaNorthwest TerritoriesLINDBURG LANDING
Canada | Northwest Territories |  | LITTLE CHICAGO | LITTLE CHICAGO, NT, Canada | 67.18N | 130.23W | 63 | -7.00 (NAM) | 94-06 | 711640 | N/A |  | N/A | N/A | 29.6 | 30.1 | 27.1 | 29 | 28.9333 |  | 27.1 | 27.7 | 24.6 | 26 | 26.4667 |  |  | CanadaNorthwest TerritoriesLITTLE CHICAGO
Canada | Northwest Territories |  | LIVERPOOL BAY | LIVERPOOL BAY, NT, Canada | 69.60N | 130.91W | 102 | -7.00 (NAM) | 94-06 | 719600 | N/A |  | N/A | N/A | 22.9 | 24.8 | 21.4 | 23 | 23.0333 |  | 19.1 | 22 | 18.3 | 20 | 19.8 |  |  | CanadaNorthwest TerritoriesLIVERPOOL BAY
Canada | Northwest Territories |  | MOULD BAY A | MOULD BAY A, NT, Canada | 76.23N | 119.33W | 12 | -7.00 (NAM) | 82-93 | 710720 | -48 |  | -54.2 | 18 | 10 | 13.2 | 8.6 | 11 | 10.6 |  | 7.8 | 11 | 6.7 | 9 | 8.5 |  |  | CanadaNorthwest TerritoriesMOULD BAY A
Canada | Northwest Territories |  | NICHOLSON PENINSULA | NICHOLSON PENINSULA, NT, Canada | 69.93N | 128.97W | 89 | -7.00 (NAM) | 82-93 | 719560 | -41.9 |  | -49 | 29.9 | 21.5 | 24.1 | 20.5 | 22 | 22.0333 |  | 17.8 | 20.8 | 17.3 | 19 | 18.6333 |  |  | CanadaNorthwest TerritoriesNICHOLSON PENINSULA
Canada | Northwest Territories |  | NORMAN WELLS A | NORMAN WELLS A, NT, Canada | 65.28N | 126.80W | 73 | -7.00 (NAM) | 82-06 | 710430 | -44 |  | -48.6 | 35.4 | 29.9 | 30.9 | 28.3 | 30 | 29.7 |  | 27.2 | 27.9 | 25.7 | 27 | 26.9333 |  |  | CanadaNorthwest TerritoriesNORMAN WELLS A
Canada | Northwest Territories |  | PELLY ISLAND | PELLY ISLAND, NT, Canada | 69.63N | 135.44W | 17 | -7.00 (NAM) | 94-06 | 715020 | N/A |  | N/A | N/A | 19.3 | 24.3 | 20.1 | 21 | 21.2333 |  | 14.2 | 20.4 | 17.4 | 17 | 17.3333 |  |  | CanadaNorthwest TerritoriesPELLY ISLAND
Canada | Northwest Territories |  | RAE LAKES | RAE LAKES, NT, Canada | 64.11N | 117.33W | 223 | -7.00 (NAM) | 94-06 | 711650 | -45.1 |  | -51.1 | 34.1 | 28.7 | 28.7 | 26.8 | 28 | 28.0667 |  | 25.1 | 26.5 | 24.1 | 25 | 25.2333 |  |  | CanadaNorthwest TerritoriesRAE LAKES
Canada | Northwest Territories |  | SACHS HARBOUR CLIMATE | SACHS HARBOUR CLIMATE, NT, Canada | 71.99N | 125.25W | 88 | -7.00 (NAM) | 94-06 | 714670 | -41.7 |  | -46.7 | 24 | 15.3 | 18.7 | 15.5 | 17 | 16.5 |  | 12.4 | 16 | 13.3 | 14 | 13.9 |  |  | CanadaNorthwest TerritoriesSACHS HARBOUR CLIMATE
Canada | Northwest Territories |  | TROUT LAKE | TROUT LAKE, NT, Canada | 60.44N | 121.24W | 498 | -7.00 (NAM) | 94-06 | 711660 | N/A |  | N/A | N/A | 28.2 | 28.2 | 28.5 | 28 | 28.3 |  | 25.9 | 26 | 25.1 | 26 | 25.6667 |  |  | CanadaNorthwest TerritoriesTROUT LAKE
Canada | Northwest Territories |  | TUKTOYAKTUK | TUKTOYAKTUK, NT, Canada | 69.43N | 133.02W | 5 | -7.00 (NAM) | 94-06 | 719850 | -41.2 |  | -46 | 32.7 | 24 | 26.6 | 23.1 | 25 | 24.5667 |  | 21 | 24.1 | 19.9 | 22 | 21.6667 |  |  | CanadaNorthwest TerritoriesTUKTOYAKTUK
Canada | Northwest Territories |  | YELLOWKNIFE A | YELLOWKNIFE A, NT, Canada | 62.46N | 114.44W | 206 | -7.00 (NAM) | 82-06 | 719360 | -42.8 |  | -49.8 | 33 | 26.3 | 28.1 | 27.2 | 27 | 27.2 |  | 23.8 | 25.7 | 24.4 | 25 | 24.6333 |  |  | CanadaNorthwest TerritoriesYELLOWKNIFE A
Canada | Northwest Territories |  | YOHIN | YOHIN, NT, Canada | 61.24N | 123.74W | 204 | -7.00 (NAM) | 82-06 | 710200 | -42.6 |  | -47.1 | 34.7 | 27.6 | 30 | 27.6 | 28 | 28.4 |  | 23 | 26.2 | 23.5 | 24 | 24.2333 |  |  | CanadaNorthwest TerritoriesYOHIN
Canada | Nova Scotia |  | AMHERST (AUT) | AMHERST (AUT), NS, Canada | 45.85N | 64.27W | 23 | -4.00 (NAA) | 94-05 | 714100 | -24.2 |  | -32.1 | 32.2 | 26.4 | 27.3 | 27.1 | 27 | 26.9333 |  | 23.6 | 25.3 | 25.3 | 25 | 24.7333 |  |  | CanadaNova ScotiaAMHERST (AUT)
Canada | Nova Scotia |  | BACCARO POINT | BACCARO POINT, NS, Canada | 43.45N | 65.47W | 13 | -4.00 (NAA) | 94-06 | 716910 | -16.5 |  | -21.5 | 25.5 | 21 | 21.3 | 21.4 | 21 | 21.2333 |  | 16.6 | 18.5 | 19.2 | 18 | 18.1 |  |  | CanadaNova ScotiaBACCARO POINT
Canada | Nova Scotia |  | BEAVER ISLAND (AUT) | BEAVER ISLAND (AUT), NS, Canada | 44.82N | 62.33W | 16 | -4.00 (NAA) | 94-06 | 714030 | -17 |  | -23.1 | 25.5 | 18.2 | 20.8 | 21.7 | 20 | 20.2333 |  | 16 | 19.1 | 20.5 | 19 | 18.5333 |  |  | CanadaNova ScotiaBEAVER ISLAND (AUT)
Canada | Nova Scotia |  | BRIER ISLAND | BRIER ISLAND, NS, Canada | 44.29N | 66.35W | 16 | -4.00 (NAA) | 94-06 | 719880 | -15.2 |  | -21.5 | 26.5 | 20.5 | 22.6 | 22.4 | 22 | 21.8333 |  | 18.1 | 20.5 | 20.6 | 20 | 19.7333 |  |  | CanadaNova ScotiaBRIER ISLAND
Canada | Nova Scotia |  | CARIBOU POINT (AUT) | CARIBOU POINT (AUT), NS, Canada | 45.77N | 62.68W | 2 | -4.00 (NAA) | 94-06 | 714150 | -21.8 |  | -29.2 | 35 | 28.2 | 29.5 | 30.1 | 29 | 29.2667 |  | 25.1 | 27.1 | 27.2 | 26 | 26.4667 |  |  | CanadaNova ScotiaCARIBOU POINT (AUT)
Canada | Nova Scotia |  | GRAND ETANG | GRAND ETANG, NS, Canada | 46.55N | 61.05W | 13 | -4.00 (NAA) | 94-06 | 715970 | -18.2 |  | -26.6 | 32.9 | 26.1 | 28.5 | 28.4 | 28 | 27.6667 |  | 24.2 | 26.7 | 26.5 | 26 | 25.8 |  |  | CanadaNova ScotiaGRAND ETANG
Canada | Nova Scotia |  | GREENWOOD A | GREENWOOD A, NS, Canada | 44.98N | 64.92W | 28 | -4.00 (NAA) | 82-06 | 713970 | -23.1 |  | -32.6 | 35.4 | 30.1 | 30.9 | 31 | 31 | 30.6667 |  | 27.3 | 28.8 | 28.7 | 28 | 28.2667 |  |  | CanadaNova ScotiaGREENWOOD A
Canada | Nova Scotia |  | HALIFAX STANFIELD INT'L A | HALIFAX STANFIELD INT'L A, NS, Canada | 44.88N | 63.52W | 145 | -4.00 (NAA) | 82-06 | 713950 | -21.9 |  | -29.2 | 35.3 | 29.4 | 29.3 | 29.7 | 29 | 29.4667 |  | 26 | 27.3 | 27.4 | 27 | 26.9 |  |  | CanadaNova ScotiaHALIFAX STANFIELD INT'L A
Canada | Nova Scotia |  | HART ISLAND (AUT) | HART ISLAND (AUT), NS, Canada | 45.35N | 60.98W | 8 | -4.00 (NAA) | 94-06 | 714190 | -17.3 |  | -25.3 | 30.1 | 22.1 | 24.2 | 24.9 | 24 | 23.7333 |  | 19.8 | 22.2 | 22.8 | 22 | 21.6 |  |  | CanadaNova ScotiaHART ISLAND (AUT)
Canada | Nova Scotia |  | KEJIMKUJIK 1 | KEJIMKUJIK 1, NS, Canada | 44.43N | 65.20W | 165 | -4.00 (NAA) | 94-06 | 715990 | -21.5 |  | -27.3 | 36 | 31 | 30.8 | 31.1 | 31 | 30.9667 |  | 28.1 | 28.8 | 28.5 | 28 | 28.4667 |  |  | CanadaNova ScotiaKEJIMKUJIK 1
Canada | Nova Scotia |  | SABLE ISLAND | SABLE ISLAND, NS, Canada | 43.93N | 60.01W | 5 | -4.00 (NAA) | 82-06 | 716000 | -12 |  | -17 | 26.7 | 17.7 | 21.6 | 23.6 | 21 | 20.9667 |  | 16.4 | 20.2 | 22.2 | 20 | 19.6 |  |  | CanadaNova ScotiaSABLE ISLAND
Canada | Nova Scotia |  | SHEARWATER A | SHEARWATER A, NS, Canada | 44.63N | 63.50W | 51 | -4.00 (NAA) | 82-05 | 716010 | -20.6 |  | -28.1 | 34.1 | 27.7 | 28.3 | 27.7 | 28 | 27.9 |  | 24.2 | 25.7 | 25.7 | 25 | 25.2 |  |  | CanadaNova ScotiaSHEARWATER A
Canada | Nova Scotia |  | SHEARWATER JETTY | SHEARWATER JETTY, NS, Canada | 44.63N | 63.52W | 6 | -4.00 (NAA) | 94-06 | CAN35X | N/A |  | N/A | N/A | 27.2 | 27.6 | 27.5 | 27 | 27.4333 |  | 24 | 25.4 | 25.7 | 25 | 25.0333 |  |  | CanadaNova ScotiaSHEARWATER JETTY
Canada | Nova Scotia |  | ST PAUL ISLAND (AUT) | ST PAUL ISLAND (AUT), NS, Canada | 47.23N | 60.14W | 27 | -4.00 (NAA) | 94-06 | 714180 | -16.6 |  | -26.1 | 29.4 | 21.6 | 23.6 | 25 | 23 | 23.4 |  | 19.1 | 22.1 | 22.9 | 21 | 21.3667 |  |  | CanadaNova ScotiaST PAUL ISLAND (AUT)
Canada | Nova Scotia |  | SYDNEY A | SYDNEY A, NS, Canada | 46.17N | 60.05W | 62 | -4.00 (NAA) | 82-06 | 717070 | -20.9 |  | -29.7 | 34.7 | 28 | 29.3 | 29.7 | 29 | 29 |  | 25.4 | 27.2 | 27.1 | 27 | 26.5667 |  |  | CanadaNova ScotiaSYDNEY A
Canada | Nova Scotia |  | WESTERN HEAD | WESTERN HEAD, NS, Canada | 43.99N | 64.66W | 10 | -4.00 (NAA) | 87-06 | 714110 | -19.4 |  | -27 | 36.1 | 27.3 | 29 | 26.8 | 28 | 27.7 |  | 22.9 | 24.7 | 23.1 | 24 | 23.5667 |  |  | CanadaNova ScotiaWESTERN HEAD
Canada | Nova Scotia |  | YARMOUTH A | YARMOUTH A, NS, Canada | 43.83N | 66.09W | 43 | -4.00 (NAA) | 82-06 | 716030 | -17.1 |  | -23 | 29.2 | 23.1 | 24.8 | 25.1 | 24 | 24.3333 |  | 21 | 22.8 | 23.2 | 22 | 22.3333 |  |  | CanadaNova ScotiaYARMOUTH A
Canada | Nunavut |  | ALERT | ALERT, NU, Canada | 82.52N | 62.28W | 30 | -5.00 (NAE) | 82-06 | 710820 | -44.8 |  | -49.4 | 21.7 | 9.4 | 14.6 | 14.3 | 13 | 12.7667 |  | 6.9 | 12.9 | 10.8 | 10 | 10.2 |  |  | CanadaNunavutALERT
Canada | Nunavut |  | BAKER LAKE A | BAKER LAKE A, NU, Canada | 64.30N | 96.08W | 18 | -6.00 (NAC) | 82-06 | 719260 | -43.7 |  | -49.9 | 33.2 | 23.1 | 26.4 | 24.2 | 25 | 24.5667 |  | 17.1 | 23.6 | 20.3 | 20 | 20.3333 |  |  | CanadaNunavutBAKER LAKE A
Canada | Nunavut |  | BREVOORT ISLAND | BREVOORT ISLAND, NU, Canada | 63.34N | 64.15W | 376 | -5.00 (NAE) | 89-06 | 710970 | -33.5 |  | -40.2 | 22.7 | 10.2 | 18.4 | 16.2 | 15 | 14.9333 |  | 8.2 | 15.6 | 13.5 | 12 | 12.4333 |  |  | CanadaNunavutBREVOORT ISLAND
Canada | Nunavut |  | BYRON BAY A | BYRON BAY A, NU, Canada | 68.75N | 109.07W | 92 | -7.00 (NAM) | 82-93 | 719290 | -43.2 |  | -46.5 | 26.2 | 17.6 | 21.2 | 18.7 | 19 | 19.1667 |  | 14.8 | 18.1 | 16.2 | 16 | 16.3667 |  |  | CanadaNunavutBYRON BAY A
Canada | Nunavut |  | CAMBRIDGE BAY A | CAMBRIDGE BAY A, NU, Canada | 69.11N | 105.14W | 27 | -7.00 (NAM) | 82-06 | 719250 | -44.1 |  | -48.8 | 27.8 | 17.1 | 21.5 | 18.8 | 19 | 19.1333 |  | 13.4 | 18.3 | 15.4 | 16 | 15.7 |  |  | CanadaNunavutCAMBRIDGE BAY A
Canada | Nunavut |  | CAPE DORSET A | CAPE DORSET A, NU, Canada | 64.23N | 76.53W | 50 | -5.00 (NAE) | 82-06 | 719100 | -35.7 |  | -41.3 | 24.2 | 13.7 | 19.1 | 15.8 | 16 | 16.2 |  | 11.2 | 16.7 | 13.6 | 14 | 13.8333 |  |  | CanadaNunavutCAPE DORSET A
Canada | Nunavut |  | CAPE DYER | CAPE DYER, NU, Canada | 66.65N | 61.38W | 725 | -5.00 (NAE) | 82-06 | 710940 | -39.9 |  | -50.7 | 20.8 | 10.9 | 16.2 | 14.1 | 14 | 13.7333 |  | 8.8 | 14 | 11.6 | 11 | 11.4667 |  |  | CanadaNunavutCAPE DYER
Canada | Nunavut |  | CAPE HOOPER | CAPE HOOPER, NU, Canada | 68.47N | 66.82W | 390 | -5.00 (NAE) | 82-06 | 710930 | -37.1 |  | -43.7 | 21 | 11.1 | 17.4 | 14.8 | 14 | 14.4333 |  | 9.4 | 15.2 | 11.8 | 12 | 12.1333 |  |  | CanadaNunavutCAPE HOOPER
Canada | Nunavut |  | CAPE MERCY | CAPE MERCY, NU, Canada | 64.96N | 63.58W | 583 | -5.00 (NAE) | 94-06 | 719750 | N/A |  | N/A | N/A | 11.6 | 17.4 | 14.6 | 15 | 14.5333 |  | 7.7 | 14.1 | 11.3 | 11 | 11.0333 |  |  | CanadaNunavutCAPE MERCY
Canada | Nunavut |  | CAPE PEEL WEST | CAPE PEEL WEST, NU, Canada | 69.04N | 107.82W | 165 | -7.00 (NAM) | 94-06 | 710640 | N/A |  | N/A | N/A | 20 | 22.9 | 21 | 21 | 21.3 |  | 16.5 | 20.4 | 17.7 | 18 | 18.2 |  |  | CanadaNunavutCAPE PEEL WEST
Canada | Nunavut |  | CLINTON POINT | CLINTON POINT, NU, Canada | 69.58N | 120.80W | 101 | -7.00 (NAM) | 82-93 | 710530 | -38.9 |  | -45.1 | 30.4 | 19.6 | 22.9 | 21.3 | 21 | 21.2667 |  | 16.6 | 19.8 | 17.5 | 18 | 17.9667 |  |  | CanadaNunavutCLINTON POINT
Canada | Nunavut |  | CLYDE A | CLYDE A, NU, Canada | 70.49N | 68.52W | 27 | -5.00 (NAE) | 82-06 | 710900 | -42.9 |  | -48.5 | 23 | 10.4 | 17.2 | 14.8 | 14 | 14.1333 |  | 8.1 | 14.5 | 12.1 | 12 | 11.5667 |  |  | CanadaNunavutCLYDE A
Canada | Nunavut |  | CORAL HARBOUR A | CORAL HARBOUR A, NU, Canada | 64.19N | 83.36W | 64 | -5.00 (NAE) | 82-06 | 719150 | -43.4 |  | -49.4 | 28.6 | 17.1 | 24 | 20.2 | 20 | 20.4333 |  | 13.5 | 20.4 | 16.6 | 17 | 16.8333 |  |  | CanadaNunavutCORAL HARBOUR A
Canada | Nunavut |  | CROKER RIVER | CROKER RIVER, NU, Canada | 69.28N | 119.22W | 69 | -7.00 (NAM) | 94-06 | 710590 | -37.9 |  | -42.3 | 31.2 | 24 | 26.1 | 22.7 | 24 | 24.2667 |  | 19.1 | 22.2 | 19.6 | 20 | 20.3 |  |  | CanadaNunavutCROKER RIVER
Canada | Nunavut |  | DEWAR LAKES | DEWAR LAKES, NU, Canada | 68.65N | 71.17W | 527 | -5.00 (NAE) | 82-06 | 710920 | -42.8 |  | -49.6 | 22.6 | 12.2 | 18.4 | 14.3 | 15 | 14.9667 |  | 9.6 | 16.4 | 11.7 | 13 | 12.5667 |  |  | CanadaNunavutDEWAR LAKES
Canada | Nunavut |  | ENNADAI LAKE (AUT) | ENNADAI LAKE (AUT), NU, Canada | 61.13N | 100.88W | 353 | -6.00 (NAC) | 94-06 | 719230 | N/A |  | N/A | N/A | 25.1 | 27.1 | 24.7 | 26 | 25.6333 |  | 22.3 | 25 | 21.7 | 23 | 23 |  |  | CanadaNunavutENNADAI LAKE (AUT)
Canada | Nunavut |  | EUREKA | EUREKA, NU, Canada | 79.98N | 85.93W | 10 | -6.00 (NAC) | 82-06 | 719170 | -49.3 |  | -54 | 21.2 | 12.9 | 15.6 | 11.9 | 13 | 13.4667 |  | 9.8 | 12.6 | 9.6 | 11 | 10.6667 |  |  | CanadaNunavutEUREKA
Canada | Nunavut |  | FOX FIVE | FOX FIVE, NU, Canada | 67.54N | 63.79W | 584 | -5.00 (NAE) | 82-06 | 710960 | -36.4 |  | -42.5 | 21.1 | 11.2 | 17.2 | 15.4 | 15 | 14.6 |  | 9.2 | 15 | 12.4 | 12 | 12.2 |  |  | CanadaNunavutFOX FIVE
Canada | Nunavut |  | GLADMAN POINT A | GLADMAN POINT A, NU, Canada | 68.67N | 97.80W | 14 | -7.00 (NAM) | 82-92 | 719270 | -46.1 |  | -51.9 | 24.7 | 14.9 | 19.6 | 16.7 | 17 | 17.0667 |  | 11.2 | 16.5 | 13.2 | 14 | 13.6333 |  |  | CanadaNunavutGLADMAN POINT A
Canada | Nunavut |  | HALL BEACH A | HALL BEACH A, NU, Canada | 68.78N | 81.24W | 8 | -5.00 (NAE) | 82-06 | 710810 | -45.8 |  | -50.8 | 25.3 | 11.1 | 18.1 | 15.7 | 15 | 14.9667 |  | 8.4 | 15.3 | 12.1 | 12 | 11.9333 |  |  | CanadaNunavutHALL BEACH A
Canada | Nunavut |  | HAT ISLAND | HAT ISLAND, NU, Canada | 68.32N | 100.09W | 36 | -7.00 (NAM) | 94-06 | 710840 | -42.9 |  | -48.8 | 25.6 | 15.3 | 19.8 | 16.9 | 17 | 17.3333 |  | 10.9 | 16.4 | 13.6 | 14 | 13.6333 |  |  | CanadaNunavutHAT ISLAND
Canada | Nunavut |  | IQALUIT A | IQALUIT A, NU, Canada | 63.75N | 68.55W | 34 | -5.00 (NAE) | 82-06 | 719090 | -41.6 |  | -47.8 | 26.9 | 15.2 | 21.2 | 18.3 | 18 | 18.2333 |  | 11.9 | 18 | 15 | 15 | 14.9667 |  |  | CanadaNunavutIQALUIT A
Canada | Nunavut |  | JENNY LIND ISLAND A | JENNY LIND ISLAND A, NU, Canada | 68.65N | 101.73W | 18 | -7.00 (NAM) | 82-92 | 710710 | -43.9 |  | -47.9 | 21.8 | 13.4 | 16.2 | 15.8 | 15 | 15.1333 |  | 10.9 | 14 | 13.2 | 13 | 12.7 |  |  | CanadaNunavutJENNY LIND ISLAND A
Canada | Nunavut |  | KUGLUKTUK A | KUGLUKTUK A, NU, Canada | 67.82N | 115.14W | 23 | -7.00 (NAM) | 82-06 | 719380 | -43.1 |  | -47.6 | 34.6 | 24.3 | 28 | 25.1 | 26 | 25.8 |  | 20.2 | 24 | 21.4 | 22 | 21.8667 |  |  | CanadaNunavutKUGLUKTUK A
Canada | Nunavut |  | LADY FRANKLIN POINT A | LADY FRANKLIN POINT A, NU, Canada | 68.50N | 113.22W | 16 | -7.00 (NAM) | 82-99 | 719370 | -40.8 |  | -46.8 | 23 | 13.9 | 17.5 | 15.8 | 16 | 15.7333 |  | 11.1 | 15.1 | 13.4 | 13 | 13.2 |  |  | CanadaNunavutLADY FRANKLIN POINT A
Canada | Nunavut |  | LONGSTAFF BLUFF | LONGSTAFF BLUFF, NU, Canada | 68.90N | 75.14W | 161 | -5.00 (NAE) | 82-06 | 710910 | -43.6 |  | -48.9 | 23.6 | 13.3 | 18.1 | 14.7 | 15 | 15.3667 |  | 11 | 16.2 | 12.2 | 13 | 13.1333 |  |  | CanadaNunavutLONGSTAFF BLUFF
Canada | Nunavut |  | MACKAR INLET | MACKAR INLET, NU, Canada | 68.30N | 85.67W | 395 | -6.00 (NAC) | 82-92 | 710800 | -45 |  | -50 | 23 | 12.7 | 18.4 | 18.1 | 16 | 16.4 |  | 10.8 | 16.6 | 13.9 | 14 | 13.7667 |  |  | CanadaNunavutMACKAR INLET
Canada | Nunavut |  | PANGNIRTUNG | PANGNIRTUNG, NU, Canada | 66.15N | 65.72W | 23 | -5.00 (NAE) | 94-06 | 718260 | N/A |  | N/A | N/A | 13.7 | 17.9 | 17 | 16 | 16.2 |  | 11.4 | 14.8 | 14 | 13 | 13.4 |  |  | CanadaNunavutPANGNIRTUNG
Canada | Nunavut |  | PELLY BAY | PELLY BAY, NU, Canada | 68.43N | 89.72W | 326 | -6.00 (NAC) | 82-92 | 719190 | -45.5 |  | -50 | 27.2 | 15.1 | 20.3 | 19.1 | 18 | 18.1667 |  | 12.3 | 17.6 | 14.9 | 15 | 14.9333 |  |  | CanadaNunavutPELLY BAY
Canada | Nunavut |  | POND INLET A | POND INLET A, NU, Canada | 72.68N | 77.98W | 55 | -5.00 (NAE) | 82-06 | 710950 | -44.5 |  | -50.1 | 23 | 12.1 | 17.5 | 13.5 | 14 | 14.3667 |  | 9.6 | 14.6 | 11.2 | 12 | 11.8 |  |  | CanadaNunavutPOND INLET A
Canada | Nunavut |  | RANKIN INLET A | RANKIN INLET A, NU, Canada | 62.82N | 92.12W | 29 | -6.00 (NAC) | 82-06 | 710830 | -43 |  | -49.2 | 30.7 | 19.7 | 24.6 | 21.8 | 22 | 22.0333 |  | 15 | 21.7 | 18.7 | 18 | 18.4667 |  |  | CanadaNunavutRANKIN INLET A
Canada | Nunavut |  | RESOLUTE CARS | RESOLUTE CARS, NU, Canada | 74.72N | 94.99W | 66 | -6.00 (NAC) | 82-06 | 719240 | -44.5 |  | -49.5 | 18.9 | 9.5 | 13.8 | 11.7 | 12 | 11.6667 |  | 7.1 | 11.9 | 8.9 | 9 | 9.3 |  |  | CanadaNunavutRESOLUTE CARS
Canada | Nunavut |  | RESOLUTION ISLAND | RESOLUTION ISLAND, NU, Canada | 61.60N | 64.63W | 369 | -5.00 (NAE) | 94-06 | 719720 | N/A |  | N/A | N/A | 10.4 | 19 | 16.2 | 15 | 15.2 |  | 8 | 15.8 | 13.6 | 12 | 12.4667 |  |  | CanadaNunavutRESOLUTION ISLAND
Canada | Nunavut |  | ROBERTSON LAKE (AUT) | ROBERTSON LAKE (AUT), NU, Canada | 65.10N | 102.43W | 244 | -7.00 (NAM) | 94-06 | 714900 | -43.3 |  | -47 | 34.7 | 23.8 | 27.4 | 24.5 | 25 | 25.2333 |  | 19.7 | 24.9 | 20.6 | 22 | 21.7333 |  |  | CanadaNunavutROBERTSON LAKE (AUT)
Canada | Nunavut |  | SHEPHERD BAY A | SHEPHERD BAY A, NU, Canada | 68.82N | 93.43W | 43 | -7.00 (NAM) | 82-06 | 719110 | -49.3 |  | -54.7 | 27.8 | 17.1 | 21.5 | 18.6 | 19 | 19.0667 |  | 12.7 | 19 | 15.4 | 16 | 15.7 |  |  | CanadaNunavutSHEPHERD BAY A
Canada | Ontario |  | ARMSTRONG (AUT) | ARMSTRONG (AUT), ON, Canada | 50.29N | 88.91W | 323 | -5.00 (NAE) | 94-06 | 718410 | N/A |  | N/A | N/A | 29.8 | 31.2 | 30.5 | 31 | 30.5 |  | 27.5 | 28.7 | 27.7 | 28 | 27.9667 |  |  | CanadaOntarioARMSTRONG (AUT)
Canada | Ontario |  | ATIKOKAN (AUT) | ATIKOKAN (AUT), ON, Canada | 48.76N | 91.63W | 389 | -6.00 (NAC) | 94-06 | 717470 | -35.9 |  | -45.7 | 37.6 | 32.1 | 31.6 | 30.7 | 31 | 31.4667 |  | 28.7 | 29 | 28.1 | 29 | 28.6 |  |  | CanadaOntarioATIKOKAN (AUT)
Canada | Ontario |  | BANCROFT AUTO | BANCROFT AUTO, ON, Canada | 45.07N | 77.88W | 331 | -5.00 (NAE) | 95-06 | 712940 | -33.3 |  | -42.3 | 37.6 | 31 | 31.7 | 31.7 | 31 | 31.4667 |  | 28.8 | 29.5 | 28.5 | 29 | 28.9333 |  |  | CanadaOntarioBANCROFT AUTO
Canada | Ontario |  | BEAUSOLEIL | BEAUSOLEIL, ON, Canada | 44.85N | 79.87W | 183 | -5.00 (NAE) | 94-06 | 712720 | -28.1 |  | -40.3 | 37.4 | 31.5 | 31.8 | 32.6 | 32 | 31.9667 |  | 29.1 | 29.7 | 29.1 | 29 | 29.3 |  |  | CanadaOntarioBEAUSOLEIL
Canada | Ontario |  | BELLE RIVER | BELLE RIVER, ON, Canada | 42.30N | 82.70W | 184 | -5.00 (NAE) | 94-05 | 712730 | -16.7 |  | -25.5 | 40.3 | 33.5 | 34.2 | 32.2 | 33 | 33.3 |  | 31.5 | 31.8 | 29.8 | 31 | 31.0333 |  |  | CanadaOntarioBELLE RIVER
Canada | Ontario |  | BIG TROUT LAKE | BIG TROUT LAKE, ON, Canada | 53.83N | 89.87W | 224 | -6.00 (NAC) | 82-91 | 718480 | -40.4 |  | -45.7 | 34.2 | 27.2 | 28.3 | 29.5 | 28 | 28.3333 |  | 24.5 | 26.3 | 26.5 | 26 | 25.7667 |  |  | CanadaOntarioBIG TROUT LAKE
Canada | Ontario |  | BIG TROUT LAKE READAC | BIG TROUT LAKE READAC, ON, Canada | 53.82N | 89.90W | 222 | -6.00 (NAC) | 94-06 | 718440 | -41 |  | -48.8 | 37.2 | 29.6 | 29.6 | 29.3 | 30 | 29.5 |  | 26.5 | 26.9 | 26.7 | 27 | 26.7 |  |  | CanadaOntarioBIG TROUT LAKE READAC
Canada | Ontario |  | BURLINGTON PIERS (AUT) | BURLINGTON PIERS (AUT), ON, Canada | 43.30N | 79.80W | 77 | -5.00 (NAE) | 94-06 | 714370 | -17.4 |  | -25.6 | 36.3 | 31.5 | 32.2 | 32.1 | 32 | 31.9333 |  | 29.6 | 30.4 | 29.1 | 30 | 29.7 |  |  | CanadaOntarioBURLINGTON PIERS (AUT)
Canada | Ontario |  | COBOURG (AUT) | COBOURG (AUT), ON, Canada | 43.95N | 78.17W | 78 | -5.00 (NAE) | 93-06 | 714310 | -22.3 |  | -32.3 | 35.9 | 25.8 | 28.6 | 27.2 | 27 | 27.2 |  | 23.9 | 25.8 | 25.7 | 25 | 25.1333 |  |  | CanadaOntarioCOBOURG (AUT)
Canada | Ontario |  | COLLINGWOOD | COLLINGWOOD, ON, Canada | 44.50N | 80.22W | 180 | -5.00 (NAE) | 94-06 | 712700 | -22.1 |  | -32 | 38 | 32.1 | 32 | 33.3 | 32 | 32.4667 |  | 29.2 | 29.5 | 29.6 | 29 | 29.4333 |  |  | CanadaOntarioCOLLINGWOOD
Canada | Ontario |  | COVE ISLAND (AUT) | COVE ISLAND (AUT), ON, Canada | 45.33N | 81.73W | 181 | -5.00 (NAE) | 94-06 | 714390 | -21 |  | -30.1 | 29.3 | 25.2 | 24.6 | 25.1 | 25 | 24.9667 |  | 22.6 | 23.4 | 23.5 | 23 | 23.1667 |  |  | CanadaOntarioCOVE ISLAND (AUT)
Canada | Ontario |  | EARLTON A | EARLTON A, ON, Canada | 47.70N | 79.85W | 243 | -5.00 (NAE) | 82-91 | 717350 | -36.9 |  | -46.5 | 37.6 | 31.1 | 32.6 | 29.4 | 31 | 31.0333 |  | 27.9 | 29.7 | 27.7 | 28 | 28.4333 |  |  | CanadaOntarioEARLTON A
Canada | Ontario |  | ERIEAU (AUT) | ERIEAU (AUT), ON, Canada | 42.25N | 81.90W | 178 | -5.00 (NAE) | 94-06 | 714650 | -16.9 |  | -24.5 | 34.9 | 27.4 | 28.6 | 27.8 | 28 | 27.9333 |  | 25 | 26.7 | 27 | 26 | 26.2333 |  |  | CanadaOntarioERIEAU (AUT)
Canada | Ontario |  | GERALDTON A | GERALDTON A, ON, Canada | 49.78N | 86.93W | 349 | -5.00 (NAE) | 82-06 | 718340 | -41 |  | -48.5 | 37 | 30 | 30.8 | 30.4 | 30 | 30.4 |  | 27.5 | 28.2 | 27.3 | 28 | 27.6667 |  |  | CanadaOntarioGERALDTON A
Canada | Ontario |  | GODERICH | GODERICH, ON, Canada | 43.77N | 81.72W | 214 | -5.00 (NAE) | 87-06 | 712610 | -20.5 |  | -28.9 | 34.1 | 30.2 | 30 | 30.1 | 30 | 30.1 |  | 28.1 | 28 | 27.5 | 28 | 27.8667 |  |  | CanadaOntarioGODERICH
Canada | Ontario |  | GORE BAY A | GORE BAY A, ON, Canada | 45.88N | 82.57W | 194 | -5.00 (NAE) | 82-05 | 717330 | -29.9 |  | -38.5 | 35.4 | 28.1 | 30.2 | 29.1 | 29 | 29.1333 |  | 25.9 | 27.7 | 26.8 | 27 | 26.8 |  |  | CanadaOntarioGORE BAY A
Canada | Ontario |  | GREAT DUCK ISLAND (AUT) | GREAT DUCK ISLAND (AUT), ON, Canada | 45.63N | 82.95W | 183 | -5.00 (NAE) | 94-06 | 714620 | N/A |  | N/A | N/A | 23.8 | 25.2 | 26.7 | 25 | 25.2333 |  | 22 | 24 | 24.8 | 24 | 23.6 |  |  | CanadaOntarioGREAT DUCK ISLAND (AUT)
Canada | Ontario |  | GRENADIER ISLAND | GRENADIER ISLAND, ON, Canada | 44.42N | 75.85W | 82 | -5.00 (NAE) | 94-06 | 712810 | -25.3 |  | -34.3 | 36.2 | 30.8 | 30.9 | 31.6 | 31 | 31.1 |  | 28.4 | 29.4 | 29.4 | 29 | 29.0667 |  |  | CanadaOntarioGRENADIER ISLAND
Canada | Ontario |  | KAPUSKASING A | KAPUSKASING A, ON, Canada | 49.41N | 82.47W | 227 | -5.00 (NAE) | 82-06 | 718310 | -38 |  | -45.8 | 37.6 | 31.6 | 31.9 | 30.2 | 31 | 31.2333 |  | 28.7 | 29.1 | 27.9 | 29 | 28.5667 |  |  | CanadaOntarioKAPUSKASING A
Canada | Ontario |  | KENORA A | KENORA A, ON, Canada | 49.79N | 94.37W | 410 | -6.00 (NAC) | 82-06 | 718500 | -34.9 |  | -42.2 | 37.8 | 31.7 | 31.3 | 31.4 | 31 | 31.4667 |  | 28.2 | 28.8 | 28.7 | 29 | 28.5667 |  |  | CanadaOntarioKENORA A
Canada | Ontario |  | KILLARNEY (AUT) | KILLARNEY (AUT), ON, Canada | 45.97N | 81.48W | 196 | -5.00 (NAE) | 94-06 | 714600 | -26.5 |  | -34.8 | 33.9 | 26 | 27.3 | 27.8 | 27 | 27.0333 |  | 23.7 | 25.2 | 24.8 | 25 | 24.5667 |  |  | CanadaOntarioKILLARNEY (AUT)
Canada | Ontario |  | LAGOON CITY | LAGOON CITY, ON, Canada | 44.55N | 79.22W | 221 | -5.00 (NAE) | 94-06 | 712820 | -27.8 |  | -37 | 37.2 | 28.9 | 29.7 | 29.2 | 29 | 29.2667 |  | 26.6 | 27.8 | 26.8 | 27 | 27.0667 |  |  | CanadaOntarioLAGOON CITY
Canada | Ontario |  | LANSDOWNE HOUSE (AUT) | LANSDOWNE HOUSE (AUT), ON, Canada | 52.20N | 87.94W | 253 | -5.00 (NAE) | 82-06 | 718460 | -41.1 |  | -48.6 | 39.1 | 30.8 | 30.1 | 29.5 | 30 | 30.1333 |  | 27.5 | 27.3 | 27.2 | 27 | 27.3333 |  |  | CanadaOntarioLANSDOWNE HOUSE (AUT)
Canada | Ontario |  | LONDON INT'L AIRPORT | LONDON INT'L AIRPORT, ON, Canada | 43.03N | 81.15W | 278 | -5.00 (NAE) | 82-06 | 716230 | -22.6 |  | -31.3 | 38.5 | 31.5 | 32.6 | 31.4 | 32 | 31.8333 |  | 29.3 | 30.3 | 29 | 30 | 29.5333 |  |  | CanadaOntarioLONDON INT'L AIRPORT
Canada | Ontario |  | LONG POINT (AUT) | LONG POINT (AUT), ON, Canada | 42.57N | 80.05W | 175 | -5.00 (NAE) | 94-06 | 714640 | N/A |  | N/A | N/A | 27.1 | 27.1 | 27.2 | 27 | 27.1333 |  | 25.2 | 25.8 | 26 | 26 | 25.6667 |  |  | CanadaOntarioLONG POINT (AUT)
Canada | Ontario |  | MOOSONEE A | MOOSONEE A, ON, Canada | 51.29N | 80.61W | 9 | -5.00 (NAE) | 94-06 | 718360 | -38.3 |  | -46.8 | 38.2 | 32.5 | 32 | 30.3 | 32 | 31.6 |  | 29.1 | 28.8 | 28.2 | 29 | 28.7 |  |  | CanadaOntarioMOOSONEE A
Canada | Ontario |  | MOUNT FOREST (AUT) | MOUNT FOREST (AUT), ON, Canada | 43.98N | 80.75W | 415 | -5.00 (NAE) | 94-06 | 716310 | -26.6 |  | -35.2 | 35.1 | 30.4 | 30.3 | 30.1 | 30 | 30.2667 |  | 28.5 | 28.5 | 27.6 | 28 | 28.2 |  |  | CanadaOntarioMOUNT FOREST (AUT)
Canada | Ontario |  | NAGAGAMI (AUT) | NAGAGAMI (AUT), ON, Canada | 49.75N | 84.16W | 264 | -5.00 (NAE) | 94-06 | 718320 | N/A |  | N/A | N/A | 31.6 | 32.7 | 30.9 | 32 | 31.7333 |  | 28.7 | 29.2 | 28.3 | 29 | 28.7333 |  |  | CanadaOntarioNAGAGAMI (AUT)
Canada | Ontario |  | NORTH BAY A | NORTH BAY A, ON, Canada | 46.36N | 79.42W | 370 | -5.00 (NAE) | 82-06 | 717310 | -31.8 |  | -40.3 | 35.9 | 29.3 | 30.5 | 29.1 | 30 | 29.6333 |  | 27.2 | 27.9 | 26.6 | 27 | 27.2333 |  |  | CanadaOntarioNORTH BAY A
Canada | Ontario |  | OTTAWA MACDONALD-CARTIER INT' | OTTAWA MACDONALD-CARTIER INT', ON, Canada | 45.32N | 75.67W | 114 | -5.00 (NAE) | 82-06 | 716280 | -27.3 |  | -35 | 37.9 | 32.3 | 32.7 | 32.2 | 32 | 32.4 |  | 29.9 | 30.5 | 29.6 | 30 | 30 |  |  | CanadaOntarioOTTAWA MACDONALD-CARTIER INT'
Canada | Ontario |  | PEAWANUCK (AUT) | PEAWANUCK (AUT), ON, Canada | 54.98N | 85.43W | 53 | -5.00 (NAE) | 94-06 | 714340 | -40.2 |  | -47.3 | 39.1 | 30.2 | 31 | 31.4 | 31 | 30.8667 |  | 27.1 | 28 | 27.5 | 28 | 27.5333 |  |  | CanadaOntarioPEAWANUCK (AUT)
Canada | Ontario |  | PETAWAWA A | PETAWAWA A, ON, Canada | 45.95N | 77.32W | 130 | -5.00 (NAE) | 82-06 | 716250 | -34.3 |  | -43.4 | 37.8 | 32.1 | 33.1 | 32.2 | 32 | 32.4667 |  | 29.4 | 30.5 | 29.4 | 30 | 29.7667 |  |  | CanadaOntarioPETAWAWA A
Canada | Ontario |  | PETERBOROUGH A | PETERBOROUGH A, ON, Canada | 44.23N | 78.37W | 191 | -5.00 (NAE) | 96-04 | 716290 | -28 |  | -38.7 | 38 | 30.4 | 31.9 | 32 | 31 | 31.4333 |  | 28.7 | 29.6 | 28.6 | 29 | 28.9667 |  |  | CanadaOntarioPETERBOROUGH A
Canada | Ontario |  | PICKLE LAKE (AUT) | PICKLE LAKE (AUT), ON, Canada | 51.45N | 90.22W | 391 | -6.00 (NAC) | 82-06 | 718350 | -38.2 |  | -46.8 | 38.6 | 31.5 | 31.3 | 30.5 | 31 | 31.1 |  | 28 | 28.1 | 27.7 | 28 | 27.9333 |  |  | CanadaOntarioPICKLE LAKE (AUT)
Canada | Ontario |  | POINT PETRE (AUT) | POINT PETRE (AUT), ON, Canada | 43.83N | 77.15W | 79 | -5.00 (NAE) | 93-06 | 714300 | -22.7 |  | -32.5 | 33.6 | 25.4 | 27 | 27.9 | 27 | 26.7667 |  | 23.6 | 25.6 | 26.3 | 25 | 25.1667 |  |  | CanadaOntarioPOINT PETRE (AUT)
Canada | Ontario |  | PORT COLBORNE (AUT) | PORT COLBORNE (AUT), ON, Canada | 42.87N | 79.25W | 184 | -5.00 (NAE) | 94-06 | 714630 | N/A |  | N/A | N/A | 27 | 28 | 27.7 | 28 | 27.5667 |  | 24.8 | 25.6 | 26.1 | 26 | 25.5 |  |  | CanadaOntarioPORT COLBORNE (AUT)
Canada | Ontario |  | PORT WELLER (AUT) | PORT WELLER (AUT), ON, Canada | 43.25N | 79.22W | 79 | -5.00 (NAE) | 93-06 | 714320 | -14.1 |  | -21.2 | 36.9 | 30.3 | 31.5 | 31.8 | 31 | 31.2 |  | 27.8 | 29.3 | 28.9 | 29 | 28.6667 |  |  | CanadaOntarioPORT WELLER (AUT)
Canada | Ontario |  | PUKASKWA (AUT) | PUKASKWA (AUT), ON, Canada | 48.59N | 86.29W | 208 | -5.00 (NAE) | 94-06 | 717500 | -32.1 |  | -43 | 31.5 | 24.6 | 25.7 | 25.1 | 25 | 25.1333 |  | 20.8 | 22.8 | 22.4 | 22 | 22 |  |  | CanadaOntarioPUKASKWA (AUT)
Canada | Ontario |  | RED LAKE A | RED LAKE A, ON, Canada | 51.07N | 93.79W | 386 | -6.00 (NAC) | 82-93 | 718540 | -39.1 |  | -44.7 | 37.6 | 30.5 | 30.8 | 31.1 | 31 | 30.8 |  | 27.4 | 28.3 | 28.9 | 28 | 28.2 |  |  | CanadaOntarioRED LAKE A
Canada | Ontario |  | ROYAL ISLAND (AUT) | ROYAL ISLAND (AUT), ON, Canada | 49.47N | 94.76W | 329 | -6.00 (NAC) | 94-06 | CAN21X | N/A |  | N/A | N/A | 27.8 | 31.3 | 31.2 | 30 | 30.1 |  | 26.2 | 28.9 | 28.6 | 28 | 27.9 |  |  | CanadaOntarioROYAL ISLAND (AUT)
Canada | Ontario |  | SAULT STE MARIE A | SAULT STE MARIE A, ON, Canada | 46.48N | 84.51W | 192 | -5.00 (NAE) | 82-06 | 712600 | -30.2 |  | -40.8 | 36.1 | 29.9 | 31.5 | 29.5 | 30 | 30.3 |  | 27.2 | 28.7 | 27.2 | 28 | 27.7 |  |  | CanadaOntarioSAULT STE MARIE A
Canada | Ontario |  | SIOUX LOOKOUT A | SIOUX LOOKOUT A, ON, Canada | 50.12N | 91.90W | 383 | -6.00 (NAC) | 82-06 | 718420 | -38 |  | -45.4 | 38.3 | 32 | 31.4 | 31.1 | 32 | 31.5 |  | 28.4 | 28.8 | 28.7 | 29 | 28.6333 |  |  | CanadaOntarioSIOUX LOOKOUT A
Canada | Ontario |  | SUDBURY A | SUDBURY A, ON, Canada | 46.62N | 80.80W | 348 | -5.00 (NAE) | 82-06 | 717300 | -31.9 |  | -40.4 | 37.8 | 30.6 | 32.4 | 30.8 | 31 | 31.2667 |  | 28.4 | 29.4 | 28 | 29 | 28.6 |  |  | CanadaOntarioSUDBURY A
Canada | Ontario |  | THUNDER BAY A | THUNDER BAY A, ON, Canada | 48.37N | 89.33W | 199 | -5.00 (NAE) | 82-06 | 717490 | -34.2 |  | -42.8 | 39.3 | 31.3 | 31.5 | 31.2 | 31 | 31.3333 |  | 27.1 | 29.1 | 28.2 | 28 | 28.1333 |  |  | CanadaOntarioTHUNDER BAY A
Canada | Ontario |  | TIMMINS VICTOR POWER A | TIMMINS VICTOR POWER A, ON, Canada | 48.57N | 81.38W | 295 | -5.00 (NAE) | 82-06 | 717390 | -38.4 |  | -46.8 | 38.1 | 31.6 | 32.5 | 30.7 | 32 | 31.6 |  | 28.7 | 29.5 | 27.7 | 29 | 28.6333 |  |  | CanadaOntarioTIMMINS VICTOR POWER A
Canada | Ontario |  | TORONTO BUTTONVILLE A | TORONTO BUTTONVILLE A, ON, Canada | 43.86N | 79.37W | 198 | -5.00 (NAE) | 86-06 | 716390 | -24.3 |  | -34.3 | 39.5 | 33.3 | 34.1 | 33.6 | 34 | 33.6667 |  | 30.7 | 31.9 | 30.6 | 31 | 31.0667 |  |  | CanadaOntarioTORONTO BUTTONVILLE A
Canada | Ontario |  | TORONTO ISLAND A | TORONTO ISLAND A, ON, Canada | 43.63N | 79.40W | 77 | -5.00 (NAE) | 94-06 | 712650 | -20 |  | -27.8 | 37.7 | 30.1 | 31.4 | 30 | 31 | 30.5 |  | 26.8 | 28.7 | 27.7 | 28 | 27.7333 |  |  | CanadaOntarioTORONTO ISLAND A
Canada | Ontario |  | TORONTO LESTER B. PEARSON INT | TORONTO LESTER B. PEARSON INT, ON, Canada | 43.68N | 79.63W | 173 | -5.00 (NAE) | 82-06 | 716240 | -22.2 |  | -30.8 | 38.9 | 32.5 | 34.1 | 33.1 | 33 | 33.2333 |  | 30 | 31.5 | 30.1 | 31 | 30.5333 |  |  | CanadaOntarioTORONTO LESTER B. PEARSON INT
Canada | Ontario |  | TRENTON A | TRENTON A, ON, Canada | 44.12N | 77.53W | 86 | -5.00 (NAE) | 82-06 | 716210 | -25.9 |  | -35.6 | 36.7 | 30 | 31.4 | 30.9 | 31 | 30.7667 |  | 28 | 29.5 | 28.6 | 29 | 28.7 |  |  | CanadaOntarioTRENTON A
Canada | Ontario |  | UPSALA (AUT) | UPSALA (AUT), ON, Canada | 49.03N | 90.47W | 489 | -5.00 (NAE) | 94-06 | 714350 | N/A |  | N/A | N/A | 30.9 | 30.9 | 30.1 | 31 | 30.6333 |  | 28 | 28.4 | 27.1 | 28 | 27.8333 |  |  | CanadaOntarioUPSALA (AUT)
Canada | Ontario |  | WAWA (AUT) | WAWA (AUT), ON, Canada | 47.97N | 84.78W | 287 | -5.00 (NAE) | 94-06 | 717380 | -35.7 |  | -43.6 | 32.8 | 27.3 | 27.5 | 27.1 | 27 | 27.3 |  | 24.8 | 25.3 | 24.6 | 25 | 24.9 |  |  | CanadaOntarioWAWA (AUT)
Canada | Ontario |  | WELCOME ISLAND (AUT) | WELCOME ISLAND (AUT), ON, Canada | 48.37N | 89.12W | 211 | -5.00 (NAE) | 94-06 | 717510 | N/A |  | N/A | N/A | 24.8 | 27.4 | 26.5 | 26 | 26.2333 |  | 22.1 | 24.8 | 24.3 | 24 | 23.7333 |  |  | CanadaOntarioWELCOME ISLAND (AUT)
Canada | Ontario |  | WIARTON A | WIARTON A, ON, Canada | 44.75N | 81.11W | 222 | -5.00 (NAE) | 82-06 | 716330 | -23.8 |  | -33.8 | 34.7 | 29.6 | 30.4 | 30.5 | 30 | 30.1667 |  | 27.4 | 28.3 | 27.7 | 28 | 27.8 |  |  | CanadaOntarioWIARTON A
Canada | Ontario |  | WINDSOR A | WINDSOR A, ON, Canada | 42.28N | 82.96W | 190 | -5.00 (NAE) | 82-06 | 715380 | -19.5 |  | -30.3 | 39.3 | 33.3 | 34.5 | 33.1 | 34 | 33.6333 |  | 31.3 | 32.2 | 30.7 | 31 | 31.4 |  |  | CanadaOntarioWINDSOR A
Canada | Prince Edward Island |  | CHARLOTTETOWN A | CHARLOTTETOWN A, PE, Canada | 46.29N | 63.13W | 49 | -4.00 (NAA) | 82-06 | 717060 | -23.9 |  | -32 | 33.1 | 27.2 | 28.5 | 29 | 28 | 28.2333 |  | 25 | 26.6 | 26.7 | 26 | 26.1 |  |  | CanadaPrince Edward IslandCHARLOTTETOWN A
Canada | Prince Edward Island |  | EAST POINT (AUT) | EAST POINT (AUT), PE, Canada | 46.46N | 61.99W | 8 | -4.00 (NAA) | 94-06 | 714120 | -20.8 |  | -29.3 | 33.7 | 23.9 | 25.8 | 26.7 | 25 | 25.4667 |  | 21.3 | 23.8 | 24.6 | 23 | 23.2333 |  |  | CanadaPrince Edward IslandEAST POINT (AUT)
Canada | Prince Edward Island |  | NORTH CAPE | NORTH CAPE, PE, Canada | 47.06N | 64.00W | 8 | -4.00 (NAA) | 94-06 | 719870 | -20.8 |  | -28 | 34 | 26.1 | 28.3 | 28.5 | 28 | 27.6333 |  | 23.7 | 26 | 25.9 | 25 | 25.2 |  |  | CanadaPrince Edward IslandNORTH CAPE
Canada | Prince Edward Island |  | SUMMERSIDE | SUMMERSIDE, PE, Canada | 46.44N | 63.84W | 12 | -4.00 (NAA) | 82-06 | 717020 | -23.1 |  | -30.3 | 33.3 | 27.2 | 28.3 | 29 | 28 | 28.1667 |  | 24.8 | 26.7 | 26.6 | 26 | 26.0333 |  |  | CanadaPrince Edward IslandSUMMERSIDE
Canada | Quebec |  | AMQUI | AMQUI, QC, Canada | 48.47N | 67.43W | 166 | -5.00 (NAE) | 95-06 | 713860 | -31.6 |  | -37 | 35.8 | 31.4 | 29.5 | 30.7 | 31 | 30.5333 |  | 27.6 | 27.7 | 27.7 | 28 | 27.6667 |  |  | CanadaQuebecAMQUI
Canada | Quebec |  | BAGOTVILLE A | BAGOTVILLE A, QC, Canada | 48.33N | 71.00W | 159 | -5.00 (NAE) | 82-06 | 717270 | -33.5 |  | -39.8 | 37.6 | 32.1 | 31.7 | 30.2 | 31 | 31.3333 |  | 28.8 | 29.1 | 27.8 | 29 | 28.5667 |  |  | CanadaQuebecBAGOTVILLE A
Canada | Quebec |  | BAIE-COMEAU | BAIE-COMEAU, QC, Canada | 49.26N | 68.15W | 130 | -5.00 (NAE) | 97-06 | 718290 | -28.5 |  | -32.8 | 32 | 27.8 | 26.7 | 26.7 | 27 | 27.0667 |  | 24.8 | 24.8 | 24.7 | 25 | 24.7667 |  |  | CanadaQuebecBAIE-COMEAU
Canada | Quebec |  | BAIE-COMEAU A | BAIE-COMEAU A, QC, Canada | 49.13N | 68.20W | 22 | -5.00 (NAE) | 82-04 | 711870 | -32.1 |  | -38.8 | 32.4 | 25.2 | 26 | 26 | 26 | 25.7333 |  | 22.5 | 23.9 | 23.4 | 23 | 23.2667 |  |  | CanadaQuebecBAIE-COMEAU A
Canada | Quebec |  | BARRAGE TEMISCAMINGUE | BARRAGE TEMISCAMINGUE, QC, Canada | 46.71N | 79.10W | 181 | -5.00 (NAE) | 97-06 | 717320 | -28.9 |  | -35.2 | 37.4 | 30.7 | 32.6 | 31.8 | 32 | 31.7 |  | 28.8 | 29.9 | 28.9 | 29 | 29.2 |  |  | CanadaQuebecBARRAGE TEMISCAMINGUE
Canada | Quebec |  | BEAUCEVILLE | BEAUCEVILLE, QC, Canada | 46.20N | 70.78W | 229 | -5.00 (NAE) | 94-06 | 713230 | -31.7 |  | -41.9 | 35.8 | 31.2 | 30.4 | 29.7 | 30 | 30.4333 |  | 28.7 | 28.3 | 27.5 | 28 | 28.1667 |  |  | CanadaQuebecBEAUCEVILLE
Canada | Quebec |  | BLANC-SABLON A | BLANC-SABLON A, QC, Canada | 51.45N | 57.18W | 37 | -4.00 (NAA) | 82-06 | 718080 | -29 |  | -35.1 | 27 | 19.5 | 21.2 | 20.7 | 20 | 20.4667 |  | 16.3 | 18.6 | 18.7 | 18 | 17.8667 |  |  | CanadaQuebecBLANC-SABLON A
Canada | Quebec |  | BONNARD 1 | BONNARD 1, QC, Canada | 50.73N | 71.01W | 498 | -5.00 (NAE) | 94-06 | 713830 | -41.1 |  | -47.4 | 33.5 | 28.5 | 28.9 | 27.1 | 28 | 28.1667 |  | 25.7 | 25.7 | 24.8 | 25 | 25.4 |  |  | CanadaQuebecBONNARD 1
Canada | Quebec |  | CAP-CHAT | CAP-CHAT, QC, Canada | 49.11N | 66.65W | 5 | -5.00 (NAE) | 96-06 | 714280 | -24.3 |  | -30.3 | 33.1 | 25.2 | 24.6 | 24.6 | 25 | 24.8 |  | 21.2 | 22.5 | 22.1 | 22 | 21.9333 |  |  | CanadaQuebecCAP-CHAT
Canada | Quebec |  | CAP-D'ESPOIR | CAP-D'ESPOIR, QC, Canada | 48.42N | 64.32W | 15 | -5.00 (NAE) | 94-06 | 714290 | -24.3 |  | -28.9 | 30.9 | 21.6 | 23 | 23.7 | 23 | 22.7667 |  | 19.3 | 21.1 | 21.7 | 21 | 20.7 |  |  | CanadaQuebecCAP-D'ESPOIR
Canada | Quebec |  | CAP-MADELEINE | CAP-MADELEINE, QC, Canada | 49.25N | 65.32W | 29 | -5.00 (NAE) | 94-06 | 714250 | -23.7 |  | -28.6 | 34.4 | 25.4 | 26.6 | 25.6 | 26 | 25.8667 |  | 22.2 | 23.6 | 23.4 | 23 | 23.0667 |  |  | CanadaQuebecCAP-MADELEINE
Canada | Quebec |  | CAP-ROUGE | CAP-ROUGE, QC, Canada | 48.37N | 70.54W | 7 | -5.00 (NAE) | 94-06 | 711860 | -29.6 |  | -34.9 | 35.2 | 30.2 | 28.9 | 28.9 | 29 | 29.3333 |  | 27.2 | 26.7 | 26.5 | 27 | 26.8 |  |  | CanadaQuebecCAP-ROUGE
Canada | Quebec |  | CAP-TOURMENTE | CAP-TOURMENTE, QC, Canada | 47.08N | 70.78W | 6 | -5.00 (NAE) | 94-06 | 713840 | -28.1 |  | -35 | 36.3 | 30.5 | 30.6 | 30.3 | 30 | 30.4667 |  | 28.1 | 28.5 | 28.2 | 28 | 28.2667 |  |  | CanadaQuebecCAP-TOURMENTE
Canada | Quebec |  | CHARLEVOIX (MRC) | CHARLEVOIX (MRC), QC, Canada | 47.28N | 70.64W | 723 | -5.00 (NAE) | 97-06 | 713190 | N/A |  | N/A | N/A | 27.3 | 26.1 | 25.4 | 26 | 26.2667 |  | 24.6 | 23.8 | 23.3 | 24 | 23.9 |  |  | CanadaQuebecCHARLEVOIX (MRC)
Canada | Quebec |  | CHEVERY | CHEVERY, QC, Canada | 50.46N | 59.64W | 8 | -4.00 (NAA) | 94-06 | 718140 | -31.4 |  | -40.3 | 30.8 | 22 | 23.7 | 24.1 | 23 | 23.2667 |  | 18.1 | 19.9 | 20.9 | 20 | 19.6333 |  |  | CanadaQuebecCHEVERY
Canada | Quebec |  | CHIBOUGAMAU CHAPAIS A | CHIBOUGAMAU CHAPAIS A, QC, Canada | 49.77N | 74.53W | 387 | -5.00 (NAE) | 82-06 | 718220 | -39.4 |  | -45.2 | 34.3 | 30.7 | 30.3 | 27.9 | 30 | 29.6333 |  | 27.3 | 28.3 | 25.6 | 27 | 27.0667 |  |  | CanadaQuebecCHIBOUGAMAU CHAPAIS A
Canada | Quebec |  | CHUTE-DES-PASSES | CHUTE-DES-PASSES, QC, Canada | 49.84N | 71.17W | 398 | -5.00 (NAE) | 94-06 | 715220 | -35.9 |  | -43 | 35.9 | 30.3 | 28.7 | 28.4 | 29 | 29.1333 |  | 27.4 | 26.5 | 25.7 | 27 | 26.5333 |  |  | CanadaQuebecCHUTE-DES-PASSES
Canada | Quebec |  | DESCHAMBAULT | DESCHAMBAULT, QC, Canada | 46.69N | 71.97W | 61 | -5.00 (NAE) | 97-06 | 713890 | -33 |  | -40.5 | 36.1 | 31.5 | 30.7 | 29.8 | 31 | 30.6667 |  | 28.7 | 28.6 | 28 | 28 | 28.4333 |  |  | CanadaQuebecDESCHAMBAULT
Canada | Quebec |  | FRELIGHSBURG | FRELIGHSBURG, QC, Canada | 45.05N | 72.86W | 152 | -5.00 (NAE) | 94-06 | 713730 | -28 |  | -40 | 35.9 | 31.5 | 31 | 30.7 | 31 | 31.0667 |  | 29.2 | 29.2 | 28.6 | 29 | 29 |  |  | CanadaQuebecFRELIGHSBURG
Canada | Quebec |  | GASPE A | GASPE A, QC, Canada | 48.78N | 64.48W | 34 | -5.00 (NAE) | 82-06 | 711880 | -29.2 |  | -35 | 37.2 | 29.8 | 30.6 | 30 | 30 | 30.1333 |  | 26.2 | 27.6 | 27.1 | 27 | 26.9667 |  |  | CanadaQuebecGASPE A
Canada | Quebec |  | HAVRE-SAINT-PIERRE A | HAVRE-SAINT-PIERRE A, QC, Canada | 50.28N | 63.60W | 38 | -5.00 (NAE) | 94-06 | 713130 | -31.3 |  | -37.4 | 29.4 | 23.5 | 24.9 | 24.7 | 24 | 24.3667 |  | 21.2 | 22.9 | 22.4 | 22 | 22.1667 |  |  | CanadaQuebecHAVRE-SAINT-PIERRE A
Canada | Quebec |  | HEATH POINT | HEATH POINT, QC, Canada | 49.09N | 61.70W | 7 | -5.00 (NAE) | 94-06 | 714230 | -22.7 |  | -30.1 | 28.2 | 19.9 | 20.8 | 21.1 | 21 | 20.6 |  | 15.9 | 18.5 | 19.2 | 18 | 17.8667 |  |  | CanadaQuebecHEATH POINT
Canada | Quebec |  | ILE AUX PERROQUETS | ILE AUX PERROQUETS, QC, Canada | 50.22N | 64.21W | 9 | -5.00 (NAE) | 94-06 | 713750 | -24.4 |  | -30.2 | 25.2 | 16.7 | 18.7 | 18.1 | 18 | 17.8333 |  | 14.8 | 17.2 | 16.4 | 16 | 16.1333 |  |  | CanadaQuebecILE AUX PERROQUETS
Canada | Quebec |  | ILE ROUGE | ILE ROUGE, QC, Canada | 48.07N | 69.56W | 6 | -5.00 (NAE) | 94-06 | 714260 | -23.7 |  | -28.5 | 28 | 19.3 | 19.7 | 20 | 20 | 19.6667 |  | 16.9 | 17.9 | 17.8 | 18 | 17.5333 |  |  | CanadaQuebecILE ROUGE
Canada | Quebec |  | ILES DE LA MADELEINE | ILES DE LA MADELEINE, QC, Canada | 47.43N | 61.77W | 8 | -4.00 (NAA) | 93-06 | 717100 | -19.5 |  | -26.8 | 30.9 | 23.6 | 25 | 27.1 | 25 | 25.2333 |  | 21 | 23.5 | 24.2 | 23 | 22.9 |  |  | CanadaQuebecILES DE LA MADELEINE
Canada | Quebec |  | INUKJUAK A | INUKJUAK A, QC, Canada | 58.47N | 78.08W | 25 | -5.00 (NAE) | 82-06 | 719070 | -39.4 |  | -44 | 31.4 | 21.9 | 24.4 | 22.6 | 23 | 22.9667 |  | 18.1 | 21.2 | 18.6 | 19 | 19.3 |  |  | CanadaQuebecINUKJUAK A
Canada | Quebec |  | JONQUIERE | JONQUIERE, QC, Canada | 48.42N | 71.15W | 128 | -5.00 (NAE) | 94-06 | 716170 | -33.2 |  | -39.6 | 37.3 | 32.2 | 30.2 | 30.1 | 31 | 30.8333 |  | 29.2 | 28.3 | 27.7 | 28 | 28.4 |  |  | CanadaQuebecJONQUIERE
Canada | Quebec |  | KUUJJUAQ A | KUUJJUAQ A, QC, Canada | 58.10N | 68.42W | 39 | -5.00 (NAE) | 82-06 | 719060 | -40 |  | -45.6 | 33.9 | 26 | 27.1 | 26.3 | 26 | 26.4667 |  | 21.8 | 24.2 | 22.6 | 23 | 22.8667 |  |  | CanadaQuebecKUUJJUAQ A
Canada | Quebec |  | KUUJJUARAPIK A | KUUJJUARAPIK A, QC, Canada | 55.28N | 77.75W | 10 | -5.00 (NAE) | 82-06 | 719050 | -41.5 |  | -47.2 | 36.1 | 28.2 | 28.5 | 27.7 | 28 | 28.1333 |  | 23.4 | 24.6 | 24.1 | 24 | 24.0333 |  |  | CanadaQuebecKUUJJUARAPIK A
Canada | Quebec |  | LA BAIE | LA BAIE, QC, Canada | 48.30N | 70.92W | 152 | -5.00 (NAE) | 97-06 | 713880 | -34.5 |  | -38.9 | 37.8 | 32.2 | 30.7 | 30.1 | 31 | 31 |  | 29.1 | 28.3 | 27.8 | 28 | 28.4 |  |  | CanadaQuebecLA BAIE
Canada | Quebec |  | LA GRANDE IV A | LA GRANDE IV A, QC, Canada | 53.76N | 73.68W | 306 | -5.00 (NAE) | 85-05 | 718230 | -44.7 |  | -52.3 | 34.8 | 30.2 | 29.4 | 28 | 29 | 29.2 |  | 25.2 | 27 | 24.8 | 26 | 25.6667 |  |  | CanadaQuebecLA GRANDE IV A
Canada | Quebec |  | LA GRANDE RIVIERE A | LA GRANDE RIVIERE A, QC, Canada | 53.63N | 77.70W | 195 | -5.00 (NAE) | 82-06 | 718270 | -38.1 |  | -43.5 | 36.2 | 29.9 | 29.6 | 28.1 | 29 | 29.2 |  | 26.2 | 26.8 | 25.1 | 26 | 26.0333 |  |  | CanadaQuebecLA GRANDE RIVIERE A
Canada | Quebec |  | LA POCATIERE | LA POCATIERE, QC, Canada | 47.36N | 70.03W | 31 | -5.00 (NAE) | 96-06 | 717130 | -26.8 |  | -33.3 | 35.4 | 30.1 | 30 | 30.2 | 30 | 30.1 |  | 27.8 | 27.9 | 28 | 28 | 27.9 |  |  | CanadaQuebecLA POCATIERE
Canada | Quebec |  | LA TUQUE | LA TUQUE, QC, Canada | 47.41N | 72.79W | 169 | -5.00 (NAE) | 94-06 | 713780 | -35.3 |  | -42.9 | 39.4 | 33.5 | 32.3 | 31.4 | 32 | 32.4 |  | 30.7 | 29.4 | 28.8 | 30 | 29.6333 |  |  | CanadaQuebecLA TUQUE
Canada | Quebec |  | LAC BENOIT | LAC BENOIT, QC, Canada | 51.53N | 71.11W | 549 | -5.00 (NAE) | 94-06 | 715200 | -46.4 |  | -53.1 | 33.9 | 28.2 | 29.3 | 27.9 | 28 | 28.4667 |  | 25.3 | 26.2 | 25.1 | 26 | 25.5333 |  |  | CanadaQuebecLAC BENOIT
Canada | Quebec |  | LAC EON | LAC EON, QC, Canada | 51.87N | 63.28W | 589 | -5.00 (NAE) | 94-06 | 714210 | N/A |  | N/A | N/A | 28.4 | 32.7 | 28.4 | 30 | 29.8333 |  | 23.9 | 27.2 | 26.1 | 26 | 25.7333 |  |  | CanadaQuebecLAC EON
Canada | Quebec |  | LAC SAINT-PIERRE | LAC SAINT-PIERRE, QC, Canada | 46.18N | 72.92W | 16 | -5.00 (NAE) | 94-06 | 711980 | N/A |  | N/A | N/A | 29.5 | 29.6 | 28.7 | 29 | 29.2667 |  | 27.2 | 27.4 | 26.9 | 27 | 27.1667 |  |  | CanadaQuebecLAC SAINT-PIERRE
Canada | Quebec |  | L'ACADIE | L'ACADIE, QC, Canada | 45.29N | 73.35W | 44 | -5.00 (NAE) | 94-06 | 713720 | -26.9 |  | -36.5 | 36.9 | 32.5 | 31.4 | 31.1 | 32 | 31.6667 |  | 30.2 | 29.4 | 29.1 | 30 | 29.5667 |  |  | CanadaQuebecL'ACADIE
Canada | Quebec |  | L'ASSOMPTION | L'ASSOMPTION, QC, Canada | 45.81N | 73.43W | 21 | -5.00 (NAE) | 94-06 | 715240 | -29.8 |  | -40.2 | 37.1 | 32.3 | 31.7 | 31.6 | 32 | 31.8667 |  | 30.1 | 29.7 | 29.5 | 30 | 29.7667 |  |  | CanadaQuebecL'ASSOMPTION
Canada | Quebec |  | LENNOXVILLE | LENNOXVILLE, QC, Canada | 45.37N | 71.82W | 181 | -5.00 (NAE) | 96-06 | 716110 | -31.1 |  | -41.7 | 35.5 | 31.8 | 30.9 | 30.7 | 31 | 31.1333 |  | 29.1 | 28.9 | 28.6 | 29 | 28.8667 |  |  | CanadaQuebecLENNOXVILLE
Canada | Quebec |  | L'ETAPE | L'ETAPE, QC, Canada | 47.56N | 71.23W | 791 | -5.00 (NAE) | 94-06 | 713820 | -38.2 |  | -47 | 34 | 27.8 | 26.8 | 25.5 | 27 | 26.7 |  | 25.3 | 24.2 | 23.6 | 24 | 24.3667 |  |  | CanadaQuebecL'ETAPE
Canada | Quebec |  | LONGUE-POINTE-DE-MINGAN | LONGUE-POINTE-DE-MINGAN, QC, Canada | 50.27N | 64.23W | 11 | -5.00 (NAE) | 94-06 | 715120 | -31.7 |  | -38.6 | 33.6 | 22 | 23.3 | 22.9 | 23 | 22.7333 |  | 19.3 | 21.4 | 20.4 | 20 | 20.3667 |  |  | CanadaQuebecLONGUE-POINTE-DE-MINGAN
Canada | Quebec |  | MANIWAKI AIRPORT | MANIWAKI AIRPORT, QC, Canada | 46.27N | 75.99W | 200 | -5.00 (NAE) | 94-06 | 717210 | -31.6 |  | -39.8 | 37.9 | 32.6 | 32.2 | 31.4 | 32 | 32.0667 |  | 29.8 | 29.4 | 28.8 | 29 | 29.3333 |  |  | CanadaQuebecMANIWAKI AIRPORT
Canada | Quebec |  | MANIWAKI UA | MANIWAKI UA, QC, Canada | 46.30N | 76.01W | 192 | -5.00 (NAE) | 82-92 | 717220 | -35.2 |  | -42.7 | 37.2 | 31 | 32 | 29.2 | 31 | 30.7333 |  | 28.2 | 29.4 | 27.5 | 28 | 28.3667 |  |  | CanadaQuebecMANIWAKI UA
Canada | Quebec |  | MANOUANE EST | MANOUANE EST, QC, Canada | 50.66N | 70.53W | 497 | -5.00 (NAE) | 94-06 | 715210 | N/A |  | N/A | N/A | 28.2 | 28.4 | 27.6 | 28 | 28.0667 |  | 25.4 | 25.9 | 25 | 25 | 25.4333 |  |  | CanadaQuebecMANOUANE EST
Canada | Quebec |  | MATAGAMI A | MATAGAMI A, QC, Canada | 49.77N | 77.80W | 280 | -5.00 (NAE) | 94-06 | 718210 | -39.5 |  | -46.7 | 37.9 | 32.3 | 32.7 | 29.2 | 31 | 31.4 |  | 29.2 | 28.3 | 27.2 | 28 | 28.2333 |  |  | CanadaQuebecMATAGAMI A
Canada | Quebec |  | MCTAVISH | MCTAVISH, QC, Canada | 45.50N | 73.58W | 73 | -5.00 (NAE) | 94-06 | 716120 | -24.4 |  | -32.6 | 36.5 | 32 | 31.5 | 31.7 | 32 | 31.7333 |  | 29.6 | 29.6 | 29.4 | 30 | 29.5333 |  |  | CanadaQuebecMCTAVISH
Canada | Quebec |  | MISTOOK | MISTOOK, QC, Canada | 48.60N | 71.72W | 113 | -5.00 (NAE) | 94-06 | 713810 | -36.4 |  | -43.3 | 37.5 | 31.9 | 30.9 | 29.6 | 31 | 30.8 |  | 29.3 | 28.4 | 27.6 | 28 | 28.4333 |  |  | CanadaQuebecMISTOOK
Canada | Quebec |  | MONT-JOLI A | MONT-JOLI A, QC, Canada | 48.60N | 68.22W | 52 | -5.00 (NAE) | 82-06 | 717180 | -26.9 |  | -33.7 | 35.7 | 28.6 | 29 | 28.3 | 29 | 28.6333 |  | 25.6 | 26.7 | 25.9 | 26 | 26.0667 |  |  | CanadaQuebecMONT-JOLI A
Canada | Quebec |  | MONT-ORFORD | MONT-ORFORD, QC, Canada | 45.31N | 72.24W | 846 | -5.00 (NAE) | 94-06 | 716180 | -30 |  | -38.4 | 33.1 | 27.9 | 26.7 | 26.3 | 27 | 26.9667 |  | 25.1 | 24.4 | 24.1 | 25 | 24.5333 |  |  | CanadaQuebecMONT-ORFORD
Canada | Quebec |  | MONTREAL/MIRABEL INT'L A | MONTREAL/MIRABEL INT'L A, QC, Canada | 45.67N | 74.03W | 82 | -5.00 (NAE) | 82-06 | 716260 | -30.2 |  | -38.6 | 35.8 | 31.1 | 31.2 | 30.7 | 31 | 31 |  | 28.8 | 29.2 | 28.6 | 29 | 28.8667 |  |  | CanadaQuebecMONTREAL/MIRABEL INT'L A
Canada | Quebec |  | MONTREAL/PIERRE ELLIOTT TRUDE | MONTREAL/PIERRE ELLIOTT TRUDE, QC, Canada | 45.47N | 73.75W | 36 | -5.00 (NAE) | 82-06 | 716270 | -26.5 |  | -34.2 | 36.3 | 31.5 | 31.8 | 31.5 | 32 | 31.6 |  | 29.2 | 29.9 | 29.2 | 29 | 29.4333 |  |  | CanadaQuebecMONTREAL/PIERRE ELLIOTT TRUDE
Canada | Quebec |  | MONTREAL/ST-HUBERT A | MONTREAL/ST-HUBERT A, QC, Canada | 45.52N | 73.42W | 27 | -5.00 (NAE) | 82-04 | 713710 | -28 |  | -35.4 | 36.6 | 31.7 | 32.2 | 31.5 | 32 | 31.8 |  | 29.4 | 30 | 29.3 | 30 | 29.5667 |  |  | CanadaQuebecMONTREAL/ST-HUBERT A
Canada | Quebec |  | MONTREAL-EST | MONTREAL-EST, QC, Canada | 45.63N | 73.55W | 50 | -5.00 (NAE) | 94-06 | 716750 | -25.2 |  | -33.4 | 36.4 | 32.1 | 31.8 | 31.8 | 32 | 31.9 |  | 30.2 | 29.9 | 29.7 | 30 | 29.9333 |  |  | CanadaQuebecMONTREAL-EST
Canada | Quebec |  | NATASHQUAN A | NATASHQUAN A, QC, Canada | 50.18N | 61.82W | 11 | -5.00 (NAE) | 82-06 | 718130 | -31.6 |  | -39.5 | 29 | 21.9 | 23.7 | 23.4 | 23 | 23 |  | 19.1 | 21.6 | 21 | 21 | 20.5667 |  |  | CanadaQuebecNATASHQUAN A
Canada | Quebec |  | NEW CARLISLE 1 | NEW CARLISLE 1, QC, Canada | 48.01N | 65.33W | 46 | -5.00 (NAE) | 94-06 | 716190 | -24.8 |  | -29.6 | 35.2 | 28.1 | 28.2 | 29.3 | 29 | 28.5333 |  | 25.4 | 26 | 26 | 26 | 25.8 |  |  | CanadaQuebecNEW CARLISLE 1
Canada | Quebec |  | NICOLET | NICOLET, QC, Canada | 46.23N | 72.66W | 8 | -5.00 (NAE) | 94-06 | 717230 | -29.7 |  | -38.3 | 34.7 | 30.7 | 30.4 | 29.6 | 30 | 30.2333 |  | 28.6 | 28.6 | 27.4 | 28 | 28.2 |  |  | CanadaQuebecNICOLET
Canada | Quebec |  | NORMANDIN | NORMANDIN, QC, Canada | 48.84N | 72.55W | 137 | -5.00 (NAE) | 94-06 | 713790 | -37.9 |  | -44.4 | 39 | 32.4 | 30.8 | 29.8 | 31 | 31 |  | 28.7 | 28.2 | 27.6 | 28 | 28.1667 |  |  | CanadaQuebecNORMANDIN
Canada | Quebec |  | ONATCHIWAY | ONATCHIWAY, QC, Canada | 48.89N | 71.03W | 304 | -5.00 (NAE) | 97-06 | 713870 | -37.7 |  | -45.7 | 37.2 | 31.8 | 29.9 | 28.2 | 30 | 29.9667 |  | 28.7 | 27.8 | 26.3 | 28 | 27.6 |  |  | CanadaQuebecONATCHIWAY
Canada | Quebec |  | PARENT | PARENT, QC, Canada | 47.92N | 74.62W | 445 | -5.00 (NAE) | 94-06 | 717260 | -38.7 |  | -48.6 | 35.8 | 30.8 | 30.4 | 28.5 | 30 | 29.9 |  | 28.3 | 27.6 | 26.5 | 27 | 27.4667 |  |  | CanadaQuebecPARENT
Canada | Quebec |  | POINTE CLAVEAU | POINTE CLAVEAU, QC, Canada | 48.26N | 70.11W | 4 | -5.00 (NAE) | 94-06 | 711890 | -27.9 |  | -33.8 | 34.3 | 28.9 | 28.4 | 28.3 | 29 | 28.5333 |  | 26 | 25.9 | 25.4 | 26 | 25.7667 |  |  | CanadaQuebecPOINTE CLAVEAU
Canada | Quebec |  | POINTE NOIRE CS | POINTE NOIRE CS, QC, Canada | 50.16N | 66.43W | 24 | -5.00 (NAE) | 97-06 | 713900 | -26 |  | -30.7 | 31.8 | 27.1 | 26.9 | 26.4 | 27 | 26.8 |  | 23.6 | 24.5 | 23.5 | 24 | 23.8667 |  |  | CanadaQuebecPOINTE NOIRE CS
Canada | Quebec |  | POINTE-AU-PERE (INRS) | POINTE-AU-PERE (INRS), QC, Canada | 48.51N | 68.47W | 5 | -5.00 (NAE) | 96-06 | 715540 | -24.7 |  | -29.9 | 33.9 | 25.7 | 25.7 | 24.7 | 25 | 25.3667 |  | 22.8 | 22.7 | 22.2 | 23 | 22.5667 |  |  | CanadaQuebecPOINTE-AU-PERE (INRS)
Canada | Quebec |  | POINTE-DES-MONTS | POINTE-DES-MONTS, QC, Canada | 49.32N | 67.38W | 6 | -5.00 (NAE) | 94-06 | 714270 | -26.6 |  | -31.3 | 31.5 | 21 | 21.8 | 21 | 21 | 21.2667 |  | 18 | 19.9 | 18.7 | 19 | 18.8667 |  |  | CanadaQuebecPOINTE-DES-MONTS
Canada | Quebec |  | PORT-MENIER | PORT-MENIER, QC, Canada | 49.84N | 64.29W | 55 | -5.00 (NAE) | 94-06 | 718100 | N/A |  | N/A | N/A | 24.4 | 26.1 | 25.8 | 25 | 25.4333 |  | 21.9 | 24 | 23.3 | 23 | 23.0667 |  |  | CanadaQuebecPORT-MENIER
Canada | Quebec |  | QUEBEC/JEAN LESAGE INTL A | QUEBEC/JEAN LESAGE INTL A, QC, Canada | 46.80N | 71.38W | 74 | -5.00 (NAE) | 82-06 | 717080 | -29.7 |  | -36.6 | 35.6 | 30.9 | 31.2 | 29.7 | 31 | 30.6 |  | 28.2 | 28.9 | 27.9 | 28 | 28.3333 |  |  | CanadaQuebecQUEBEC/JEAN LESAGE INTL A
Canada | Quebec |  | RIVIERE-DU-LOUP | RIVIERE-DU-LOUP, QC, Canada | 47.81N | 69.55W | 147 | -5.00 (NAE) | 94-06 | 717150 | -27.1 |  | -32 | 33.4 | 28.5 | 28.4 | 27.8 | 28 | 28.2333 |  | 25.5 | 26.1 | 25.6 | 26 | 25.7333 |  |  | CanadaQuebecRIVIERE-DU-LOUP
Canada | Quebec |  | ROBERVAL A | ROBERVAL A, QC, Canada | 48.52N | 72.27W | 179 | -5.00 (NAE) | 82-06 | 717280 | -33.6 |  | -40.5 | 37.6 | 31.4 | 31.2 | 29.5 | 31 | 30.7 |  | 28.2 | 28.5 | 27.6 | 28 | 28.1 |  |  | CanadaQuebecROBERVAL A
Canada | Quebec |  | ROUYN | ROUYN, QC, Canada | 48.25N | 79.03W | 318 | -5.00 (NAE) | 94-06 | 717340 | -34 |  | -41.3 | 38.4 | 31 | 32.4 | 30 | 31 | 31.1333 |  | 28.4 | 29 | 27.2 | 28 | 28.2 |  |  | CanadaQuebecROUYN
Canada | Quebec |  | ROUYN A | ROUYN A, QC, Canada | 48.22N | 78.83W | 301 | -5.00 (NAE) | 82-06 | 717400 | -37.6 |  | -44.7 | 37.4 | 31.1 | 32.2 | 29.7 | 31 | 31 |  | 28.4 | 29.3 | 27.4 | 28 | 28.3667 |  |  | CanadaQuebecROUYN A
Canada | Quebec |  | SCHEFFERVILLE A | SCHEFFERVILLE A, QC, Canada | 54.80N | 66.82W | 522 | -5.00 (NAE) | 82-06 | 718280 | -41.6 |  | -48.5 | 32.9 | 27.3 | 26 | 25.7 | 26 | 26.3333 |  | 22.4 | 23.3 | 22.6 | 23 | 22.7667 |  |  | CanadaQuebecSCHEFFERVILLE A
Canada | Quebec |  | SEPT-ILES A | SEPT-ILES A, QC, Canada | 50.22N | 66.27W | 55 | -5.00 (NAE) | 82-06 | 718110 | -32 |  | -37.6 | 33 | 24 | 25.2 | 25 | 25 | 24.7333 |  | 21.3 | 22.8 | 22.4 | 22 | 22.1667 |  |  | CanadaQuebecSEPT-ILES A
Canada | Quebec |  | SHERBROOKE A | SHERBROOKE A, QC, Canada | 45.43N | 71.68W | 241 | -5.00 (NAE) | 82-04 | 716100 | -33.3 |  | -42.4 | 34.8 | 30.2 | 30.9 | 29.7 | 30 | 30.2667 |  | 27.9 | 28.6 | 27.6 | 28 | 28.0333 |  |  | CanadaQuebecSHERBROOKE A
Canada | Quebec |  | ST-ANICET 1 | ST-ANICET 1, QC, Canada | 45.12N | 74.29W | 49 | -5.00 (NAE) | 94-06 | 717120 | -29.2 |  | -39.4 | 36.3 | 32.2 | 31.2 | 31.4 | 32 | 31.6 |  | 29.9 | 29.7 | 29.3 | 30 | 29.6333 |  |  | CanadaQuebecST-ANICET 1
Canada | Quebec |  | STE AGATHE DES MONTS | STE AGATHE DES MONTS, QC, Canada | 46.05N | 74.28W | 395 | -5.00 (NAE) | 82-92 | 717200 | -32.3 |  | -36.1 | 34.2 | 29.2 | 30.1 | 27.6 | 29 | 28.9667 |  | 27 | 27.9 | 26.2 | 27 | 27.0333 |  |  | CanadaQuebecSTE AGATHE DES MONTS
Canada | Quebec |  | STE-ANNE-DE-BELLEVUE 1 | STE-ANNE-DE-BELLEVUE 1, QC, Canada | 45.43N | 73.93W | 39 | -5.00 (NAE) | 94-06 | 713770 | -27.4 |  | -34.9 | 36.3 | 31.7 | 31.3 | 31.6 | 32 | 31.5333 |  | 29.7 | 29.4 | 29.3 | 29 | 29.4667 |  |  | CanadaQuebecSTE-ANNE-DE-BELLEVUE 1
Canada | Quebec |  | STE-CLOTHILDE | STE-CLOTHILDE, QC, Canada | 45.17N | 73.68W | 53 | -5.00 (NAE) | 94-06 | 716140 | -29.8 |  | -40.4 | 37.2 | 32.4 | 32 | 32.2 | 32 | 32.2 |  | 30.2 | 29.8 | 29.8 | 30 | 29.9333 |  |  | CanadaQuebecSTE-CLOTHILDE
Canada | Quebec |  | STE-FOY (U. LAVAL) | STE-FOY (U. LAVAL), QC, Canada | 46.78N | 71.29W | 91 | -5.00 (NAE) | 97-06 | 713920 | N/A |  | N/A | N/A | 31.9 | 30.9 | 30.6 | 31 | 31.1333 |  | 28.8 | 28.7 | 28.4 | 29 | 28.6333 |  |  | CanadaQuebecSTE-FOY (U. LAVAL)
Canada | Quebec |  | ST-JOVITE | ST-JOVITE, QC, Canada | 46.08N | 74.56W | 239 | -5.00 (NAE) | 94-06 | 713760 | -35.5 |  | -43.9 | 37.6 | 31.7 | 31.1 | 30.4 | 31 | 31.0667 |  | 29 | 28.7 | 28.3 | 29 | 28.6667 |  |  | CanadaQuebecST-JOVITE
Canada | Quebec |  | TROIS-RIVIERES | TROIS-RIVIERES, QC, Canada | 46.35N | 72.52W | 6 | -5.00 (NAE) | 94-06 | 717240 | -26.7 |  | -36.1 | 35.9 | 28.5 | 29.4 | 28.7 | 29 | 28.8667 |  | 26.4 | 27.5 | 27.2 | 27 | 27.0333 |  |  | CanadaQuebecTROIS-RIVIERES
Canada | Quebec |  | VAL-D'OR A | VAL-D'OR A, QC, Canada | 48.06N | 77.79W | 337 | -5.00 (NAE) | 82-06 | 717250 | -37 |  | -43.8 | 36.4 | 30.8 | 31.6 | 29.3 | 31 | 30.5667 |  | 28.2 | 28.7 | 27.1 | 28 | 28 |  |  | CanadaQuebecVAL-D'OR A
Canada | Quebec |  | VARENNES | VARENNES, QC, Canada | 45.72N | 73.38W | 18 | -5.00 (NAE) | 94-06 | 711840 | -27.6 |  | -38 | 36.6 | 32.5 | 31.6 | 31.2 | 32 | 31.7667 |  | 30.4 | 29.5 | 29.3 | 30 | 29.7333 |  |  | CanadaQuebecVARENNES
Canada | Saskatchewan |  | ASSINIBOIA AIRPORT | ASSINIBOIA AIRPORT, SK, Canada | 49.73N | 105.93W | 726 | -6.00 (NAS) | 94-06 | 714870 | -33.8 |  | -42.9 | 39.9 | 31.7 | 34.2 | 35.2 | 34 | 33.7 |  | 28.5 | 31.6 | 32.9 | 31 | 31 |  |  | CanadaSaskatchewanASSINIBOIA AIRPORT
Canada | Saskatchewan |  | BROADVIEW | BROADVIEW, SK, Canada | 50.37N | 102.57W | 600 | -6.00 (NAS) | 82-06 | 718610 | -37.1 |  | -46.4 | 38.6 | 31.8 | 32.2 | 33.2 | 32 | 32.4 |  | 28.2 | 29.5 | 30.2 | 29 | 29.3 |  |  | CanadaSaskatchewanBROADVIEW
Canada | Saskatchewan |  | COLLINS BAY | COLLINS BAY, SK, Canada | 58.18N | 103.70W | 492 | -6.00 (NAS) | 82-06 | 710750 | -40.4 |  | -47.1 | 34.1 | 26.9 | 28.1 | 28.2 | 28 | 27.7333 |  | 24.3 | 25.6 | 24.9 | 25 | 24.9333 |  |  | CanadaSaskatchewanCOLLINS BAY
Canada | Saskatchewan |  | CORONACH SPC | CORONACH SPC, SK, Canada | 49.05N | 105.48W | 756 | -6.00 (NAS) | 96-06 | 715160 | -34.5 |  | -41.9 | 40 | 32.3 | 34.9 | 35.5 | 34 | 34.2333 |  | 28.5 | 32.8 | 33.2 | 32 | 31.5 |  |  | CanadaSaskatchewanCORONACH SPC
Canada | Saskatchewan |  | CREE LAKE | CREE LAKE, SK, Canada | 57.35N | 107.13W | 495 | -6.00 (NAS) | 82-96 | 719200 | -44.7 |  | -52.7 | 35.6 | 26.5 | 29.2 | 30.6 | 29 | 28.7667 |  | 24.1 | 26.6 | 27.4 | 26 | 26.0333 |  |  | CanadaSaskatchewanCREE LAKE
Canada | Saskatchewan |  | CYPRESS HILLS PARK | CYPRESS HILLS PARK, SK, Canada | 49.65N | 109.52W | 1271 | -6.00 (NAS) | 94-06 | 711390 | -31.5 |  | -43.2 | 35 | 26.9 | 30 | 30.9 | 29 | 29.2667 |  | 23.9 | 28.1 | 28.7 | 27 | 26.9 |  |  | CanadaSaskatchewanCYPRESS HILLS PARK
Canada | Saskatchewan |  | EASTEND CYPRESS (AUT) | EASTEND CYPRESS (AUT), SK, Canada | 49.43N | 108.98W | 1080 | -6.00 (NAS) | 94-06 | 711310 | -32.1 |  | -40.3 | 36.7 | 28.6 | 31.9 | 32.7 | 31 | 31.0667 |  | 25.6 | 30.2 | 30.9 | 29 | 28.9 |  |  | CanadaSaskatchewanEASTEND CYPRESS (AUT)
Canada | Saskatchewan |  | ELBOW CS | ELBOW CS, SK, Canada | 51.13N | 106.58W | 595 | -6.00 (NAS) | 94-06 | 714500 | -34.9 |  | -40.9 | 42.4 | 31.9 | 34.4 | 35.9 | 34 | 34.0667 |  | 28.5 | 31.6 | 32.5 | 31 | 30.8667 |  |  | CanadaSaskatchewanELBOW CS
Canada | Saskatchewan |  | ESTEVAN A | ESTEVAN A, SK, Canada | 49.22N | 102.97W | 581 | -6.00 (NAS) | 82-06 | 718620 | -35.6 |  | -45.4 | 41.1 | 34 | 34.5 | 35.2 | 35 | 34.5667 |  | 30.2 | 31.3 | 32.3 | 31 | 31.2667 |  |  | CanadaSaskatchewanESTEVAN A
Canada | Saskatchewan |  | HUDSON BAY | HUDSON BAY, SK, Canada | 52.82N | 102.32W | 358 | -6.00 (NAS) | 89-06 | 718680 | -39.6 |  | -44.6 | 37.5 | 30.7 | 31.3 | 31.9 | 31 | 31.3 |  | 27.2 | 28.8 | 29.1 | 28 | 28.3667 |  |  | CanadaSaskatchewanHUDSON BAY
Canada | Saskatchewan |  | INDIAN HEAD CDA | INDIAN HEAD CDA, SK, Canada | 50.55N | 103.65W | 579 | -6.00 (NAS) | 95-06 | 715150 | -37.8 |  | -45.4 | 38.8 | 31.2 | 31 | 33.2 | 32 | 31.8 |  | 27.7 | 29 | 30.9 | 29 | 29.2 |  |  | CanadaSaskatchewanINDIAN HEAD CDA
Canada | Saskatchewan |  | KEY LAKE A | KEY LAKE A, SK, Canada | 57.25N | 105.60W | 510 | -6.00 (NAS) | 94-06 | 714880 | -47.5 |  | -52.2 | 35.7 | 28.5 | 29.4 | 29.4 | 29 | 29.1 |  | 26.1 | 27.2 | 26.2 | 27 | 26.5 |  |  | CanadaSaskatchewanKEY LAKE A
Canada | Saskatchewan |  | KINDERSLEY A | KINDERSLEY A, SK, Canada | 51.52N | 109.18W | 694 | -6.00 (NAS) | 84-06 | 711290 | -36.1 |  | -46 | 39.7 | 32.4 | 33.3 | 34 | 33 | 33.2333 |  | 28.7 | 30.6 | 31.3 | 30 | 30.2 |  |  | CanadaSaskatchewanKINDERSLEY A
Canada | Saskatchewan |  | LA RONGE A | LA RONGE A, SK, Canada | 55.15N | 105.27W | 379 | -6.00 (NAS) | 82-06 | 719220 | -40.5 |  | -48.9 | 37.1 | 28.8 | 30.2 | 31.2 | 30 | 30.0667 |  | 26.1 | 27.9 | 28 | 27 | 27.3333 |  |  | CanadaSaskatchewanLA RONGE A
Canada | Saskatchewan |  | LAST MOUNTAIN CS | LAST MOUNTAIN CS, SK, Canada | 51.42N | 105.25W | 497 | -6.00 (NAS) | 96-06 | 715560 | -37.8 |  | -45.1 | 37.8 | 30.1 | 32.1 | 33.2 | 32 | 31.8 |  | 27 | 29.9 | 30.6 | 29 | 29.1667 |  |  | CanadaSaskatchewanLAST MOUNTAIN CS
Canada | Saskatchewan |  | LEADER AIRPORT | LEADER AIRPORT, SK, Canada | 50.90N | 109.50W | 676 | -6.00 (NAS) | 94-06 | 714590 | -35.6 |  | -45 | 40.2 | 31.3 | 35.1 | 35.2 | 34 | 33.8667 |  | 28.4 | 32.6 | 33.1 | 31 | 31.3667 |  |  | CanadaSaskatchewanLEADER AIRPORT
Canada | Saskatchewan |  | LUCKY LAKE | LUCKY LAKE, SK, Canada | 50.95N | 107.15W | 665 | -6.00 (NAS) | 94-06 | 714550 | -34 |  | -42.2 | 37.2 | 31 | 33 | 33.8 | 33 | 32.6 |  | 27.6 | 30.4 | 31.5 | 30 | 29.8333 |  |  | CanadaSaskatchewanLUCKY LAKE
Canada | Saskatchewan |  | MAPLE CREEK | MAPLE CREEK, SK, Canada | 49.90N | 109.47W | 767 | -6.00 (NAS) | 94-06 | 714530 | -35.2 |  | -44.1 | 38.2 | 30.5 | 33.9 | 34.4 | 33 | 32.9333 |  | 27.5 | 32.1 | 32.1 | 31 | 30.5667 |  |  | CanadaSaskatchewanMAPLE CREEK
Canada | Saskatchewan |  | MEADOW LAKE A | MEADOW LAKE A, SK, Canada | 54.13N | 108.52W | 480 | -6.00 (NAS) | 82-06 | 711250 | -41.8 |  | -52.7 | 38.2 | 29.4 | 30.7 | 31.4 | 31 | 30.5 |  | 26.5 | 27.9 | 28.5 | 28 | 27.6333 |  |  | CanadaSaskatchewanMEADOW LAKE A
Canada | Saskatchewan |  | MELFORT | MELFORT, SK, Canada | 52.82N | 104.60W | 490 | -6.00 (NAS) | 94-06 | 714560 | -37.2 |  | -45 | 38.6 | 31.4 | 30.6 | 32.6 | 32 | 31.5333 |  | 27.4 | 28.1 | 29.7 | 28 | 28.4 |  |  | CanadaSaskatchewanMELFORT
Canada | Saskatchewan |  | MOOSE JAW A | MOOSE JAW A, SK, Canada | 50.33N | 105.55W | 577 | -6.00 (NAS) | 82-97 | 718640 | -36.4 |  | -46.2 | 41.7 | 35.2 | 34.3 | 35 | 35 | 34.8333 |  | 31.1 | 31.6 | 32.5 | 32 | 31.7333 |  |  | CanadaSaskatchewanMOOSE JAW A
Canada | Saskatchewan |  | MOOSE JAW CS | MOOSE JAW CS, SK, Canada | 50.33N | 105.56W | 577 | -6.00 (NAS) | 98-06 | 715390 | -34.3 |  | -44.9 | 41.5 | 32.4 | 34 | 36 | 34 | 34.1333 |  | 28.4 | 31.4 | 32.8 | 31 | 30.8667 |  |  | CanadaSaskatchewanMOOSE JAW CS
Canada | Saskatchewan |  | NIPAWIN A | NIPAWIN A, SK, Canada | 53.33N | 104.00W | 372 | -6.00 (NAS) | 82-94 | 711300 | -39 |  | -46.7 | 39.6 | 31.8 | 31.1 | 31.8 | 32 | 31.5667 |  | 28 | 28 | 29.2 | 28 | 28.4 |  |  | CanadaSaskatchewanNIPAWIN A
Canada | Saskatchewan |  | NORTH BATTLEFORD A | NORTH BATTLEFORD A, SK, Canada | 52.77N | 108.26W | 548 | -6.00 (NAS) | 82-05 | 718760 | -38.4 |  | -48.2 | 40.5 | 31.5 | 32.2 | 33.2 | 32 | 32.3 |  | 27.7 | 28.9 | 30 | 29 | 28.8667 |  |  | CanadaSaskatchewanNORTH BATTLEFORD A
Canada | Saskatchewan |  | OUTLOOK PFRA | OUTLOOK PFRA, SK, Canada | 51.48N | 107.05W | 541 | -6.00 (NAS) | 96-06 | 715510 | -33.9 |  | -42.6 | 39.7 | 31.5 | 33.9 | 34.8 | 33 | 33.4 |  | 27.7 | 30.7 | 31.6 | 30 | 30 |  |  | CanadaSaskatchewanOUTLOOK PFRA
Canada | Saskatchewan |  | PRINCE ALBERT A | PRINCE ALBERT A, SK, Canada | 53.22N | 105.67W | 428 | -6.00 (NAS) | 82-06 | 718690 | -39.7 |  | -49.3 | 39.3 | 31.3 | 31.1 | 32.2 | 32 | 31.5333 |  | 27.5 | 28.4 | 29.4 | 28 | 28.4333 |  |  | CanadaSaskatchewanPRINCE ALBERT A
Canada | Saskatchewan |  | REGINA A | REGINA A, SK, Canada | 50.43N | 104.67W | 577 | -6.00 (NAS) | 82-06 | 718630 | -37.3 |  | -45.4 | 40.4 | 33.4 | 33.4 | 34 | 34 | 33.6 |  | 29.9 | 30.5 | 31.5 | 31 | 30.6333 |  |  | CanadaSaskatchewanREGINA A
Canada | Saskatchewan |  | ROCKGLEN (AUT) | ROCKGLEN (AUT), SK, Canada | 49.17N | 105.98W | 917 | -6.00 (NAS) | 94-06 | 711350 | -34.1 |  | -43.5 | 38.7 | 29.9 | 33.1 | 34.5 | 33 | 32.5 |  | 26.7 | 30.7 | 31.9 | 30 | 29.7667 |  |  | CanadaSaskatchewanROCKGLEN (AUT)
Canada | Saskatchewan |  | ROSETOWN EAST | ROSETOWN EAST, SK, Canada | 51.57N | 107.92W | 586 | -6.00 (NAS) | 94-06 | 715100 | -37.4 |  | -46.7 | 40.3 | 31.2 | 33.6 | 34.2 | 33 | 33 |  | 27.9 | 30.5 | 31.4 | 30 | 29.9333 |  |  | CanadaSaskatchewanROSETOWN EAST
Canada | Saskatchewan |  | SASKATOON DIEFENBAKER INT'L A | SASKATOON DIEFENBAKER INT'L A, SK, Canada | 52.17N | 106.72W | 504 | -6.00 (NAS) | 82-06 | 718660 | -38 |  | -48.4 | 41.7 | 33.4 | 33 | 34.1 | 34 | 33.5 |  | 28.9 | 30.1 | 31 | 30 | 30 |  |  | CanadaSaskatchewanSASKATOON DIEFENBAKER INT'L A
Canada | Saskatchewan |  | SASKATOON KERNEN FARM | SASKATOON KERNEN FARM, SK, Canada | 52.15N | 106.55W | 510 | -6.00 (NAS) | 96-05 | 715130 | -36.9 |  | -41.9 | 41.1 | 31.8 | 32.9 | 34.5 | 33 | 33.0667 |  | 27.7 | 30.1 | 31.1 | 30 | 29.6333 |  |  | CanadaSaskatchewanSASKATOON KERNEN FARM
Canada | Saskatchewan |  | SCOTT CDA | SCOTT CDA, SK, Canada | 52.36N | 108.83W | 660 | -6.00 (NAS) | 97-06 | 714890 | -36.4 |  | -46.5 | 42.4 | 31.3 | 33.2 | 33.7 | 33 | 32.7333 |  | 27 | 30 | 30.5 | 29 | 29.1667 |  |  | CanadaSaskatchewanSCOTT CDA
Canada | Saskatchewan |  | SOUTHEND | SOUTHEND, SK, Canada | 56.33N | 103.28W | 344 | -6.00 (NAS) | 94-06 | 714510 | -41.6 |  | -49.1 | 36.5 | 28.9 | 30.4 | 30.6 | 30 | 29.9667 |  | 26.2 | 27.6 | 27.1 | 27 | 26.9667 |  |  | CanadaSaskatchewanSOUTHEND
Canada | Saskatchewan |  | SPIRITWOOD WEST | SPIRITWOOD WEST, SK, Canada | 53.37N | 107.55W | 584 | -6.00 (NAS) | 94-06 | 711330 | -39.3 |  | -48.5 | 40.2 | 29.4 | 30.6 | 31.5 | 31 | 30.5 |  | 26.1 | 27.8 | 28.5 | 27 | 27.4667 |  |  | CanadaSaskatchewanSPIRITWOOD WEST
Canada | Saskatchewan |  | STONY RAPIDS A | STONY RAPIDS A, SK, Canada | 59.25N | 105.83W | 245 | -6.00 (NAS) | 86-06 | 711320 | -44 |  | -51.1 | 36.8 | 29.2 | 30.9 | 30.5 | 30 | 30.2 |  | 26.7 | 28 | 27 | 27 | 27.2333 |  |  | CanadaSaskatchewanSTONY RAPIDS A
Canada | Saskatchewan |  | SWIFT CURRENT A | SWIFT CURRENT A, SK, Canada | 50.30N | 107.68W | 818 | -6.00 (NAS) | 86-06 | 718700 | -34.5 |  | -44.1 | 39 | 32.1 | 32.8 | 34.2 | 33 | 33.0333 |  | 28.7 | 30.5 | 31.7 | 30 | 30.3 |  |  | CanadaSaskatchewanSWIFT CURRENT A
Canada | Saskatchewan |  | SWIFT CURRENT CDA | SWIFT CURRENT CDA, SK, Canada | 50.27N | 107.73W | 825 | -6.00 (NAS) | 94-06 | 714460 | -33.5 |  | -42.3 | 38.7 | 30.3 | 32.9 | 34.2 | 32 | 32.4667 |  | 27.2 | 30.6 | 32.1 | 30 | 29.9667 |  |  | CanadaSaskatchewanSWIFT CURRENT CDA
Canada | Saskatchewan |  | URANIUM CITY (AUT) | URANIUM CITY (AUT), SK, Canada | 59.57N | 108.48W | 318 | -6.00 (NAS) | 94-06 | 710760 | N/A |  | N/A | N/A | 28.5 | 29 | 26.8 | 28 | 28.1 |  | 25.8 | 26.7 | 24.7 | 26 | 25.7333 |  |  | CanadaSaskatchewanURANIUM CITY (AUT)
Canada | Saskatchewan |  | VAL MARIE SOUTHEAST | VAL MARIE SOUTHEAST, SK, Canada | 49.07N | 107.58W | 796 | -6.00 (NAS) | 94-06 | 711370 | -37.4 |  | -47.2 | 40.3 | 32.1 | 35.9 | 36.2 | 35 | 34.7333 |  | 28.8 | 33.6 | 34 | 32 | 32.1333 |  |  | CanadaSaskatchewanVAL MARIE SOUTHEAST
Canada | Saskatchewan |  | WASKESIU LAKE | WASKESIU LAKE, SK, Canada | 53.92N | 106.07W | 569 | -6.00 (NAS) | 94-06 | 714540 | -36.4 |  | -43.4 | 36.4 | 29.2 | 30 | 30.4 | 30 | 29.8667 |  | 26 | 27.4 | 27.6 | 27 | 27 |  |  | CanadaSaskatchewanWASKESIU LAKE
Canada | Saskatchewan |  | WATROUS EAST | WATROUS EAST, SK, Canada | 51.67N | 105.40W | 526 | -6.00 (NAS) | 94-06 | 715110 | -38.3 |  | -47.3 | 38.9 | 30.9 | 31.2 | 33.9 | 32 | 32 |  | 27.8 | 29.1 | 30.7 | 29 | 29.2 |  |  | CanadaSaskatchewanWATROUS EAST
Canada | Saskatchewan |  | WEYBURN | WEYBURN, SK, Canada | 49.70N | 103.80W | 589 | -6.00 (NAS) | 94-06 | 714520 | -35.5 |  | -45.9 | 39.7 | 32.2 | 33.6 | 35.2 | 34 | 33.6667 |  | 28.9 | 31.1 | 32.5 | 31 | 30.8333 |  |  | CanadaSaskatchewanWEYBURN
Canada | Saskatchewan |  | WYNYARD (AUT) | WYNYARD (AUT), SK, Canada | 51.77N | 104.20W | 560 | -6.00 (NAS) | 82-06 | 718650 | -36.4 |  | -46.4 | 39.6 | 31.7 | 32.2 | 32 | 32 | 31.9667 |  | 28.1 | 28.9 | 29.4 | 29 | 28.8 |  |  | CanadaSaskatchewanWYNYARD (AUT)
Canada | Saskatchewan |  | YORKTON A | YORKTON A, SK, Canada | 51.27N | 102.47W | 498 | -6.00 (NAS) | 82-05 | 711380 | -38.2 |  | -47.5 | 37.6 | 31.7 | 31.6 | 32.5 | 32 | 31.9333 |  | 28 | 29 | 29.9 | 29 | 28.9667 |  |  | CanadaSaskatchewanYORKTON A
Canada | Yukon |  | BURWASH A | BURWASH A, YT, Canada | 61.37N | 139.05W | 807 | -8.00 (NAP) | 82-06 | 719670 | -45.5 |  | -54.9 | 31.7 | 27 | 24.9 | 26.2 | 26 | 26.0333 |  | 23.4 | 22.8 | 22.6 | 23 | 22.9333 |  |  | CanadaYukonBURWASH A
Canada | Yukon |  | FARO (AUT) | FARO (AUT), YT, Canada | 62.23N | 133.35W | 717 | -8.00 (NAP) | 94-06 | 719490 | -45.2 |  | -55.1 | 34.7 | 29.3 | 27.6 | 28.9 | 29 | 28.6 |  | 26.1 | 25.1 | 25.8 | 26 | 25.6667 |  |  | CanadaYukonFARO (AUT)
Canada | Yukon |  | HAINES JUNCTION | HAINES JUNCTION, YT, Canada | 60.77N | 137.58W | 599 | -8.00 (NAP) | 94-06 | 715050 | -44.9 |  | -51.5 | 34.7 | 28.2 | 25.8 | 27.7 | 27 | 27.2333 |  | 24.1 | 23.8 | 25.1 | 24 | 24.3333 |  |  | CanadaYukonHAINES JUNCTION
Canada | Yukon |  | HERSCHEL ISLAND | HERSCHEL ISLAND, YT, Canada | 69.57N | 138.91W | 1 | -8.00 (NAP) | 94-06 | 715010 | N/A |  | N/A | N/A | 15.9 | 24.4 | 18.4 | 20 | 19.5667 |  | 12.8 | 19.1 | 15.4 | 16 | 15.7667 |  |  | CanadaYukonHERSCHEL ISLAND
Canada | Yukon |  | IVVAVIK NAT. PARK | IVVAVIK NAT. PARK, YT, Canada | 69.16N | 140.15W | 244 | -8.00 (NAP) | 95-06 | 719780 | -41.6 |  | -48.1 | 32.7 | 26.4 | 27.1 | 24.7 | 26 | 26.0667 |  | 22.9 | 24.6 | 20.9 | 23 | 22.8 |  |  | CanadaYukonIVVAVIK NAT. PARK
Canada | Yukon |  | KOMAKUK BEACH | KOMAKUK BEACH, YT, Canada | 69.61N | 140.20W | 13 | -8.00 (NAP) | 94-06 | 710460 | -39.8 |  | -43.3 | 28.7 | 18.2 | 21.7 | 20.7 | 20 | 20.2 |  | 14.3 | 18.9 | 16.7 | 17 | 16.6333 |  |  | CanadaYukonKOMAKUK BEACH
Canada | Yukon |  | MAYO A | MAYO A, YT, Canada | 63.62N | 135.87W | 504 | -8.00 (NAP) | 82-06 | 719650 | -49.2 |  | -58.1 | 34.9 | 29.9 | 29.3 | 29.1 | 29 | 29.4333 |  | 26.8 | 26.8 | 25.3 | 26 | 26.3 |  |  | CanadaYukonMAYO A
Canada | Yukon |  | ROCK RIVER | ROCK RIVER, YT, Canada | 66.98N | 136.22W | 731 | -8.00 (NAP) | 94-06 | 715060 | -34.5 |  | -41.4 | 31.9 | 24.7 | 25 | 25.8 | 25 | 25.1667 |  | 22 | 22.5 | 21.1 | 22 | 21.8667 |  |  | CanadaYukonROCK RIVER
Canada | Yukon |  | SHINGLE POINT A | SHINGLE POINT A, YT, Canada | 68.95N | 137.22W | 49 | -8.00 (NAP) | 82-06 | 719680 | -42.3 |  | -49.2 | 31.2 | 24.2 | 25.9 | 22.6 | 24 | 24.2333 |  | 21.1 | 23.2 | 19.2 | 21 | 21.1667 |  |  | CanadaYukonSHINGLE POINT A
Canada | Yukon |  | TESLIN (AUT) | TESLIN (AUT), YT, Canada | 60.17N | 132.73W | 705 | -8.00 (NAP) | 94-06 | 710450 | -42.4 |  | -52.3 | 34.1 | 29 | 27.2 | 27.6 | 28 | 27.9333 |  | 25.1 | 24.2 | 24.3 | 25 | 24.5333 |  |  | CanadaYukonTESLIN (AUT)
Canada | Yukon |  | WATSON LAKE A | WATSON LAKE A, YT, Canada | 60.12N | 128.82W | 687 | -8.00 (NAP) | 82-06 | 719530 | -47.6 |  | -56.3 | 34.8 | 28.9 | 28.1 | 29 | 29 | 28.6667 |  | 25.7 | 25.8 | 25.3 | 26 | 25.6 |  |  | CanadaYukonWATSON LAKE A
Canada | Yukon |  | WHITEHORSE A | WHITEHORSE A, YT, Canada | 60.71N | 135.07W | 706 | -8.00 (NAP) | 82-06 | 719640 | -41.7 |  | -50.8 | 34.4 | 28.9 | 27.6 | 28.1 | 28 | 28.2 |  | 24.8 | 25.1 | 25 | 25 | 24.9667 |  |  | CanadaYukonWHITEHORSE A
Mexico | BCN_Baja_California_N |  | GENERAL ABELARDO L | GENERAL ABELARDO L, Mexico | 32.53N | 116.97W | 156 | -8.00 (MET) | 86-06 | 760013 | 3.5 |  | 0.1 | 41 | 30.8 | 31.8 | 33.1 | 32 | 31.9 |  | 27.2 | 29.8 | 30.8 | 29 | 29.2667 |  |  | MexicoBCN_Baja_California_NGENERAL ABELARDO L
Mexico | GRO_Guerrero |  | GENERAL JUAN N ALVA | GENERAL JUAN N ALVA, Mexico | 16.75N | 99.75W | 5 | -6.00 (MEX) | 82-06 | 768056 | 17.7 |  | 14.1 | 38.8 | 34.1 | 34 | 34.1 | 34 | 34.0667 |  | 33.2 | 33.1 | 33.2 | 33 | 33.1667 |  |  | MexicoGRO_GuerreroGENERAL JUAN N ALVA
Mexico | GUA_Guanajuato |  | DE GUANAJUATO INTL | DE GUANAJUATO INTL, Mexico | 20.98N | 101.48W | 1861 | -6.00 (MEX) | 92-06 | 765773 | N/A |  | N/A | N/A | 36.1 | 31.8 | 29.2 | 32 | 32.3667 |  | 33 | 29.2 | 28.5 | 30 | 30.2333 |  |  | MexicoGUA_GuanajuatoDE GUANAJUATO INTL
Mexico | GUA_Guanajuato |  | GUANAJUATO | GUANAJUATO, Mexico | 21.00N | 101.28W | 1999 | -6.00 (MEX) | 82-06 | 765770 | N/A |  | N/A | N/A | 33 | 29.8 | 28.8 | 31 | 30.5333 |  | 30.8 | 28.2 | 27.4 | 29 | 28.8 |  |  | MexicoGUA_GuanajuatoGUANAJUATO
Mexico | JAL_Jalisco |  | DON MIGUEL Y HIDALG | DON MIGUEL Y HIDALG, Mexico | 20.52N | 103.30W | 1566 | -6.00 (MEX) | 82-06 | 766133 | -0.5 |  | -5 | 38 | 34.9 | 29.2 | 29 | 31 | 31.0333 |  | 33 | 28.1 | 27.9 | 30 | 29.6667 |  |  | MexicoJAL_JaliscoDON MIGUEL Y HIDALG
Mexico | JAL_Jalisco |  | LICENCIADO GUSTAVO | LICENCIADO GUSTAVO, Mexico | 20.67N | 105.25W | 6 | -6.00 (MEX) | 90-06 | 766013 | 12.1 |  | 8.6 | 39.1 | 33.8 | 34.1 | 34.1 | 34 | 34 |  | 33 | 33.2 | 33.2 | 33 | 33.1333 |  |  | MexicoJAL_JaliscoLICENCIADO GUSTAVO
Mexico | JAL_Jalisco |  | PUERTO VALLARTA | PUERTO VALLARTA, Mexico | 20.68N | 105.25W | 6 | -7.00 (MEC) | 82-94 | 766014 | 12.5 |  | 10.3 | 37 | 33.2 | 33.9 | 33.9 | 34 | 33.6667 |  | 32.8 | 33 | 33.1 | 33 | 32.9667 |  |  | MexicoJAL_JaliscoPUERTO VALLARTA
Mexico | MEX_México |  | AEROP. INTERNACIONA | AEROP. INTERNACIONA, Mexico | 19.43N | 99.13W | 2235 | -6.00 (MEX) | 82-94 | 766790 | 0.4 |  | -5.6 | 34 | 29.9 | 26.2 | 26.6 | 28 | 27.5667 |  | 27.9 | 25.1 | 25.2 | 26 | 26.0667 |  |  | MexicoMEX_MéxicoAEROP. INTERNACIONA
Mexico | MEX_México |  | LICENCIADO ADOLFO L | LICENCIADO ADOLFO L, Mexico | 19.33N | 99.57W | 2643 | -6.00 (MEX) | 92-06 | 766753 | -6 |  | -10.2 | 32 | 27 | 23.2 | 23.2 | 24 | 24.4667 |  | 25 | 22.1 | 22.1 | 23 | 23.0667 |  |  | MexicoMEX_MéxicoLICENCIADO ADOLFO L
Mexico | MEX_México |  | LICENCIADO BENITO J | LICENCIADO BENITO J, Mexico | 19.43N | 99.07W | 2286 | -6.00 (MEX) | 90-06 | 766793 | 0 |  | -3.3 | 34.2 | 30.2 | 26.2 | 26.1 | 28 | 27.5 |  | 28.1 | 25.1 | 24.9 | 26 | 26.0333 |  |  | MexicoMEX_MéxicoLICENCIADO BENITO J
Mexico | NLE_Nuevo_León |  | GENERAL MARIANO ESC | GENERAL MARIANO ESC, Mexico | 25.77N | 100.10W | 399 | -6.00 (MEX) | 90-06 | 763943 | 0.5 |  | -5.7 | 49.2 | 40 | 39.2 | 39 | 39 | 39.4 |  | 38 | 38.1 | 37.8 | 38 | 37.9667 |  |  | MexicoNLE_Nuevo_LeónGENERAL MARIANO ESC
Mexico | NLE_Nuevo_León |  | MONTERREY (CITY) | MONTERREY (CITY), Mexico | 25.73N | 100.30W | 515 | -6.00 (MEX) | 88-06 | 763930 | N/A |  | N/A | N/A | 39.7 | 39 | 38.1 | 39 | 38.9333 |  | 37.3 | 37.6 | 36.9 | 37 | 37.2667 |  |  | MexicoNLE_Nuevo_LeónMONTERREY (CITY)
Mexico | ROO_Quintana_Roo |  | CANCUN INTL | CANCUN INTL, Mexico | 21.03N | 86.87W | 6 | -6.00 (MEX) | 91-06 | 765906 | 10.9 |  | 5.3 | 39.6 | 33.9 | 35.1 | 35.1 | 35 | 34.7 |  | 33.1 | 34 | 34.1 | 34 | 33.7333 |  |  | MexicoROO_Quintana_RooCANCUN INTL
Mexico | SIN_Sinaloa |  | GENERAL RAFAEL BUEL | GENERAL RAFAEL BUEL, Mexico | 23.15N | 106.27W | 12 | -7.00 (MEC) | 90-06 | 764593 | 6.9 |  | 2.8 | 38.9 | 34.9 | 34.8 | 34.2 | 35 | 34.6333 |  | 33.9 | 33.9 | 33.2 | 34 | 33.6667 |  |  | MexicoSIN_SinaloaGENERAL RAFAEL BUEL
Mexico | SIN_Sinaloa |  | MAZATLAN/G.BUELNA I | MAZATLAN/G.BUELNA I, Mexico | 23.15N | 106.25W | 5 | -7.00 (MEC) | 82-93 | 764594 | 8.2 |  | 5.3 | 39 | 35 | 35.8 | 35 | 35 | 35.2667 |  | 33.9 | 34.2 | 34.1 | 34 | 34.0667 |  |  | MexicoSIN_SinaloaMAZATLAN/G.BUELNA I
Mexico | SLP_San_Luis_Potosí |  | SAN LUIS POTOSI | SAN LUIS POTOSI, Mexico | 22.18N | 100.98W | 1883 | -6.00 (MEX) | 88-06 | 765390 | -3.9 |  | -8.8 | 38.3 | 34 | 30 | 28.6 | 31 | 30.8667 |  | 31.1 | 28.2 | 27.2 | 29 | 28.8333 |  |  | MexicoSLP_San_Luis_PotosíSAN LUIS POTOSI
Mexico | TAM_Tamaulipas |  | GENERAL FRANCISCO J | GENERAL FRANCISCO J, Mexico | 22.28N | 97.87W | 25 | -6.00 (MEX) | 90-05 | 765493 | 7 |  | -0.5 | 45.8 | 35 | 34.2 | 34.9 | 35 | 34.7 |  | 34 | 33.2 | 34 | 34 | 33.7333 |  |  | MexicoTAM_TamaulipasGENERAL FRANCISCO J
Mexico | TAM_Tamaulipas |  | TAMPICO/GEN FJ MINA | TAMPICO/GEN FJ MINA, Mexico | 22.28N | 97.85W | 24 | -6.00 (MEX) | 82-94 | 765494 | 7.5 |  | 1.3 | 43.9 | 34.1 | 33 | 33.2 | 33 | 33.4333 |  | 33.1 | 32.1 | 32.9 | 33 | 32.7 |  |  | MexicoTAM_TamaulipasTAMPICO/GEN FJ MINA
Mexico | VER_Veracruz |  | GENERAL HERIBERTO J | GENERAL HERIBERTO J, Mexico | 19.13N | 96.18W | 33 | -6.00 (MEX) | 90-06 | 766913 | 11.7 |  | 7.2 | 44 | 36.1 | 34.2 | 34.2 | 35 | 34.8333 |  | 34.8 | 33.2 | 33.2 | 34 | 33.7333 |  |  | MexicoVER_VeracruzGENERAL HERIBERTO J
Mexico | VER_Veracruz |  | VERACRUZ/GEN JARA | VERACRUZ/GEN JARA, Mexico | 19.15N | 96.18W | 29 | -6.00 (MEX) | 82-94 | 766910 | 10 |  | 3.2 | 41.9 | 35.2 | 33.2 | 33.2 | 34 | 33.8667 |  | 33.9 | 32.2 | 32.8 | 33 | 32.9667 |  |  | MexicoVER_VeracruzVERACRUZ/GEN JARA
Mexico | YUC_Yucatán |  | AEROP.INTERNACIONAL | AEROP.INTERNACIONAL, Mexico | 20.98N | 89.65W | 9 | -6.00 (MEX) | 82-06 | 766440 | 8.1 |  | 4.8 | 44.1 | 38.2 | 37 | 36.2 | 37 | 37.1333 |  | 36.8 | 35.3 | 35.1 | 36 | 35.7333 |  |  | MexicoYUC_YucatánAEROP.INTERNACIONAL
Mexico | ZAC_Zacatecas |  | GENERAL LEOBARDO C | GENERAL LEOBARDO C, Mexico | 22.88N | 102.68W | 2232 | -6.00 (MEX) | 89-06 | 765255 | -8.4 |  | -16.9 | 35.1 | 31.5 | 28.9 | 28.1 | 30 | 29.5 |  | 30 | 27.2 | 26.8 | 28 | 28 |  |  | MexicoZAC_ZacatecasGENERAL LEOBARDO C
United_States | Alabama | E1 | ANNISTON METROPOLITAN AP | ANNISTON METROPOLITAN AP, AL, USA | 33.59N | 85.86W | 183 | -6.00 (NAC) | 82-06 | 722287 | -11.3 | -11 | -19.8 | 40.6 | 35.2 | 36.5 | 36.9 | 36 | 36.2 | 37 | 33.3 | 34.8 | 34.6 | 34 | 34.2333 | 34 | 1 | United_StatesAlabamaANNISTON METROPOLITAN AP
United_States | Alabama | E1 | AUBURN-OPELIKA APT | AUBURN-OPELIKA APT, AL, USA | 32.62N | 85.43W | 236 | -6.00 (NAC) | 92-06 | 722284 | -8.9 | -9 | -15.4 | 40.1 | 34.1 | 36.2 | 36 | 35 | 35.4333 | 36 | 32.7 | 34.1 | 33 | 33 | 33.2667 | 33 | 2 | United_StatesAlabamaAUBURN-OPELIKA APT
United_States | Alabama | E1 | BIRMINGHAM MUNICIPAL AP | BIRMINGHAM MUNICIPAL AP, AL, USA | 33.56N | 86.75W | 192 | -6.00 (NAC) | 82-06 | 722280 | -11.8 | -12 | -21.4 | 41 | 35.2 | 36.7 | 37.1 | 36 | 36.3333 | 37 | 33.4 | 34.9 | 34.9 | 34 | 34.4 | 34 | 3 | United_StatesAlabamaBIRMINGHAM MUNICIPAL AP
United_States | Alabama | E1 | CAIRNS AAF/OZARK | CAIRNS AAF/OZARK, AL, USA | 31.28N | 85.72W | 91 | -6.00 (NAC) | 82-06 | 722269 | -7.5 | -8 | -15.5 | 40.4 | 37.2 | 37.2 | 36.2 | 37 | 36.8667 | 37 | 34.8 | 35.2 | 34.8 | 35 | 34.9333 | 35 | 4 | United_StatesAlabamaCAIRNS AAF/OZARK
United_States | Alabama | E1 | CENTREVILLE WSMO | CENTREVILLE WSMO, AL, USA | 32.90N | 87.25W | 138 | -6.00 (NAC) | 84-94 | 722290 | -11.1 | -11 | -23.1 | 38 | 35.1 | 35.9 | 35.7 | 36 | 35.5667 | 36 | 33.5 | 34.2 | 34 | 34 | 33.9 | 34 | 5 | United_StatesAlabamaCENTREVILLE WSMO
United_States | Alabama | E1 | DAUPHIN ISLAND | DAUPHIN ISLAND, AL, USA | 30.25N | 88.08W | 9 | -6.00 (NAC) | 89-06 | 994420 | -2.1 | -2 | -9.5 | 35.6 | 30.8 | 31.8 | 32.4 | 32 | 31.6667 | 32 | 30 | 31 | 31.1 | 31 | 30.7 | 31 | 6 | United_StatesAlabamaDAUPHIN ISLAND
United_States | Alabama | E1 | DOTHAN MUNICIPAL | DOTHAN MUNICIPAL, AL, USA | 31.32N | 85.45W | 98 | -6.00 (NAC) | 82-06 | 722268 | -7.5 | -8 | -16.4 | 40.7 | 36.8 | 37.2 | 36.6 | 37 | 36.8667 | 37 | 34.7 | 35.1 | 34.7 | 35 | 34.8333 | 35 | 7 | United_StatesAlabamaDOTHAN MUNICIPAL
United_States | Alabama | E1 | GADSEN MUNI (AWOS) | GADSEN MUNI (AWOS), AL, USA | 33.97N | 86.08W | 173 | -6.00 (NAC) | 92-06 | 722285 | -11.6 | -12 | -18.1 | 41.1 | 34.1 | 36.2 | 36.4 | 36 | 35.5667 | 36 | 32.7 | 34.1 | 34 | 34 | 33.6 | 34 | 8 | United_StatesAlabamaGADSEN MUNI (AWOS)
United_States | Alabama | E1 | HUNTSVILLE INTL/JONES FIELD | HUNTSVILLE INTL/JONES FIELD, AL, USA | 34.64N | 86.79W | 196 | -6.00 (NAC) | 82-06 | 723230 | -12.9 | -13 | -23.8 | 41 | 35.1 | 36.2 | 36.7 | 36 | 36 | 36 | 33.2 | 34.6 | 34.7 | 34 | 34.1667 | 34 | 9 | United_StatesAlabamaHUNTSVILLE INTL/JONES FIELD
United_States | Alabama | E1 | MAXWELL AFB/MONTGOM | MAXWELL AFB/MONTGOM, AL, USA | 32.38N | 86.37W | 53 | -6.00 (NAC) | 85-99 | 722265 | -5.8 | -6 | -10.3 | 40.3 | 37.2 | 37.7 | 37.5 | 37 | 37.4667 | 38 | 35.4 | 36.2 | 35.8 | 36 | 35.8 | 36 | 10 | United_StatesAlabamaMAXWELL AFB/MONTGOM
United_States | Alabama | E1 | MOBILE REGIONAL AP | MOBILE REGIONAL AP, AL, USA | 30.69N | 88.25W | 67 | -6.00 (NAC) | 82-06 | 722230 | -7.2 | -7 | -16.5 | 39.3 | 34.7 | 35.7 | 35.5 | 35 | 35.3 | 36 | 33.3 | 34.1 | 34 | 34 | 33.8 | 34 | 11 | United_StatesAlabamaMOBILE REGIONAL AP
United_States | Alabama | E1 | MONTGOMERY DANNELLY FIELD | MONTGOMERY DANNELLY FIELD, AL, USA | 32.30N | 86.39W | 62 | -6.00 (NAC) | 82-06 | 722260 | -9.3 | -9 | -17.7 | 41 | 36.3 | 37.1 | 37.4 | 37 | 36.9333 | 37 | 34.5 | 35.5 | 35.6 | 35 | 35.2 | 35 | 12 | United_StatesAlabamaMONTGOMERY DANNELLY FIELD
United_States | Alabama | E1 | MUSCLE SHOALS REGIONAL AP | MUSCLE SHOALS REGIONAL AP, AL, USA | 34.75N | 87.61W | 171 | -6.00 (NAC) | 82-06 | 723235 | -12.3 | -12 | -23.9 | 41.6 | 35.2 | 36.9 | 37.3 | 36 | 36.4667 | 37 | 33.6 | 35.2 | 35.4 | 35 | 34.7333 | 35 | 13 | United_StatesAlabamaMUSCLE SHOALS REGIONAL AP
United_States | Alabama | E1 | TUSCALOOSA MUNICIPAL AP | TUSCALOOSA MUNICIPAL AP, AL, USA | 33.21N | 87.62W | 57 | -6.00 (NAC) | 82-06 | 722286 | -11.1 | -11 | -20.7 | 39.4 | 35.7 | 37 | 37.3 | 37 | 36.6667 | 37 | 34 | 35.2 | 35.4 | 35 | 34.8667 | 35 | 14 | United_StatesAlabamaTUSCALOOSA MUNICIPAL AP
United_States | Alaska | X | ADAK NAS | ADAK NAS, AK, USA | 51.88N | 176.65W | 6 | -10.00 (NAH) | 82-06 | 704540 | -11.1 | -11 | -15.5 | 24.5 | 13.7 | 17.2 | 18 | 16 | 16.3 | 17 | 11.3 | 14.7 | 15.8 | 14 | 13.9333 | 14 | 15 | United_StatesAlaskaADAK NAS
United_States | Alaska | X | AMBLER | AMBLER, AK, USA | 67.10N | 157.85W | 88 | -9.00 (NAK) | 92-06 | 701718 | N/A | N/A | N/A | N/A | 27.4 | 27.1 | 25.2 | 27 | 26.5667 | 27 | 24.7 | 24.9 | 22 | 24 | 23.8667 | 24 | 16 | United_StatesAlaskaAMBLER
United_States | Alaska | X | ANAKTUVUK PASS | ANAKTUVUK PASS, AK, USA | 68.13N | 151.73W | 657 | -9.00 (NAK) | 85-06 | 701625 | N/A | N/A | N/A | N/A | 23.7 | 24 | 22.7 | 23 | 23.4667 | 24 | 21.3 | 21.7 | 18.6 | 21 | 20.5333 | 21 | 17 | United_StatesAlaskaANAKTUVUK PASS
United_States | Alaska | X | ANCHORAGE INTL AP | ANCHORAGE INTL AP, AK, USA | 61.18N | 149.99W | 40 | -9.00 (NAK) | 82-06 | 702730 | -25.6 | -26 | -33.7 | 28.6 | 23.4 | 24.2 | 23.2 | 24 | 23.6 | 24 | 21.1 | 22.1 | 20.8 | 21 | 21.3333 | 21 | 18 | United_StatesAlaskaANCHORAGE INTL AP
United_States | Alaska | X | ANCHORAGE MERRILL FIELD | ANCHORAGE MERRILL FIELD, AK, USA | 61.22N | 149.86W | 42 | -9.00 (NAK) | 82-06 | 702735 | -26.4 | -26 | -34.1 | 29.3 | 24.2 | 25.2 | 24 | 24 | 24.4667 | 25 | 22.2 | 22.8 | 22 | 22 | 22.3333 | 22 | 19 | United_StatesAlaskaANCHORAGE MERRILL FIELD
United_States | Alaska | X | ANCHORAGE/ELMENDORF | ANCHORAGE/ELMENDORF, AK, USA | 61.25N | 149.80W | 59 | -9.00 (NAK) | 82-06 | 702720 | -29 | -29 | -37.9 | 31.1 | 24.8 | 26.2 | 25.2 | 25 | 25.4 | 26 | 22.5 | 23.3 | 22.5 | 23 | 22.7667 | 23 | 20 | United_StatesAlaskaANCHORAGE/ELMENDORF
United_States | Alaska | X | ANNETTE ISLAND AP | ANNETTE ISLAND AP, AK, USA | 55.04N | 131.57W | 34 | -9.00 (NAK) | 82-06 | 703980 | -12.6 | -13 | -20.9 | 34.2 | 27.9 | 24.6 | 25.4 | 26 | 25.9667 | 25 | 22.3 | 21.9 | 21.8 | 22 | 22 | 22 | 21 | United_StatesAlaskaANNETTE ISLAND AP
United_States | Alaska | X | ANVIK | ANVIK, AK, USA | 62.65N | 160.18W | 99 | -9.00 (NAK) | 95-06 | 702075 | -34.4 | -34 | -44.9 | 29.1 | 24.9 | 24.2 | 25.8 | 25 | 24.9667 | 24 | 22.8 | 22.8 | 21 | 22 | 22.2 | 22 | 22 | United_StatesAlaskaANVIK
United_States | Alaska | X | BARROW W POST-W ROGERS ARPT | BARROW W POST-W ROGERS ARPT, AK, USA | 71.29N | 156.76W | 4 | -9.00 (NAK) | 82-06 | 700260 | -42.6 | -43 | -49.3 | 25.7 | 15.2 | 18.2 | 16.8 | 17 | 16.7333 | 18 | 11.4 | 14.8 | 13.6 | 13 | 13.2667 | 13 | 23 | United_StatesAlaskaBARROW W POST-W ROGERS ARPT
United_States | Alaska | X | BARTER ISLAND (DEW) | BARTER ISLAND (DEW), AK, USA | 70.13N | 143.63W | 12 | -9.00 (NAK) | 82-99 | 700860 | N/A | N/A | N/A | N/A | 13.7 | 15.7 | 28.5 | 19 | 19.3 | 16 | 8.9 | 12.8 | 17.4 | 13 | 13.0333 | 13 | 24 | United_StatesAlaskaBARTER ISLAND (DEW)
United_States | Alaska | X | BETHEL AIRPORT | BETHEL AIRPORT, AK, USA | 60.79N | 161.83W | 46 | -9.00 (NAK) | 82-06 | 702190 | -34.7 | -35 | -43.6 | 31.8 | 25.5 | 25.1 | 24.1 | 25 | 24.9 | 25 | 21.8 | 22.5 | 20.5 | 22 | 21.6 | 22 | 25 | United_StatesAlaskaBETHEL AIRPORT
United_States | Alaska | X | BETTLES FIELD | BETTLES FIELD, AK, USA | 66.92N | 151.51W | 196 | -9.00 (NAK) | 82-06 | 701740 | -47.6 | -48 | -53.2 | 34.1 | 29.2 | 28.8 | 26.2 | 28 | 28.0667 | 29 | 26.4 | 26.4 | 22.7 | 25 | 25.1667 | 25 | 26 | United_StatesAlaskaBETTLES FIELD
United_States | Alaska | X | BIG DELTA ALLEN AAF | BIG DELTA ALLEN AAF, AK, USA | 64.00N | 145.72W | 388 | -9.00 (NAK) | 82-06 | 702670 | -42.2 | -42 | -52.2 | 32.5 | 27.9 | 27.9 | 27.7 | 28 | 27.8333 | 28 | 25.4 | 25.5 | 24.5 | 25 | 25.1333 | 25 | 27 | United_StatesAlaskaBIG DELTA ALLEN AAF
United_States | Alaska | X | CAPE LISBURNE(AWOS) | CAPE LISBURNE(AWOS), AK, USA | 68.88N | 166.13W | 3 | -9.00 (NAK) | 82-06 | 701040 | N/A | N/A | N/A | N/A | 15.3 | 16.7 | 17.2 | 16 | 16.4 | 17 | 11.8 | 15 | 14.7 | 14 | 13.8333 | 14 | 28 | United_StatesAlaskaCAPE LISBURNE(AWOS)
United_States | Alaska | X | CAPE NEWENHAM AFS | CAPE NEWENHAM AFS, AK, USA | 58.65N | 162.07W | 161 | -9.00 (NAK) | 82-06 | 703050 | N/A | N/A | N/A | N/A | 18.7 | 18 | 18 | 18 | 18.2333 | 18 | 15.6 | 16.2 | 16.2 | 16 | 16 | 16 | 29 | United_StatesAlaskaCAPE NEWENHAM AFS
United_States | Alaska | X | CAPE ROMANZOFF AWOS | CAPE ROMANZOFF AWOS, AK, USA | 61.78N | 166.03W | 123 | -9.00 (NAK) | 82-06 | 702120 | N/A | N/A | N/A | N/A | 21.3 | 19.9 | 21.1 | 21 | 20.7667 | 20 | 17.2 | 17.4 | 18 | 18 | 17.5333 | 18 | 30 | United_StatesAlaskaCAPE ROMANZOFF AWOS
United_States | Alaska | X | COLD BAY ARPT | COLD BAY ARPT, AK, USA | 55.21N | 162.72W | 31 | -9.00 (NAK) | 82-06 | 703160 | -16.4 | -16 | -24.2 | 24.3 | 15.8 | 17 | 17.7 | 17 | 16.8333 | 17 | 13.1 | 15 | 15.7 | 15 | 14.6 | 15 | 31 | United_StatesAlaskaCOLD BAY ARPT
United_States | Alaska | X | CORDOVA | CORDOVA, AK, USA | 60.49N | 145.45W | 15 | -9.00 (NAK) | 82-06 | 702960 | -22.4 | -22 | -31.2 | 31.4 | 24.3 | 24.3 | 24.4 | 24 | 24.3333 | 24 | 20.9 | 20.9 | 21 | 21 | 20.9333 | 21 | 32 | United_StatesAlaskaCORDOVA
United_States | Alaska | X | DEADHORSE | DEADHORSE, AK, USA | 70.19N | 148.48W | 18 | -9.00 (NAK) | 82-06 | 700637 | -44.7 | -45 | -51.8 | 29.4 | 20.2 | 22.9 | 21.8 | 22 | 21.6333 | 23 | 17.2 | 20 | 17.9 | 18 | 18.3667 | 18 | 33 | United_StatesAlaskaDEADHORSE
United_States | Alaska | X | DILLINGHAM MUNI | DILLINGHAM MUNI, AK, USA | 59.05N | 158.52W | 29 | -9.00 (NAK) | 82-06 | 703210 | -32.6 | -33 | -45 | 30.7 | 22.8 | 23.9 | 22.7 | 23 | 23.1333 | 24 | 19.9 | 21.4 | 20.2 | 21 | 20.5 | 21 | 34 | United_StatesAlaskaDILLINGHAM MUNI
United_States | Alaska | X | DUTCH HARBOR | DUTCH HARBOR, AK, USA | 53.90N | 166.55W | 4 | -9.00 (NAK) | 92-06 | 704890 | -9.8 | -10 | -19.2 | 24.3 | 15.9 | 19 | 19.9 | 18 | 18.2667 | 19 | 12.6 | 17 | 17.6 | 16 | 15.7333 | 16 | 35 | United_StatesAlaskaDUTCH HARBOR
United_States | Alaska | X | FAIRBANKS INTL ARPT | FAIRBANKS INTL ARPT, AK, USA | 64.82N | 147.86W | 138 | -9.00 (NAK) | 82-06 | 702610 | -42.8 | -43 | -51.2 | 35.6 | 30 | 29.7 | 27.6 | 29 | 29.1 | 30 | 27.5 | 27.4 | 24.5 | 26 | 26.4667 | 26 | 36 | United_StatesAlaskaFAIRBANKS INTL ARPT
United_States | Alaska | X | FAIRBANKS/EIELSON A | FAIRBANKS/EIELSON A, AK, USA | 64.65N | 147.07W | 167 | -9.00 (NAK) | 82-00 | 702650 | -43.6 | -44 | -52.7 | 36.2 | 30 | 29.8 | 28 | 29 | 29.2667 | 30 | 27.6 | 27.4 | 24.2 | 26 | 26.4 | 26 | 37 | United_StatesAlaskaFAIRBANKS/EIELSON A
United_States | Alaska | X | FIVE FINGER ISLAND | FIVE FINGER ISLAND, AK, USA | 57.27N | 133.63W | 21 | -9.00 (NAK) | 85-06 | 994080 | -9 | -9 | -15.7 | 25.3 | 20 | 20.4 | 20.2 | 20 | 20.2 | 20 | 17.7 | 18.4 | 18.2 | 18 | 18.1 | 18 | 38 | United_StatesAlaskaFIVE FINGER ISLAND
United_States | Alaska | X | FORT YUKON | FORT YUKON, AK, USA | 66.57N | 145.27W | 138 | -9.00 (NAK) | 82-06 | 701940 | -48.6 | -49 | -57 | 35.6 | 28.2 | 29.4 | 27.5 | 28 | 28.3667 | 29 | 26 | 26.9 | 24.3 | 26 | 25.7333 | 26 | 39 | United_StatesAlaskaFORT YUKON
United_States | Alaska | X | FT. RICHARDSON/BRYA | FT. RICHARDSON/BRYA, AK, USA | 61.27N | 149.65W | 115 | -9.00 (NAK) | 82-94 | 702700 | -30.9 | -31 | -41 | 29.7 | 25.1 | 26.2 | 24.2 | 25 | 25.1667 | 26 | 22.7 | 23.6 | 21.8 | 23 | 22.7 | 23 | 40 | United_StatesAlaskaFT. RICHARDSON/BRYA
United_States | Alaska | X | GALENA A. | GALENA A., AK, USA | 64.73N | 156.93W | 49 | -9.00 (NAK) | 82-06 | 702220 | -45.5 | -46 | -56.8 | 32.1 | 27.7 | 28 | 26.4 | 27 | 27.3667 | 28 | 25.4 | 26 | 22.6 | 25 | 24.6667 | 25 | 41 | United_StatesAlaskaGALENA A.
United_States | Alaska | X | GULKANA INTERMEDIATE FIELD | GULKANA INTERMEDIATE FIELD, AK, USA | 62.16N | 145.46W | 481 | -9.00 (NAK) | 82-06 | 702710 | -40.7 | -41 | -48.8 | 32.7 | 27.9 | 27.3 | 27.5 | 28 | 27.5667 | 27 | 24.7 | 25.1 | 24.5 | 25 | 24.7667 | 25 | 42 | United_StatesAlaskaGULKANA INTERMEDIATE FIELD
United_States | Alaska | X | HOMER ARPT | HOMER ARPT, AK, USA | 59.65N | 151.48W | 22 | -9.00 (NAK) | 82-06 | 703410 | -20.4 | -20 | -29.3 | 27 | 19 | 21.1 | 20.3 | 20 | 20.1333 | 21 | 16.9 | 18.5 | 18.4 | 18 | 17.9333 | 18 | 43 | United_StatesAlaskaHOMER ARPT
United_States | Alaska | X | HOOPER BAY | HOOPER BAY, AK, USA | 61.52N | 166.13W | 6 | -9.00 (NAK) | 92-06 | 702186 | N/A | N/A | N/A | N/A | 22 | 19.2 | 20.1 | 20 | 20.4333 | 19 | 17.1 | 17.3 | 17.2 | 17 | 17.2 | 17 | 44 | United_StatesAlaskaHOOPER BAY
United_States | Alaska | X | ILIAMNA ARPT | ILIAMNA ARPT, AK, USA | 59.75N | 154.92W | 49 | -9.00 (NAK) | 82-06 | 703400 | -29.1 | -29 | -39.1 | 31.4 | 23.1 | 25.6 | 23.7 | 24 | 24.1333 | 26 | 20 | 21.9 | 20.7 | 21 | 20.8667 | 21 | 45 | United_StatesAlaskaILIAMNA ARPT
United_States | Alaska | X | INDIAN MTN AFS AWOS | INDIAN MTN AFS AWOS, AK, USA | 66.00N | 153.70W | 372 | -9.00 (NAK) | 82-06 | 701730 | N/A | N/A | N/A | N/A | 27.5 | 26.8 | 25.1 | 26 | 26.4667 | 27 | 25.1 | 25 | 21.6 | 24 | 23.9 | 24 | 46 | United_StatesAlaskaINDIAN MTN AFS AWOS
United_States | Alaska | X | JUNEAU INT'L ARPT | JUNEAU INT'L ARPT, AK, USA | 58.36N | 134.58W | 7 | -9.00 (NAK) | 82-06 | 703810 | -18 | -18 | -24.8 | 30.7 | 26.2 | 25.6 | 24.5 | 25 | 25.4333 | 26 | 22.7 | 22.8 | 22.1 | 23 | 22.5333 | 23 | 47 | United_StatesAlaskaJUNEAU INT'L ARPT
United_States | Alaska | X | KAKE SEAPLANE BASE | KAKE SEAPLANE BASE, AK, USA | 56.97N | 133.95W | 0 | -9.00 (NAK) | 93-06 | 703855 | -13.9 | -14 | -18.5 | 30.1 | 23 | 22.2 | 22.9 | 23 | 22.7 | 22 | 20 | 19.7 | 20.3 | 20 | 20 | 20 | 48 | United_StatesAlaskaKAKE SEAPLANE BASE
United_States | Alaska | X | KENAI MUNICIPAL AP | KENAI MUNICIPAL AP, AK, USA | 60.58N | 151.24W | 28 | -9.00 (NAK) | 82-06 | 702590 | -32.9 | -33 | -41.6 | 29.4 | 22.9 | 23.9 | 22.9 | 23 | 23.2333 | 24 | 19.9 | 20.6 | 20.3 | 20 | 20.2667 | 20 | 49 | United_StatesAlaskaKENAI MUNICIPAL AP
United_States | Alaska | X | KETCHIKAN INTL AP | KETCHIKAN INTL AP, AK, USA | 55.36N | 131.71W | 29 | -9.00 (NAK) | 82-06 | 703950 | -14.4 | -14 | -21.6 | 29.7 | 23.9 | 23.8 | 23.8 | 24 | 23.8333 | 24 | 21 | 21.7 | 21.6 | 21 | 21.4333 | 21 | 50 | United_StatesAlaskaKETCHIKAN INTL AP
United_States | Alaska | X | KING SALMON ARPT | KING SALMON ARPT, AK, USA | 58.68N | 156.65W | 15 | -9.00 (NAK) | 82-06 | 703260 | -34.3 | -34 | -46.8 | 31.1 | 24.2 | 25.3 | 24.1 | 25 | 24.5333 | 25 | 21 | 22.4 | 21.1 | 22 | 21.5 | 22 | 51 | United_StatesAlaskaKING SALMON ARPT
United_States | Alaska | X | KLAWOCK | KLAWOCK, AK, USA | 55.58N | 133.08W | 15 | -9.00 (NAK) | 97-06 | 703894 | -11.6 | -12 | -15.1 | 37 | 27.8 | 21.9 | 25.7 | 25 | 25.1333 | 22 | 20.7 | 19.3 | 21.7 | 21 | 20.5667 | 21 | 52 | United_StatesAlaskaKLAWOCK
United_States | Alaska | X | KODIAK AIRPORT | KODIAK AIRPORT, AK, USA | 57.75N | 152.49W | 34 | -9.00 (NAK) | 82-06 | 703500 | -17 | -17 | -25.5 | 29.4 | 22 | 24.2 | 22.8 | 23 | 23 | 24 | 18.2 | 20.5 | 20.2 | 20 | 19.6333 | 20 | 53 | United_StatesAlaskaKODIAK AIRPORT
United_States | Alaska | X | KOTZEBUE RALPH WEIN MEMORIAL | KOTZEBUE RALPH WEIN MEMORIAL, AK, USA | 66.89N | 162.60W | 5 | -9.00 (NAK) | 82-06 | 701330 | -38.9 | -39 | -47.7 | 30.7 | 23.1 | 22.8 | 21.1 | 22 | 22.3333 | 23 | 18.6 | 20.3 | 18.2 | 19 | 19.0333 | 19 | 54 | United_StatesAlaskaKOTZEBUE RALPH WEIN MEMORIAL
United_States | Alaska | X | LAKE HOOD SEAPLANE | LAKE HOOD SEAPLANE, AK, USA | 61.18N | 149.96W | 40 | -9.00 (NAK) | 94-06 | 702725 | -24.4 | -24 | -32.8 | 32.6 | 24.1 | 26.3 | 25.3 | 25 | 25.2333 | 26 | 22.6 | 23.8 | 22.7 | 23 | 23.0333 | 23 | 55 | United_StatesAlaskaLAKE HOOD SEAPLANE
United_States | Alaska | X | MCGRATH ARPT | MCGRATH ARPT, AK, USA | 62.95N | 155.60W | 103 | -9.00 (NAK) | 82-06 | 702310 | -45.5 | -46 | -52.9 | 32.2 | 28 | 27.9 | 26.3 | 27 | 27.4 | 28 | 25.4 | 26 | 22.9 | 25 | 24.7667 | 25 | 56 | United_StatesAlaskaMCGRATH ARPT
United_States | Alaska | X | MCKINLEY PARK | MCKINLEY PARK, AK, USA | 63.73N | 148.92W | 524 | -9.00 (NAK) | 95-06 | 702645 | N/A | N/A | N/A | N/A | 26.3 | 25.8 | 26.1 | 26 | 26.0667 | 26 | 23 | 22.7 | 22.9 | 23 | 22.8667 | 23 | 57 | United_StatesAlaskaMCKINLEY PARK
United_States | Alaska | X | MEKORYUK | MEKORYUK, AK, USA | 60.37N | 166.27W | 15 | -9.00 (NAK) | 92-06 | 702185 | -28.8 | -29 | -33.2 | 27.3 | 16.4 | 17.9 | 18.7 | 18 | 17.6667 | 18 | 13.9 | 16 | 16.2 | 15 | 15.3667 | 15 | 58 | United_StatesAlaskaMEKORYUK
United_States | Alaska | X | MIDDLETON ISL. AMOS | MIDDLETON ISL. AMOS, AK, USA | 59.43N | 146.33W | 37 | -9.00 (NAK) | 82-06 | 703430 | -9 | -9 | -17.4 | 25.1 | 17.3 | 19.6 | 20.2 | 19 | 19.0333 | 20 | 15.1 | 17.6 | 17.7 | 17 | 16.8 | 17 | 59 | United_StatesAlaskaMIDDLETON ISL. AMOS
United_States | Alaska | X | MINCHUMINA | MINCHUMINA, AK, USA | 63.90N | 152.27W | 213 | -9.00 (NAK) | 93-06 | 702460 | N/A | N/A | N/A | N/A | 27.2 | 26.4 | 26.9 | 27 | 26.8333 | 26 | 24.3 | 24.4 | 23.7 | 24 | 24.1333 | 24 | 60 | United_StatesAlaskaMINCHUMINA
United_States | Alaska | X | NENANA MUNICIPAL AP | NENANA MUNICIPAL AP, AK, USA | 64.55N | 149.07W | 110 | -9.00 (NAK) | 82-06 | 702600 | -46.3 | -46 | -55.5 | 35.7 | 29 | 29.8 | 27.2 | 29 | 28.6667 | 30 | 26.7 | 27.2 | 24.2 | 26 | 26.0333 | 26 | 61 | United_StatesAlaskaNENANA MUNICIPAL AP
United_States | Alaska | X | NOME MUNICIPAL ARPT | NOME MUNICIPAL ARPT, AK, USA | 64.51N | 165.44W | 7 | -9.00 (NAK) | 82-06 | 702000 | -35.8 | -36 | -45.2 | 30.6 | 23.4 | 23.9 | 20.7 | 23 | 22.6667 | 24 | 20.3 | 20.4 | 18 | 20 | 19.5667 | 20 | 62 | United_StatesAlaskaNOME MUNICIPAL ARPT
United_States | Alaska | X | NORTHWAY AIRPORT | NORTHWAY AIRPORT, AK, USA | 62.96N | 141.95W | 525 | -9.00 (NAK) | 82-06 | 702910 | -47.4 | -47 | -56.3 | 32.2 | 28.5 | 28 | 27.4 | 28 | 27.9667 | 28 | 25.2 | 25.5 | 23.7 | 25 | 24.8 | 25 | 63 | United_StatesAlaskaNORTHWAY AIRPORT
United_States | Alaska | X | PALMER MUNICIPAL | PALMER MUNICIPAL, AK, USA | 61.60N | 149.09W | 76 | -9.00 (NAK) | 97-06 | 702740 | -27.9 | -28 | -39.7 | 31.1 | 24.9 | 26.4 | 25.9 | 26 | 25.7333 | 26 | 22.7 | 23.5 | 23.2 | 23 | 23.1333 | 23 | 64 | United_StatesAlaskaPALMER MUNICIPAL
United_States | Alaska | X | PETERSBURG | PETERSBURG, AK, USA | 56.82N | 132.97W | 33 | -9.00 (NAK) | 92-06 | 703860 | -15.8 | -16 | -20.8 | 30.7 | 23.9 | 22.7 | 22.9 | 23 | 23.1667 | 23 | 21 | 20.3 | 20.5 | 21 | 20.6 | 21 | 65 | United_StatesAlaskaPETERSBURG
United_States | Alaska | X | POINT HOPE (AWOS) | POINT HOPE (AWOS), AK, USA | 68.35N | 166.80W | 4 | -9.00 (NAK) | 92-06 | 701043 | N/A | N/A | N/A | N/A | 16.2 | 17.7 | 16.3 | 17 | 16.7333 | 18 | 12.4 | 16.1 | 13.7 | 14 | 14.0667 | 14 | 66 | United_StatesAlaskaPOINT HOPE (AWOS)
United_States | Alaska | X | PORT HEIDEN | PORT HEIDEN, AK, USA | 56.95N | 158.62W | 29 | -9.00 (NAK) | 82-06 | 703330 | -24 | -24 | -35.5 | 26.1 | 17.9 | 20.9 | 21.3 | 20 | 20.0333 | 21 | 15.9 | 17.7 | 18.4 | 17 | 17.3333 | 17 | 67 | United_StatesAlaskaPORT HEIDEN
United_States | Alaska | X | SAINT MARY`S (AWOS) | SAINT MARY`S (AWOS), AK, USA | 62.07N | 163.30W | 95 | -9.00 (NAK) | 90-06 | 702005 | -34.4 | -34 | -42.8 | 31.3 | 23 | 24 | 23 | 23 | 23.3333 | 24 | 21.1 | 21.3 | 19.1 | 21 | 20.5 | 21 | 68 | United_StatesAlaskaSAINT MARY`S (AWOS)
United_States | Alaska | X | SAND POINT | SAND POINT, AK, USA | 55.32N | 160.52W | 7 | -9.00 (NAK) | 94-06 | 703165 | -11.7 | -12 | -17.4 | 20.6 | 17.1 | 17.5 | 17.5 | 17 | 17.3667 | 18 | 13.9 | 16.1 | 16.3 | 15 | 15.4333 | 15 | 69 | United_StatesAlaskaSAND POINT
United_States | Alaska | X | SEWARD | SEWARD, AK, USA | 60.12N | 149.45W | 18 | -9.00 (NAK) | 82-06 | 702770 | -17.3 | -17 | -26.8 | 32.6 | 23.3 | 26 | 22.8 | 24 | 24.0333 | 26 | 19.3 | 21.5 | 20.4 | 20 | 20.4 | 20 | 70 | United_StatesAlaskaSEWARD
United_States | Alaska | X | SHEMYA AFB | SHEMYA AFB, AK, USA | 52.72N | 174.12E | 31 | -10.00 (NAH) | 82-95 | 704140 | -7.6 | -8 | -10.6 | 18.5 | 10.5 | 13.4 | 14.1 | 13 | 12.6667 | 13 | 9.2 | 11.7 | 12.9 | 11 | 11.2667 | 11 | 71 | United_StatesAlaskaSHEMYA AFB
United_States | Alaska | X | SHISHMAREF (AWOS) | SHISHMAREF (AWOS), AK, USA | 66.27N | 166.05W | 2 | -9.00 (NAK) | 90-06 | 701195 | N/A | N/A | N/A | N/A | 16 | 18.7 | 17.1 | 17 | 17.2667 | 19 | 12.7 | 16.2 | 14.8 | 15 | 14.5667 | 15 | 72 | United_StatesAlaskaSHISHMAREF (AWOS)
United_States | Alaska | X | SITKA JAPONSKI AP | SITKA JAPONSKI AP, AK, USA | 57.05N | 135.36W | 20 | -9.00 (NAK) | 82-06 | 703710 | -10.8 | -11 | -17.1 | 29.4 | 20.8 | 20.1 | 22.9 | 21 | 21.2667 | 20 | 17.6 | 17.9 | 19.3 | 18 | 18.2667 | 18 | 73 | United_StatesAlaskaSITKA JAPONSKI AP
United_States | Alaska | X | SKAGWAY AIRPORT | SKAGWAY AIRPORT, AK, USA | 59.46N | 135.31W | 13 | -9.00 (NAK) | 96-06 | 703620 | -17.5 | -18 | -23.7 | 33.4 | 24.8 | 24 | 25.4 | 25 | 24.7333 | 24 | 22 | 21.2 | 21.8 | 22 | 21.6667 | 22 | 74 | United_StatesAlaskaSKAGWAY AIRPORT
United_States | Alaska | X | SOLDOTNA | SOLDOTNA, AK, USA | 60.47N | 151.03W | 34 | -9.00 (NAK) | 92-06 | 702595 | -32.7 | -33 | -42.8 | 28.3 | 23.7 | 25 | 23.3 | 24 | 24 | 25 | 21.1 | 22.3 | 21.2 | 22 | 21.5333 | 22 | 75 | United_StatesAlaskaSOLDOTNA
United_States | Alaska | X | SPARREVOHN AFS | SPARREVOHN AFS, AK, USA | 61.10N | 155.57W | 484 | -9.00 (NAK) | 82-06 | 702350 | -35 | -35 | -38.7 | 31.8 | 24.2 | 24.3 | 25.3 | 25 | 24.6 | 24 | 21.2 | 22 | 21.6 | 22 | 21.6 | 22 | 76 | United_StatesAlaskaSPARREVOHN AFS
United_States | Alaska | X | ST PAUL ISLAND ARPT | ST PAUL ISLAND ARPT, AK, USA | 57.16N | 170.22W | 9 | -9.00 (NAK) | 82-06 | 703080 | -18.1 | -18 | -26.8 | 18.9 | 12.6 | 14.2 | 13.9 | 14 | 13.5667 | 14 | 10.3 | 12.7 | 12.6 | 12 | 11.8667 | 12 | 77 | United_StatesAlaskaST PAUL ISLAND ARPT
United_States | Alaska | X | TALKEETNA STATE ARPT | TALKEETNA STATE ARPT, AK, USA | 62.32N | 150.09W | 109 | -9.00 (NAK) | 82-06 | 702510 | -35.1 | -35 | -45.1 | 33 | 27.6 | 28 | 27.1 | 28 | 27.5667 | 28 | 24.7 | 25.4 | 23.2 | 24 | 24.4333 | 24 | 78 | United_StatesAlaskaTALKEETNA STATE ARPT
United_States | Alaska | X | TATALINA LRRS | TATALINA LRRS, AK, USA | 62.88N | 155.97W | 301 | -9.00 (NAK) | 82-06 | 702315 | N/A | N/A | N/A | N/A | 26.3 | 27.1 | 26.1 | 27 | 26.5 | 27 | 24.1 | 24.7 | 22.7 | 24 | 23.8333 | 24 | 79 | United_StatesAlaskaTATALINA LRRS
United_States | Alaska | X | TIN CITY AFS (AWOS) | TIN CITY AFS (AWOS), AK, USA | 65.57N | 167.92W | 83 | -9.00 (NAK) | 82-06 | 701170 | N/A | N/A | N/A | N/A | 18.9 | 20.2 | 16.5 | 19 | 18.5333 | 20 | 14.9 | 16.8 | 14 | 15 | 15.2333 | 15 | 80 | United_StatesAlaskaTIN CITY AFS (AWOS)
United_States | Alaska | X | TOGIAC VILLAGE AWOS | TOGIAC VILLAGE AWOS, AK, USA | 59.05N | 160.40W | 6 | -9.00 (NAK) | 92-06 | 703606 | -31.2 | -31 | -39.4 | 28.9 | 22.9 | 22.4 | 20.3 | 22 | 21.8667 | 22 | 19.1 | 19.9 | 17.9 | 19 | 18.9667 | 19 | 81 | United_StatesAlaskaTOGIAC VILLAGE AWOS
United_States | Alaska | X | UNALAKLEET FIELD | UNALAKLEET FIELD, AK, USA | 63.88N | 160.80W | 6 | -9.00 (NAK) | 83-06 | 702070 | N/A | N/A | N/A | N/A | 24.9 | 24.8 | 22.3 | 24 | 24 | 25 | 19.6 | 21.6 | 19.1 | 20 | 20.1 | 20 | 82 | United_StatesAlaskaUNALAKLEET FIELD
United_States | Alaska | X | VALDEZ PIONEER FIEL | VALDEZ PIONEER FIEL, AK, USA | 61.13N | 146.25W | 38 | -9.00 (NAK) | 96-06 | 702756 | -20.8 | -21 | -27.1 | 29.9 | 23 | 22.9 | 24 | 23 | 23.3 | 23 | 20.9 | 19.9 | 20.9 | 21 | 20.5667 | 21 | 83 | United_StatesAlaskaVALDEZ PIONEER FIEL
United_States | Alaska | X | VALDEZ WSO | VALDEZ WSO, AK, USA | 61.13N | 146.35W | 11 | -9.00 (NAK) | 82-05 | 702750 | -17.1 | -17 | -23.4 | 30.8 | 23 | 24.6 | 23.4 | 24 | 23.6667 | 25 | 20.5 | 20.8 | 20.2 | 21 | 20.5 | 21 | 84 | United_StatesAlaskaVALDEZ WSO
United_States | Alaska | X | WHITTIER | WHITTIER, AK, USA | 60.77N | 148.68W | 9 | -9.00 (NAK) | 87-06 | 702757 | -16.3 | -16 | -26.2 | 28.2 | 22.5 | 23.8 | 22.7 | 23 | 23 | 24 | 20.8 | 21.9 | 20.7 | 21 | 21.1333 | 21 | 85 | United_StatesAlaskaWHITTIER
United_States | Alaska | X | WRANGELL | WRANGELL, AK, USA | 56.48N | 132.37W | 13 | -9.00 (NAK) | 92-06 | 703870 | -13.4 | -13 | -18.2 | 30 | 24.1 | 23.2 | 23.7 | 24 | 23.6667 | 23 | 21.2 | 21.2 | 21.1 | 21 | 21.1667 | 21 | 86 | United_StatesAlaskaWRANGELL
United_States | Alaska | X | YAKUTAT STATE ARPT | YAKUTAT STATE ARPT, AK, USA | 59.51N | 139.63W | 9 | -9.00 (NAK) | 82-06 | 703610 | -20 | -20 | -28.4 | 32.1 | 23.2 | 21.7 | 22.5 | 22 | 22.4667 | 22 | 18.3 | 18.4 | 19.4 | 19 | 18.7 | 19 | 87 | United_StatesAlaskaYAKUTAT STATE ARPT
United_States | Arizona | M2 | CASA GRANDA (AWOS) | CASA GRANDA (AWOS), AZ, USA | 32.95N | 111.77W | 446 | -7.00 (NAZ) | 92-06 | 722748 | -3.6 | -4 | -6.6 | 48.7 | 43.4 | 44.4 | 43 | 44 | 43.6 | 44 | 42.1 | 42.7 | 41.9 | 42 | 42.2333 | 42 | 88 | United_StatesArizonaCASA GRANDA (AWOS)
United_States | Arizona | M2 | DAVIS-MONTHAN AFB | DAVIS-MONTHAN AFB, AZ, USA | 32.17N | 110.88W | 809 | -7.00 (NAZ) | 82-06 | 722745 | -2.5 | -3 | -5.9 | 46.7 | 42.5 | 42.3 | 40.8 | 42 | 41.8667 | 42 | 40.9 | 40.8 | 38.7 | 40 | 40.1333 | 40 | 89 | United_StatesArizonaDAVIS-MONTHAN AFB
United_States | Arizona | M2 | DOUGLAS BISBEE-DOUGLAS INTL A | DOUGLAS BISBEE-DOUGLAS INTL A, AZ, USA | 31.47N | 109.60W | 1250 | -7.00 (NAZ) | 86-06 | 722735 | -9.1 | -9 | -13 | 43.1 | 39.4 | 39 | 36.6 | 38 | 38.3333 | 39 | 37.8 | 37.4 | 34.8 | 37 | 36.6667 | 37 | 90 | United_StatesArizonaDOUGLAS BISBEE-DOUGLAS INTL A
United_States | Arizona | M2 | FLAGSTAFF AIRPORT | FLAGSTAFF AIRPORT, AZ, USA | 35.13N | 111.67W | 2135 | -7.00 (NAZ) | 82-06 | 723750 | -21.4 | -21 | -30.3 | 35.8 | 31.4 | 31.9 | 30.3 | 31 | 31.2 | 32 | 29.3 | 30.1 | 28.3 | 29 | 29.2333 | 29 | 91 | United_StatesArizonaFLAGSTAFF AIRPORT
United_States | Arizona | M2 | GRAND CANYON NATL P | GRAND CANYON NATL P, AZ, USA | 35.95N | 112.13W | 2065 | -7.00 (NAZ) | 93-06 | 723783 | -22.3 | -22 | -29.9 | 38.1 | 32.7 | 33.9 | 32.4 | 33 | 33 | 34 | 31.3 | 32.5 | 31.1 | 32 | 31.6333 | 32 | 92 | United_StatesArizonaGRAND CANYON NATL P
United_States | Arizona | M2 | KINGMAN (AMOS) | KINGMAN (AMOS), AZ, USA | 35.26N | 113.94W | 1050 | -7.00 (NAZ) | 82-06 | 723700 | -8 | -8 | -14 | 45.3 | 39.1 | 41.2 | 39.1 | 40 | 39.8 | 41 | 37.4 | 38.9 | 37.6 | 38 | 37.9667 | 38 | 93 | United_StatesArizonaKINGMAN (AMOS)
United_States | Arizona | M2 | LUKE AFB/PHOENIX | LUKE AFB/PHOENIX, AZ, USA | 33.53N | 112.38W | 331 | -7.00 (NAZ) | 82-06 | 722785 | -1 | -1 | -6.2 | 51 | 46.1 | 45.9 | 44.8 | 46 | 45.6 | 46 | 43.3 | 43.9 | 42.9 | 43 | 43.3667 | 43 | 94 | United_StatesArizonaLUKE AFB/PHOENIX
United_States | Arizona | M2 | NOGALES INTL | NOGALES INTL, AZ, USA | 31.42N | 110.85W | 1236 | -7.00 (NAZ) | 89-06 | 722728 | -6.3 | -6 | -10.6 | 44 | 39.8 | 39.4 | 37.4 | 39 | 38.8667 | 39 | 37.8 | 37.8 | 35.2 | 37 | 36.9333 | 37 | 95 | United_StatesArizonaNOGALES INTL
United_States | Arizona | M2 | PAGE MUNI (AMOS) | PAGE MUNI (AMOS), AZ, USA | 36.93N | 111.45W | 1304 | -7.00 (NAZ) | 82-06 | 723710 | -8.5 | -9 | -17.5 | 44.6 | 38.3 | 40.2 | 38 | 39 | 38.8333 | 40 | 36.9 | 38.2 | 36.3 | 37 | 37.1333 | 37 | 96 | United_StatesArizonaPAGE MUNI (AMOS)
United_States | Arizona | M2 | PHOENIX SKY HARBOR INTL AP | PHOENIX SKY HARBOR INTL AP, AZ, USA | 33.44N | 111.99W | 337 | -7.00 (NAZ) | 82-06 | 722780 | 1.3 | 1 | -2.5 | 49.8 | 45.1 | 45.4 | 44 | 45 | 44.8333 | 45 | 42.9 | 43.7 | 42.5 | 43 | 43.0333 | 43 | 97 | United_StatesArizonaPHOENIX SKY HARBOR INTL AP
United_States | Arizona | M2 | PRESCOTT LOVE FIELD | PRESCOTT LOVE FIELD, AZ, USA | 34.65N | 112.42W | 1540 | -7.00 (NAZ) | 82-06 | 723723 | -12.3 | -12 | -21.1 | 41 | 36.3 | 37.1 | 35.2 | 36 | 36.2 | 37 | 33.9 | 35.1 | 33.1 | 34 | 34.0333 | 34 | 98 | United_StatesArizonaPRESCOTT LOVE FIELD
United_States | Arizona | M2 | SAFFORD (AMOS) | SAFFORD (AMOS), AZ, USA | 32.82N | 109.68W | 950 | -7.00 (NAZ) | 83-06 | 722747 | -7.3 | -7 | -11.7 | 46 | 42.4 | 42.3 | 39.9 | 42 | 41.5333 | 42 | 40.3 | 40.3 | 37.8 | 39 | 39.4667 | 39 | 99 | United_StatesArizonaSAFFORD (AMOS)
United_States | Arizona | M2 | TUCSON INTERNATIONAL AP | TUCSON INTERNATIONAL AP, AZ, USA | 32.13N | 110.96W | 779 | -7.00 (NAZ) | 82-06 | 722740 | -3.1 | -3 | -7.9 | 47.4 | 43.5 | 42.7 | 41 | 42 | 42.4 | 43 | 41.2 | 41.2 | 39.1 | 41 | 40.5 | 41 | 100 | United_StatesArizonaTUCSON INTERNATIONAL AP
United_States | Arizona | M2 | WINSLOW MUNICIPAL AP | WINSLOW MUNICIPAL AP, AZ, USA | 35.02N | 110.72W | 1488 | -7.00 (NAZ) | 82-06 | 723740 | -15.4 | -15 | -23.1 | 43.9 | 37.2 | 38.8 | 36.6 | 38 | 37.5333 | 39 | 35.6 | 37 | 34.7 | 36 | 35.7667 | 36 | 101 | United_StatesArizonaWINSLOW MUNICIPAL AP
United_States | Arizona | M2 | YUMA INTL AIRPORT | YUMA INTL AIRPORT, AZ, USA | 32.65N | 114.60W | 63 | -7.00 (NAZ) | 82-06 | 722800 | 2.2 | 2 | -0.6 | 50.3 | 45.1 | 45.5 | 45 | 45 | 45.2 | 46 | 42.9 | 43.7 | 43.3 | 43 | 43.3 | 43 | 102 | United_StatesArizonaYUMA INTL AIRPORT
United_States | Arizona | M2 | YUMA MCAS | YUMA MCAS, AZ, USA | 32.65N | 114.62W | 65 | -7.00 (NAZ) | 82-06 | 699604 | 2.3 | 2 | -0.9 | 50.8 | 45 | 45.7 | 45 | 45 | 45.2333 | 46 | 42.8 | 43.9 | 43.3 | 43 | 43.3333 | 43 | 103 | United_StatesArizonaYUMA MCAS
United_States | Arkansas | M2 | BATESVILLE (AWOS) | BATESVILLE (AWOS), AR, USA | 35.73N | 91.65W | 141 | -6.00 (NAC) | 92-06 | 723448 | -12.8 | -13 | -18 | 42.5 | 35.2 | 37.6 | 38.7 | 37 | 37.1667 | 38 | 33.7 | 36.2 | 36.4 | 35 | 35.4333 | 35 | 104 | United_StatesArkansasBATESVILLE (AWOS)
United_States | Arkansas | M2 | BENTONVILLE (AWOS) | BENTONVILLE (AWOS), AR, USA | 36.35N | 94.22W | 395 | -6.00 (NAC) | 92-06 | 723444 | -16.2 | -16 | -23.8 | 41.1 | 33 | 36.3 | 37.1 | 35 | 35.4667 | 36 | 31.9 | 34.1 | 35 | 34 | 33.6667 | 34 | 105 | United_StatesArkansasBENTONVILLE (AWOS)
United_States | Arkansas | M2 | EAKER AFB | EAKER AFB, AR, USA | 35.97N | 89.95W | 80 | -6.00 (NAC) | 82-92 | 723408 | -14.9 | -15 | -28 | 43.7 | 37.3 | 38.6 | 37.2 | 38 | 37.7 | 39 | 35.3 | 36.3 | 35.5 | 36 | 35.7 | 36 | 106 | United_StatesArkansasEAKER AFB
United_States | Arkansas | M2 | EL DORADO GOODWIN FIELD | EL DORADO GOODWIN FIELD, AR, USA | 33.22N | 92.81W | 87 | -6.00 (NAC) | 91-06 | 723419 | -9.2 | -9 | -14 | 44.9 | 35.1 | 37.9 | 39.8 | 38 | 37.6 | 38 | 33.8 | 36.3 | 37.5 | 36 | 35.8667 | 36 | 107 | United_StatesArkansasEL DORADO GOODWIN FIELD
United_States | Arkansas | M2 | FAYETTEVILLE DRAKE FIELD | FAYETTEVILLE DRAKE FIELD, AR, USA | 36.01N | 94.17W | 384 | -6.00 (NAC) | 82-06 | 723445 | -17.2 | -17 | -29.2 | 42.3 | 33.7 | 37.1 | 37 | 36 | 35.9333 | 37 | 32.3 | 35 | 35.5 | 34 | 34.2667 | 34 | 108 | United_StatesArkansasFAYETTEVILLE DRAKE FIELD
United_States | Arkansas | M2 | FLIPPIN (AWOS) | FLIPPIN (AWOS), AR, USA | 36.30N | 92.47W | 350 | -6.00 (NAC) | 92-06 | 723447 | -14.9 | -15 | -19.4 | 43.8 | 34.9 | 37.8 | 38.6 | 37 | 37.1 | 38 | 33 | 36.3 | 36.3 | 35 | 35.2 | 35 | 109 | United_StatesArkansasFLIPPIN (AWOS)
United_States | Arkansas | M2 | FORT SMITH REGIONAL AP | FORT SMITH REGIONAL AP, AR, USA | 35.33N | 94.37W | 141 | -6.00 (NAC) | 82-06 | 723440 | -12.6 | -13 | -21.9 | 44.5 | 36.1 | 39.2 | 39.2 | 38 | 38.1667 | 39 | 33.9 | 37.1 | 37.5 | 36 | 36.1667 | 36 | 110 | United_StatesArkansasFORT SMITH REGIONAL AP
United_States | Arkansas | M2 | HARRISON FAA AP | HARRISON FAA AP, AR, USA | 36.26N | 93.16W | 422 | -6.00 (NAC) | 88-06 | 723446 | -15.4 | -15 | -23.1 | 41.5 | 33.6 | 36.4 | 36.9 | 36 | 35.6333 | 36 | 32.1 | 34.5 | 34.8 | 34 | 33.8 | 34 | 111 | United_StatesArkansasHARRISON FAA AP
United_States | Arkansas | M2 | JONESBORO MUNI | JONESBORO MUNI, AR, USA | 35.83N | 90.63W | 82 | -6.00 (NAC) | 82-06 | 723407 | -14.6 | -15 | -25.9 | 41.8 | 36.2 | 37.3 | 37.2 | 37 | 36.9 | 37 | 34.3 | 35.7 | 35.5 | 35 | 35.1667 | 35 | 112 | United_StatesArkansasJONESBORO MUNI
United_States | Arkansas | M2 | LITTLE ROCK ADAMS FIELD | LITTLE ROCK ADAMS FIELD, AR, USA | 34.75N | 92.23W | 78 | -6.00 (NAC) | 82-06 | 723403 | -11.3 | -11 | -20.6 | 44 | 36.1 | 38.6 | 38.9 | 38 | 37.8667 | 39 | 34.1 | 36.4 | 36.9 | 36 | 35.8 | 36 | 113 | United_StatesArkansasLITTLE ROCK ADAMS FIELD
United_States | Arkansas | M2 | LITTLE ROCK AFB | LITTLE ROCK AFB, AR, USA | 34.92N | 92.15W | 103 | -6.00 (NAC) | 82-06 | 723405 | -13.4 | -13 | -22.1 | 44 | 37.2 | 39.9 | 39.8 | 39 | 38.9667 | 40 | 34.7 | 37.4 | 37.4 | 37 | 36.5 | 37 | 114 | United_StatesArkansasLITTLE ROCK AFB
United_States | Arkansas | M2 | LITTLE ROCK/ADAMS F | LITTLE ROCK/ADAMS F, AR, USA | 34.83N | 92.25W | 351 | -6.00 (NAC) | 82-06 | 723400 | -11.7 | -12 | -21.7 | 42.1 | 34.1 | 37 | 37.3 | 36 | 36.1333 | 37 | 32.7 | 35.1 | 35.3 | 34 | 34.3667 | 34 | 115 | United_StatesArkansasLITTLE ROCK/ADAMS F
United_States | Arkansas | M2 | PINE BLUFF FAA AP | PINE BLUFF FAA AP, AR, USA | 34.18N | 91.94W | 65 | -6.00 (NAC) | 88-06 | 723417 | -8.7 | -9 | -16.4 | 41.6 | 35.9 | 37.8 | 37.5 | 37 | 37.0667 | 38 | 34.4 | 36.3 | 36.1 | 36 | 35.6 | 36 | 116 | United_StatesArkansasPINE BLUFF FAA AP
United_States | Arkansas | M2 | ROGERS (AWOS) | ROGERS (AWOS), AR, USA | 36.37N | 94.10W | 415 | -6.00 (NAC) | 92-06 | 723449 | -15.3 | -15 | -20.1 | 40.9 | 32.8 | 36.3 | 37.1 | 35 | 35.4 | 36 | 31.2 | 33.9 | 34.8 | 33 | 33.3 | 33 | 117 | United_StatesArkansasROGERS (AWOS)
United_States | Arkansas | M2 | SILOAM SPRING(AWOS) | SILOAM SPRING(AWOS), AR, USA | 36.18N | 94.48W | 364 | -6.00 (NAC) | 92-06 | 723443 | -15.4 | -15 | -23.9 | 41.8 | 33.5 | 37 | 37.6 | 36 | 36.0333 | 37 | 31.5 | 34.9 | 36 | 34 | 34.1333 | 34 | 118 | United_StatesArkansasSILOAM SPRING(AWOS)
United_States | Arkansas | M2 | STUTTGART (AWOS) | STUTTGART (AWOS), AR, USA | 34.60N | 91.57W | 68 | -6.00 (NAC) | 92-06 | 723416 | -8.7 | -9 | -13.5 | 41.2 | 36.1 | 37.2 | 37.4 | 37 | 36.9 | 37 | 33.9 | 35.8 | 36 | 35 | 35.2333 | 35 | 119 | United_StatesArkansasSTUTTGART (AWOS)
United_States | Arkansas | M2 | TEXARKANA WEBB FIELD | TEXARKANA WEBB FIELD, AR, USA | 33.45N | 94.01W | 122 | -6.00 (NAC) | 82-06 | 723418 | -9.2 | -9 | -17.5 | 43.2 | 36 | 38.6 | 38.6 | 38 | 37.7333 | 39 | 34.1 | 36.7 | 37.2 | 36 | 36 | 36 | 120 | United_StatesArkansasTEXARKANA WEBB FIELD
United_States | Arkansas | M2 | WALNUT RIDGE (AWOS) | WALNUT RIDGE (AWOS), AR, USA | 36.13N | 90.92W | 83 | -6.00 (NAC) | 92-06 | 723406 | -13.2 | -13 | -18.9 | 42.6 | 35.3 | 37.2 | 36.3 | 36 | 36.2667 | 37 | 33.8 | 35.2 | 34.1 | 34 | 34.3667 | 34 | 121 | United_StatesArkansasWALNUT RIDGE (AWOS)
United_States | California | W3 | ALAMEDA NAS | ALAMEDA NAS, CA, USA | 37.73N | 122.32W | 4 | -8.00 (NAP) | 82-96 | 745060 | 2.8 | 3 | -2.7 | 40.4 | 31.1 | 30.1 | 29.1 | 30 | 30.1 | 30 | 26.2 | 26 | 25.7 | 26 | 25.9667 | 26 | 122 | United_StatesCaliforniaALAMEDA NAS
United_States | California | W3 | ARCATA AIRPORT | ARCATA AIRPORT, CA, USA | 40.98N | 124.11W | 64 | -8.00 (NAP) | 82-06 | 725945 | -2.5 | -3 | -6.8 | 33.9 | 21.4 | 21.2 | 21.5 | 21 | 21.3667 | 21 | 18.3 | 19 | 19.8 | 19 | 19.0333 | 19 | 123 | United_StatesCaliforniaARCATA AIRPORT
United_States | California | W2 | BAKERSFIELD MEADOWS FIELD | BAKERSFIELD MEADOWS FIELD, CA, USA | 35.43N | 119.06W | 150 | -8.00 (NAP) | 82-06 | 723840 | -2.2 | -2 | -7.9 | 44.5 | 39.7 | 41.5 | 41 | 41 | 40.7333 | 42 | 37.9 | 39.6 | 39.2 | 39 | 38.9 | 39 | 124 | United_StatesCaliforniaBAKERSFIELD MEADOWS FIELD
United_States | California | W3 | BEALE AFB/MARYSVILE | BEALE AFB/MARYSVILE, CA, USA | 39.13N | 121.43W | 38 | -8.00 (NAP) | 82-02 | 724837 | -2.6 | -3 | -7.4 | 44.9 | 39 | 40.7 | 40 | 40 | 39.9 | 41 | 37 | 38 | 37.8 | 38 | 37.6 | 38 | 125 | United_StatesCaliforniaBEALE AFB/MARYSVILE
United_States | California | W3 | BISHOP AIRPORT | BISHOP AIRPORT, CA, USA | 37.37N | 118.36W | 1263 | -8.00 (NAP) | 82-06 | 724800 | -13.4 | -13 | -22.4 | 43.1 | 38.5 | 40.3 | 39.2 | 39 | 39.3333 | 40 | 36.8 | 38.8 | 37.7 | 38 | 37.7667 | 38 | 126 | United_StatesCaliforniaBISHOP AIRPORT
United_States | California | W3 | BLUE CANYON AP | BLUE CANYON AP, CA, USA | 39.29N | 120.71W | 1610 | -8.00 (NAP) | 82-06 | 725845 | -8.4 | -8 | -14.9 | 35.7 | 28.6 | 30.8 | 30.1 | 30 | 29.8333 | 31 | 26.3 | 28.5 | 28.4 | 28 | 27.7333 | 28 | 127 | United_StatesCaliforniaBLUE CANYON AP
United_States | California | W1 | BLYTHE RIVERSIDE CO ARPT | BLYTHE RIVERSIDE CO ARPT, CA, USA | 33.62N | 114.72W | 120 | -8.00 (NAP) | 88-06 | 747188 | -0.9 | -1 | -5.3 | 51.8 | 45.9 | 47.2 | 46 | 46 | 46.3667 | 47 | 43.7 | 45.1 | 44.2 | 44 | 44.3333 | 44 | 128 | United_StatesCaliforniaBLYTHE RIVERSIDE CO ARPT
United_States | California | W2 | BURBANK-GLENDALE-PASSADENA AP | BURBANK-GLENDALE-PASSADENA AP, CA, USA | 34.20N | 118.36W | 223 | -8.00 (NAP) | 82-06 | 722880 | 1 | 1 | -4.3 | 46 | 36.8 | 38.2 | 38.7 | 38 | 37.9 | 38 | 33 | 35 | 36.1 | 35 | 34.7 | 35 | 129 | United_StatesCaliforniaBURBANK-GLENDALE-PASSADENA AP
United_States | California | W2 | CAMARILLO (AWOS) | CAMARILLO (AWOS), CA, USA | 34.22N | 119.08W | 23 | -8.00 (NAP) | 92-06 | 723926 | 1.1 | 1 | -1.6 | 40.8 | 27.4 | 28 | 30 | 28 | 28.4667 | 28 | 25.1 | 27.1 | 27.6 | 27 | 26.6 | 27 | 130 | United_StatesCaliforniaCAMARILLO (AWOS)
United_States | California | W1 | CAMP PENDLETON MCAS | CAMP PENDLETON MCAS, CA, USA | 33.30N | 117.35W | 24 | -8.00 (NAP) | 85-06 | 722926 | -2.4 | -2 | -7.1 | 44 | 32.3 | 32.3 | 34 | 33 | 32.8667 | 32 | 27.6 | 29.4 | 31 | 29 | 29.3333 | 29 | 131 | United_StatesCaliforniaCAMP PENDLETON MCAS
United_States | California | W1 | CARLSBAD/PALOMAR | CARLSBAD/PALOMAR, CA, USA | 33.13N | 117.28W | 100 | -8.00 (NAP) | 98-06 | 722927 | 3.8 | 4 | 1.1 | 40.1 | 26.1 | 27.9 | 28 | 27 | 27.3333 | 28 | 22.9 | 26.3 | 26.3 | 25 | 25.1667 | 25 | 132 | United_StatesCaliforniaCARLSBAD/PALOMAR
United_States | California | W3 | CASTLE AFB/MERCED | CASTLE AFB/MERCED, CA, USA | 37.38N | 120.57W | 60 | -8.00 (NAP) | 82-93 | 724810 | -2.8 | -3 | -6.8 | 44 | 37.9 | 40.1 | 39.4 | 39 | 39.1333 | 40 | 36 | 37.6 | 37.1 | 37 | 36.9 | 37 | 133 | United_StatesCaliforniaCASTLE AFB/MERCED
United_States | California | W3 | CRESCENT CITY FAA AI | CRESCENT CITY FAA AI, CA, USA | 41.78N | 124.24W | 17 | -8.00 (NAP) | 92-06 | 725946 | -1.2 | -1 | -10.7 | 31.7 | 18 | 19.2 | 21 | 19 | 19.4 | 19 | 17.4 | 18 | 19 | 18 | 18.1333 | 18 | 134 | United_StatesCaliforniaCRESCENT CITY FAA AI
United_States | California | W2 | DAGGETT BARSTOW-DAGGETT AP | DAGGETT BARSTOW-DAGGETT AP, CA, USA | 34.85N | 116.79W | 588 | -8.00 (NAP) | 88-06 | 723815 | -5 | -5 | -11.5 | 48.9 | 42.7 | 44.9 | 43.7 | 44 | 43.7667 | 45 | 41.1 | 43 | 42.3 | 42 | 42.1333 | 42 | 135 | United_StatesCaliforniaDAGGETT BARSTOW-DAGGETT AP
United_States | California | W2 | EDWARDS AFB | EDWARDS AFB, CA, USA | 34.90N | 117.88W | 706 | -8.00 (NAP) | 91-06 | 723810 | -9.5 | -10 | -16.8 | 46.2 | 41.3 | 42.9 | 42.5 | 42 | 42.2333 | 43 | 38.8 | 40.9 | 41.1 | 40 | 40.2667 | 40 | 136 | United_StatesCaliforniaEDWARDS AFB
United_States | California | W1 | EL TORO MCAS | EL TORO MCAS, CA, USA | 33.68N | 117.73W | 117 | -8.00 (NAP) | 82-98 | 690140 | 2.6 | 3 | -2 | 44.6 | 32.9 | 34 | 35.3 | 34 | 34.0667 | 34 | 29.1 | 30.7 | 32.6 | 31 | 30.8 | 31 | 137 | United_StatesCaliforniaEL TORO MCAS
United_States | California | W3 | EUREKA | EUREKA, CA, USA | 40.80N | 124.17W | 18 | -8.00 (NAP) | 82-06 | 725940 | -0.9 | -1 | -3.1 | 34.2 | 18.7 | 19.4 | 20.8 | 20 | 19.6333 | 19 | 17.4 | 18.2 | 19.2 | 18 | 18.2667 | 18 | 138 | United_StatesCaliforniaEUREKA
United_States | California | W2 | FRESNO YOSEMITE INTL AP | FRESNO YOSEMITE INTL AP, CA, USA | 36.78N | 119.72W | 100 | -8.00 (NAP) | 82-06 | 723890 | -1.9 | -2 | -7.6 | 44.8 | 40.2 | 41.9 | 40.9 | 41 | 41 | 42 | 38.3 | 40.1 | 39.2 | 39 | 39.2 | 39 | 139 | United_StatesCaliforniaFRESNO YOSEMITE INTL AP
United_States | California | W1 | FULLERTON MUNICIPAL | FULLERTON MUNICIPAL, CA, USA | 33.87N | 117.98W | 29 | -8.00 (NAP) | 98-06 | 722976 | 2.2 | 2 | -0.4 | 43.6 | 32.8 | 34 | 35 | 34 | 33.9333 | 34 | 29 | 32.3 | 32.7 | 31 | 31.3333 | 31 | 140 | United_StatesCaliforniaFULLERTON MUNICIPAL
United_States | California | W2 | GEORGE AFB | GEORGE AFB, CA, USA | 34.58N | 117.38W | 876 | -8.00 (NAP) | 82-05 | 723825 | -5.5 | -6 | -11.1 | 44.9 | 37.9 | 41.5 | 38.8 | 39 | 39.4 | 42 | 36.4 | 39 | 37.5 | 38 | 37.6333 | 38 | 141 | United_StatesCaliforniaGEORGE AFB
United_States | California | W3 | HAYWARD AIR TERM | HAYWARD AIR TERM, CA, USA | 37.66N | 122.12W | 14 | -8.00 (NAP) | 98-06 | 724935 | 1 | 1 | -1.6 | 42.8 | 33.6 | 33.1 | 32 | 33 | 32.9 | 33 | 28.1 | 28.5 | 27.2 | 28 | 27.9333 | 28 | 142 | United_StatesCaliforniaHAYWARD AIR TERM
United_States | California | W1 | IMPERIAL | IMPERIAL, CA, USA | 32.83N | 115.58W | -17 | -8.00 (NAP) | 88-06 | 747185 | -0.9 | -1 | -5.8 | 51.4 | 44.6 | 46.3 | 45.6 | 46 | 45.5 | 46 | 42.8 | 44 | 43.7 | 44 | 43.5 | 44 | 143 | United_StatesCaliforniaIMPERIAL
United_States | California | W1 | JACK NORTHROP FLD H | JACK NORTHROP FLD H, CA, USA | 33.92N | 118.33W | 21 | -8.00 (NAP) | 98-06 | 722956 | 3.9 | 4 | -1.9 | 40.6 | 27.7 | 30.8 | 28.9 | 29 | 29.1333 | 31 | 24.1 | 27.7 | 27.3 | 26 | 26.3667 | 26 | 144 | United_StatesCaliforniaJACK NORTHROP FLD H
United_States | California | W2 | LANCASTER GEN WM FOX FIELD | LANCASTER GEN WM FOX FIELD, CA, USA | 34.74N | 118.22W | 713 | -8.00 (NAP) | 82-06 | 723816 | -9 | -9 | -14.9 | 45 | 38.9 | 41.7 | 40.9 | 41 | 40.5 | 42 | 37 | 39.4 | 38.9 | 38 | 38.4333 | 38 | 145 | United_StatesCaliforniaLANCASTER GEN WM FOX FIELD
United_States | California | W2 | LEMOORE REEVES NAS | LEMOORE REEVES NAS, CA, USA | 36.33N | 119.95W | 71 | -8.00 (NAP) | 82-06 | 747020 | -3.4 | -3 | -9.8 | 47.1 | 40.6 | 41.2 | 40.9 | 41 | 40.9 | 41 | 38.5 | 39.4 | 38.9 | 39 | 38.9333 | 39 | 146 | United_StatesCaliforniaLEMOORE REEVES NAS
United_States | California | W3 | LIVERMORE MUNICIPAL | LIVERMORE MUNICIPAL, CA, USA | 37.69N | 121.82W | 121 | -8.00 (NAP) | 98-06 | 724927 | -2.8 | -3 | -4.5 | 45.6 | 37.9 | 41.3 | 38.5 | 39 | 39.2333 | 41 | 34.6 | 37.2 | 35.9 | 36 | 35.9 | 36 | 147 | United_StatesCaliforniaLIVERMORE MUNICIPAL
United_States | California | W2 | LOMPOC (AWOS) | LOMPOC (AWOS), CA, USA | 34.67N | 120.47W | 27 | -8.00 (NAP) | 92-06 | 722895 | -2.2 | -2 | -4.8 | 49.8 | 27.4 | 26 | 26.3 | 27 | 26.5667 | 26 | 23 | 23 | 23.7 | 23 | 23.2333 | 23 | 148 | United_StatesCaliforniaLOMPOC (AWOS)
United_States | California | W1 | LONG BEACH DAUGHERTY FLD | LONG BEACH DAUGHERTY FLD, CA, USA | 33.83N | 118.16W | 12 | -8.00 (NAP) | 82-06 | 722970 | 2.3 | 2 | -1.5 | 44.7 | 32.2 | 33.1 | 35 | 33 | 33.4333 | 33 | 28 | 30.4 | 31.7 | 30 | 30.0333 | 30 | 149 | United_StatesCaliforniaLONG BEACH DAUGHERTY FLD
United_States | California | W1 | LOS ANGELES INTL ARPT | LOS ANGELES INTL ARPT, CA, USA | 33.94N | 118.41W | 99 | -8.00 (NAP) | 82-06 | 722950 | 4.4 | 4 | 0.7 | 40.9 | 26.4 | 28.1 | 29.5 | 28 | 28 | 28 | 23.8 | 26 | 26.9 | 26 | 25.5667 | 26 | 150 | United_StatesCaliforniaLOS ANGELES INTL ARPT
United_States | California | W1 | MARCH AFB/RIVERSIDE | MARCH AFB/RIVERSIDE, CA, USA | 33.88N | 117.27W | 462 | -8.00 (NAP) | 82-06 | 722860 | -1.8 | -2 | -6.2 | 45.6 | 38.1 | 39.9 | 40.2 | 39 | 39.4 | 40 | 35.6 | 37.4 | 37.9 | 37 | 36.9667 | 37 | 151 | United_StatesCaliforniaMARCH AFB/RIVERSIDE
United_States | California | W3 | MCCLELLAN AFB | MCCLELLAN AFB, CA, USA | 38.67N | 121.40W | 25 | -8.00 (NAP) | 82-00 | 724836 | -2.7 | -3 | -9.7 | 44.8 | 39.4 | 41 | 41.1 | 41 | 40.5 | 41 | 37.3 | 38.7 | 38.7 | 38 | 38.2333 | 38 | 152 | United_StatesCaliforniaMCCLELLAN AFB
United_States | California | W3 | MODESTO CITY-COUNTY AP | MODESTO CITY-COUNTY AP, CA, USA | 37.63N | 120.95W | 30 | -8.00 (NAP) | 86-06 | 724926 | -2.3 | -2 | -4.6 | 45.8 | 39.4 | 42 | 39 | 40 | 40.1333 | 42 | 36.9 | 39 | 37.3 | 38 | 37.7333 | 38 | 153 | United_StatesCaliforniaMODESTO CITY-COUNTY AP
United_States | California | W3 | MONTAGUE SISKIYOU COUNTY AP | MONTAGUE SISKIYOU COUNTY AP, CA, USA | 41.78N | 122.47W | 805 | -8.00 (NAP) | 90-06 | 725955 | -12 | N/A | N/A | N/A | 35.1 | 37.9 | 37.3 | 37 | 36.7667 | 38 | 32 | 36.3 | 35.1 | 34 | 34.4667 | 34 | 154 | United_StatesCaliforniaMONTAGUE SISKIYOU COUNTY AP
United_States | California | W2 | MONTEREY PENINSULA | MONTEREY PENINSULA, CA, USA | 36.58N | 121.85W | 50 | -8.00 (NAP) | 88-06 | 724915 | 1 | 1 | -0.4 | 39 | 27.3 | 23.8 | 24.7 | 25 | 25.2667 | 24 | 22.3 | 22 | 22.2 | 22 | 22.1667 | 22 | 155 | United_StatesCaliforniaMONTEREY PENINSULA
United_States | California | W3 | MOUNT SHASTA | MOUNT SHASTA, CA, USA | 41.33N | 122.33W | 1078 | -8.00 (NAP) | 82-06 | 725957 | -12 | -12 | -21.4 | 38.9 | 31.8 | 34.9 | 34.6 | 34 | 33.7667 | 35 | 29.1 | 32.7 | 32.4 | 31 | 31.4 | 31 | 156 | United_StatesCaliforniaMOUNT SHASTA
United_States | California | W3 | MOUNTAIN VIEW MOFFETT FLD NAS | MOUNTAIN VIEW MOFFETT FLD NAS, CA, USA | 37.42N | 122.05W | 10 | -8.00 (NAP) | 82-06 | 745090 | -0.2 | 0 | -5.3 | 40.4 | 33.6 | 33.1 | 32.4 | 33 | 33.0333 | 33 | 28.6 | 29 | 28.5 | 29 | 28.7 | 29 | 157 | United_StatesCaliforniaMOUNTAIN VIEW MOFFETT FLD NAS
United_States | California | W3 | NAPA CO. AIRPORT | NAPA CO. AIRPORT, CA, USA | 38.21N | 122.28W | 17 | -8.00 (NAP) | 98-06 | 724955 | -4.2 | -4 | -6.7 | 44 | 35.2 | 35.2 | 34.7 | 35 | 35.0333 | 35 | 31 | 30.7 | 30.3 | 31 | 30.6667 | 31 | 158 | United_StatesCaliforniaNAPA CO. AIRPORT
United_States | California | W2 | NORTON AFB/SAN BERN | NORTON AFB/SAN BERN, CA, USA | 34.10N | 117.23W | 353 | -8.00 (NAP) | 82-93 | 722866 | -1.6 | -2 | -5.6 | 46.2 | 39.5 | 41 | 41 | 41 | 40.5 | 41 | 37 | 38.7 | 38.7 | 38 | 38.1333 | 38 | 159 | United_StatesCaliforniaNORTON AFB/SAN BERN
United_States | California | W3 | OAKLAND METROPOLITAN ARPT | OAKLAND METROPOLITAN ARPT, CA, USA | 37.76N | 122.22W | 27 | -8.00 (NAP) | 82-06 | 724930 | 0.8 | 1 | -3.8 | 39 | 29.2 | 29.4 | 28.9 | 29 | 29.1667 | 29 | 24.6 | 25.4 | 25 | 25 | 25 | 25 | 160 | United_StatesCaliforniaOAKLAND METROPOLITAN ARPT
United_States | California | W2 | ONTARIO | ONTARIO, CA, USA | 34.07N | 117.65W | 304 | -8.00 (NAP) | 82-01 | 722865 | -0.8 | -1 | -5.9 | 45.9 | 38.6 | 39.3 | 40.2 | 39 | 39.3667 | 39 | 35.1 | 36.9 | 37.8 | 37 | 36.6 | 37 | 161 | United_StatesCaliforniaONTARIO
United_States | California | W1 | PALM SPRINGS INTL | PALM SPRINGS INTL, CA, USA | 33.83N | 116.50W | 145 | -8.00 (NAP) | 98-06 | 722868 | 2.6 | 3 | -0.1 | 51.4 | 44 | 47.4 | 46.1 | 46 | 45.8333 | 47 | 42.7 | 44.9 | 43.7 | 44 | 43.7667 | 44 | 162 | United_StatesCaliforniaPALM SPRINGS INTL
United_States | California | W1 | PALM SPRINGS THERMAL AP | PALM SPRINGS THERMAL AP, CA, USA | 33.63N | 116.16W | -36 | -8.00 (NAP) | 82-06 | 747187 | -4.6 | -5 | -10 | 53.5 | 45.6 | 47.3 | 46 | 46 | 46.3 | 47 | 42.9 | 44.1 | 43.7 | 44 | 43.5667 | 44 | 163 | United_StatesCaliforniaPALM SPRINGS THERMAL AP
United_States | California | W2 | PASO ROBLES MUNICIPAL ARPT | PASO ROBLES MUNICIPAL ARPT, CA, USA | 35.67N | 120.63W | 249 | -8.00 (NAP) | 82-06 | 723965 | -5.6 | -6 | -11.5 | 46.8 | 39.6 | 41.6 | 41.5 | 41 | 40.9 | 42 | 36.5 | 38.6 | 38.7 | 38 | 37.9333 | 38 | 164 | United_StatesCaliforniaPASO ROBLES MUNICIPAL ARPT
United_States | California | W3 | POINT ARENA | POINT ARENA, CA, USA | 38.95N | 123.73W | 19 | -8.00 (NAP) | 85-06 | 994120 | 1.5 | 2 | -3 | 28.2 | 15.7 | 16.5 | 17.5 | 17 | 16.5667 | 17 | 14.8 | 15.3 | 16.2 | 15 | 15.4333 | 15 | 165 | United_StatesCaliforniaPOINT ARENA
United_States | California | W2 | POINT ARGUELLO | POINT ARGUELLO, CA, USA | 34.57N | 120.63W | 34 | -8.00 (NAP) | 85-06 | 994210 | 5.4 | 5 | 0.3 | 28.3 | 18 | 20.8 | 18.8 | 19 | 19.2 | 21 | 16.5 | 18.5 | 17.5 | 18 | 17.5 | 18 | 166 | United_StatesCaliforniaPOINT ARGUELLO
United_States | California | W2 | POINT MUGU NF | POINT MUGU NF, CA, USA | 34.12N | 119.12W | 4 | -8.00 (NAP) | 82-06 | 723910 | 2 | 2 | -2.2 | 40.7 | 24.5 | 26.4 | 27.3 | 26 | 26.0667 | 26 | 22.8 | 24.5 | 25.4 | 24 | 24.2333 | 24 | 167 | United_StatesCaliforniaPOINT MUGU NF
United_States | California | W2 | PORTERVILLE (AWOS) | PORTERVILLE (AWOS), CA, USA | 36.03N | 119.07W | 135 | -8.00 (NAP) | 92-06 | 723895 | -2.3 | -2 | -5.1 | 43.9 | 39.1 | 40.9 | 39.1 | 40 | 39.7 | 41 | 37.5 | 38 | 37.7 | 38 | 37.7333 | 38 | 168 | United_StatesCaliforniaPORTERVILLE (AWOS)
United_States | California | W2 | PT.PIEDRAS BLANCA | PT.PIEDRAS BLANCA, CA, USA | 35.67N | 121.29W | 21 | -8.00 (NAP) | 82-05 | 723900 | 3.4 | 3 | -2.1 | 35.7 | 23.8 | 21.2 | 22.8 | 23 | 22.6 | 21 | 20 | 18.9 | 21.1 | 20 | 20 | 20 | 169 | United_StatesCaliforniaPT.PIEDRAS BLANCA
United_States | California | W3 | RED BLUFF MUNICIPAL ARPT | RED BLUFF MUNICIPAL ARPT, CA, USA | 40.15N | 122.25W | 108 | -8.00 (NAP) | 82-06 | 725910 | -3.7 | -4 | -8.3 | 47.7 | 41.2 | 43.6 | 42.3 | 42 | 42.3667 | 44 | 38.2 | 40.9 | 39.8 | 40 | 39.6333 | 40 | 170 | United_StatesCaliforniaRED BLUFF MUNICIPAL ARPT
United_States | California | W3 | REDDING MUNICIPAL ARPT | REDDING MUNICIPAL ARPT, CA, USA | 40.52N | 122.31W | 153 | -8.00 (NAP) | 86-06 | 725920 | -4.4 | -4 | -8.6 | 49.1 | 41.3 | 44 | 42.8 | 43 | 42.7 | 44 | 38.4 | 41.3 | 40.5 | 40 | 40.0667 | 40 | 171 | United_StatesCaliforniaREDDING MUNICIPAL ARPT
United_States | California | W1 | RIVERSIDE MUNI | RIVERSIDE MUNI, CA, USA | 33.95N | 117.43W | 256 | -8.00 (NAP) | 98-06 | 722869 | -0.9 | -1 | -4.1 | 46 | 37.2 | 38.7 | 39.1 | 38 | 38.3333 | 39 | 34.1 | 37.2 | 37.5 | 36 | 36.2667 | 36 | 172 | United_StatesCaliforniaRIVERSIDE MUNI
United_States | California | W3 | SACRAMENTO EXECUTIVE ARPT | SACRAMENTO EXECUTIVE ARPT, CA, USA | 38.51N | 121.49W | 8 | -8.00 (NAP) | 82-06 | 724830 | -2.6 | -3 | -7.1 | 45.3 | 38.6 | 40.6 | 40.2 | 40 | 39.8 | 41 | 36.2 | 37.9 | 37.3 | 37 | 37.1333 | 37 | 173 | United_StatesCaliforniaSACRAMENTO EXECUTIVE ARPT
United_States | California | W3 | SACRAMENTO MATHER AIRPORT | SACRAMENTO MATHER AIRPORT, CA, USA | 38.55N | 121.29W | 29 | -8.00 (NAP) | 82-06 | 724833 | -3.2 | -3 | -9.3 | 46.5 | 38.8 | 42.2 | 40.1 | 40 | 40.3667 | 42 | 36.4 | 38.9 | 37.7 | 38 | 37.6667 | 38 | 174 | United_StatesCaliforniaSACRAMENTO MATHER AIRPORT
United_States | California | W3 | SACRAMENTO METROPOLITAN AP | SACRAMENTO METROPOLITAN AP, CA, USA | 38.70N | 121.59W | 10 | -8.00 (NAP) | 82-06 | 724839 | -2.7 | -3 | -9.1 | 44.8 | 38.9 | 41.1 | 40.5 | 40 | 40.1667 | 41 | 36.7 | 38 | 37.7 | 37 | 37.4667 | 37 | 175 | United_StatesCaliforniaSACRAMENTO METROPOLITAN AP
United_States | California | W2 | SALINAS MUNICIPAL AP | SALINAS MUNICIPAL AP, CA, USA | 36.66N | 121.61W | 24 | -8.00 (NAP) | 82-06 | 724917 | -1.2 | -1 | -4.7 | 41 | 29.1 | 28.5 | 27.9 | 29 | 28.5 | 29 | 24.4 | 24.6 | 24.5 | 25 | 24.5 | 25 | 176 | United_StatesCaliforniaSALINAS MUNICIPAL AP
United_States | California | W1 | SAN DIEGO LINDBERGH FIELD | SAN DIEGO LINDBERGH FIELD, CA, USA | 32.74N | 117.17W | 9 | -8.00 (NAP) | 82-06 | 722900 | 5 | 5 | 1.5 | 41.4 | 27.3 | 29.2 | 29.7 | 29 | 28.7333 | 29 | 24.1 | 27 | 27.7 | 26 | 26.2667 | 26 | 177 | United_StatesCaliforniaSAN DIEGO LINDBERGH FIELD
United_States | California | W1 | SAN DIEGO MIRAMAR NAS | SAN DIEGO MIRAMAR NAS, CA, USA | 32.87N | 117.15W | 146 | -8.00 (NAP) | 89-04 | 722930 | 1.2 | 1 | -6.4 | 40.7 | 32 | 32 | 33.9 | 33 | 32.6333 | 32 | 28.3 | 29.2 | 31.3 | 30 | 29.6 | 30 | 178 | United_StatesCaliforniaSAN DIEGO MIRAMAR NAS
United_States | California | W1 | SAN DIEGO NORTH ISLAND NAS | SAN DIEGO NORTH ISLAND NAS, CA, USA | 32.70N | 117.20W | 8 | -8.00 (NAP) | 82-06 | 722906 | 4.4 | 4 | 1.6 | 42 | 26.3 | 27.7 | 28.8 | 28 | 27.6 | 28 | 23.2 | 25.9 | 26.6 | 25 | 25.2333 | 25 | 179 | United_StatesCaliforniaSAN DIEGO NORTH ISLAND NAS
United_States | California | W1 | SAN DIEGO/BROWN FLD | SAN DIEGO/BROWN FLD, CA, USA | 32.57N | 116.98W | 159 | -8.00 (NAP) | 97-06 | 722904 | 1.6 | 2 | -1.2 | 44.1 | 29.1 | 31.1 | 32.4 | 31 | 30.8667 | 31 | 26.1 | 28.6 | 29 | 28 | 27.9 | 28 | 180 | United_StatesCaliforniaSAN DIEGO/BROWN FLD
United_States | California | W1 | SAN DIEGO/MONTGOMER | SAN DIEGO/MONTGOMER, CA, USA | 32.82N | 117.13W | 129 | -8.00 (NAP) | 82-06 | 722903 | 2.8 | 3 | 0.5 | 41.7 | 31 | 32.3 | 32.7 | 32 | 32 | 32 | 26.3 | 28.9 | 29.3 | 28 | 28.1667 | 28 | 181 | United_StatesCaliforniaSAN DIEGO/MONTGOMER
United_States | California | W3 | SAN FRANCISCO INTL AP | SAN FRANCISCO INTL AP, CA, USA | 37.62N | 122.40W | 6 | -8.00 (NAP) | 82-06 | 724940 | 1.8 | 2 | -1.9 | 40.5 | 31.5 | 29.4 | 29.2 | 30 | 30.0333 | 29 | 25.6 | 25.3 | 25 | 25 | 25.3 | 25 | 182 | United_StatesCaliforniaSAN FRANCISCO INTL AP
United_States | California | W3 | SAN JOSE INTL AP | SAN JOSE INTL AP, CA, USA | 37.36N | 121.93W | 15 | -8.00 (NAP) | 82-06 | 724945 | 0 | 0 | -5 | 42.1 | 35.2 | 36 | 34.8 | 35 | 35.3333 | 36 | 31.7 | 32.3 | 32 | 32 | 32 | 32 | 183 | United_StatesCaliforniaSAN JOSE INTL AP
United_States | California | W2 | SAN LUIS CO RGNL | SAN LUIS CO RGNL, CA, USA | 35.23N | 120.63W | 66 | -8.00 (NAP) | 85-06 | 722897 | -1.5 | -2 | -5.8 | 43.4 | 31.6 | 32 | 31.5 | 32 | 31.7 | 32 | 27.6 | 28.2 | 28.2 | 28 | 28 | 28 | 184 | United_StatesCaliforniaSAN LUIS CO RGNL
United_States | California | W2 | SANDBERG | SANDBERG, CA, USA | 34.74N | 118.72W | 1379 | -8.00 (NAP) | 82-06 | 723830 | -5.2 | -5 | -12.1 | 39.1 | 33.6 | 35.2 | 35 | 35 | 34.6 | 35 | 30.8 | 33.1 | 33 | 32 | 32.3 | 32 | 185 | United_StatesCaliforniaSANDBERG
United_States | California | W2 | SANTA BARBARA MUNICIPAL AP | SANTA BARBARA MUNICIPAL AP, CA, USA | 34.43N | 119.84W | 6 | -8.00 (NAP) | 82-06 | 723925 | -1 | -1 | -5.7 | 43.4 | 27.6 | 28.8 | 28.9 | 28 | 28.4333 | 29 | 24.3 | 25.8 | 26.4 | 26 | 25.5 | 26 | 186 | United_StatesCaliforniaSANTA BARBARA MUNICIPAL AP
United_States | California | W2 | SANTA MARIA PUBLIC ARPT | SANTA MARIA PUBLIC ARPT, CA, USA | 34.92N | 120.47W | 73 | -8.00 (NAP) | 82-06 | 723940 | -2.6 | -3 | -6.9 | 41.9 | 28.4 | 29.2 | 28.4 | 29 | 28.6667 | 29 | 24.1 | 25.9 | 25.4 | 25 | 25.1333 | 25 | 187 | United_StatesCaliforniaSANTA MARIA PUBLIC ARPT
United_States | California | W3 | SANTA ROSA (AWOS) | SANTA ROSA (AWOS), CA, USA | 38.51N | 122.81W | 45 | -8.00 (NAP) | 98-06 | 724957 | -3 | -3 | -4.3 | 44 | 37.5 | 37.8 | 36.3 | 37 | 37.2 | 38 | 33.3 | 33.8 | 33.5 | 34 | 33.5333 | 34 | 188 | United_StatesCaliforniaSANTA ROSA (AWOS)
United_States | California | W3 | STOCKTON METROPOLITAN ARPT | STOCKTON METROPOLITAN ARPT, CA, USA | 37.89N | 121.24W | 8 | -8.00 (NAP) | 82-06 | 724920 | -3 | -3 | -7.8 | 45.4 | 39.2 | 41.1 | 39.9 | 40 | 40.0667 | 41 | 36.7 | 38.4 | 37.7 | 38 | 37.6 | 38 | 189 | United_StatesCaliforniaSTOCKTON METROPOLITAN ARPT
United_States | California | W3 | TRAVIS AFB/FAIRFLD | TRAVIS AFB/FAIRFLD, CA, USA | 38.27N | 121.93W | 18 | -8.00 (NAP) | 82-06 | 745160 | -3 | -3 | -9.2 | 46 | 38.7 | 40 | 38.9 | 39 | 39.2 | 40 | 35.5 | 36.9 | 36 | 36 | 36.1333 | 36 | 190 | United_StatesCaliforniaTRAVIS AFB/FAIRFLD
United_States | California | W3 | TRUCKEE-TAHOE | TRUCKEE-TAHOE, CA, USA | 39.32N | 120.13W | 1798 | -8.00 (NAP) | 94-06 | 725846 | -3 | N/A | N/A | N/A | 30.9 | 33.6 | 32.4 | 32 | 32.3 | 34 | 27.9 | 32.3 | 31 | 30 | 30.4 | 30 | 191 | United_StatesCaliforniaTRUCKEE-TAHOE
United_States | California | W1 | TUSTIN MCAF | TUSTIN MCAF, CA, USA | 33.70N | 117.83W | 17 | -8.00 (NAP) | 82-97 | 690160 | 1.6 | 2 | -1.8 | 46.2 | 33.8 | 34 | 35.6 | 34 | 34.4667 | 34 | 29.5 | 31.4 | 33 | 31 | 31.3 | 31 | 192 | United_StatesCaliforniaTUSTIN MCAF
United_States | California | W3 | UKIAH MUNICIPAL AP | UKIAH MUNICIPAL AP, CA, USA | 39.13N | 123.20W | 191 | -8.00 (NAP) | 92-06 | 725905 | -3.3 | -3 | -7.7 | 47 | 37.7 | 41.2 | 41.2 | 40 | 40.0333 | 41 | 35 | 37.6 | 37.8 | 37 | 36.8 | 37 | 193 | United_StatesCaliforniaUKIAH MUNICIPAL AP
United_States | California | W2 | VISALIA MUNI (AWOS) | VISALIA MUNI (AWOS), CA, USA | 36.32N | 119.40W | 89 | -8.00 (NAP) | 92-06 | 723896 | -2.8 | -3 | -7.7 | 42.5 | 38.8 | 39.1 | 38.8 | 39 | 38.9 | 39 | 37.3 | 37.6 | 37.3 | 37 | 37.4 | 37 | 194 | United_StatesCaliforniaVISALIA MUNI (AWOS)
United_States | Colorado | M3 | AKRON WASHINGTON CO AP | AKRON WASHINGTON CO AP, CO, USA | 40.17N | 103.23W | 1409 | -7.00 (NAM) | 88-06 | 724698 | -23.2 | -23 | -34.2 | 41.6 | 36.2 | 37.5 | 35.3 | 36 | 36.3333 | 38 | 33.3 | 35.5 | 33.3 | 34 | 34.0333 | 34 | 195 | United_StatesColoradoAKRON WASHINGTON CO AP
United_States | Colorado | M3 | ALAMOSA SAN LUIS VALLEY RGNL | ALAMOSA SAN LUIS VALLEY RGNL, CO, USA | 37.44N | 105.87W | 2299 | -7.00 (NAM) | 82-06 | 724620 | -29.8 | -30 | -40.5 | 35.1 | 30.8 | 31.8 | 29.8 | 31 | 30.8 | 32 | 28.8 | 30.1 | 28.2 | 29 | 29.0333 | 29 | 196 | United_StatesColoradoALAMOSA SAN LUIS VALLEY RGNL
United_States | Colorado | M3 | ASPEN PITKIN CO SAR | ASPEN PITKIN CO SAR, CO, USA | 39.22N | 106.87W | 2444 | -7.00 (NAM) | 98-06 | 724676 | -24 | -24 | -30.6 | 34.8 | 29 | 32 | 29.1 | 30 | 30.0333 | 32 | 27.5 | 30.2 | 27.7 | 28 | 28.4667 | 28 | 197 | United_StatesColoradoASPEN PITKIN CO SAR
United_States | Colorado | M3 | BUCKLEY ANGB/DENVER | BUCKLEY ANGB/DENVER, CO, USA | 39.72N | 104.75W | 1726 | -7.00 (NAM) | 82-06 | 724695 | -22.3 | -22 | -31.9 | 40.4 | 34.8 | 36.4 | 34.8 | 35 | 35.3333 | 36 | 32.5 | 34.7 | 32.6 | 33 | 33.2667 | 33 | 198 | United_StatesColoradoBUCKLEY ANGB/DENVER
United_States | Colorado | M3 | COLORADO SPRINGS MUNI AP | COLORADO SPRINGS MUNI AP, CO, USA | 38.81N | 104.71W | 1881 | -7.00 (NAM) | 82-06 | 724660 | -22.6 | -23 | -33.5 | 37.8 | 33.3 | 34.7 | 32.7 | 34 | 33.5667 | 35 | 31.3 | 33 | 30.9 | 32 | 31.7333 | 32 | 199 | United_StatesColoradoCOLORADO SPRINGS MUNI AP
United_States | Colorado | M3 | CORTEZ/MONTEZUMA CO | CORTEZ/MONTEZUMA CO, CO, USA | 37.30N | 108.63W | 1803 | -7.00 (NAM) | 96-06 | 724767 | -19 | -19 | -22.9 | 39.9 | 34.1 | 37.2 | 34.1 | 35 | 35.1333 | 37 | 32.8 | 35.2 | 32.7 | 34 | 33.5667 | 34 | 200 | United_StatesColoradoCORTEZ/MONTEZUMA CO
United_States | Colorado | M3 | CRAIG-MOFFAT | CRAIG-MOFFAT, CO, USA | 40.50N | 107.53W | 1915 | -7.00 (NAM) | 82-06 | 725700 | -31.2 | -31 | -46.7 | 38.3 | 32.5 | 34.9 | 32.7 | 33 | 33.3667 | 35 | 30.2 | 32.8 | 31.2 | 31 | 31.4 | 31 | 201 | United_StatesColoradoCRAIG-MOFFAT
United_States | Colorado | M3 | DENVER INTL AP | DENVER INTL AP, CO, USA | 39.83N | 104.66W | 1655 | -7.00 (NAM) | 94-06 | 725650 | -22.7 | -23 | -29.9 | 40.5 | 34.6 | 37.3 | 35.2 | 36 | 35.7 | 37 | 32.8 | 35.5 | 33.6 | 34 | 33.9667 | 34 | 202 | United_StatesColoradoDENVER INTL AP
United_States | Colorado | M3 | DENVER STAPLETON INT'L ARPT | DENVER STAPLETON INT'L ARPT, CO, USA | 39.77N | 104.87W | 1611 | -7.00 (NAM) | 82-95 | 724690 | -24.6 | -25 | -35.1 | 40.7 | 36.1 | 36.4 | 34.8 | 36 | 35.7667 | 36 | 33.3 | 34.6 | 32.9 | 34 | 33.6 | 34 | 203 | United_StatesColoradoDENVER STAPLETON INT'L ARPT
United_States | Colorado | M3 | DENVER/CENTENNIAL | DENVER/CENTENNIAL, CO, USA | 39.57N | 104.85W | 1793 | -7.00 (NAM) | 83-06 | 724666 | -22.9 | -23 | -32.8 | 39.2 | 34 | 36.1 | 33.8 | 35 | 34.6333 | 36 | 32.2 | 33.8 | 32.2 | 33 | 32.7333 | 33 | 204 | United_StatesColoradoDENVER/CENTENNIAL
United_States | Colorado | M3 | DURANGO/LA PLATA CO | DURANGO/LA PLATA CO, CO, USA | 37.15N | 107.75W | 2038 | -7.00 (NAM) | 96-06 | 724625 | -20.7 | -21 | -28 | 38.4 | 32.7 | 34.1 | 32.7 | 33 | 33.1667 | 34 | 31.3 | 32.8 | 31.2 | 32 | 31.7667 | 32 | 205 | United_StatesColoradoDURANGO/LA PLATA CO
United_States | Colorado | M3 | EAGLE COUNTY AP | EAGLE COUNTY AP, CO, USA | 39.64N | 106.92W | 1992 | -7.00 (NAM) | 82-06 | 724675 | -27.7 | -28 | -37.2 | 37.2 | 31.4 | 33 | 31.6 | 32 | 32 | 33 | 29.3 | 32.1 | 29.9 | 30 | 30.4333 | 30 | 206 | United_StatesColoradoEAGLE COUNTY AP
United_States | Colorado | M3 | FORT COLLINS (AWOS) | FORT COLLINS (AWOS), CO, USA | 40.45N | 105.02W | 1529 | -7.00 (NAM) | 92-06 | 724769 | -22.5 | -23 | -31 | 41.2 | 35.9 | 37.6 | 34.9 | 36 | 36.1333 | 38 | 32.7 | 35.7 | 32.7 | 34 | 33.7 | 34 | 207 | United_StatesColoradoFORT COLLINS (AWOS)
United_States | Colorado | M3 | FORT COLLINS(SAWRS) | FORT COLLINS(SAWRS), CO, USA | 40.58N | 105.08W | 1525 | -7.00 (NAM) | 82-94 | 724697 | -23 | -23 | -35.5 | 37.7 | 33.8 | 34.4 | 32.9 | 34 | 33.7 | 34 | 31.3 | 32.4 | 31.1 | 32 | 31.6 | 32 | 208 | United_StatesColoradoFORT COLLINS(SAWRS)
United_States | Colorado | M3 | GRAND JUNCTION WALKER FIELD | GRAND JUNCTION WALKER FIELD, CO, USA | 39.13N | 108.54W | 1475 | -7.00 (NAM) | 82-06 | 724760 | -17.2 | -17 | -28.4 | 42 | 37.5 | 38.6 | 36.5 | 38 | 37.5333 | 39 | 35 | 37 | 34.9 | 36 | 35.6333 | 36 | 209 | United_StatesColoradoGRAND JUNCTION WALKER FIELD
United_States | Colorado | M3 | GREELEY/WELD (AWOS) | GREELEY/WELD (AWOS), CO, USA | 40.43N | 104.63W | 1420 | -7.00 (NAM) | 92-06 | 724768 | -26.9 | -27 | -35.4 | 41.8 | 36.4 | 37.9 | 36 | 37 | 36.7667 | 38 | 33.8 | 36.3 | 33.6 | 35 | 34.5667 | 35 | 210 | United_StatesColoradoGREELEY/WELD (AWOS)
United_States | Colorado | M3 | GUNNISON CO. (AWOS) | GUNNISON CO. (AWOS), CO, USA | 38.53N | 106.93W | 2339 | -7.00 (NAM) | 92-06 | 724677 | -31.1 | -31 | -40.6 | 33.7 | 28.2 | 31.1 | 27.9 | 29 | 29.0667 | 31 | 27.2 | 28.9 | 26.9 | 28 | 27.6667 | 28 | 211 | United_StatesColoradoGUNNISON CO. (AWOS)
United_States | Colorado | M3 | HAYDEN/YAMPA (AWOS) | HAYDEN/YAMPA (AWOS), CO, USA | 40.48N | 107.22W | 2012 | -7.00 (NAM) | 92-06 | 725715 | -24.6 | -25 | -32.3 | 37.7 | 31.1 | 32.9 | 32 | 32 | 32 | 33 | 28.7 | 32.1 | 29.8 | 30 | 30.2 | 30 | 212 | United_StatesColoradoHAYDEN/YAMPA (AWOS)
United_States | Colorado | M3 | LA JUNTA MUNICIPAL AP | LA JUNTA MUNICIPAL AP, CO, USA | 38.05N | 103.53W | 1285 | -7.00 (NAM) | 83-06 | 724635 | -21 | -21 | -33.4 | 44.1 | 38.9 | 39.5 | 38.5 | 39 | 38.9667 | 40 | 36.8 | 38 | 36.7 | 37 | 37.1667 | 37 | 213 | United_StatesColoradoLA JUNTA MUNICIPAL AP
United_States | Colorado | M3 | LAMAR MUNICIPAL | LAMAR MUNICIPAL, CO, USA | 38.07N | 102.68W | 1129 | -7.00 (NAM) | 95-06 | 724636 | -21.8 | -22 | -33.9 | 43.8 | 38.7 | 40.1 | 37.9 | 39 | 38.9 | 40 | 36.4 | 38 | 37 | 37 | 37.1333 | 37 | 214 | United_StatesColoradoLAMAR MUNICIPAL
United_States | Colorado | M3 | LIMON | LIMON, CO, USA | 39.19N | 103.72W | 1635 | -7.00 (NAM) | 82-06 | 724665 | -24.7 | -25 | -33.7 | 39.9 | 34 | 36.3 | 33.8 | 35 | 34.7 | 36 | 32.1 | 33.9 | 32 | 33 | 32.6667 | 33 | 215 | United_StatesColoradoLIMON
United_States | Colorado | M3 | MONTROSE CO. ARPT | MONTROSE CO. ARPT, CO, USA | 38.50N | 107.90W | 1755 | -7.00 (NAM) | 93-06 | 724765 | -18.5 | -19 | -26.4 | 38.5 | 35.2 | 37 | 34.2 | 35 | 35.4667 | 37 | 32.9 | 35.1 | 32.7 | 34 | 33.5667 | 34 | 216 | United_StatesColoradoMONTROSE CO. ARPT
United_States | Colorado | M3 | PUEBLO MEMORIAL AP | PUEBLO MEMORIAL AP, CO, USA | 38.29N | 104.50W | 1439 | -7.00 (NAM) | 82-06 | 724640 | -23.8 | -24 | -34.7 | 41.7 | 37.8 | 39.3 | 37.2 | 38 | 38.1 | 39 | 35.9 | 37.5 | 35.4 | 36 | 36.2667 | 36 | 217 | United_StatesColoradoPUEBLO MEMORIAL AP
United_States | Colorado | M3 | RIFLE/GARFIELD RGNL | RIFLE/GARFIELD RGNL, CO, USA | 39.53N | 107.72W | 1691 | -7.00 (NAM) | 97-06 | 725717 | -22 | -22 | -30.3 | 40.1 | 35.9 | 37.7 | 36 | 37 | 36.5333 | 38 | 33.6 | 36.4 | 33 | 34 | 34.3333 | 34 | 218 | United_StatesColoradoRIFLE/GARFIELD RGNL
United_States | Colorado | M3 | TRINIDAD LAS ANIMAS COUNTY AP | TRINIDAD LAS ANIMAS COUNTY AP, CO, USA | 37.26N | 104.34W | 1751 | -7.00 (NAM) | 82-06 | 724645 | -22.6 | -23 | -33.1 | 39.7 | 35.4 | 35.9 | 34.1 | 35 | 35.1333 | 36 | 33.1 | 34.1 | 32.6 | 33 | 33.2667 | 33 | 219 | United_StatesColoradoTRINIDAD LAS ANIMAS COUNTY AP
United_States | Connecticut | E4 | BRIDGEPORT SIKORSKY MEMORIAL | BRIDGEPORT SIKORSKY MEMORIAL, CT, USA | 41.18N | 73.15W | 5 | -5.00 (NAE) | 89-06 | 725040 | -14.3 | -14 | -22.1 | 40.6 | 31.5 | 33.3 | 32.8 | 33 | 32.5333 | 33 | 29.2 | 31.2 | 30.4 | 30 | 30.2667 | 30 | 220 | United_StatesConnecticutBRIDGEPORT SIKORSKY MEMORIAL
United_States | Connecticut | E4 | HARTFORD BRADLEY INTL AP | HARTFORD BRADLEY INTL AP, CT, USA | 41.94N | 72.68W | 55 | -5.00 (NAE) | 82-06 | 725080 | -19.7 | -20 | -28.4 | 39.5 | 34 | 35.4 | 34.7 | 35 | 34.7 | 35 | 31.9 | 33.2 | 32.2 | 32 | 32.4333 | 32 | 221 | United_StatesConnecticutHARTFORD BRADLEY INTL AP
United_States | Connecticut | E4 | HARTFORD BRAINARD FD | HARTFORD BRAINARD FD, CT, USA | 41.74N | 72.65W | 6 | -5.00 (NAE) | 83-06 | 725087 | -19.5 | N/A | N/A | N/A | 33.9 | 35.8 | 34.1 | 35 | 34.6 | 36 | 31.5 | 32.7 | 31.9 | 32 | 32.0333 | 32 | 222 | United_StatesConnecticutHARTFORD BRAINARD FD
United_States | Connecticut | E4 | OXFORD (AWOS) | OXFORD (AWOS), CT, USA | 41.48N | 73.13W | 222 | -5.00 (NAE) | 92-06 | 725029 | -19 | -19 | -25.7 | 37.6 | 31.3 | 32.9 | 32.5 | 32 | 32.2333 | 33 | 29 | 31 | 29.7 | 30 | 29.9 | 30 | 223 | United_StatesConnecticutOXFORD (AWOS)
United_States | Connecticut | E4 | WILLIMANTIC (ASOS) | WILLIMANTIC (ASOS), CT, USA | 41.73N | 72.18W | 76 | -5.00 (NAE) | 97-06 | 725084 | -19 | -19 | -24.9 | 38.4 | 32.7 | 34 | 33 | 33 | 33.2333 | 34 | 31.2 | 32.2 | 31.1 | 32 | 31.5 | 32 | 224 | United_StatesConnecticutWILLIMANTIC (ASOS)
United_States | Delaware | E3 | DOVER AFB | DOVER AFB, DE, USA | 39.13N | 75.47W | 7 | -5.00 (NAE) | 82-06 | 724088 | -13.4 | -13 | -22 | 40.3 | 34.2 | 36 | 34.7 | 35 | 34.9667 | 36 | 32.3 | 33.9 | 32.5 | 33 | 32.9 | 33 | 225 | United_StatesDelawareDOVER AFB
United_States | Delaware | E3 | GEORGETOWN/SUSSEX | GEORGETOWN/SUSSEX, DE, USA | 38.68N | 75.37W | 16 | -5.00 (NAE) | 97-06 | 724093 | -11.4 | -11 | -18.1 | 39.8 | 33.7 | 35.9 | 34.9 | 35 | 34.8333 | 36 | 32.4 | 33.6 | 32.9 | 33 | 32.9667 | 33 | 226 | United_StatesDelawareGEORGETOWN/SUSSEX
United_States | Delaware | E3 | WILMINGTON NEW CASTLE CNTY AP | WILMINGTON NEW CASTLE CNTY AP, DE, USA | 39.67N | 75.60W | 24 | -5.00 (NAE) | 82-06 | 724089 | -15.3 | -15 | -27 | 39.8 | 33.9 | 35.7 | 34.5 | 35 | 34.7 | 36 | 31.8 | 33.7 | 32.4 | 33 | 32.6333 | 33 | 227 | United_StatesDelawareWILMINGTON NEW CASTLE CNTY AP
United_States | Florida | E1 | APALACHICOLA MUNI AP | APALACHICOLA MUNI AP, FL, USA | 29.73N | 85.03W | 6 | -5.00 (NAE) | 82-06 | 722200 | -4.6 | -5 | -14.5 | 38.7 | 33.5 | 34.6 | 34.4 | 34 | 34.1667 | 35 | 32.3 | 33 | 33 | 33 | 32.7667 | 33 | 228 | United_StatesFloridaAPALACHICOLA MUNI AP
United_States | Florida | E1 | CAPE SAN BLAS | CAPE SAN BLAS, FL, USA | 29.67N | 85.37W | 2 | -6.00 (NAC) | 85-04 | 994360 | -1.8 | -2 | -10.2 | 34.7 | 30 | 30.7 | 31.4 | 31 | 30.7 | 31 | 29.2 | 30 | 30.5 | 30 | 29.9 | 30 | 229 | United_StatesFloridaCAPE SAN BLAS
United_States | Florida | E1 | CECIL FIELD | CECIL FIELD, FL, USA | 30.22N | 81.87W | 27 | -5.00 (NAE) | 82-98 | 722067 | -5.6 | -6 | -15 | 40.4 | 37.4 | 36.9 | 36.3 | 37 | 36.8667 | 37 | 35.7 | 35.5 | 35 | 35 | 35.4 | 35 | 230 | United_StatesFloridaCECIL FIELD
United_States | Florida | E1 | CRESTVIEW BOB SIKES AP | CRESTVIEW BOB SIKES AP, FL, USA | 30.78N | 86.52W | 56 | -6.00 (NAC) | 82-06 | 722215 | -8.7 | -9 | -15.7 | 40.8 | 36.7 | 37 | 36.2 | 37 | 36.6333 | 37 | 34.7 | 35.1 | 34.3 | 35 | 34.7 | 35 | 231 | United_StatesFloridaCRESTVIEW BOB SIKES AP
United_States | Florida | E1 | CROSS CITY AIRPORT | CROSS CITY AIRPORT, FL, USA | 29.55N | 83.11W | 13 | -5.00 (NAE) | 82-06 | 722120 | -6.2 | -6 | -10.5 | 39.2 | 35.7 | 35.9 | 35.6 | 36 | 35.7333 | 36 | 33.6 | 34.1 | 34.1 | 34 | 33.9333 | 34 | 232 | United_StatesFloridaCROSS CITY AIRPORT
United_States | Florida | E1 | DAYTONA BEACH INTL AP | DAYTONA BEACH INTL AP, FL, USA | 29.18N | 81.06W | 13 | -5.00 (NAE) | 82-06 | 722056 | -2.3 | -2 | -9.5 | 38.7 | 35.5 | 35.1 | 34.5 | 35 | 35.0333 | 35 | 33.1 | 33.5 | 33.2 | 33 | 33.2667 | 33 | 233 | United_StatesFloridaDAYTONA BEACH INTL AP
United_States | Florida | E1 | DESTIN FT. WALTON | DESTIN FT. WALTON, FL, USA | 30.40N | 86.47W | 7 | -6.00 (NAC) | 97-06 | 722069 | -6.3 | N/A | N/A | N/A | 32.5 | 34.1 | 33.9 | 34 | 33.5 | 34 | 31.3 | 32.7 | 32.7 | 32 | 32.2333 | 32 | 234 | United_StatesFloridaDESTIN FT. WALTON
United_States | Florida | E1 | EGLIN AFB/VALPARAIS | EGLIN AFB/VALPARAIS, FL, USA | 30.48N | 86.53W | 20 | -6.00 (NAC) | 82-06 | 722210 | -6.3 | -6 | -14.8 | 39.4 | 33.9 | 35.6 | 34.8 | 35 | 34.7667 | 36 | 32.4 | 33.7 | 33 | 33 | 33.0333 | 33 | 235 | United_StatesFloridaEGLIN AFB/VALPARAIS
United_States | Florida | E1 | FORT LAUDERDALE HOLLYWOOD INT | FORT LAUDERDALE HOLLYWOOD INT, FL, USA | 26.07N | 80.15W | 3 | -5.00 (NAE) | 82-06 | 722025 | 4.5 | 5 | -3.1 | 40.2 | 34.3 | 34.1 | 34.1 | 34 | 34.1667 | 34 | 32.7 | 32.9 | 32.9 | 33 | 32.8333 | 33 | 236 | United_StatesFloridaFORT LAUDERDALE HOLLYWOOD INT
United_States | Florida | E1 | FORT MYERS PAGE FIELD | FORT MYERS PAGE FIELD, FL, USA | 26.59N | 81.86W | 6 | -5.00 (NAE) | 82-06 | 722106 | 1.5 | 2 | -4.4 | 38 | 35.1 | 35.1 | 35.1 | 35 | 35.1 | 35 | 33.9 | 34.1 | 34 | 34 | 34 | 34 | 237 | United_StatesFloridaFORT MYERS PAGE FIELD
United_States | Florida | E1 | GAINESVILLE REGIONAL AP | GAINESVILLE REGIONAL AP, FL, USA | 29.69N | 82.27W | 50 | -5.00 (NAE) | 82-06 | 722146 | -5.2 | -5 | -12 | 40.9 | 35.9 | 35.2 | 35 | 35 | 35.3667 | 35 | 34 | 34 | 33.7 | 34 | 33.9 | 34 | 238 | United_StatesFloridaGAINESVILLE REGIONAL AP
United_States | Florida | E1 | HOMESTEAD AFB | HOMESTEAD AFB, FL, USA | 25.48N | 80.38W | 5 | -5.00 (NAE) | 82-06 | 722026 | 4.6 | 5 | -2 | 37.2 | 33.6 | 34 | 33.7 | 34 | 33.7667 | 34 | 32.4 | 32.7 | 32.7 | 33 | 32.6 | 33 | 239 | United_StatesFloridaHOMESTEAD AFB
United_States | Florida | E1 | HURLBURT FIELD (AF) | HURLBURT FIELD (AF), FL, USA | 30.43N | 86.68W | 12 | -6.00 (NAC) | 83-06 | 747770 | -5.2 | -5 | -11.7 | 39 | 33.9 | 35.1 | 34.9 | 35 | 34.6333 | 35 | 32.4 | 33.2 | 33.1 | 33 | 32.9 | 33 | 240 | United_StatesFloridaHURLBURT FIELD (AF)
United_States | Florida | E1 | JACKSONVILLE INTL ARPT | JACKSONVILLE INTL ARPT, FL, USA | 30.49N | 81.69W | 10 | -5.00 (NAE) | 82-06 | 722060 | -5.3 | -5 | -12.7 | 39.8 | 36.3 | 36.2 | 35.4 | 36 | 35.9667 | 36 | 34.4 | 34.7 | 34.1 | 34 | 34.4 | 34 | 241 | United_StatesFloridaJACKSONVILLE INTL ARPT
United_States | Florida | E1 | JACKSONVILLE NAS | JACKSONVILLE NAS, FL, USA | 30.23N | 81.68W | 7 | -5.00 (NAE) | 82-06 | 722065 | -3.7 | -4 | -13 | 40.9 | 37.4 | 36.9 | 36.6 | 37 | 36.9667 | 37 | 34.8 | 35.1 | 34.7 | 35 | 34.8667 | 35 | 242 | United_StatesFloridaJACKSONVILLE NAS
United_States | Florida | E1 | JACKSONVILLE/CRAIG | JACKSONVILLE/CRAIG, FL, USA | 30.34N | 81.52W | 13 | -5.00 (NAE) | 82-06 | 722068 | -4.1 | -4 | -12.2 | 38.8 | 36.2 | 35.8 | 35.1 | 36 | 35.7 | 36 | 33.7 | 34.1 | 33.5 | 34 | 33.7667 | 34 | 243 | United_StatesFloridaJACKSONVILLE/CRAIG
United_States | Florida | E1 | KEY WEST INTL ARPT | KEY WEST INTL ARPT, FL, USA | 24.55N | 81.75W | 6 | -5.00 (NAE) | 82-06 | 722010 | 10 | 10 | 4.4 | 35.2 | 32.6 | 33 | 33.3 | 33 | 32.9667 | 33 | 31.8 | 32.4 | 32.6 | 32 | 32.2667 | 32 | 244 | United_StatesFloridaKEY WEST INTL ARPT
United_States | Florida | E1 | KEY WEST NAS | KEY WEST NAS, FL, USA | 24.58N | 81.68W | 7 | -5.00 (NAE) | 82-06 | 722015 | 10.3 | 10 | 5.1 | 36.3 | 32.5 | 32.8 | 32.9 | 33 | 32.7333 | 33 | 31.9 | 32.3 | 32.4 | 32 | 32.2 | 32 | 245 | United_StatesFloridaKEY WEST NAS
United_States | Florida | E1 | MACDILL AFB/TAMPA | MACDILL AFB/TAMPA, FL, USA | 27.85N | 82.52W | 8 | -5.00 (NAE) | 82-06 | 747880 | 0.8 | 1 | -6.5 | 38 | 34.2 | 34.9 | 34.6 | 35 | 34.5667 | 35 | 33.3 | 33.7 | 33.6 | 34 | 33.5333 | 34 | 246 | United_StatesFloridaMACDILL AFB/TAMPA
United_States | Florida | E1 | MARATHON AIRPORT | MARATHON AIRPORT, FL, USA | 24.73N | 81.05W | 2 | -5.00 (NAE) | 95-06 | 722016 | 10 | N/A | N/A | N/A | 33 | 33.9 | 33.9 | 34 | 33.6 | 34 | 32.7 | 32.9 | 33 | 33 | 32.8667 | 33 | 247 | United_StatesFloridaMARATHON AIRPORT
United_States | Florida | E1 | MAYPORT NS | MAYPORT NS, FL, USA | 30.40N | 81.42W | 4 | -5.00 (NAE) | 84-06 | 722066 | -2.8 | -3 | -13.4 | 40.7 | 36.3 | 36.5 | 35.8 | 36 | 36.2 | 37 | 34.1 | 34.8 | 33.8 | 34 | 34.2333 | 34 | 248 | United_StatesFloridaMAYPORT NS
United_States | Florida | E1 | MELBOURNE REGIONAL AP | MELBOURNE REGIONAL AP, FL, USA | 28.10N | 80.65W | 8 | -5.00 (NAE) | 82-06 | 722040 | -0.3 | 0 | -8.8 | 39 | 35 | 35.2 | 34.4 | 35 | 34.8667 | 35 | 33 | 33.5 | 33 | 33 | 33.1667 | 33 | 249 | United_StatesFloridaMELBOURNE REGIONAL AP
United_States | Florida | E1 | MIAMI INTL AP | MIAMI INTL AP, FL, USA | 25.82N | 80.30W | 9 | -5.00 (NAE) | 82-06 | 722020 | 5.1 | 5 | -2.9 | 37.4 | 33.8 | 34.2 | 34.1 | 34 | 34.0333 | 34 | 32.6 | 33 | 33 | 33 | 32.8667 | 33 | 250 | United_StatesFloridaMIAMI INTL AP
United_States | Florida | E1 | MIAMI/KENDALL-TAMIA | MIAMI/KENDALL-TAMIA, FL, USA | 25.65N | 80.43W | 3 | -5.00 (NAE) | 83-06 | 722029 | 4.1 | 4 | -3.2 | 40.1 | 34.1 | 34.1 | 34.2 | 34 | 34.1333 | 34 | 32.9 | 33.2 | 33.4 | 33 | 33.1667 | 33 | 251 | United_StatesFloridaMIAMI/KENDALL-TAMIA
United_States | Florida | E1 | MOLASSES REEF | MOLASSES REEF, FL, USA | 25.02N | 80.38W | 11 | -5.00 (NAE) | 89-06 | 994430 | 8.8 | 9 | 1 | 32.1 | 29.9 | 30.6 | 30.6 | 30 | 30.3667 | 31 | 29.5 | 30 | 30.2 | 30 | 29.9 | 30 | 252 | United_StatesFloridaMOLASSES REEF
United_States | Florida | E1 | NAPLES MUNICIPAL | NAPLES MUNICIPAL, FL, USA | 26.15N | 81.78W | 7 | -5.00 (NAE) | 92-06 | 722038 | 2.8 | 3 | -1.4 | 36.9 | 33.1 | 33.5 | 33.2 | 33 | 33.2667 | 34 | 32.3 | 32.5 | 32.5 | 32 | 32.4333 | 32 | 253 | United_StatesFloridaNAPLES MUNICIPAL
United_States | Florida | E1 | NASA SHUTTLE FCLTY | NASA SHUTTLE FCLTY, FL, USA | 28.62N | 80.72W | 3 | -5.00 (NAE) | 82-06 | 747946 | -0.4 | 0 | -8 | 38.5 | 34.5 | 34.4 | 34.3 | 34 | 34.4 | 34 | 32.7 | 33.1 | 32.9 | 33 | 32.9 | 33 | 254 | United_StatesFloridaNASA SHUTTLE FCLTY
United_States | Florida | E1 | OCALA MUNI (AWOS) | OCALA MUNI (AWOS), FL, USA | 29.17N | 82.22W | 27 | -5.00 (NAE) | 92-06 | 722055 | -5.5 | -6 | -10 | 38.1 | 36.1 | 34.9 | 34.7 | 35 | 35.2333 | 35 | 33.9 | 33.8 | 33.7 | 34 | 33.8 | 34 | 255 | United_StatesFloridaOCALA MUNI (AWOS)
United_States | Florida | E1 | ORLANDO EXECUTIVE AP | ORLANDO EXECUTIVE AP, FL, USA | 28.55N | 81.33W | 34 | -5.00 (NAE) | 88-06 | 722053 | 0.9 | 1 | -5.4 | 38.9 | 36.3 | 35.2 | 35 | 36 | 35.5 | 35 | 34.1 | 34.1 | 34 | 34 | 34.0667 | 34 | 256 | United_StatesFloridaORLANDO EXECUTIVE AP
United_States | Florida | E1 | ORLANDO INTL ARPT | ORLANDO INTL ARPT, FL, USA | 28.43N | 81.33W | 32 | -5.00 (NAE) | 82-06 | 722050 | -0.9 | -1 | -9.1 | 38.1 | 35.5 | 35.1 | 35 | 35 | 35.2 | 35 | 34 | 34.1 | 33.9 | 34 | 34 | 34 | 257 | United_StatesFloridaORLANDO INTL ARPT
United_States | Florida | E1 | ORLANDO SANFORD AIRPORT | ORLANDO SANFORD AIRPORT, FL, USA | 28.78N | 81.24W | 17 | -5.00 (NAE) | 92-06 | 722057 | 0.6 | 1 | -4.3 | 39.3 | 37 | 36.2 | 36 | 36 | 36.4 | 36 | 34.6 | 34.3 | 34.1 | 34 | 34.3333 | 34 | 258 | United_StatesFloridaORLANDO SANFORD AIRPORT
United_States | Florida | E1 | PANAMA CITY BAY CO | PANAMA CITY BAY CO, FL, USA | 30.20N | 85.68W | 6 | -6.00 (NAC) | 98-06 | 722245 | -3.5 | -4 | -8.9 | 40 | 33.8 | 36.2 | 34.2 | 35 | 34.7333 | 36 | 32.6 | 33.8 | 33 | 33 | 33.1333 | 33 | 259 | United_StatesFloridaPANAMA CITY BAY CO
United_States | Florida | E1 | PENSACOLA FOREST SHERMAN NAS | PENSACOLA FOREST SHERMAN NAS, FL, USA | 30.35N | 87.32W | 9 | -6.00 (NAC) | 82-06 | 722225 | -6.2 | -6 | -15.7 | 41.2 | 34.2 | 36.2 | 35.4 | 35 | 35.2667 | 36 | 32.9 | 34.2 | 33.7 | 34 | 33.6 | 34 | 260 | United_StatesFloridaPENSACOLA FOREST SHERMAN NAS
United_States | Florida | E1 | PENSACOLA REGIONAL AP | PENSACOLA REGIONAL AP, FL, USA | 30.47N | 87.19W | 36 | -6.00 (NAC) | 82-06 | 722223 | -5.5 | -6 | -13.7 | 40.5 | 35.2 | 36.4 | 35.3 | 36 | 35.6333 | 36 | 33.3 | 34.4 | 33.7 | 34 | 33.8 | 34 | 261 | United_StatesFloridaPENSACOLA REGIONAL AP
United_States | Florida | E1 | SARASOTA BRADENTON | SARASOTA BRADENTON, FL, USA | 27.38N | 82.55W | 10 | -5.00 (NAE) | 82-06 | 722115 | 0 | 0 | -6.5 | 39 | 34 | 34.5 | 34.3 | 34 | 34.2667 | 35 | 32.7 | 33 | 33.3 | 33 | 33 | 33 | 262 | United_StatesFloridaSARASOTA BRADENTON
United_States | Florida | E1 | SOMBRERO KEY | SOMBRERO KEY, FL, USA | 24.62N | 81.10W | 37 | -5.00 (NAE) | 89-06 | 994450 | 10.9 | 11 | 6 | 33.5 | 30.8 | 31.5 | 31.9 | 31 | 31.4 | 32 | 30.1 | 30.8 | 31.2 | 31 | 30.7 | 31 | 263 | United_StatesFloridaSOMBRERO KEY
United_States | Florida | E1 | SOUTHWEST FLORIDA I | SOUTHWEST FLORIDA I, FL, USA | 26.53N | 81.75W | 9 | -5.00 (NAE) | 88-06 | 722108 | 0.9 | 1 | -6 | 38 | 35.3 | 35.1 | 35.1 | 35 | 35.1667 | 35 | 34.1 | 34 | 34 | 34 | 34.0333 | 34 | 264 | United_StatesFloridaSOUTHWEST FLORIDA I
United_States | Florida | E1 | ST AUGSUTINE ARPT | ST AUGSUTINE ARPT, FL, USA | 29.97N | 81.33W | 3 | -5.00 (NAE) | 97-06 | 722212 | 0 | N/A | N/A | N/A | 36.2 | 35.2 | 33.9 | 35 | 35.1 | 35 | 33 | 32.9 | 32.6 | 33 | 32.8333 | 33 | 265 | United_StatesFloridaST AUGSUTINE ARPT
United_States | Florida | E1 | ST PETERSBURG CLEAR | ST PETERSBURG CLEAR, FL, USA | 27.90N | 82.68W | 3 | -5.00 (NAE) | 82-06 | 722116 | 1.1 | 1 | -6.1 | 38.3 | 34.9 | 35.1 | 34.7 | 35 | 34.9 | 35 | 33.4 | 33.8 | 33.7 | 34 | 33.6333 | 34 | 266 | United_StatesFloridaST PETERSBURG CLEAR
United_States | Florida | E1 | ST. AUGUSTINE | ST. AUGUSTINE, FL, USA | 29.87N | 81.27W | 9 | -5.00 (NAE) | 89-06 | 994410 | -0.2 | 0 | -6.7 | 38.2 | 34.1 | 33.9 | 34 | 34 | 34 | 34 | 30.9 | 31.8 | 31.3 | 31 | 31.3333 | 31 | 267 | United_StatesFloridaST. AUGUSTINE
United_States | Florida | E1 | TALLAHASSEE REGIONAL AP | TALLAHASSEE REGIONAL AP, FL, USA | 30.39N | 84.35W | 21 | -5.00 (NAE) | 82-06 | 722140 | -7.5 | -8 | -13.2 | 40.5 | 36.7 | 36.9 | 36.2 | 37 | 36.6 | 37 | 34.7 | 35.1 | 34.8 | 35 | 34.8667 | 35 | 268 | United_StatesFloridaTALLAHASSEE REGIONAL AP
United_States | Florida | E1 | TAMPA INTERNATIONAL AP | TAMPA INTERNATIONAL AP, FL, USA | 27.96N | 82.54W | 3 | -5.00 (NAE) | 82-06 | 722110 | -0.7 | -1 | -8.3 | 37.1 | 34.4 | 34.2 | 34.2 | 34 | 34.2667 | 34 | 33.1 | 33.3 | 33.4 | 33 | 33.2667 | 33 | 269 | United_StatesFloridaTAMPA INTERNATIONAL AP
United_States | Florida | E1 | TYNDALL AFB | TYNDALL AFB, FL, USA | 30.07N | 85.58W | 7 | -6.00 (NAC) | 82-04 | 747750 | -4.5 | -5 | -12.4 | 39.7 | 32.8 | 34.5 | 34 | 34 | 33.7667 | 35 | 31.7 | 32.7 | 32.8 | 32 | 32.4 | 32 | 270 | United_StatesFloridaTYNDALL AFB
United_States | Florida | E1 | VENICE PIER | VENICE PIER, FL, USA | 27.07N | 82.45W | 5 | -5.00 (NAE) | 86-06 | 994220 | 1.4 | 1 | -4.3 | 34.1 | 30.7 | 32.1 | 31.9 | 32 | 31.5667 | 32 | 29.6 | 30.5 | 30.8 | 30 | 30.3 | 30 | 271 | United_StatesFloridaVENICE PIER
United_States | Florida | E1 | VERO BEACH MUNICIPAL ARPT | VERO BEACH MUNICIPAL ARPT, FL, USA | 27.66N | 80.42W | 9 | -5.00 (NAE) | 82-06 | 722045 | 0.1 | 0 | -7.8 | 38.1 | 34 | 34.8 | 33.9 | 34 | 34.2333 | 35 | 32.6 | 33 | 32.9 | 33 | 32.8333 | 33 | 272 | United_StatesFloridaVERO BEACH MUNICIPAL ARPT
United_States | Florida | E1 | WEST PALM BEACH INTL ARPT | WEST PALM BEACH INTL ARPT, FL, USA | 26.69N | 80.10W | 6 | -5.00 (NAE) | 82-06 | 722030 | 2.7 | 3 | -4.7 | 37.1 | 33.7 | 34 | 34 | 34 | 33.9 | 34 | 32.3 | 32.7 | 32.9 | 33 | 32.6333 | 33 | 273 | United_StatesFloridaWEST PALM BEACH INTL ARPT
United_States | Florida | E1 | WHITING FIELD NAAS | WHITING FIELD NAAS, FL, USA | 30.72N | 87.02W | 61 | -6.00 (NAC) | 82-98 | 722226 | -7.4 | -7 | -17 | 39.4 | 35.7 | 35.9 | 36.1 | 36 | 35.9 | 36 | 34.1 | 34.7 | 34.6 | 34 | 34.4667 | 34 | 274 | United_StatesFloridaWHITING FIELD NAAS
United_States | Georgia | E1 | ALBANY DOUGHERTY COUNTY AP | ALBANY DOUGHERTY COUNTY AP, GA, USA | 31.54N | 84.19W | 59 | -5.00 (NAE) | 82-06 | 722160 | -7.7 | -8 | -16.6 | 41 | 37.1 | 37.3 | 36.9 | 37 | 37.1 | 37 | 35.4 | 35.9 | 35.3 | 36 | 35.5333 | 36 | 275 | United_StatesGeorgiaALBANY DOUGHERTY COUNTY AP
United_States | Georgia | E2 | ATHENS BEN EPPS AP | ATHENS BEN EPPS AP, GA, USA | 33.95N | 83.33W | 244 | -5.00 (NAE) | 82-06 | 723110 | -10.5 | -11 | -20.4 | 42 | 35.9 | 37.2 | 36.8 | 37 | 36.6333 | 37 | 33.9 | 35.4 | 34.5 | 35 | 34.6 | 35 | 276 | United_StatesGeorgiaATHENS BEN EPPS AP
United_States | Georgia | E2 | ATLANTA (NEXRAD) | ATLANTA (NEXRAD), GA, USA | 33.37N | 84.55W | 296 | -5.00 (NAE) | 96-06 | 722197 | -10.6 | -11 | -14.7 | 39.2 | 34 | 36 | 36 | 35 | 35.3333 | 36 | 32.7 | 33.7 | 33.7 | 33 | 33.3667 | 33 | 277 | United_StatesGeorgiaATLANTA (NEXRAD)
United_States | Georgia | E2 | ATLANTA HARTSFIELD INTL AP | ATLANTA HARTSFIELD INTL AP, GA, USA | 33.64N | 84.43W | 313 | -5.00 (NAE) | 82-06 | 722190 | -11.2 | -11 | -22.1 | 40.6 | 34.9 | 36.6 | 35.7 | 36 | 35.7333 | 37 | 33.2 | 34.8 | 33.8 | 34 | 33.9333 | 34 | 278 | United_StatesGeorgiaATLANTA HARTSFIELD INTL AP
United_States | Georgia | E2 | AUGUSTA BUSH FIELD | AUGUSTA BUSH FIELD, GA, USA | 33.37N | 81.97W | 45 | -5.00 (NAE) | 82-06 | 722180 | -9.6 | -10 | -17.7 | 42.8 | 37.4 | 38.1 | 37.7 | 38 | 37.7333 | 38 | 35.2 | 36.3 | 35.5 | 36 | 35.6667 | 36 | 279 | United_StatesGeorgiaAUGUSTA BUSH FIELD
United_States | Georgia | E2 | AUGUSTA\DANIEL FLD | AUGUSTA\DANIEL FLD, GA, USA | 33.47N | 82.03W | 128 | -5.00 (NAE) | 97-06 | 722181 | -6.2 | -6 | -12.2 | 42.2 | 37.1 | 37.3 | 37.4 | 37 | 37.2667 | 37 | 34.1 | 36 | 35.1 | 35 | 35.0667 | 35 | 280 | United_StatesGeorgiaAUGUSTA\DANIEL FLD
United_States | Georgia | E1 | BRUNSWICK MALCOLM MCKINNON AP | BRUNSWICK MALCOLM MCKINNON AP, GA, USA | 31.25N | 81.39W | 7 | -5.00 (NAE) | 82-06 | 722137 | -5.2 | -5 | -14.7 | 38.9 | 34.6 | 35.6 | 35.2 | 35 | 35.1333 | 36 | 32.7 | 33.8 | 33.1 | 33 | 33.2 | 33 | 281 | United_StatesGeorgiaBRUNSWICK MALCOLM MCKINNON AP
United_States | Georgia | E2 | COLUMBUS METROPOLITAN ARPT | COLUMBUS METROPOLITAN ARPT, GA, USA | 32.52N | 84.94W | 120 | -5.00 (NAE) | 82-06 | 722255 | -8.6 | -9 | -17.7 | 41.1 | 36.3 | 37.4 | 37.2 | 37 | 36.9667 | 37 | 34.6 | 36 | 35.3 | 35 | 35.3 | 35 | 282 | United_StatesGeorgiaCOLUMBUS METROPOLITAN ARPT
United_States | Georgia | E2 | DEKALB PEACHTREE | DEKALB PEACHTREE, GA, USA | 33.87N | 84.30W | 313 | -5.00 (NAE) | 98-06 | 722196 | -9.2 | -9 | -14.6 | 41 | 34.2 | 36.1 | 36.3 | 36 | 35.5333 | 36 | 32.9 | 34 | 34 | 34 | 33.6333 | 34 | 283 | United_StatesGeorgiaDEKALB PEACHTREE
United_States | Georgia | E2 | DOBBINS AFB/MARIETT | DOBBINS AFB/MARIETT, GA, USA | 33.92N | 84.52W | 330 | -5.00 (NAE) | 82-05 | 722270 | -11.5 | -12 | -21.1 | 41.4 | 34.6 | 36.1 | 36.5 | 36 | 35.7333 | 36 | 32.7 | 34.5 | 33.8 | 34 | 33.6667 | 34 | 284 | United_StatesGeorgiaDOBBINS AFB/MARIETT
United_States | Georgia | E2 | FORT BENNING | FORT BENNING, GA, USA | 32.33N | 85.00W | 88 | -5.00 (NAE) | 82-06 | 722250 | -9.7 | -10 | -17.3 | 42.4 | 37.4 | 37.8 | 37.2 | 37 | 37.4667 | 38 | 35.2 | 36.1 | 35.2 | 36 | 35.5 | 36 | 285 | United_StatesGeorgiaFORT BENNING
United_States | Georgia | E2 | FULTON CO ARPT BROW | FULTON CO ARPT BROW, GA, USA | 33.77N | 84.52W | 263 | -5.00 (NAE) | 82-06 | 722195 | -11.1 | -11 | -21.4 | 40.6 | 34.7 | 36.4 | 36.1 | 36 | 35.7333 | 36 | 33 | 34.6 | 34 | 34 | 33.8667 | 34 | 286 | United_StatesGeorgiaFULTON CO ARPT BROW
United_States | Georgia | E2 | GAINESVILLE\LEE GIL | GAINESVILLE\LEE GIL, GA, USA | 34.27N | 83.83W | 389 | -5.00 (NAE) | 97-06 | 722185 | -8.4 | -8 | -14.5 | 39.8 | 33.7 | 34.8 | 35.1 | 35 | 34.5333 | 35 | 32.4 | 32.9 | 32.9 | 33 | 32.7333 | 33 | 287 | United_StatesGeorgiaGAINESVILLE\LEE GIL
United_States | Georgia | E1 | HUNTER AAF | HUNTER AAF, GA, USA | 32.00N | 81.13W | 13 | -5.00 (NAE) | 82-06 | 747804 | -5.2 | -5 | -11.1 | 41.2 | 36.8 | 37.5 | 36.2 | 37 | 36.8333 | 38 | 34.5 | 35.7 | 34.5 | 35 | 34.9 | 35 | 288 | United_StatesGeorgiaHUNTER AAF
United_States | Georgia | E2 | MACON MIDDLE GA REGIONAL AP | MACON MIDDLE GA REGIONAL AP, GA, USA | 32.69N | 83.65W | 110 | -5.00 (NAE) | 82-06 | 722170 | -9.4 | -9 | -18.9 | 41.9 | 37 | 37.8 | 37.4 | 37 | 37.4 | 38 | 34.9 | 36.1 | 35.4 | 35 | 35.4667 | 35 | 289 | United_StatesGeorgiaMACON MIDDLE GA REGIONAL AP
United_States | Georgia | E1 | MOODY AFB/VALDOSTA | MOODY AFB/VALDOSTA, GA, USA | 30.97N | 83.20W | 71 | -5.00 (NAE) | 82-00 | 747810 | -6.7 | -7 | -19.4 | 41 | 37.3 | 36.8 | 36.2 | 37 | 36.7667 | 37 | 35.2 | 35.3 | 34.7 | 35 | 35.0667 | 35 | 290 | United_StatesGeorgiaMOODY AFB/VALDOSTA
United_States | Georgia | E2 | ROME R B RUSSELL AP | ROME R B RUSSELL AP, GA, USA | 34.35N | 85.16W | 196 | -5.00 (NAE) | 82-06 | 723200 | -11.3 | -11 | -22.1 | 41.8 | 36.2 | 37.7 | 37.2 | 37 | 37.0333 | 38 | 34 | 36 | 35.1 | 35 | 35.0333 | 35 | 291 | United_StatesGeorgiaROME R B RUSSELL AP
United_States | Georgia | E2 | SAVANNAH INTL AP | SAVANNAH INTL AP, GA, USA | 32.12N | 81.20W | 16 | -5.00 (NAE) | 82-06 | 722070 | -6.8 | -7 | -15.1 | 41.1 | 36.6 | 37.3 | 36.1 | 37 | 36.6667 | 37 | 34.4 | 35.6 | 34.5 | 35 | 34.8333 | 35 | 292 | United_StatesGeorgiaSAVANNAH INTL AP
United_States | Georgia | E1 | VALDOSTA WB AIRPORT | VALDOSTA WB AIRPORT, GA, USA | 30.78N | 83.28W | 60 | -5.00 (NAE) | 82-06 | 722166 | -7 | -7 | -15.8 | 41.6 | 37.4 | 37 | 36.4 | 37 | 36.9333 | 37 | 34.9 | 35.1 | 34.9 | 35 | 34.9667 | 35 | 293 | United_StatesGeorgiaVALDOSTA WB AIRPORT
United_States | Georgia | E2 | WARNER ROBINS AFB | WARNER ROBINS AFB, GA, USA | 32.63N | 83.60W | 92 | -5.00 (NAE) | 82-06 | 722175 | -8.4 | -8 | -16.7 | 42.6 | 37.5 | 37.9 | 37.5 | 38 | 37.6333 | 38 | 35.3 | 36.3 | 35.8 | 36 | 35.8 | 36 | 294 | United_StatesGeorgiaWARNER ROBINS AFB
United_States | Georgia | E1 | WAYCROSS WARE CO AP | WAYCROSS WARE CO AP, GA, USA | 31.25N | 82.40W | 43 | -5.00 (NAE) | 83-06 | 722130 | -6.4 | -6 | -20.9 | 42.1 | 36.7 | 37.8 | 36.2 | 37 | 36.9 | 38 | 34.8 | 35.9 | 34.9 | 35 | 35.2 | 35 | 295 | United_StatesGeorgiaWAYCROSS WARE CO AP
United_States | Hawaii | X | BARBERS POINT NAS | BARBERS POINT NAS, HI, USA | 21.30N | 158.07W | 10 | -10.00 (PCH) | 82-99 | 911780 | 12.7 | 13 | 10.2 | 37 | 32.6 | 33.6 | 33.3 | 33 | 33.1667 | 34 | 31.8 | 32.4 | 32.4 | 32 | 32.2 | 32 | 296 | United_StatesHawaiiBARBERS POINT NAS
United_States | Hawaii | X | HILO INTERNATIONAL AP | HILO INTERNATIONAL AP, HI, USA | 19.72N | 155.05W | 11 | -10.00 (PCH) | 82-06 | 912850 | 14.7 | 15 | 12.3 | 33.7 | 29.4 | 29.9 | 30.2 | 30 | 29.8333 | 30 | 28.5 | 29 | 29.4 | 29 | 28.9667 | 29 | 297 | United_StatesHawaiiHILO INTERNATIONAL AP
United_States | Hawaii | X | HONOLULU INTL ARPT | HONOLULU INTL ARPT, HI, USA | 21.33N | 157.94W | 5 | -10.00 (PCH) | 82-06 | 911820 | 14.2 | 14 | 11 | 35.5 | 31.7 | 32.3 | 32.9 | 32 | 32.3 | 32 | 31 | 31.7 | 32.2 | 32 | 31.6333 | 32 | 298 | United_StatesHawaiiHONOLULU INTL ARPT
United_States | Hawaii | X | KAHULUI AIRPORT | KAHULUI AIRPORT, HI, USA | 20.90N | 156.43W | 15 | -10.00 (PCH) | 82-06 | 911900 | 12.7 | 13 | 10.3 | 36.1 | 31.7 | 32.3 | 32.7 | 32 | 32.2333 | 32 | 30.6 | 31.2 | 31.7 | 31 | 31.1667 | 31 | 299 | United_StatesHawaiiKAHULUI AIRPORT
United_States | Hawaii | X | KANEOHE BAY MCAS | KANEOHE BAY MCAS, HI, USA | 21.45N | 157.77W | 6 | -10.00 (PCH) | 82-06 | 911760 | 16.3 | 16 | 10.5 | 33.7 | 28.9 | 29.6 | 30.2 | 30 | 29.5667 | 30 | 28.2 | 28.9 | 29.3 | 29 | 28.8 | 29 | 300 | United_StatesHawaiiKANEOHE BAY MCAS
United_States | Hawaii | X | KONA INTL AT KEAHOL | KONA INTL AT KEAHOL, HI, USA | 19.73N | 156.03W | 15 | -10.00 (PCH) | 89-06 | 911975 | 14.4 | 14 | 2.8 | 34.7 | 30.5 | 31.3 | 32 | 31 | 31.2667 | 31 | 29.1 | 30.2 | 31.2 | 30 | 30.1667 | 30 | 301 | United_StatesHawaiiKONA INTL AT KEAHOL
United_States | Hawaii | X | LIHUE AIRPORT | LIHUE AIRPORT, HI, USA | 21.98N | 159.34W | 45 | -10.00 (PCH) | 82-06 | 911650 | 13.7 | 14 | 10.7 | 32.7 | 29.4 | 29.6 | 30.3 | 30 | 29.7667 | 30 | 28.6 | 29.1 | 29.5 | 29 | 29.0667 | 29 | 302 | United_StatesHawaiiLIHUE AIRPORT
United_States | Hawaii | X | MOLOKAI (AMOS) | MOLOKAI (AMOS), HI, USA | 21.15N | 157.10W | 137 | -10.00 (PCH) | 82-06 | 911860 | 12.8 | 13 | 9.9 | 38.3 | 30.5 | 31.2 | 31.6 | 31 | 31.1 | 31 | 29.3 | 30 | 30.6 | 30 | 29.9667 | 30 | 303 | United_StatesHawaiiMOLOKAI (AMOS)
United_States | Idaho | M4 | BOISE AIR TERMINAL | BOISE AIR TERMINAL, ID, USA | 43.57N | 116.22W | 874 | -7.00 (NAM) | 82-06 | 726810 | -17.2 | -17 | -33.2 | 43.7 | 36.7 | 39.4 | 38.5 | 38 | 38.2 | 39 | 34.1 | 37.2 | 36.2 | 36 | 35.8333 | 36 | 304 | United_StatesIdahoBOISE AIR TERMINAL
United_States | Idaho | M4 | BURLEY MUNICIPAL ARPT | BURLEY MUNICIPAL ARPT, ID, USA | 42.54N | 113.77W | 1267 | -7.00 (NAM) | 82-06 | 725867 | -20.3 | -20 | -33.9 | 42.8 | 34.4 | 37.2 | 36.4 | 36 | 36 | 37 | 31.6 | 34.7 | 34.1 | 33 | 33.4667 | 33 | 305 | United_StatesIdahoBURLEY MUNICIPAL ARPT
United_States | Idaho | M4 | CALDWELL (AWOS) | CALDWELL (AWOS), ID, USA | 43.63N | 116.63W | 740 | -7.00 (NAM) | 92-06 | 726813 | -13.4 | -13 | -23 | 43.6 | 35.2 | 38.8 | 37.4 | 37 | 37.1333 | 39 | 32.5 | 37 | 35.2 | 35 | 34.9 | 35 | 306 | United_StatesIdahoCALDWELL (AWOS)
United_States | Idaho | M4 | CHALLIS | CHALLIS, ID, USA | 44.52N | 114.22W | 1546 | -7.00 (NAM) | 83-06 | 722142 | -29.3 | -29 | -39.6 | 41.1 | 33.4 | 36.1 | 34.2 | 35 | 34.5667 | 36 | 31 | 33.7 | 32.3 | 32 | 32.3333 | 32 | 307 | United_StatesIdahoCHALLIS
United_States | Idaho | M4 | COEUR D`ALENE(AWOS) | COEUR D`ALENE(AWOS), ID, USA | 47.77N | 116.82W | 707 | -8.00 (NAP) | 90-06 | 727834 | -17.7 | -18 | -29 | 41.6 | 32.2 | 36.4 | 35.3 | 35 | 34.6333 | 36 | 28.6 | 33.6 | 33.3 | 32 | 31.8333 | 32 | 308 | United_StatesIdahoCOEUR D`ALENE(AWOS)
United_States | Idaho | M4 | ELK CITY (RAMOS) | ELK CITY (RAMOS), ID, USA | 45.82N | 115.43W | 1249 | -8.00 (NAP) | 83-06 | 725784 | -15.4 | -15 | -25.9 | 42 | 35.9 | 37.5 | 38 | 37 | 37.1333 | 38 | 31.4 | 35.1 | 34.1 | 34 | 33.5333 | 34 | 309 | United_StatesIdahoELK CITY (RAMOS)
United_States | Idaho | M4 | IDAHO FALLS FANNING FIELD | IDAHO FALLS FANNING FIELD, ID, USA | 43.52N | 112.07W | 1446 | -7.00 (NAM) | 82-06 | 725785 | -26.1 | -26 | -40.6 | 40.7 | 33.2 | 35.5 | 35.1 | 35 | 34.6 | 36 | 30.8 | 33.7 | 33 | 33 | 32.5 | 33 | 310 | United_StatesIdahoIDAHO FALLS FANNING FIELD
United_States | Idaho | M4 | JOSLIN FLD MAGIC VA | JOSLIN FLD MAGIC VA, ID, USA | 42.48N | 114.48W | 1297 | -7.00 (NAM) | 97-06 | 725866 | -16.1 | -16 | -24.8 | 42.4 | 32.9 | 37.8 | 36.2 | 36 | 35.6333 | 38 | 31.3 | 36 | 33.9 | 34 | 33.7333 | 34 | 311 | United_StatesIdahoJOSLIN FLD MAGIC VA
United_States | Idaho | M4 | LEWISTON NEZ PERCE CNTY AP | LEWISTON NEZ PERCE CNTY AP, ID, USA | 46.38N | 117.01W | 438 | -8.00 (NAP) | 82-06 | 727830 | -14.2 | -14 | -27.9 | 44.1 | 35.9 | 39.5 | 38.7 | 38 | 38.0333 | 40 | 32.7 | 37.1 | 36.3 | 35 | 35.3667 | 35 | 312 | United_StatesIdahoLEWISTON NEZ PERCE CNTY AP
United_States | Idaho | M4 | MCCALL ARPT | MCCALL ARPT, ID, USA | 44.88N | 116.10W | 1530 | -7.00 (NAM) | 87-06 | 725864 | -26 | -26 | -32.5 | 37.1 | 29 | 32.7 | 31.3 | 31 | 31 | 33 | 27.1 | 30.9 | 29.5 | 29 | 29.1667 | 29 | 313 | United_StatesIdahoMCCALL ARPT
United_States | Idaho | M4 | MOUNTAIN HOME AFB | MOUNTAIN HOME AFB, ID, USA | 43.05N | 115.87W | 912 | -7.00 (NAM) | 82-06 | 726815 | -19 | -19 | -31.9 | 45.1 | 37.6 | 39.8 | 39.1 | 39 | 38.8333 | 40 | 34.6 | 37.8 | 37.2 | 37 | 36.5333 | 37 | 314 | United_StatesIdahoMOUNTAIN HOME AFB
United_States | Idaho | M4 | MULLAN (AWRS) | MULLAN (AWRS), ID, USA | 47.47N | 115.80W | 1011 | -8.00 (NAP) | 82-96 | 727836 | -21.1 | -21 | -32.4 | 36 | 30.7 | 32.4 | 32.4 | 32 | 31.8333 | 32 | 28.4 | 30.4 | 30.6 | 30 | 29.8 | 30 | 315 | United_StatesIdahoMULLAN (AWRS)
United_States | Idaho | M4 | POCATELLO REGIONAL AP | POCATELLO REGIONAL AP, ID, USA | 42.92N | 112.57W | 1365 | -7.00 (NAM) | 82-06 | 725780 | -24.3 | -24 | -39 | 41.2 | 34.4 | 37.3 | 36.4 | 36 | 36.0333 | 37 | 31.8 | 35.2 | 34.3 | 34 | 33.7667 | 34 | 316 | United_StatesIdahoPOCATELLO REGIONAL AP
United_States | Idaho | M4 | SALMON/LEMHI (AWOS) | SALMON/LEMHI (AWOS), ID, USA | 45.12N | 113.88W | 1233 | -7.00 (NAM) | 92-06 | 726865 | -23.6 | -24 | -32.8 | 40 | 31.6 | 36.2 | 33.6 | 34 | 33.8 | 36 | 28.7 | 33.5 | 31.9 | 31 | 31.3667 | 31 | 317 | United_StatesIdahoSALMON/LEMHI (AWOS)
United_States | Illinois | M3 | AURORA MUNICIPAL | AURORA MUNICIPAL, IL, USA | 41.77N | 88.47W | 215 | -6.00 (NAC) | 98-06 | 744655 | -24.9 | -25 | -32.3 | 40.7 | 33.8 | 35 | 33.8 | 34 | 34.2 | 35 | 32.4 | 32.8 | 31.8 | 32 | 32.3333 | 32 | 318 | United_StatesIllinoisAURORA MUNICIPAL
United_States | Illinois | M3 | CAHOKIA/ST. LOUIS | CAHOKIA/ST. LOUIS, IL, USA | 38.57N | 90.15W | 126 | -6.00 (NAC) | 97-06 | 725314 | -17.2 | -17 | -25.6 | 41.3 | 34.1 | 37.3 | 36.4 | 36 | 35.9333 | 37 | 32.8 | 35.8 | 33.9 | 34 | 34.1667 | 34 | 319 | United_StatesIllinoisCAHOKIA/ST. LOUIS
United_States | Illinois | M3 | CHICAGO MIDWAY AP | CHICAGO MIDWAY AP, IL, USA | 41.79N | 87.75W | 188 | -6.00 (NAC) | 82-06 | 725340 | -22.3 | -22 | -33.1 | 41.7 | 34.1 | 36.4 | 34.8 | 35 | 35.1 | 36 | 32.4 | 33.8 | 32.5 | 33 | 32.9 | 33 | 320 | United_StatesIllinoisCHICAGO MIDWAY AP
United_States | Illinois | M3 | CHICAGO OHARE INTL AP | CHICAGO OHARE INTL AP, IL, USA | 41.99N | 87.91W | 205 | -6.00 (NAC) | 82-06 | 725300 | -23.7 | -24 | -35.5 | 40.9 | 34.3 | 35.9 | 35 | 35 | 35.0667 | 36 | 32.4 | 33.6 | 32.4 | 33 | 32.8 | 33 | 321 | United_StatesIllinoisCHICAGO OHARE INTL AP
United_States | Illinois | M3 | DECATUR | DECATUR, IL, USA | 39.83N | 88.87W | 213 | -6.00 (NAC) | 82-06 | 725316 | -22 | -22 | -33 | 40.1 | 34.6 | 35.9 | 35.8 | 35 | 35.4333 | 36 | 32.7 | 33.9 | 33.4 | 33 | 33.3333 | 33 | 322 | United_StatesIllinoisDECATUR
United_States | Illinois | M3 | GLENVIEW NAS | GLENVIEW NAS, IL, USA | 42.08N | 87.82W | 199 | -6.00 (NAC) | 82-95 | 725306 | -24.3 | -24 | -36.3 | 40.7 | 35.1 | 36.1 | 36.7 | 36 | 35.9667 | 36 | 32.7 | 34.1 | 33.5 | 33 | 33.4333 | 33 | 323 | United_StatesIllinoisGLENVIEW NAS
United_States | Illinois | M3 | LAWRENCEVILLE\VIN. | LAWRENCEVILLE\VIN., IL, USA | 38.77N | 87.60W | 131 | -6.00 (NAC) | 97-06 | 725342 | -18.2 | -18 | -26.5 | 40.1 | 34 | 36.1 | 35.9 | 35 | 35.3333 | 36 | 32.7 | 34 | 33 | 33 | 33.2333 | 33 | 324 | United_StatesIllinoisLAWRENCEVILLE\VIN.
United_States | Illinois | M3 | MARSEILLES ISLAND | MARSEILLES ISLAND, IL, USA | 41.37N | 88.68W | 225 | -6.00 (NAC) | 82-96 | 744600 | -24.5 | -25 | -33.7 | 40.9 | 34.7 | 36.2 | 36.2 | 36 | 35.7 | 36 | 32.6 | 33.7 | 33.2 | 33 | 33.1667 | 33 | 325 | United_StatesIllinoisMARSEILLES ISLAND
United_States | Illinois | M3 | MATTOON/CHARLESTON | MATTOON/CHARLESTON, IL, USA | 39.48N | 88.28W | 220 | -6.00 (NAC) | 98-06 | 725317 | -19.7 | -20 | -27.7 | 38.4 | 32.9 | 35.2 | 33.8 | 34 | 33.9667 | 35 | 31.4 | 33 | 32.4 | 32 | 32.2667 | 32 | 326 | United_StatesIllinoisMATTOON/CHARLESTON
United_States | Illinois | M3 | MOLINE QUAD CITY INTL AP | MOLINE QUAD CITY INTL AP, IL, USA | 41.47N | 90.52W | 181 | -6.00 (NAC) | 82-06 | 725440 | -24.9 | -25 | -35.9 | 41 | 34.9 | 36.6 | 36.4 | 36 | 35.9667 | 37 | 32.9 | 34.3 | 33.4 | 34 | 33.5333 | 34 | 327 | United_StatesIllinoisMOLINE QUAD CITY INTL AP
United_States | Illinois | M3 | MOUNT VERNON (AWOS) | MOUNT VERNON (AWOS), IL, USA | 38.32N | 88.87W | 146 | -6.00 (NAC) | 92-06 | 724335 | -21.4 | -21 | -33.6 | 39 | 34.9 | 36.3 | 35.2 | 35 | 35.4667 | 36 | 33 | 34.1 | 33.7 | 34 | 33.6 | 34 | 328 | United_StatesIllinoisMOUNT VERNON (AWOS)
United_States | Illinois | M3 | PEORIA GREATER PEORIA AP | PEORIA GREATER PEORIA AP, IL, USA | 40.67N | 89.68W | 202 | -6.00 (NAC) | 82-06 | 725320 | -23.3 | -23 | -33.6 | 40.6 | 34.4 | 36.3 | 36.1 | 36 | 35.6 | 36 | 32.4 | 33.9 | 33.2 | 33 | 33.1667 | 33 | 329 | United_StatesIllinoisPEORIA GREATER PEORIA AP
United_States | Illinois | M3 | QUINCY MUNI BALDWIN FLD | QUINCY MUNI BALDWIN FLD, IL, USA | 39.94N | 91.19W | 234 | -6.00 (NAC) | 82-06 | 724396 | -22.7 | -23 | -32.5 | 41 | 34.1 | 37 | 36.8 | 36 | 35.9667 | 37 | 32.1 | 34.2 | 33.8 | 33 | 33.3667 | 33 | 330 | United_StatesIllinoisQUINCY MUNI BALDWIN FLD
United_States | Illinois | M3 | ROCKFORD GREATER ROCKFORD AP | ROCKFORD GREATER ROCKFORD AP, IL, USA | 42.20N | 89.09W | 227 | -6.00 (NAC) | 82-06 | 725430 | -26 | -26 | -36.5 | 40 | 34.5 | 35.1 | 35.2 | 35 | 34.9333 | 35 | 32.1 | 33.1 | 32.5 | 33 | 32.5667 | 33 | 331 | United_StatesIllinoisROCKFORD GREATER ROCKFORD AP
United_States | Illinois | M3 | SCOTT AFB/BELLEVILL | SCOTT AFB/BELLEVILL, IL, USA | 38.55N | 89.85W | 135 | -6.00 (NAC) | 82-06 | 724338 | -19 | -19 | -28 | 41 | 35.7 | 37.2 | 36.4 | 36 | 36.4333 | 37 | 33.7 | 35.1 | 34.8 | 35 | 34.5333 | 35 | 332 | United_StatesIllinoisSCOTT AFB/BELLEVILL
United_States | Illinois | M3 | SOUTHERN ILLINOIS | SOUTHERN ILLINOIS, IL, USA | 37.77N | 89.25W | 128 | -6.00 (NAC) | 96-06 | 724336 | -16.5 | -17 | -25.7 | 39.3 | 34 | 36.1 | 36.1 | 35 | 35.4 | 36 | 32.8 | 33.9 | 33.8 | 34 | 33.5 | 34 | 333 | United_StatesIllinoisSOUTHERN ILLINOIS
United_States | Illinois | M3 | SPRINGFIELD CAPITAL AP | SPRINGFIELD CAPITAL AP, IL, USA | 39.85N | 89.68W | 187 | -6.00 (NAC) | 82-06 | 724390 | -23.3 | -23 | -33.2 | 39.8 | 34.4 | 36 | 35.8 | 35 | 35.4 | 36 | 32.6 | 33.8 | 33.6 | 33 | 33.3333 | 33 | 334 | United_StatesIllinoisSPRINGFIELD CAPITAL AP
United_States | Illinois | M3 | STERLING ROCKFALLS | STERLING ROCKFALLS, IL, USA | 41.75N | 89.67W | 197 | -6.00 (NAC) | 92-06 | 725326 | -24.5 | -25 | -33.9 | 40.4 | 33.9 | 35.2 | 33.7 | 34 | 34.2667 | 35 | 32.3 | 32.5 | 31.6 | 32 | 32.1333 | 32 | 335 | United_StatesIllinoisSTERLING ROCKFALLS
United_States | Illinois | M3 | UNIV OF ILLINOIS WI | UNIV OF ILLINOIS WI, IL, USA | 40.03N | 88.27W | 236 | -6.00 (NAC) | 85-06 | 725315 | -23.1 | -23 | -33.6 | 40 | 35.1 | 35.8 | 35.1 | 35 | 35.3333 | 36 | 33 | 33.3 | 32.4 | 33 | 32.9 | 33 | 336 | United_StatesIllinoisUNIV OF ILLINOIS WI
United_States | Illinois | M3 | W. CHICAGO/DU PAGE | W. CHICAGO/DU PAGE, IL, USA | 41.92N | 88.25W | 231 | -6.00 (NAC) | 82-06 | 725305 | -24.3 | -24 | -33.8 | 40 | 33.9 | 34.6 | 34 | 34 | 34.1667 | 35 | 32.1 | 32.6 | 31.9 | 32 | 32.2 | 32 | 337 | United_StatesIllinoisW. CHICAGO/DU PAGE
United_States | Indiana | M3 | EVANSVILLE REGIONAL AP | EVANSVILLE REGIONAL AP, IN, USA | 38.04N | 87.54W | 118 | -6.00 (NAC) | 82-06 | 724320 | -18.8 | -19 | -31.4 | 39.7 | 35 | 36.4 | 36.2 | 36 | 35.8667 | 36 | 33.2 | 34.3 | 34.3 | 34 | 33.9333 | 34 | 338 | United_StatesIndianaEVANSVILLE REGIONAL AP
United_States | Indiana | M3 | FORT WAYNE INTL AP | FORT WAYNE INTL AP, IN, USA | 41.01N | 85.21W | 252 | -5.00 (NAE) | 82-06 | 725330 | -22.6 | -23 | -33.7 | 40 | 34.4 | 35.4 | 33.9 | 35 | 34.5667 | 35 | 32.4 | 32.9 | 31.7 | 32 | 32.3333 | 32 | 339 | United_StatesIndianaFORT WAYNE INTL AP
United_States | Indiana | M3 | GRISSOM ARB | GRISSOM ARB, IN, USA | 40.65N | 86.15W | 253 | -5.00 (NAE) | 82-01 | 725335 | -22.5 | -23 | -33.2 | 41.3 | 34.6 | 36.1 | 35.4 | 35 | 35.3667 | 36 | 32.4 | 33.7 | 32.5 | 33 | 32.8667 | 33 | 340 | United_StatesIndianaGRISSOM ARB
United_States | Indiana | M3 | HUNTINGBURG | HUNTINGBURG, IN, USA | 38.25N | 86.95W | 161 | -5.00 (NAE) | 94-06 | 724365 | -19 | N/A | N/A | N/A | 33.1 | 34.8 | 34 | 34 | 33.9667 | 35 | 32.3 | 32.9 | 32.7 | 33 | 32.6333 | 33 | 341 | United_StatesIndianaHUNTINGBURG
United_States | Indiana | M3 | INDIANAPOLIS INTL AP | INDIANAPOLIS INTL AP, IN, USA | 39.71N | 86.27W | 246 | -5.00 (NAE) | 82-06 | 724380 | -22.1 | -22 | -35.5 | 38.9 | 33.4 | 35.4 | 34.2 | 34 | 34.3333 | 35 | 31.7 | 33 | 32.3 | 32 | 32.3333 | 32 | 342 | United_StatesIndianaINDIANAPOLIS INTL AP
United_States | Indiana | M3 | LAFAYETTE PURDUE UNIV AP | LAFAYETTE PURDUE UNIV AP, IN, USA | 40.41N | 86.94W | 194 | -5.00 (NAE) | 82-06 | 724386 | -22.8 | -23 | -34.9 | 40.7 | 34.6 | 36.4 | 34.7 | 35 | 35.2333 | 36 | 32.8 | 33.9 | 32.7 | 33 | 33.1333 | 33 | 343 | United_StatesIndianaLAFAYETTE PURDUE UNIV AP
United_States | Indiana | M3 | MONROE CO | MONROE CO, IN, USA | 39.13N | 86.62W | 264 | -5.00 (NAE) | 98-06 | 724375 | -21.2 | -21 | -34.4 | 39.5 | 32.7 | 34.1 | 33 | 33 | 33.2667 | 34 | 32 | 32.7 | 32.3 | 32 | 32.3333 | 32 | 344 | United_StatesIndianaMONROE CO
United_States | Indiana | M3 | SOUTH BEND MICHIANA RGNL AP | SOUTH BEND MICHIANA RGNL AP, IN, USA | 41.71N | 86.33W | 236 | -5.00 (NAE) | 82-06 | 725350 | -22.2 | -22 | -32.6 | 40.2 | 34.2 | 35.5 | 34.1 | 35 | 34.6 | 36 | 32 | 32.9 | 31.6 | 32 | 32.1667 | 32 | 345 | United_StatesIndianaSOUTH BEND MICHIANA RGNL AP
United_States | Indiana | M3 | TERRE HAUTE/HULMAN | TERRE HAUTE/HULMAN, IN, USA | 39.45N | 87.32W | 175 | -5.00 (NAI) | 82-06 | 724373 | -22.5 | -23 | -34.7 | 40.1 | 34.8 | 35.8 | 34.1 | 35 | 34.9 | 36 | 32.9 | 33.7 | 32.6 | 33 | 33.0667 | 33 | 346 | United_StatesIndianaTERRE HAUTE/HULMAN
United_States | Iowa | M3 | AMES MUNI ARPT | AMES MUNI ARPT, IA, USA | 42.00N | 93.62W | 291 | -6.00 (NAC) | 97-06 | 725472 | -25.6 | -26 | -33.7 | 38.7 | 32.9 | 34 | 32.9 | 33 | 33.2667 | 34 | 32 | 32.6 | 31.2 | 32 | 31.9333 | 32 | 347 | United_StatesIowaAMES MUNI ARPT
United_States | Iowa | M3 | ANKENY REGIONAL ARP | ANKENY REGIONAL ARP, IA, USA | 41.68N | 93.55W | 275 | -6.00 (NAC) | 82-06 | 725466 | -22.2 | -22 | -29.5 | 42.7 | 36 | 37.2 | 37.8 | 37 | 37 | 37 | 32.7 | 34.9 | 35 | 34 | 34.2 | 34 | 348 | United_StatesIowaANKENY REGIONAL ARP
United_States | Iowa | M3 | ATLANTIC | ATLANTIC, IA, USA | 41.40N | 95.05W | 360 | -6.00 (NAC) | 95-06 | 725453 | -23 | N/A | N/A | N/A | 34 | 36 | 36.2 | 35 | 35.4 | 36 | 32.6 | 34 | 33 | 33 | 33.2 | 33 | 349 | United_StatesIowaATLANTIC
United_States | Iowa | M3 | BOONE MUNI | BOONE MUNI, IA, USA | 42.05N | 93.85W | 354 | -6.00 (NAC) | 95-06 | 725486 | -25 | N/A | N/A | N/A | 33.8 | 35.1 | 34.8 | 35 | 34.5667 | 35 | 32.3 | 33.5 | 32.4 | 33 | 32.7333 | 33 | 350 | United_StatesIowaBOONE MUNI
United_States | Iowa | M3 | BURLINGTON MUNICIPAL AP | BURLINGTON MUNICIPAL AP, IA, USA | 40.78N | 91.13W | 214 | -6.00 (NAC) | 82-06 | 725455 | -23 | -23 | -33.1 | 41 | 34.6 | 36.6 | 36 | 36 | 35.7333 | 37 | 32.7 | 34.4 | 33.1 | 33 | 33.4 | 33 | 351 | United_StatesIowaBURLINGTON MUNICIPAL AP
United_States | Iowa | M3 | CARROLL | CARROLL, IA, USA | 42.05N | 94.78W | 375 | -6.00 (NAC) | 95-06 | 725468 | -25 | N/A | N/A | N/A | 35.1 | 35.2 | 35 | 35 | 35.1 | 35 | 33.3 | 33 | 32.7 | 33 | 33 | 33 | 352 | United_StatesIowaCARROLL
United_States | Iowa | M3 | CEDAR RAPIDS MUNICIPAL AP | CEDAR RAPIDS MUNICIPAL AP, IA, USA | 41.88N | 91.71W | 266 | -6.00 (NAC) | 82-06 | 725450 | -26.3 | -26 | -34.1 | 39.7 | 33.8 | 35.5 | 35.5 | 35 | 34.9333 | 36 | 31.8 | 33.2 | 32.7 | 33 | 32.5667 | 33 | 353 | United_StatesIowaCEDAR RAPIDS MUNICIPAL AP
United_States | Iowa | M3 | CHARITON | CHARITON, IA, USA | 41.03N | 93.37W | 320 | -6.00 (NAC) | 95-06 | 725469 | -22.7 | -23 | -33.1 | 40.3 | 33.9 | 37.1 | 34.8 | 35 | 35.2667 | 37 | 32.4 | 34.9 | 32.9 | 33 | 33.4 | 33 | 354 | United_StatesIowaCHARITON
United_States | Iowa | M3 | CHARLES CITY | CHARLES CITY, IA, USA | 43.07N | 92.62W | 343 | -6.00 (NAC) | 95-06 | 725463 | -25 | N/A | N/A | N/A | 33.8 | 33 | 32.5 | 33 | 33.1 | 33 | 32.1 | 32.4 | 30.9 | 32 | 31.8 | 32 | 355 | United_StatesIowaCHARLES CITY
United_States | Iowa | M3 | CLARION | CLARION, IA, USA | 42.75N | 93.77W | 354 | -6.00 (NAC) | 95-06 | 725458 | -25 | N/A | N/A | N/A | 34 | 35.1 | 32.7 | 34 | 33.9333 | 35 | 32.3 | 32.9 | 31.2 | 32 | 32.1333 | 32 | 356 | United_StatesIowaCLARION
United_States | Iowa | M3 | CLINTON MUNI (AWOS) | CLINTON MUNI (AWOS), IA, USA | 41.83N | 90.33W | 216 | -6.00 (NAC) | 92-06 | 725473 | -24.8 | -25 | -32.9 | 38.3 | 33.7 | 34.5 | 33 | 34 | 33.7333 | 35 | 32.2 | 32.5 | 31.3 | 32 | 32 | 32 | 357 | United_StatesIowaCLINTON MUNI (AWOS)
United_States | Iowa | M3 | CRESTON | CRESTON, IA, USA | 41.02N | 94.37W | 394 | -6.00 (NAC) | 95-06 | 725474 | -23.1 | -23 | -29.3 | 43.1 | 32.7 | 36.3 | 36.4 | 35 | 35.1333 | 36 | 32.1 | 34.7 | 33.6 | 33 | 33.4667 | 33 | 358 | United_StatesIowaCRESTON
United_States | Iowa | M3 | DAVENPORT NEXRAD | DAVENPORT NEXRAD, IA, USA | 41.62N | 90.58W | 259 | -6.00 (NAC) | 97-06 | 725349 | -24.6 | -25 | -32.5 | 37.9 | 32.8 | 34 | 32.7 | 33 | 33.1667 | 34 | 31.4 | 32.5 | 31.2 | 32 | 31.7 | 32 | 359 | United_StatesIowaDAVENPORT NEXRAD
United_States | Iowa | M3 | DES MOINES INTL AP | DES MOINES INTL AP, IA, USA | 41.54N | 93.67W | 294 | -6.00 (NAC) | 82-06 | 725460 | -24.6 | -25 | -33 | 41.9 | 34.6 | 36.6 | 37.1 | 36 | 36.1 | 37 | 32 | 34.2 | 33.9 | 33 | 33.3667 | 33 | 360 | United_StatesIowaDES MOINES INTL AP
United_States | Iowa | M3 | DUBUQUE REGIONAL AP | DUBUQUE REGIONAL AP, IA, USA | 42.40N | 90.70W | 329 | -6.00 (NAC) | 87-06 | 725470 | -26.1 | -26 | -34.5 | 38.7 | 32.9 | 34.1 | 33.9 | 34 | 33.6333 | 34 | 30.7 | 32 | 31.1 | 31 | 31.2667 | 31 | 361 | United_StatesIowaDUBUQUE REGIONAL AP
United_States | Iowa | M3 | ESTHERVILLE MUNI | ESTHERVILLE MUNI, IA, USA | 43.40N | 94.75W | 401 | -6.00 (NAC) | 96-06 | 726499 | -26 | -26 | -30.5 | 37.6 | 33.9 | 33.9 | 32.2 | 33 | 33.3333 | 34 | 32.2 | 32.3 | 29.8 | 31 | 31.4333 | 31 | 362 | United_StatesIowaESTHERVILLE MUNI
United_States | Iowa | M3 | FAIR FIELD | FAIR FIELD, IA, USA | 41.05N | 91.98W | 244 | -6.00 (NAC) | 95-06 | 726498 | -24 | N/A | N/A | N/A | 34.1 | 37.3 | 36.1 | 36 | 35.8333 | 37 | 32.7 | 35 | 33.7 | 34 | 33.8 | 34 | 363 | United_StatesIowaFAIR FIELD
United_States | Iowa | M3 | FORT DODGE (AWOS) | FORT DODGE (AWOS), IA, USA | 42.55N | 94.18W | 355 | -6.00 (NAC) | 82-06 | 725490 | -27.2 | -27 | -34.7 | 41.1 | 34.2 | 34.7 | 35.1 | 35 | 34.6667 | 35 | 32.1 | 32.8 | 32.2 | 32 | 32.3667 | 32 | 364 | United_StatesIowaFORT DODGE (AWOS)
United_States | Iowa | M3 | KEOKUK MUNI | KEOKUK MUNI, IA, USA | 40.47N | 91.43W | 205 | -6.00 (NAC) | 95-06 | 725456 | -23 | N/A | N/A | N/A | 33 | 37.7 | 36.2 | 36 | 35.6333 | 38 | 32.3 | 35.2 | 34 | 34 | 33.8333 | 34 | 365 | United_StatesIowaKEOKUK MUNI
United_States | Iowa | M3 | MARSHALL TOWN MUNI | MARSHALL TOWN MUNI, IA, USA | 42.10N | 92.92W | 296 | -6.00 (NAC) | 99-06 | 725461 | -25.9 | -26 | -33.5 | 37.9 | 32.4 | 33.9 | 32.9 | 33 | 33.0667 | 34 | 31.1 | 32.5 | 31.2 | 32 | 31.6 | 32 | 366 | United_StatesIowaMARSHALL TOWN MUNI
United_States | Iowa | M3 | MASON CITY MUNICIPAL ARPT | MASON CITY MUNICIPAL ARPT, IA, USA | 43.16N | 93.33W | 373 | -6.00 (NAC) | 82-06 | 725485 | -28.3 | -28 | -37.1 | 40.8 | 34.5 | 35 | 34.4 | 35 | 34.6333 | 35 | 32 | 32.8 | 31.5 | 32 | 32.1 | 32 | 367 | United_StatesIowaMASON CITY MUNICIPAL ARPT
United_States | Iowa | M3 | OTTUMWA INDUSTRIAL AP | OTTUMWA INDUSTRIAL AP, IA, USA | 41.11N | 92.45W | 258 | -6.00 (NAC) | 82-06 | 725465 | -23.5 | -24 | -32.4 | 41.3 | 34.9 | 36.7 | 36.6 | 36 | 36.0667 | 37 | 32.4 | 34.5 | 33.2 | 33 | 33.3667 | 33 | 368 | United_StatesIowaOTTUMWA INDUSTRIAL AP
United_States | Iowa | M3 | SIOUX CITY SIOUX GATEWAY AP | SIOUX CITY SIOUX GATEWAY AP, IA, USA | 42.39N | 96.38W | 336 | -6.00 (NAC) | 82-06 | 725570 | -26.2 | -26 | -33.2 | 42.7 | 36.1 | 36.5 | 35.6 | 36 | 36.0667 | 37 | 33.3 | 34 | 33 | 33 | 33.4333 | 33 | 369 | United_StatesIowaSIOUX CITY SIOUX GATEWAY AP
United_States | Iowa | M3 | SPENCER | SPENCER, IA, USA | 43.17N | 95.15W | 408 | -6.00 (NAC) | 82-06 | 726500 | -28 | -28 | -33.3 | 41 | 35 | 36 | 33.9 | 35 | 34.9667 | 36 | 32.4 | 32.9 | 31.7 | 32 | 32.3333 | 32 | 370 | United_StatesIowaSPENCER
United_States | Iowa | M3 | STORM LAKE | STORM LAKE, IA, USA | 42.60N | 95.23W | 454 | -6.00 (NAC) | 95-06 | 725496 | -25 | N/A | N/A | N/A | 34.9 | 36.1 | 33 | 35 | 34.6667 | 36 | 32.8 | 33 | 31.9 | 33 | 32.5667 | 33 | 371 | United_StatesIowaSTORM LAKE
United_States | Iowa | M3 | WASHINGTON | WASHINGTON, IA, USA | 41.28N | 91.67W | 230 | -6.00 (NAC) | 95-06 | 725454 | -24 | N/A | N/A | N/A | 34.7 | 36.1 | 34.9 | 35 | 35.2333 | 36 | 32.8 | 34.1 | 32.8 | 33 | 33.2333 | 33 | 372 | United_StatesIowaWASHINGTON
United_States | Iowa | M3 | WATERLOO MUNICIPAL AP | WATERLOO MUNICIPAL AP, IA, USA | 42.55N | 92.40W | 268 | -6.00 (NAC) | 82-06 | 725480 | -27.7 | -28 | -38.3 | 41 | 34.5 | 35.5 | 35.8 | 35 | 35.2667 | 36 | 32.1 | 33.2 | 32.3 | 33 | 32.5333 | 33 | 373 | United_StatesIowaWATERLOO MUNICIPAL AP
United_States | Iowa | M3 | WEBSTER CITY | WEBSTER CITY, IA, USA | 42.43N | 93.87W | 342 | -6.00 (NAC) | 95-06 | 725478 | -25.1 | -25 | -30.7 | 38.5 | 34.9 | 35.2 | 33.8 | 35 | 34.6333 | 35 | 32.9 | 34 | 32.2 | 33 | 33.0333 | 33 | 374 | United_StatesIowaWEBSTER CITY
United_States | Kansas | M3 | CHANUTE MARTIN JOHNSON AP | CHANUTE MARTIN JOHNSON AP, KS, USA | 37.67N | 95.48W | 308 | -6.00 (NAC) | 82-06 | 724507 | -19.4 | -19 | -26 | 44.1 | 34.1 | 38.2 | 38.7 | 37 | 37 | 38 | 32.4 | 36.6 | 37.1 | 35 | 35.3667 | 35 | 375 | United_StatesKansasCHANUTE MARTIN JOHNSON AP
United_States | Kansas | M3 | COFFEYVILLE MUNI | COFFEYVILLE MUNI, KS, USA | 37.10N | 95.57W | 230 | -6.00 (NAC) | 97-06 | 724519 | -17.4 | -17 | -27.8 | 45 | 36 | 38 | 39.8 | 38 | 37.9333 | 38 | 32.9 | 37.3 | 37.8 | 36 | 36 | 36 | 376 | United_StatesKansasCOFFEYVILLE MUNI
United_States | Kansas | M3 | CONCORDIA BLOSSER MUNI AP | CONCORDIA BLOSSER MUNI AP, KS, USA | 39.55N | 97.65W | 452 | -6.00 (NAC) | 82-06 | 724580 | -21.2 | -21 | -31.4 | 45.2 | 37.4 | 40.3 | 39.5 | 39 | 39.0667 | 40 | 34.9 | 37.9 | 37.2 | 37 | 36.6667 | 37 | 377 | United_StatesKansasCONCORDIA BLOSSER MUNI AP
United_States | Kansas | M3 | DODGE CITY REGIONAL AP | DODGE CITY REGIONAL AP, KS, USA | 37.77N | 99.97W | 790 | -6.00 (NAC) | 82-06 | 724510 | -20 | -20 | -29.1 | 44.1 | 38.4 | 39.9 | 39.1 | 39 | 39.1333 | 40 | 35.6 | 38.2 | 37.4 | 37 | 37.0667 | 37 | 378 | United_StatesKansasDODGE CITY REGIONAL AP
United_States | Kansas | M3 | ELKHART (AWOS) | ELKHART (AWOS), KS, USA | 37.00N | 101.90W | 1099 | -6.00 (NAC) | 92-06 | 724604 | -20 | N/A | N/A | N/A | 38 | 39 | 37.9 | 38 | 38.3 | 39 | 36.9 | 37.6 | 36.4 | 37 | 36.9667 | 37 | 379 | United_StatesKansasELKHART (AWOS)
United_States | Kansas | M3 | FT RILEY/MARSHALL A | FT RILEY/MARSHALL A, KS, USA | 39.05N | 96.77W | 324 | -6.00 (NAC) | 82-95 | 724550 | -20.4 | -20 | -33.9 | 43.1 | 38.1 | 39.9 | 39.4 | 39 | 39.1333 | 40 | 34.9 | 37.7 | 37.5 | 37 | 36.7 | 37 | 380 | United_StatesKansasFT RILEY/MARSHALL A
United_States | Kansas | M3 | GARDEN CITY MUNICIPAL AP | GARDEN CITY MUNICIPAL AP, KS, USA | 37.93N | 100.73W | 878 | -6.00 (NAC) | 82-06 | 724515 | -21.7 | -22 | -30.7 | 43.5 | 39 | 39.1 | 39.1 | 39 | 39.0667 | 39 | 36.1 | 37.4 | 36.9 | 37 | 36.8 | 37 | 381 | United_StatesKansasGARDEN CITY MUNICIPAL AP
United_States | Kansas | M3 | GOODLAND RENNER FIELD | GOODLAND RENNER FIELD, KS, USA | 39.37N | 101.69W | 1124 | -7.00 (NAM) | 82-06 | 724650 | -23.1 | -23 | -34.2 | 42.2 | 37.4 | 38.6 | 37.5 | 38 | 37.8333 | 39 | 35 | 36.7 | 35.4 | 36 | 35.7 | 36 | 382 | United_StatesKansasGOODLAND RENNER FIELD
United_States | Kansas | M3 | GREAT BEND (AWOS) | GREAT BEND (AWOS), KS, USA | 38.35N | 98.87W | 575 | -6.00 (NAC) | 92-06 | 724517 | -19 | -19 | -22.7 | 44.2 | 37.9 | 40.7 | 38.8 | 39 | 39.1333 | 41 | 35.3 | 37.9 | 37.3 | 37 | 36.8333 | 37 | 383 | United_StatesKansasGREAT BEND (AWOS)
United_States | Kansas | M3 | HAYS MUNI (AWOS) | HAYS MUNI (AWOS), KS, USA | 38.85N | 99.27W | 609 | -6.00 (NAC) | 92-06 | 724518 | -20 | -20 | -24.3 | 45 | 38.9 | 41.2 | 39.2 | 40 | 39.7667 | 41 | 36.2 | 38.9 | 37.6 | 38 | 37.5667 | 38 | 384 | United_StatesKansasHAYS MUNI (AWOS)
United_States | Kansas | M3 | HILL CITY MUNICIPAL AP | HILL CITY MUNICIPAL AP, KS, USA | 39.38N | 99.83W | 677 | -6.00 (NAC) | 96-06 | 724655 | -21 | -21 | -28 | 44.1 | 38 | 42 | 39.8 | 40 | 39.9333 | 42 | 36.3 | 39.1 | 37.5 | 38 | 37.6333 | 38 | 385 | United_StatesKansasHILL CITY MUNICIPAL AP
United_States | Kansas | M3 | LAWRENCE MUNI ARPT | LAWRENCE MUNI ARPT, KS, USA | 39.00N | 95.22W | 254 | -6.00 (NAC) | 97-06 | 724508 | -21.2 | -21 | -31.7 | 44.7 | 34.9 | 38.7 | 40.2 | 38 | 37.9333 | 39 | 32.9 | 37.2 | 37.5 | 36 | 35.8667 | 36 | 386 | United_StatesKansasLAWRENCE MUNI ARPT
United_States | Kansas | M3 | LIBERAL MUNI | LIBERAL MUNI, KS, USA | 37.03N | 100.95W | 901 | -6.00 (NAC) | 92-06 | 724516 | -17.8 | -18 | -24.7 | 43 | 38.8 | 39 | 38 | 39 | 38.6 | 39 | 36.3 | 37.7 | 37.2 | 37 | 37.0667 | 37 | 387 | United_StatesKansasLIBERAL MUNI
United_States | Kansas | M3 | MANHATTAN RGNL | MANHATTAN RGNL, KS, USA | 39.13N | 96.67W | 330 | -6.00 (NAC) | 96-06 | 724555 | -21.6 | -22 | -29.6 | 45.3 | 36.3 | 40 | 41.1 | 39 | 39.1333 | 40 | 34 | 37.9 | 37.7 | 37 | 36.5333 | 37 | 388 | United_StatesKansasMANHATTAN RGNL
United_States | Kansas | M3 | MCCONNELL AFB | MCCONNELL AFB, KS, USA | 37.62N | 97.27W | 414 | -6.00 (NAC) | 82-06 | 724505 | -17.4 | -17 | -26.9 | 44.9 | 37.5 | 40.1 | 39.9 | 39 | 39.1667 | 40 | 35 | 37.7 | 37.8 | 37 | 36.8333 | 37 | 389 | United_StatesKansasMCCONNELL AFB
United_States | Kansas | M3 | MEDICINE LODGE ASOS | MEDICINE LODGE ASOS, KS, USA | 37.28N | 98.55W | 469 | -6.00 (NAC) | 83-06 | 724520 | -17.1 | -17 | -27.2 | 46 | 39.1 | 41.4 | 40.7 | 40 | 40.4 | 41 | 36.5 | 39.6 | 38.9 | 38 | 38.3333 | 38 | 390 | United_StatesKansasMEDICINE LODGE ASOS
United_States | Kansas | M3 | NEWTON (AWOS) | NEWTON (AWOS), KS, USA | 38.05N | 97.28W | 467 | -6.00 (NAC) | 92-06 | 724509 | -17.4 | -17 | -25.9 | 43.2 | 35.9 | 39.8 | 37.9 | 38 | 37.8667 | 40 | 33.1 | 37.6 | 37 | 36 | 35.9 | 36 | 391 | United_StatesKansasNEWTON (AWOS)
United_States | Kansas | M3 | OLATHE/JOHNSON CO. | OLATHE/JOHNSON CO., KS, USA | 38.85N | 94.73W | 334 | -6.00 (NAC) | 96-06 | 724468 | -19.5 | -20 | -25 | 42.5 | 32.8 | 37.4 | 37.8 | 36 | 36 | 37 | 32 | 35.9 | 36.1 | 35 | 34.6667 | 35 | 392 | United_StatesKansasOLATHE/JOHNSON CO.
United_States | Kansas | M3 | PARSONS\TRI CITY | PARSONS\TRI CITY, KS, USA | 37.33N | 95.52W | 274 | -6.00 (NAC) | 97-06 | 745431 | -18.6 | -19 | -25.5 | 44.4 | 34.8 | 37.8 | 38.9 | 37 | 37.1667 | 38 | 32.7 | 36.4 | 37.5 | 36 | 35.5333 | 36 | 393 | United_StatesKansasPARSONS\TRI CITY
United_States | Kansas | M3 | RUSSELL MUNICIPAL AP | RUSSELL MUNICIPAL AP, KS, USA | 38.87N | 98.83W | 568 | -6.00 (NAC) | 82-06 | 724585 | -21.3 | -21 | -30.9 | 45.5 | 38 | 40.9 | 39.1 | 39 | 39.3333 | 41 | 35.7 | 38.7 | 37.3 | 37 | 37.2333 | 37 | 394 | United_StatesKansasRUSSELL MUNICIPAL AP
United_States | Kansas | M3 | SALINA MUNICIPAL AP | SALINA MUNICIPAL AP, KS, USA | 38.81N | 97.66W | 391 | -6.00 (NAC) | 82-06 | 724586 | -20.2 | -20 | -31.1 | 44.9 | 38 | 41.3 | 40.1 | 40 | 39.8 | 41 | 36.1 | 39 | 38 | 38 | 37.7 | 38 | 395 | United_StatesKansasSALINA MUNICIPAL AP
United_States | Kansas | M3 | TOPEKA FORBES FIELD | TOPEKA FORBES FIELD, KS, USA | 38.95N | 95.66W | 329 | -6.00 (NAC) | 82-06 | 724565 | -20.4 | -20 | -30.4 | 44.3 | 34.8 | 38.1 | 38.6 | 37 | 37.1667 | 38 | 33 | 36.1 | 35.9 | 35 | 35 | 35 | 396 | United_StatesKansasTOPEKA FORBES FIELD
United_States | Kansas | M3 | TOPEKA MUNICIPAL AP | TOPEKA MUNICIPAL AP, KS, USA | 39.07N | 95.63W | 270 | -6.00 (NAC) | 82-06 | 724560 | -20.9 | -21 | -31.8 | 43.8 | 35.2 | 37.9 | 39.1 | 37 | 37.4 | 38 | 33.2 | 36.2 | 36.3 | 35 | 35.2333 | 35 | 397 | United_StatesKansasTOPEKA MUNICIPAL AP
United_States | Kansas | M3 | WICHITA MID-CONTINENT AP | WICHITA MID-CONTINENT AP, KS, USA | 37.65N | 97.43W | 408 | -6.00 (NAC) | 82-06 | 724500 | -18.2 | -18 | -28.6 | 44.7 | 38 | 40.5 | 39.7 | 39 | 39.4 | 41 | 35.2 | 38.3 | 37.7 | 37 | 37.0667 | 37 | 398 | United_StatesKansasWICHITA MID-CONTINENT AP
United_States | Kansas | M3 | WICHITA/COL. JABARA | WICHITA/COL. JABARA, KS, USA | 37.75N | 97.22W | 433 | -6.00 (NAC) | 95-06 | 724504 | -16.9 | -17 | -26.6 | 44.9 | 35.3 | 40.8 | 39.1 | 38 | 38.4 | 41 | 32.9 | 37.8 | 37.6 | 36 | 36.1 | 36 | 399 | United_StatesKansasWICHITA/COL. JABARA
United_States | Kansas | M3 | WINFIELD\ARK CITY | WINFIELD\ARK CITY, KS, USA | 37.30N | 97.00W | 353 | -6.00 (NAC) | 99-06 | 724502 | -17.2 | -17 | -21.6 | 44.4 | 36.3 | 40.1 | 40.9 | 39 | 39.1 | 40 | 33.7 | 38 | 38 | 37 | 36.5667 | 37 | 400 | United_StatesKansasWINFIELD\ARK CITY
United_States | Kentucky | E2 | BOWLING GREEN WARREN CO AP | BOWLING GREEN WARREN CO AP, KY, USA | 36.98N | 86.44W | 164 | -6.00 (NAC) | 82-06 | 746716 | -17 | -17 | -30.1 | 41.3 | 33.8 | 36.2 | 35.8 | 35 | 35.2667 | 36 | 32.4 | 33.9 | 33.9 | 33 | 33.4 | 33 | 401 | United_StatesKentuckyBOWLING GREEN WARREN CO AP
United_States | Kentucky | E2 | CAPITAL CITY ARPT | CAPITAL CITY ARPT, KY, USA | 38.18N | 84.90W | 245 | -5.00 (NAE) | 97-06 | 724233 | -17.2 | -17 | -25.7 | 41.5 | 32.8 | 34.8 | 35.9 | 35 | 34.5 | 35 | 31.4 | 32.9 | 32.9 | 32 | 32.4 | 32 | 402 | United_StatesKentuckyCAPITAL CITY ARPT
United_States | Kentucky | E2 | CINCINNATI NORTHERN KY AP | CINCINNATI NORTHERN KY AP, KY, USA | 39.04N | 84.67W | 269 | -5.00 (NAE) | 82-06 | 724210 | -20.9 | -21 | -34.2 | 40 | 33.5 | 35.6 | 34.8 | 35 | 34.6333 | 36 | 31.5 | 33.2 | 32.6 | 32 | 32.4333 | 32 | 403 | United_StatesKentuckyCINCINNATI NORTHERN KY AP
United_States | Kentucky | E2 | FORT CAMPBELL (AAF) | FORT CAMPBELL (AAF), KY, USA | 36.67N | 87.50W | 173 | -6.00 (NAC) | 82-06 | 746710 | -16.3 | -16 | -28.3 | 40.7 | 35 | 36.7 | 36.4 | 36 | 36.0333 | 37 | 32.9 | 34.5 | 34.6 | 34 | 34 | 34 | 404 | United_StatesKentuckyFORT CAMPBELL (AAF)
United_States | Kentucky | E2 | FORT KNOX/GODMAN | FORT KNOX/GODMAN, KY, USA | 37.90N | 85.97W | 239 | -5.00 (NAE) | 82-06 | 724240 | -17.8 | -18 | -30.1 | 41.5 | 34 | 36.9 | 36 | 36 | 35.6333 | 37 | 32.3 | 34 | 33.7 | 33 | 33.3333 | 33 | 405 | United_StatesKentuckyFORT KNOX/GODMAN
United_States | Kentucky | E2 | HENDERSON CITY | HENDERSON CITY, KY, USA | 37.82N | 87.68W | 117 | -6.00 (NAC) | 92-06 | 724238 | -19.4 | -19 | -36.7 | 38.5 | 34 | 35.1 | 36.1 | 35 | 35.0667 | 35 | 32.8 | 33.5 | 33.8 | 33 | 33.3667 | 33 | 406 | United_StatesKentuckyHENDERSON CITY
United_States | Kentucky | E2 | JACKSON JULIAN CARROLL AP | JACKSON JULIAN CARROLL AP, KY, USA | 37.59N | 83.31W | 414 | -5.00 (NAE) | 82-06 | 724236 | -17.9 | -18 | -30.9 | 38.5 | 32.1 | 34 | 34.1 | 33 | 33.4 | 34 | 30.4 | 32 | 31.9 | 31 | 31.4333 | 31 | 407 | United_StatesKentuckyJACKSON JULIAN CARROLL AP
United_States | Kentucky | E2 | LEXINGTON BLUEGRASS AP | LEXINGTON BLUEGRASS AP, KY, USA | 38.04N | 84.61W | 301 | -5.00 (NAE) | 82-06 | 724220 | -18.8 | -19 | -31.5 | 40.3 | 33.5 | 35.2 | 35 | 35 | 34.5667 | 35 | 31.5 | 33.2 | 33 | 33 | 32.5667 | 33 | 408 | United_StatesKentuckyLEXINGTON BLUEGRASS AP
United_States | Kentucky | E2 | LONDON-CORBIN AP | LONDON-CORBIN AP, KY, USA | 37.09N | 84.08W | 369 | -5.00 (NAE) | 82-06 | 724243 | -18 | -18 | -31.2 | 38.9 | 32.3 | 33.8 | 34 | 33 | 33.3667 | 34 | 30.7 | 32.3 | 32.3 | 32 | 31.7667 | 32 | 409 | United_StatesKentuckyLONDON-CORBIN AP
United_States | Kentucky | E2 | LOUISVILLE BOWMAN FIELD | LOUISVILLE BOWMAN FIELD, KY, USA | 38.23N | 85.66W | 170 | -5.00 (NAE) | 82-06 | 724235 | -17.7 | -18 | -31.5 | 41.6 | 34.4 | 37 | 36.2 | 36 | 35.8667 | 37 | 32.7 | 34.1 | 33.9 | 34 | 33.5667 | 34 | 410 | United_StatesKentuckyLOUISVILLE BOWMAN FIELD
United_States | Kentucky | E2 | LOUISVILLE STANDIFORD FIELD | LOUISVILLE STANDIFORD FIELD, KY, USA | 38.18N | 85.73W | 149 | -5.00 (NAE) | 82-06 | 724230 | -17.3 | -17 | -30.6 | 40.8 | 34.1 | 36.3 | 35.8 | 35 | 35.4 | 36 | 32.6 | 34.2 | 34 | 34 | 33.6 | 34 | 411 | United_StatesKentuckyLOUISVILLE STANDIFORD FIELD
United_States | Kentucky | E2 | PADUCAH BARKLEY REGIONAL AP | PADUCAH BARKLEY REGIONAL AP, KY, USA | 37.06N | 88.77W | 126 | -6.00 (NAC) | 82-06 | 724350 | -17.1 | -17 | -28.3 | 40 | 35 | 36.4 | 36.5 | 36 | 35.9667 | 36 | 33.4 | 34.7 | 34.7 | 34 | 34.2667 | 34 | 412 | United_StatesKentuckyPADUCAH BARKLEY REGIONAL AP
United_States | Kentucky | E2 | SOMERSET(AWOS) | SOMERSET(AWOS), KY, USA | 38.00N | 84.60W | 283 | -5.00 (NAE) | 92-06 | 724354 | -13 | -13 | -18.4 | 41.4 | 34.2 | 36.5 | 36.4 | 36 | 35.7 | 37 | 32.9 | 34.7 | 34.6 | 34 | 34.0667 | 34 | 413 | United_StatesKentuckySOMERSET(AWOS)
United_States | Louisiana | E1 | ALEXANDRIA ESLER REGIONAL AP | ALEXANDRIA ESLER REGIONAL AP, LA, USA | 31.40N | 92.30W | 36 | -6.00 (NAC) | 87-06 | 722487 | -6.6 | -7 | -10.3 | 44 | 36.2 | 37.7 | 38.1 | 37 | 37.3333 | 38 | 33.9 | 36 | 36.4 | 35 | 35.4333 | 35 | 414 | United_StatesLouisianaALEXANDRIA ESLER REGIONAL AP
United_States | Louisiana | E1 | ALEXANDRIA INTERNATIONAL | ALEXANDRIA INTERNATIONAL, LA, USA | 31.33N | 92.55W | 27 | -6.00 (NAC) | 82-06 | 747540 | -6.6 | -7 | -13.7 | 42 | 36.3 | 37.1 | 37.6 | 37 | 37 | 37 | 34.1 | 35.1 | 36 | 35 | 35.0667 | 35 | 415 | United_StatesLouisianaALEXANDRIA INTERNATIONAL
United_States | Louisiana | E1 | BARKSDALE AFB | BARKSDALE AFB, LA, USA | 32.50N | 93.67W | 54 | -6.00 (NAC) | 82-06 | 722485 | -8.7 | -9 | -17.1 | 42.8 | 36 | 37.7 | 37.9 | 37 | 37.2 | 38 | 34 | 35.9 | 36.5 | 35 | 35.4667 | 35 | 416 | United_StatesLouisianaBARKSDALE AFB
United_States | Louisiana | E1 | BATON ROUGE RYAN ARPT | BATON ROUGE RYAN ARPT, LA, USA | 30.54N | 91.15W | 23 | -6.00 (NAC) | 82-06 | 722317 | -6.2 | -6 | -14.6 | 39.6 | 35 | 35.4 | 35.9 | 35 | 35.4333 | 35 | 33.8 | 34.2 | 34.6 | 34 | 34.2 | 34 | 417 | United_StatesLouisianaBATON ROUGE RYAN ARPT
United_States | Louisiana | E1 | FORT POLK (ARMY) | FORT POLK (ARMY), LA, USA | 31.05N | 93.20W | 102 | -6.00 (NAC) | 82-06 | 722390 | -6.3 | -6 | -13.5 | 42 | 35.6 | 37.2 | 37.5 | 37 | 36.7667 | 37 | 33.9 | 35.1 | 35.8 | 35 | 34.9333 | 35 | 418 | United_StatesLouisianaFORT POLK (ARMY)
United_States | Louisiana | E1 | GRAND ISLE | GRAND ISLE, LA, USA | 29.27N | 89.95W | 10 | -6.00 (NAC) | 85-05 | 994290 | 0.4 | 0 | -9.8 | 35.1 | 31.3 | 32.4 | 32.7 | 32 | 32.1333 | 32 | 30.2 | 31.3 | 31.5 | 31 | 31 | 31 | 419 | United_StatesLouisianaGRAND ISLE
United_States | Louisiana | E1 | LAFAYETTE REGIONAL AP | LAFAYETTE REGIONAL AP, LA, USA | 30.21N | 91.99W | 13 | -6.00 (NAC) | 82-06 | 722405 | -5.7 | -6 | -15.3 | 39.5 | 34.9 | 35.3 | 36 | 35 | 35.4 | 35 | 33.6 | 34.1 | 34.7 | 34 | 34.1333 | 34 | 420 | United_StatesLouisianaLAFAYETTE REGIONAL AP
United_States | Louisiana | E1 | LAKE CHARLES REGIONAL ARPT | LAKE CHARLES REGIONAL ARPT, LA, USA | 30.13N | 93.23W | 3 | -6.00 (NAC) | 82-06 | 722400 | -4.7 | -5 | -11.9 | 40.5 | 34.3 | 35.3 | 36 | 35 | 35.2 | 35 | 33.1 | 34.1 | 34.7 | 34 | 33.9667 | 34 | 421 | United_StatesLouisianaLAKE CHARLES REGIONAL ARPT
United_States | Louisiana | E1 | MONROE REGIONAL AP | MONROE REGIONAL AP, LA, USA | 32.51N | 92.04W | 25 | -6.00 (NAC) | 82-06 | 722486 | -8 | -8 | -17.2 | 41.3 | 36.4 | 37.3 | 37.8 | 37 | 37.1667 | 37 | 34.6 | 35.8 | 36.2 | 36 | 35.5333 | 36 | 422 | United_StatesLouisianaMONROE REGIONAL AP
United_States | Louisiana | E1 | NEW ORLEANS ALVIN CALLENDER F | NEW ORLEANS ALVIN CALLENDER F, LA, USA | 29.83N | 90.03W | 0 | -6.00 (NAC) | 82-06 | 722316 | -4.5 | -5 | -13.6 | 38 | 33.9 | 34.5 | 34.9 | 34 | 34.4333 | 35 | 32.8 | 33.5 | 33.7 | 33 | 33.3333 | 33 | 423 | United_StatesLouisianaNEW ORLEANS ALVIN CALLENDER F
United_States | Louisiana | E1 | NEW ORLEANS INTL ARPT | NEW ORLEANS INTL ARPT, LA, USA | 29.99N | 90.25W | 6 | -6.00 (NAC) | 82-06 | 722310 | -3.9 | -4 | -12.2 | 38.6 | 34.4 | 35.6 | 35.5 | 35 | 35.1667 | 36 | 33.1 | 34.1 | 34.1 | 34 | 33.7667 | 34 | 424 | United_StatesLouisianaNEW ORLEANS INTL ARPT
United_States | Louisiana | E1 | NEW ORLEANS LAKEFRONT AP | NEW ORLEANS LAKEFRONT AP, LA, USA | 30.04N | 90.03W | 3 | -6.00 (NAC) | 85-06 | 722315 | -1.3 | -1 | -10.1 | 40.6 | 34.4 | 35.2 | 35.7 | 35 | 35.1 | 35 | 33.3 | 34 | 34.2 | 34 | 33.8333 | 34 | 425 | United_StatesLouisianaNEW ORLEANS LAKEFRONT AP
United_States | Louisiana | E1 | PATTERSON MEMORIAL | PATTERSON MEMORIAL, LA, USA | 29.72N | 91.33W | 3 | -6.00 (NAC) | 92-06 | 722329 | -2.5 | -3 | -11 | 41 | 33.9 | 36.3 | 36 | 35 | 35.4 | 36 | 32.7 | 33.8 | 33.9 | 33 | 33.4667 | 33 | 426 | United_StatesLouisianaPATTERSON MEMORIAL
United_States | Louisiana | E1 | SALT POINT (RAMOS) | SALT POINT (RAMOS), LA, USA | 29.60N | 91.30W | 3 | -6.00 (NAC) | 89-06 | 722403 | -2 | N/A | N/A | N/A | 33.5 | 34.3 | 34.4 | 34 | 34.0667 | 34 | 32.4 | 33.1 | 33.1 | 33 | 32.8667 | 33 | 427 | United_StatesLouisianaSALT POINT (RAMOS)
United_States | Louisiana | E1 | SHREVEPORT DOWNTOWN | SHREVEPORT DOWNTOWN, LA, USA | 32.54N | 93.74W | 55 | -6.00 (NAC) | 97-06 | 722484 | -6 | -6 | -8.8 | 44.7 | 37.3 | 39 | 39 | 38 | 38.4333 | 39 | 35.2 | 37.3 | 37.4 | 37 | 36.6333 | 37 | 428 | United_StatesLouisianaSHREVEPORT DOWNTOWN
United_States | Louisiana | E1 | SHREVEPORT REGIONAL ARPT | SHREVEPORT REGIONAL ARPT, LA, USA | 32.45N | 93.82W | 79 | -6.00 (NAC) | 82-06 | 722480 | -7.9 | -8 | -15.9 | 42.5 | 36.4 | 38.1 | 38.7 | 38 | 37.7333 | 38 | 34.2 | 36.1 | 36.8 | 36 | 35.7 | 36 | 429 | United_StatesLouisianaSHREVEPORT REGIONAL ARPT
United_States | Louisiana | E1 | SOUTHWEST PASS | SOUTHWEST PASS, LA, USA | 28.90N | 89.43W | 12 | -6.00 (NAC) | 89-06 | 994010 | 1.9 | 2 | -6.6 | 35.7 | 30.8 | 31.8 | 32.2 | 32 | 31.6 | 32 | 29.9 | 30.8 | 31.3 | 31 | 30.6667 | 31 | 430 | United_StatesLouisianaSOUTHWEST PASS
United_States | Maine | E5 | AUBURN-LEWISTON | AUBURN-LEWISTON, ME, USA | 44.05N | 70.28W | 88 | -5.00 (NAE) | 92-06 | 726184 | -26.7 | -27 | -37.4 | 38.3 | 32.4 | 32.8 | 32.5 | 33 | 32.5667 | 33 | 29.5 | 30.6 | 30.1 | 30 | 30.0667 | 30 | 431 | United_StatesMaineAUBURN-LEWISTON
United_States | Maine | E5 | AUGUSTA AIRPORT | AUGUSTA AIRPORT, ME, USA | 44.32N | 69.80W | 110 | -5.00 (NAE) | 82-06 | 726185 | -23.4 | -23 | -30.6 | 37.9 | 32.1 | 33 | 32.2 | 32 | 32.4333 | 33 | 29.1 | 30.3 | 30 | 30 | 29.8 | 30 | 432 | United_StatesMaineAUGUSTA AIRPORT
United_States | Maine | E5 | BANGOR INTERNATIONAL AP | BANGOR INTERNATIONAL AP, ME, USA | 44.81N | 68.82W | 59 | -5.00 (NAE) | 82-06 | 726088 | -26.7 | -27 | -35.1 | 37.6 | 32.8 | 32.9 | 32.6 | 33 | 32.7667 | 33 | 29.8 | 30.6 | 30.2 | 30 | 30.2 | 30 | 433 | United_StatesMaineBANGOR INTERNATIONAL AP
United_States | Maine | E5 | BAR HARBOR (AWOS) | BAR HARBOR (AWOS), ME, USA | 44.45N | 68.37W | 26 | -5.00 (NAE) | 92-06 | 726077 | -22 | -22 | -31.2 | 35.8 | 29 | 29.9 | 30.1 | 30 | 29.6667 | 30 | 26 | 27.5 | 27.3 | 27 | 26.9333 | 27 | 434 | United_StatesMaineBAR HARBOR (AWOS)
United_States | Maine | E5 | BRUNSWICK NAS | BRUNSWICK NAS, ME, USA | 43.90N | 69.93W | 23 | -5.00 (NAE) | 82-06 | 743920 | -24.4 | -24 | -33.1 | 37.6 | 31.8 | 32.7 | 32.3 | 32 | 32.2667 | 33 | 28.8 | 30.2 | 29.8 | 30 | 29.6 | 30 | 435 | United_StatesMaineBRUNSWICK NAS
United_States | Maine | E5 | CARIBOU MUNICIPAL ARPT | CARIBOU MUNICIPAL ARPT, ME, USA | 46.87N | 68.03W | 190 | -5.00 (NAE) | 82-06 | 727120 | -30.6 | -31 | -37.9 | 35.9 | 30.9 | 31.5 | 30.7 | 31 | 31.0333 | 32 | 28.2 | 28.8 | 28.3 | 28 | 28.4333 | 28 | 436 | United_StatesMaineCARIBOU MUNICIPAL ARPT
United_States | Maine | E5 | GREENVILLE (AMOS) | GREENVILLE (AMOS), ME, USA | 45.47N | 69.58W | 316 | -5.00 (NAE) | 91-06 | 726190 | -29.6 | -30 | -40.6 | 35.1 | 30.2 | 30 | 30.1 | 30 | 30.1 | 30 | 27.7 | 27.8 | 27.7 | 28 | 27.7333 | 28 | 437 | United_StatesMaineGREENVILLE (AMOS)
United_States | Maine | E5 | HOULTON INTL ARPT | HOULTON INTL ARPT, ME, USA | 46.12N | 67.79W | 145 | -5.00 (NAE) | 82-06 | 727033 | -32.2 | -32 | -40.5 | 37.3 | 32 | 31.7 | 31.7 | 32 | 31.8 | 32 | 29 | 29.5 | 29.1 | 29 | 29.2 | 29 | 438 | United_StatesMaineHOULTON INTL ARPT
United_States | Maine | E5 | LORING AFB/LIMESTON | LORING AFB/LIMESTON, ME, USA | 46.95N | 67.88W | 227 | -5.00 (NAE) | 82-94 | 727125 | -28.8 | -29 | -32.9 | 36 | 30.4 | 31.7 | 30.3 | 31 | 30.8 | 32 | 27.3 | 29 | 28 | 28 | 28.1 | 28 | 439 | United_StatesMaineLORING AFB/LIMESTON
United_States | Maine | E5 | MATINICUS ROCK | MATINICUS ROCK, ME, USA | 43.78N | 68.87W | 27 | -5.00 (NAE) | 85-06 | 994370 | -18.1 | -18 | -24 | 27.8 | 19.5 | 21.8 | 21.6 | 21 | 20.9667 | 22 | 17.3 | 20 | 20.2 | 19 | 19.1667 | 19 | 440 | United_StatesMaineMATINICUS ROCK
United_States | Maine | E5 | MT DESERT ROCK | MT DESERT ROCK, ME, USA | 43.97N | 68.12W | 16 | -5.00 (NAE) | 89-06 | 994060 | -17.8 | -18 | -24.1 | 25.2 | 18.2 | 20.8 | 20.8 | 20 | 19.9333 | 21 | 16 | 18.9 | 19.4 | 18 | 18.1 | 18 | 441 | United_StatesMaineMT DESERT ROCK
United_States | Maine | E5 | NORTHERN AROOSTOOK | NORTHERN AROOSTOOK, ME, USA | 47.28N | 68.30W | 309 | -5.00 (NAE) | 95-06 | 726083 | -28.3 | -28 | -35.2 | 34.6 | 30.8 | 28.8 | 30.8 | 30 | 30.1333 | 29 | 27.5 | 27.2 | 27.7 | 27 | 27.4667 | 27 | 442 | United_StatesMaineNORTHERN AROOSTOOK
United_States | Maine | E5 | PORTLAND INTL JETPORT | PORTLAND INTL JETPORT, ME, USA | 43.64N | 70.30W | 19 | -5.00 (NAE) | 82-06 | 726060 | -22.7 | -23 | -30.2 | 38.5 | 32.4 | 33.1 | 32.5 | 33 | 32.6667 | 33 | 29.2 | 30.4 | 29.6 | 30 | 29.7333 | 30 | 443 | United_StatesMainePORTLAND INTL JETPORT
United_States | Maine | E5 | PRESQUE ISLE MUNICIP | PRESQUE ISLE MUNICIP, ME, USA | 46.69N | 68.03W | 163 | -5.00 (NAE) | 92-06 | 727130 | -34.1 | -34 | -45.1 | 36.1 | 31.7 | 31.3 | 31.3 | 31 | 31.4333 | 31 | 29 | 28.8 | 28.6 | 29 | 28.8 | 29 | 444 | United_StatesMainePRESQUE ISLE MUNICIP
United_States | Maine | E5 | ROCKLAND/KNOX(AWOS) | ROCKLAND/KNOX(AWOS), ME, USA | 44.07N | 69.10W | 17 | -5.00 (NAE) | 92-06 | 726079 | -21.3 | -21 | -30.1 | 34.4 | 28.9 | 30.9 | 29.1 | 30 | 29.6333 | 31 | 26.3 | 27.6 | 27 | 27 | 26.9667 | 27 | 445 | United_StatesMaineROCKLAND/KNOX(AWOS)
United_States | Maine | E5 | SANFORD MUNI (AWOS) | SANFORD MUNI (AWOS), ME, USA | 43.40N | 70.72W | 74 | -5.00 (NAE) | 92-06 | 726064 | -27.2 | -27 | -36.9 | 37.9 | 32.8 | 34 | 32.9 | 33 | 33.2333 | 34 | 31.1 | 31.2 | 30.2 | 31 | 30.8333 | 31 | 446 | United_StatesMaineSANFORD MUNI (AWOS)
United_States | Maine | E5 | WATERVILLE (AWOS) | WATERVILLE (AWOS), ME, USA | 44.53N | 69.68W | 101 | -5.00 (NAE) | 92-06 | 726073 | -25 | N/A | N/A | N/A | 32.2 | 32.4 | 32.1 | 32 | 32.2333 | 32 | 28.8 | 29.1 | 29.1 | 29 | 29 | 29 | 447 | United_StatesMaineWATERVILLE (AWOS)
United_States | Maine | E5 | WISCASSET | WISCASSET, ME, USA | 43.97N | 69.72W | 21 | -5.00 (NAE) | 95-06 | 727135 | -22.8 | -23 | -34.4 | 36.8 | 31.3 | 32.4 | 32.2 | 32 | 31.9667 | 32 | 28 | 29.2 | 28.9 | 29 | 28.7 | 29 | 448 | United_StatesMaineWISCASSET
United_States | Maryland | E3 | ANDREWS AFB | ANDREWS AFB, MD, USA | 38.82N | 76.87W | 86 | -5.00 (NAE) | 82-06 | 745940 | -14.8 | -15 | -24.2 | 40.9 | 34.6 | 36.9 | 36.2 | 36 | 35.9 | 37 | 32.6 | 34.9 | 33.8 | 34 | 33.7667 | 34 | 449 | United_StatesMarylandANDREWS AFB
United_States | Maryland | E3 | BALTIMORE BLT-WASHNGTN INT'L | BALTIMORE BLT-WASHNGTN INT'L, MD, USA | 39.17N | 76.68W | 47 | -5.00 (NAE) | 82-06 | 724060 | -14.9 | -15 | -24 | 41.3 | 34.8 | 36.7 | 36 | 36 | 35.8333 | 37 | 32.9 | 34.8 | 33.7 | 34 | 33.8 | 34 | 450 | United_StatesMarylandBALTIMORE BLT-WASHNGTN INT'L
United_States | Maryland | E3 | PATUXENT RIVER NAS | PATUXENT RIVER NAS, MD, USA | 38.28N | 76.40W | 12 | -5.00 (NAE) | 82-06 | 724040 | -12.5 | -13 | -20.4 | 39.9 | 34 | 36 | 34.7 | 35 | 34.9 | 36 | 32.2 | 34 | 32.4 | 33 | 32.8667 | 33 | 451 | United_StatesMarylandPATUXENT RIVER NAS
United_States | Maryland | E3 | SALISBURY WICOMICO CO AP | SALISBURY WICOMICO CO AP, MD, USA | 38.34N | 75.51W | 18 | -5.00 (NAE) | 82-06 | 724045 | -14.4 | -14 | -22.3 | 39.6 | 34.4 | 35.9 | 34.9 | 35 | 35.0667 | 36 | 32.5 | 34.1 | 32.8 | 33 | 33.1333 | 33 | 452 | United_StatesMarylandSALISBURY WICOMICO CO AP
United_States | Maryland | E3 | THOMAS POINT | THOMAS POINT, MD, USA | 38.90N | 76.43W | 12 | -5.00 (NAE) | 85-06 | 994400 | -10.2 | -10 | -19.3 | 36 | 30.9 | 32.6 | 31.7 | 32 | 31.7333 | 33 | 28.9 | 30.7 | 30 | 30 | 29.8667 | 30 | 453 | United_StatesMarylandTHOMAS POINT
United_States | Massachusetts | E5 | BARNSTABLE MUNI BOA | BARNSTABLE MUNI BOA, MA, USA | 41.67N | 70.27W | 17 | -5.00 (NAE) | 87-06 | 725067 | -15.8 | -16 | -24.6 | 39.6 | 30 | 32.2 | 31.2 | 31 | 31.1333 | 32 | 27.1 | 29.1 | 28.7 | 28 | 28.3 | 28 | 454 | United_StatesMassachusettsBARNSTABLE MUNI BOA
United_States | Massachusetts | E5 | BOSTON LOGAN INT'L ARPT | BOSTON LOGAN INT'L ARPT, MA, USA | 42.36N | 71.01W | 9 | -5.00 (NAE) | 82-06 | 725090 | -16.5 | -17 | -22.9 | 39.5 | 34 | 35.4 | 34.1 | 35 | 34.5 | 35 | 31.3 | 32.8 | 31.9 | 32 | 32 | 32 | 455 | United_StatesMassachusettsBOSTON LOGAN INT'L ARPT
United_States | Massachusetts | E5 | BUZZARDS BAY | BUZZARDS BAY, MA, USA | 41.38N | 71.03W | 17 | -5.00 (NAE) | 85-06 | 994140 | -14.9 | -15 | -20.8 | 29.5 | 23.8 | 26.7 | 25.5 | 25 | 25.3333 | 27 | 21.7 | 24.4 | 24.2 | 23 | 23.4333 | 23 | 456 | United_StatesMassachusettsBUZZARDS BAY
United_States | Massachusetts | E5 | CHATHAM MUNI ARPT | CHATHAM MUNI ARPT, MA, USA | 41.68N | 70.00W | 19 | -5.00 (NAE) | 82-06 | 725069 | -15 | N/A | N/A | N/A | 27.8 | 31.2 | 30.1 | 30 | 29.7 | 31 | 25 | 27.8 | 27.5 | 27 | 26.7667 | 27 | 457 | United_StatesMassachusettsCHATHAM MUNI ARPT
United_States | Massachusetts | E5 | LAWRENCE MUNI | LAWRENCE MUNI, MA, USA | 42.72N | 71.12W | 46 | -5.00 (NAE) | 97-06 | 744904 | -18.1 | -18 | -26.7 | 38.8 | 32.9 | 33.9 | 33.8 | 34 | 33.5333 | 34 | 31.4 | 32.2 | 32.1 | 32 | 31.9 | 32 | 458 | United_StatesMassachusettsLAWRENCE MUNI
United_States | Massachusetts | E5 | MARTHAS VINEYARD | MARTHAS VINEYARD, MA, USA | 41.40N | 70.62W | 21 | -5.00 (NAE) | 97-06 | 725066 | -16.9 | -17 | -23.9 | 36.3 | 28.8 | 31.3 | 31.3 | 30 | 30.4667 | 31 | 26.3 | 28 | 28 | 27 | 27.4333 | 27 | 459 | United_StatesMassachusettsMARTHAS VINEYARD
United_States | Massachusetts | E5 | NEW BEDFORD RGNL | NEW BEDFORD RGNL, MA, USA | 41.67N | 70.95W | 25 | -5.00 (NAE) | 96-06 | 725065 | -16.9 | -17 | -25.9 | 39.8 | 31.4 | 33.8 | 32.8 | 33 | 32.6667 | 34 | 29 | 32 | 30.8 | 31 | 30.6 | 31 | 460 | United_StatesMassachusettsNEW BEDFORD RGNL
United_States | Massachusetts | E5 | NORWOOD MEMORIAL | NORWOOD MEMORIAL, MA, USA | 42.18N | 71.18W | 15 | -5.00 (NAE) | 98-06 | 725098 | -19 | N/A | N/A | N/A | 32.9 | 34.8 | 34 | 34 | 33.9 | 35 | 31.3 | 32.5 | 32.2 | 32 | 32 | 32 | 461 | United_StatesMassachusettsNORWOOD MEMORIAL
United_States | Massachusetts | E5 | OTIS ANGB | OTIS ANGB, MA, USA | 41.65N | 70.52W | 40 | -5.00 (NAE) | 82-06 | 725060 | -16.2 | -16 | -23.9 | 36.9 | 30.9 | 32.2 | 31.1 | 31 | 31.4 | 32 | 27.6 | 29.4 | 28.7 | 29 | 28.5667 | 29 | 462 | United_StatesMassachusettsOTIS ANGB
United_States | Massachusetts | E5 | PLYMOUTH MUNICIPAL | PLYMOUTH MUNICIPAL, MA, USA | 41.92N | 70.73W | 45 | -5.00 (NAE) | 95-06 | 725064 | -17.8 | -18 | -25.9 | 40 | 32.3 | 34 | 33.7 | 33 | 33.3333 | 34 | 29.9 | 32.1 | 30.2 | 31 | 30.7333 | 31 | 463 | United_StatesMassachusettsPLYMOUTH MUNICIPAL
United_States | Massachusetts | E5 | PROVINCETOWN (AWOS) | PROVINCETOWN (AWOS), MA, USA | 42.07N | 70.22W | 2 | -5.00 (NAE) | 92-06 | 725073 | -13.7 | -14 | -21.9 | 36.2 | 28.8 | 31.8 | 29 | 30 | 29.8667 | 32 | 26.3 | 28.8 | 27.6 | 28 | 27.5667 | 28 | 464 | United_StatesMassachusettsPROVINCETOWN (AWOS)
United_States | Massachusetts | E5 | SOUTH WEYMOUTH NAS | SOUTH WEYMOUTH NAS, MA, USA | 42.15N | 70.93W | 49 | -5.00 (NAE) | 82-93 | 725097 | -18.9 | -19 | -24.2 | 38.8 | 35.1 | 35.4 | 34.4 | 35 | 34.9667 | 35 | 31.7 | 32.8 | 32 | 32 | 32.1667 | 32 | 465 | United_StatesMassachusettsSOUTH WEYMOUTH NAS
United_States | Massachusetts | E5 | WORCESTER REGIONAL ARPT | WORCESTER REGIONAL ARPT, MA, USA | 42.27N | 71.88W | 310 | -5.00 (NAE) | 82-06 | 725095 | -20 | -20 | -26.2 | 35.3 | 30.8 | 32 | 31.2 | 31 | 31.3333 | 32 | 28.9 | 29.8 | 29.2 | 29 | 29.3 | 29 | 466 | United_StatesMassachusettsWORCESTER REGIONAL ARPT
United_States | Michigan | M4 | ALPENA COUNTY REGIONAL AP | ALPENA COUNTY REGIONAL AP, MI, USA | 45.07N | 83.58W | 211 | -5.00 (NAE) | 82-06 | 726390 | -25.5 | -26 | -34.4 | 39.9 | 33.5 | 33.8 | 32.7 | 33 | 33.3333 | 34 | 30.3 | 31.3 | 29.5 | 30 | 30.3667 | 30 | 467 | United_StatesMichiganALPENA COUNTY REGIONAL AP
United_States | Michigan | M4 | ANTRIM CO ARPT | ANTRIM CO ARPT, MI, USA | 44.98N | 85.20W | 190 | -5.00 (NAE) | 82-06 | 727436 | -24.6 | -25 | -36.1 | 38.4 | 32.5 | 32.8 | 32.4 | 33 | 32.5667 | 33 | 30.8 | 31.1 | 29 | 30 | 30.3 | 30 | 468 | United_StatesMichiganANTRIM CO ARPT
United_States | Michigan | M4 | BENTON HARBOR/ROSS | BENTON HARBOR/ROSS, MI, USA | 42.13N | 86.43W | 196 | -5.00 (NAE) | 96-06 | 726355 | -18.9 | -19 | -29.3 | 39.9 | 32.7 | 34 | 33 | 33 | 33.2333 | 34 | 31.2 | 32.2 | 30.2 | 31 | 31.2 | 31 | 469 | United_StatesMichiganBENTON HARBOR/ROSS
United_States | Michigan | M4 | CADILLAC WEXFORD CO AP | CADILLAC WEXFORD CO AP, MI, USA | 44.28N | 85.42W | 398 | -5.00 (NAE) | 93-06 | 726384 | -28.5 | -29 | -45.7 | 39.5 | 33.3 | 32.9 | 31.2 | 32 | 32.4667 | 33 | 31.2 | 30.9 | 28.6 | 30 | 30.2333 | 30 | 470 | United_StatesMichiganCADILLAC WEXFORD CO AP
United_States | Michigan | M4 | CHIPPEWA CO INTL | CHIPPEWA CO INTL, MI, USA | 46.25N | 84.47W | 250 | -5.00 (NAE) | 90-06 | 727344 | -27 | -27 | -39.3 | 38.7 | 30.2 | 30.9 | 28.9 | 30 | 30 | 31 | 27.7 | 27.9 | 27.1 | 28 | 27.5667 | 28 | 471 | United_StatesMichiganCHIPPEWA CO INTL
United_States | Michigan | M4 | COPPER HARBOR RAMOS | COPPER HARBOR RAMOS, MI, USA | 47.45N | 87.90W | 186 | -5.00 (NAE) | 82-06 | 725387 | -22.4 | -22 | -31.2 | 36.6 | 28 | 30.9 | 30.2 | 30 | 29.7 | 31 | 24.2 | 27.1 | 26.7 | 26 | 26 | 26 | 472 | United_StatesMichiganCOPPER HARBOR RAMOS
United_States | Michigan | M4 | DETROIT CITY AIRPORT | DETROIT CITY AIRPORT, MI, USA | 42.41N | 83.01W | 191 | -5.00 (NAE) | 82-06 | 725375 | -18.5 | -19 | -27.9 | 40 | 33.9 | 35.1 | 33.7 | 34 | 34.2333 | 35 | 32.1 | 32.9 | 31.7 | 32 | 32.2333 | 32 | 473 | United_StatesMichiganDETROIT CITY AIRPORT
United_States | Michigan | M4 | DETROIT METROPOLITAN ARPT | DETROIT METROPOLITAN ARPT, MI, USA | 42.22N | 83.35W | 202 | -5.00 (NAE) | 82-06 | 725370 | -20.3 | -20 | -30.9 | 39.4 | 34 | 34.8 | 33.9 | 34 | 34.2333 | 35 | 31.6 | 32.5 | 31.3 | 32 | 31.8 | 32 | 474 | United_StatesMichiganDETROIT METROPOLITAN ARPT
United_States | Michigan | M4 | DETROIT WILLOW RUN AP | DETROIT WILLOW RUN AP, MI, USA | 42.23N | 83.53W | 218 | -5.00 (NAE) | 90-06 | 725376 | -20.4 | -20 | -33.2 | 38.6 | 34.2 | 34.5 | 33.2 | 34 | 33.9667 | 35 | 32.3 | 32.4 | 31.2 | 32 | 31.9667 | 32 | 475 | United_StatesMichiganDETROIT WILLOW RUN AP
United_States | Michigan | M4 | ESCANABA (AWOS) | ESCANABA (AWOS), MI, USA | 45.75N | 87.03W | 187 | -5.00 (NAE) | 82-06 | 726480 | -26.3 | -26 | -34.8 | 37.1 | 29.5 | 30.9 | 28.8 | 30 | 29.7333 | 31 | 27 | 28 | 27.2 | 27 | 27.4 | 27 | 476 | United_StatesMichiganESCANABA (AWOS)
United_States | Michigan | M4 | FLINT BISHOP INTL ARPT | FLINT BISHOP INTL ARPT, MI, USA | 42.97N | 83.75W | 234 | -5.00 (NAE) | 82-06 | 726370 | -22.6 | -23 | -30.6 | 38.7 | 33.6 | 34.5 | 33.2 | 34 | 33.7667 | 35 | 31.2 | 32.1 | 30.8 | 31 | 31.3667 | 31 | 477 | United_StatesMichiganFLINT BISHOP INTL ARPT
United_States | Michigan | M4 | GRAND RAPIDS KENT COUNTY INT' | GRAND RAPIDS KENT COUNTY INT', MI, USA | 42.88N | 85.52W | 245 | -5.00 (NAE) | 82-06 | 726350 | -21.9 | -22 | -31.4 | 37.6 | 33.1 | 34 | 33.4 | 34 | 33.5 | 34 | 31.2 | 31.9 | 30.8 | 31 | 31.3 | 31 | 478 | United_StatesMichiganGRAND RAPIDS KENT COUNTY INT'
United_States | Michigan | M4 | GROSSE ISLE ARPT | GROSSE ISLE ARPT, MI, USA | 42.10N | 83.15W | 176 | -5.00 (NAE) | 97-06 | 725373 | -16.4 | -16 | -24.3 | 39.6 | 32.7 | 34 | 32.9 | 33 | 33.2 | 34 | 30.3 | 32.4 | 31.1 | 31 | 31.2667 | 31 | 479 | United_StatesMichiganGROSSE ISLE ARPT
United_States | Michigan | M4 | HANCOCK HOUGHTON CO AP | HANCOCK HOUGHTON CO AP, MI, USA | 47.17N | 88.51W | 329 | -6.00 (NAC) | 82-06 | 727440 | -23.9 | -24 | -31.9 | 39.1 | 31.8 | 32.9 | 30.8 | 32 | 31.8333 | 33 | 28.1 | 29.1 | 28.1 | 28 | 28.4333 | 28 | 480 | United_StatesMichiganHANCOCK HOUGHTON CO AP
United_States | Michigan | M4 | HARBOR BEACH(RAMOS) | HARBOR BEACH(RAMOS), MI, USA | 44.02N | 82.80W | 183 | -5.00 (NAE) | 82-06 | 725386 | -17 | -17 | -25.3 | 38.8 | 32.9 | 34.7 | 33.4 | 34 | 33.6667 | 35 | 30.2 | 31.8 | 30.7 | 31 | 30.9 | 31 | 481 | United_StatesMichiganHARBOR BEACH(RAMOS)
United_States | Michigan | M4 | HOLLAND/TULIP CITY | HOLLAND/TULIP CITY, MI, USA | 42.75N | 86.10W | 210 | -5.00 (NAE) | 97-06 | 725394 | -18.9 | -19 | -25.3 | 37.2 | 32.5 | 32.8 | 32.2 | 33 | 32.5 | 33 | 31 | 31.3 | 29.1 | 30 | 30.4667 | 30 | 482 | United_StatesMichiganHOLLAND/TULIP CITY
United_States | Michigan | M4 | HOUGHTON LAKE ROSCOMMON CO AR | HOUGHTON LAKE ROSCOMMON CO AR, MI, USA | 44.37N | 84.69W | 354 | -5.00 (NAE) | 83-06 | 726380 | -26.4 | -26 | -36.6 | 38.7 | 32.8 | 32.7 | 32 | 33 | 32.5 | 33 | 30 | 30.6 | 29.5 | 30 | 30.0333 | 30 | 483 | United_StatesMichiganHOUGHTON LAKE ROSCOMMON CO AR
United_States | Michigan | M4 | HOWELL | HOWELL, MI, USA | 42.63N | 83.98W | 293 | -5.00 (NAE) | 94-06 | 725378 | -19.7 | -20 | -27.4 | 38.8 | 33 | 34.1 | 33 | 33 | 33.3667 | 34 | 32.2 | 32.5 | 31.1 | 32 | 31.9333 | 32 | 484 | United_StatesMichiganHOWELL
United_States | Michigan | M4 | IRON MOUNTAIN/FORD | IRON MOUNTAIN/FORD, MI, USA | 45.82N | 88.12W | 360 | -6.00 (NAC) | 82-06 | 727437 | -29 | -29 | -37.6 | 39.6 | 33 | 33.8 | 32.3 | 33 | 33.0333 | 34 | 30.1 | 31.3 | 28.8 | 30 | 30.0667 | 30 | 485 | United_StatesMichiganIRON MOUNTAIN/FORD
United_States | Michigan | M4 | IRONWOOD (AWOS) | IRONWOOD (AWOS), MI, USA | 46.53N | 90.13W | 375 | -6.00 (NAC) | 82-06 | 727445 | -29.5 | -30 | -38.5 | 38.7 | 31.4 | 33.1 | 31.9 | 32 | 32.1333 | 33 | 28.8 | 30 | 28.1 | 29 | 28.9667 | 29 | 486 | United_StatesMichiganIRONWOOD (AWOS)
United_States | Michigan | M4 | JACKSON REYNOLDS FIELD | JACKSON REYNOLDS FIELD, MI, USA | 42.26N | 84.46W | 311 | -5.00 (NAE) | 82-06 | 725395 | -22.2 | -22 | -31.1 | 37.1 | 32.8 | 33.2 | 32.6 | 33 | 32.8667 | 33 | 30.9 | 31.4 | 30.3 | 31 | 30.8667 | 31 | 487 | United_StatesMichiganJACKSON REYNOLDS FIELD
United_States | Michigan | M4 | KALAMAZOO BATTLE CR | KALAMAZOO BATTLE CR, MI, USA | 42.23N | 85.55W | 273 | -5.00 (NAE) | 98-06 | 726357 | -19.9 | -20 | -29 | 38.4 | 33 | 33.7 | 32.6 | 33 | 33.1 | 34 | 32.1 | 32.3 | 31 | 32 | 31.8 | 32 | 488 | United_StatesMichiganKALAMAZOO BATTLE CR
United_States | Michigan | M4 | LANSING CAPITAL CITY ARPT | LANSING CAPITAL CITY ARPT, MI, USA | 42.78N | 84.58W | 266 | -5.00 (NAE) | 82-06 | 725390 | -24.1 | -24 | -32.9 | 38 | 33.5 | 34.1 | 33.5 | 34 | 33.7 | 34 | 31.2 | 32 | 30.8 | 31 | 31.3333 | 31 | 489 | United_StatesMichiganLANSING CAPITAL CITY ARPT
United_States | Michigan | M4 | MACKINACK ISLAND | MACKINACK ISLAND, MI, USA | 45.87N | 84.63W | 300 | -5.00 (NAE) | 82-06 | 727435 | -25.6 | -26 | -38.7 | 38.7 | 31 | 33.1 | 31.4 | 32 | 31.8333 | 33 | 27.7 | 29.5 | 28 | 28 | 28.4 | 28 | 490 | United_StatesMichiganMACKINACK ISLAND
United_States | Michigan | M4 | MANISTEE (AWOS) | MANISTEE (AWOS), MI, USA | 44.27N | 86.25W | 189 | -5.00 (NAE) | 91-06 | 726385 | -21.4 | -21 | -31.4 | 36.2 | 31.2 | 32.1 | 31.2 | 32 | 31.5 | 32 | 29 | 29.1 | 28.1 | 29 | 28.7333 | 29 | 491 | United_StatesMichiganMANISTEE (AWOS)
United_States | Michigan | M4 | MANISTIQUE (AMOS) | MANISTIQUE (AMOS), MI, USA | 45.95N | 86.23W | 178 | -5.00 (NAE) | 82-04 | 726399 | -22.2 | -22 | -31.3 | 31.4 | 25 | 27.8 | 27.4 | 27 | 26.7333 | 28 | 22.7 | 25.4 | 25.8 | 25 | 24.6333 | 25 | 492 | United_StatesMichiganMANISTIQUE (AMOS)
United_States | Michigan | M4 | MARQUETTE COUNTY ARPT | MARQUETTE COUNTY ARPT, MI, USA | 46.53N | 87.55W | 431 | -6.00 (NAC) | 82-99 | 727430 | -30.2 | -30 | -39.2 | 38.5 | 31.7 | 33 | 30.6 | 32 | 31.7667 | 33 | 28.1 | 29.7 | 27.8 | 29 | 28.5333 | 29 | 493 | United_StatesMichiganMARQUETTE COUNTY ARPT
United_States | Michigan | M4 | MENOMINEE (AWOS) | MENOMINEE (AWOS), MI, USA | 45.13N | 87.63W | 191 | -6.00 (NAC) | 92-06 | 726487 | -25.8 | -26 | -36 | 39 | 32.1 | 32.7 | 31.2 | 32 | 32 | 33 | 28.9 | 30.9 | 28 | 29 | 29.2667 | 29 | 494 | United_StatesMichiganMENOMINEE (AWOS)
United_States | Michigan | M4 | MUSKEGON COUNTY ARPT | MUSKEGON COUNTY ARPT, MI, USA | 43.17N | 86.24W | 193 | -5.00 (NAE) | 82-06 | 726360 | -19.6 | -20 | -28.1 | 36.1 | 31.4 | 32 | 31.4 | 32 | 31.6 | 32 | 29.4 | 30.1 | 29.4 | 30 | 29.6333 | 30 | 495 | United_StatesMichiganMUSKEGON COUNTY ARPT
United_States | Michigan | M4 | NEWBERRY LUCE CO. | NEWBERRY LUCE CO., MI, USA | 46.32N | 85.45W | 265 | -5.00 (NAE) | 88-06 | 726394 | -25.8 | -26 | -36 | 37.2 | 29.1 | 32.4 | 29.9 | 30 | 30.4667 | 32 | 27.5 | 29.9 | 27.4 | 28 | 28.2667 | 28 | 496 | United_StatesMichiganNEWBERRY LUCE CO.
United_States | Michigan | M4 | OAKLAND CO INTL | OAKLAND CO INTL, MI, USA | 42.67N | 83.42W | 306 | -5.00 (NAE) | 88-06 | 726375 | -20 | -20 | -27.1 | 37.5 | 32.9 | 33.7 | 33 | 33 | 33.2 | 34 | 31.2 | 32 | 31 | 31 | 31.4 | 31 | 497 | United_StatesMichiganOAKLAND CO INTL
United_States | Michigan | M4 | OSCODA WURTSMITH AFB | OSCODA WURTSMITH AFB, MI, USA | 44.45N | 83.37W | 193 | -5.00 (NAE) | 82-06 | 726395 | -22.2 | -22 | -30.3 | 40.7 | 33.6 | 35.3 | 33.7 | 34 | 34.2 | 35 | 31 | 32.4 | 30.7 | 31 | 31.3667 | 31 | 498 | United_StatesMichiganOSCODA WURTSMITH AFB
United_States | Michigan | M4 | PASSAGE ISLAND | PASSAGE ISLAND, MI, USA | 48.22N | 88.37W | 209 | -6.00 (NAC) | 85-06 | 994090 | -23.8 | -24 | -31.4 | 27.8 | 18.5 | 21.8 | 21.8 | 21 | 20.7 | 22 | 16.3 | 20 | 20.4 | 19 | 18.9 | 19 | 499 | United_StatesMichiganPASSAGE ISLAND
United_States | Michigan | M4 | PELLSTON EMMET COUNTY AP | PELLSTON EMMET COUNTY AP, MI, USA | 45.57N | 84.80W | 218 | -5.00 (NAE) | 82-06 | 727347 | -29.2 | -29 | -37.8 | 37.8 | 32.6 | 33 | 31.6 | 32 | 32.4 | 33 | 29.9 | 30.9 | 29.1 | 30 | 29.9667 | 30 | 500 | United_StatesMichiganPELLSTON EMMET COUNTY AP
United_States | Michigan | M4 | ROCK OF AGES | ROCK OF AGES, MI, USA | 47.87N | 89.32W | 223 | -6.00 (NAC) | 85-06 | 994130 | -26.1 | -26 | -33.4 | 31.8 | 22.3 | 24.9 | 24.2 | 24 | 23.8 | 25 | 19.1 | 21.7 | 22.2 | 21 | 21 | 21 | 501 | United_StatesMichiganROCK OF AGES
United_States | Michigan | M4 | SAGINAW TRI CITY INTL AP | SAGINAW TRI CITY INTL AP, MI, USA | 43.53N | 84.08W | 204 | -5.00 (NAE) | 82-06 | 726379 | -21.3 | -21 | -29.3 | 39.4 | 34.1 | 34.9 | 33.6 | 34 | 34.2 | 35 | 31.6 | 32.3 | 30.8 | 32 | 31.5667 | 32 | 502 | United_StatesMichiganSAGINAW TRI CITY INTL AP
United_States | Michigan | M4 | SAULT STE MARIE SANDERSON FIE | SAULT STE MARIE SANDERSON FIE, MI, USA | 46.47N | 84.37W | 221 | -5.00 (NAE) | 82-06 | 727340 | -28.6 | -29 | -40.1 | 36.6 | 30 | 31.7 | 30.2 | 31 | 30.6333 | 32 | 27.4 | 29 | 27.6 | 28 | 28 | 28 | 503 | United_StatesMichiganSAULT STE MARIE SANDERSON FIE
United_States | Michigan | M4 | SELFRIDGE ANGB | SELFRIDGE ANGB, MI, USA | 42.62N | 82.83W | 177 | -5.00 (NAE) | 82-06 | 725377 | -19.7 | -20 | -27.1 | 40 | 33.9 | 35 | 33.7 | 34 | 34.2 | 35 | 31.8 | 32.5 | 31.2 | 32 | 31.8333 | 32 | 504 | United_StatesMichiganSELFRIDGE ANGB
United_States | Michigan | M4 | ST.CLAIR COUNTY INT | ST.CLAIR COUNTY INT, MI, USA | 42.92N | 82.53W | 198 | -5.00 (NAE) | 94-06 | 725384 | -21.6 | -22 | -32.1 | 49.4 | 32.9 | 33.3 | 32.9 | 33 | 33.0333 | 33 | 32 | 32.4 | 31 | 32 | 31.8 | 32 | 505 | United_StatesMichiganST.CLAIR COUNTY INT
United_States | Michigan | M4 | STANNARD ROCK | STANNARD ROCK, MI, USA | 47.18N | 87.22W | 212 | -5.00 (NAE) | 85-06 | 994200 | -19.7 | -20 | -27.2 | 34.4 | 25.1 | 26.4 | 26 | 26 | 25.8333 | 26 | 22.3 | 23.4 | 23.8 | 23 | 23.1667 | 23 | 506 | United_StatesMichiganSTANNARD ROCK
United_States | Michigan | M4 | STURGIS\KIRSH MUNI | STURGIS\KIRSH MUNI, MI, USA | 41.82N | 85.43W | 282 | -5.00 (NAE) | 99-06 | 725383 | -21.2 | -21 | -30.3 | 47.5 | 33 | 32.8 | 32.7 | 33 | 32.8333 | 33 | 32.1 | 32.1 | 30.9 | 32 | 31.7 | 32 | 507 | United_StatesMichiganSTURGIS\KIRSH MUNI
United_States | Michigan | M4 | TRAVERSE CITY CHERRY CAPITAL | TRAVERSE CITY CHERRY CAPITAL, MI, USA | 44.74N | 85.58W | 192 | -5.00 (NAE) | 82-06 | 726387 | -22.5 | -23 | -32.8 | 38.5 | 33.5 | 34.1 | 33.4 | 34 | 33.6667 | 34 | 31.1 | 31.9 | 30.5 | 31 | 31.1667 | 31 | 508 | United_StatesMichiganTRAVERSE CITY CHERRY CAPITAL
United_States | Minnesota | M4 | AITKIN NDB(AWOS) | AITKIN NDB(AWOS), MN, USA | 46.55N | 93.68W | 367 | -6.00 (NAC) | 92-06 | 727504 | -33.4 | -33 | -45.7 | 37.1 | 31.1 | 32.4 | 31.2 | 32 | 31.5667 | 32 | 28.7 | 30.1 | 28.4 | 29 | 29.0667 | 29 | 509 | United_StatesMinnesotaAITKIN NDB(AWOS)
United_States | Minnesota | M4 | ALBERT LEA (AWOS) | ALBERT LEA (AWOS), MN, USA | 43.68N | 93.37W | 383 | -6.00 (NAC) | 92-06 | 726589 | -27.7 | -28 | -38.3 | 38.2 | 33 | 33.8 | 31.8 | 33 | 32.8667 | 34 | 31.1 | 32 | 29.8 | 31 | 30.9667 | 31 | 510 | United_StatesMinnesotaALBERT LEA (AWOS)
United_States | Minnesota | M4 | ALEXANDRIA MUNICIPAL AP | ALEXANDRIA MUNICIPAL AP, MN, USA | 45.88N | 95.39W | 436 | -6.00 (NAC) | 82-06 | 726557 | -31.3 | -31 | -40.1 | 39.6 | 33.7 | 34.6 | 33.2 | 34 | 33.8333 | 35 | 30.6 | 31.7 | 30.7 | 31 | 31 | 31 | 511 | United_StatesMinnesotaALEXANDRIA MUNICIPAL AP
United_States | Minnesota | M4 | AUSTIN MUNI | AUSTIN MUNI, MN, USA | 43.67N | 92.93W | 375 | -6.00 (NAC) | 92-06 | 727566 | -27.8 | -28 | -37.7 | 39.3 | 32.7 | 33.8 | 32.4 | 33 | 32.9667 | 34 | 30.7 | 32.1 | 29.8 | 31 | 30.8667 | 31 | 512 | United_StatesMinnesotaAUSTIN MUNI
United_States | Minnesota | M4 | BAUDETTE INTERNATIONAL AP | BAUDETTE INTERNATIONAL AP, MN, USA | 48.73N | 94.61W | 330 | -6.00 (NAC) | 95-06 | 727476 | -35 | -35 | -47.4 | 36.3 | 32.4 | 32.2 | 31.2 | 32 | 31.9333 | 32 | 28.8 | 29.6 | 28.4 | 29 | 28.9333 | 29 | 513 | United_StatesMinnesotaBAUDETTE INTERNATIONAL AP
United_States | Minnesota | M4 | BEMIDJI MUNICIPAL | BEMIDJI MUNICIPAL, MN, USA | 47.50N | 94.93W | 420 | -6.00 (NAC) | 87-06 | 727550 | -34.3 | -34 | -44.5 | 37.8 | 32.4 | 32.9 | 33 | 33 | 32.7667 | 33 | 29.4 | 30.9 | 30 | 30 | 30.1 | 30 | 514 | United_StatesMinnesotaBEMIDJI MUNICIPAL
United_States | Minnesota | M4 | BENSON MUNI | BENSON MUNI, MN, USA | 45.32N | 95.65W | 317 | -6.00 (NAC) | 94-06 | 727507 | -29.6 | -30 | -39.5 | 40.2 | 34 | 36.1 | 33.8 | 35 | 34.6333 | 36 | 32 | 32.6 | 31.2 | 32 | 31.9333 | 32 | 515 | United_StatesMinnesotaBENSON MUNI
United_States | Minnesota | M4 | BRAINERD/WIELAND | BRAINERD/WIELAND, MN, USA | 46.40N | 94.13W | 374 | -6.00 (NAC) | 89-06 | 726555 | -32.8 | -33 | -46.6 | 39 | 32.3 | 34.1 | 32.5 | 33 | 32.9667 | 34 | 29.4 | 32 | 29.8 | 30 | 30.4 | 30 | 516 | United_StatesMinnesotaBRAINERD/WIELAND
United_States | Minnesota | M4 | CAMBRIDGE MUNI | CAMBRIDGE MUNI, MN, USA | 45.57N | 93.27W | 287 | -6.00 (NAC) | 92-06 | 727503 | -30.7 | -31 | -42.4 | 46.3 | 33.5 | 37.1 | 34.1 | 35 | 34.9 | 37 | 31.1 | 32.9 | 30.9 | 32 | 31.6333 | 32 | 517 | United_StatesMinnesotaCAMBRIDGE MUNI
United_States | Minnesota | M4 | CLOQUET (AWOS) | CLOQUET (AWOS), MN, USA | 46.70N | 92.50W | 390 | -6.00 (NAC) | 92-06 | 726558 | -31.3 | -31 | -43.4 | 36.5 | 31.5 | 32.5 | 31.2 | 32 | 31.7333 | 33 | 27.9 | 29.7 | 27.9 | 29 | 28.5 | 29 | 518 | United_StatesMinnesotaCLOQUET (AWOS)
United_States | Minnesota | M4 | CRANE LAKE (AWOS) | CRANE LAKE (AWOS), MN, USA | 46.27N | 92.57W | 350 | -6.00 (NAC) | 92-06 | 727473 | -34 | -34 | -42 | 39.3 | 33.3 | 32.6 | 31.6 | 33 | 32.5 | 33 | 29 | 29.8 | 28.8 | 29 | 29.2 | 29 | 519 | United_StatesMinnesotaCRANE LAKE (AWOS)
United_States | Minnesota | M4 | CROOKSTON MUNI FLD | CROOKSTON MUNI FLD, MN, USA | 47.85N | 96.62W | 273 | -6.00 (NAC) | 92-06 | 727452 | -33.5 | -34 | -45.6 | 47.1 | 32.3 | 32.4 | 32.4 | 32 | 32.3667 | 32 | 29.2 | 30 | 29.7 | 30 | 29.6333 | 30 | 520 | United_StatesMinnesotaCROOKSTON MUNI FLD
United_States | Minnesota | M4 | DETROIT LAKES(AWOS) | DETROIT LAKES(AWOS), MN, USA | 46.83N | 95.88W | 426 | -6.00 (NAC) | 92-06 | 727457 | -32.3 | -32 | -46.2 | 38.3 | 32.6 | 32.5 | 32.6 | 33 | 32.5667 | 33 | 29.4 | 31.1 | 29.8 | 30 | 30.1 | 30 | 521 | United_StatesMinnesotaDETROIT LAKES(AWOS)
United_States | Minnesota | M4 | DULUTH HARBOR (CGS) | DULUTH HARBOR (CGS), MN, USA | 46.77N | 92.08W | 186 | -6.00 (NAC) | 83-06 | 727456 | -26.9 | -27 | -35.1 | 40.5 | 31.3 | 33 | 32.3 | 32 | 32.2 | 33 | 27.5 | 31 | 28.8 | 29 | 29.1 | 29 | 522 | United_StatesMinnesotaDULUTH HARBOR (CGS)
United_States | Minnesota | M4 | DULUTH INTERNATIONAL ARPT | DULUTH INTERNATIONAL ARPT, MN, USA | 46.84N | 92.19W | 432 | -6.00 (NAC) | 82-06 | 727450 | -32.1 | -32 | -41 | 36.8 | 30.6 | 32.2 | 31.1 | 31 | 31.3 | 32 | 27.6 | 29.5 | 28.2 | 28 | 28.4333 | 28 | 523 | United_StatesMinnesotaDULUTH INTERNATIONAL ARPT
United_States | Minnesota | M4 | ELY MUNI | ELY MUNI, MN, USA | 47.82N | 91.83W | 455 | -6.00 (NAC) | 92-06 | 727459 | -36.7 | -37 | -48.8 | 38.3 | 32.7 | 32.2 | 31.4 | 32 | 32.1 | 32 | 28.9 | 29 | 27.9 | 29 | 28.6 | 29 | 524 | United_StatesMinnesotaELY MUNI
United_States | Minnesota | M4 | EVELETH MUNI (AWOS) | EVELETH MUNI (AWOS), MN, USA | 47.40N | 92.50W | 421 | -6.00 (NAC) | 92-06 | 727474 | -35.3 | -35 | -47.8 | 37.8 | 32.3 | 32.9 | 31.3 | 32 | 32.1667 | 33 | 29 | 30.1 | 28 | 29 | 29.0333 | 29 | 525 | United_StatesMinnesotaEVELETH MUNI (AWOS)
United_States | Minnesota | M4 | FAIRMONT MUNI(AWOS) | FAIRMONT MUNI(AWOS), MN, USA | 43.65N | 94.42W | 354 | -6.00 (NAC) | 92-06 | 726586 | -26.2 | -26 | -33.3 | 38.4 | 33.8 | 32.9 | 32.3 | 33 | 33 | 33 | 31.5 | 32 | 29.9 | 31 | 31.1333 | 31 | 526 | United_StatesMinnesotaFAIRMONT MUNI(AWOS)
United_States | Minnesota | M4 | FARIBAULT MUNI AWOS | FARIBAULT MUNI AWOS, MN, USA | 44.33N | 93.32W | 322 | -6.00 (NAC) | 92-06 | 726563 | -29.2 | -29 | -42.8 | 39 | 32.9 | 34 | 32.5 | 33 | 33.1333 | 34 | 31.2 | 32.4 | 29.9 | 31 | 31.1667 | 31 | 527 | United_StatesMinnesotaFARIBAULT MUNI AWOS
United_States | Minnesota | M4 | FERGUS FALLS(AWOS) | FERGUS FALLS(AWOS), MN, USA | 46.28N | 96.15W | 361 | -6.00 (NAC) | 92-06 | 726560 | -30.7 | -31 | -40.9 | 42.5 | 33.8 | 34.7 | 33.5 | 34 | 34 | 35 | 30.9 | 32.1 | 31.1 | 31 | 31.3667 | 31 | 528 | United_StatesMinnesotaFERGUS FALLS(AWOS)
United_States | Minnesota | M4 | FLYING CLOUD | FLYING CLOUD, MN, USA | 44.82N | 93.45W | 283 | -6.00 (NAC) | 97-06 | 726579 | -27.1 | -27 | -35 | 37.9 | 33.6 | 35.2 | 34 | 34 | 34.2667 | 35 | 31.1 | 32.8 | 31.3 | 32 | 31.7333 | 32 | 529 | United_StatesMinnesotaFLYING CLOUD
United_States | Minnesota | M4 | FOSSTON(AWOS) | FOSSTON(AWOS), MN, USA | 47.58N | 95.77W | 388 | -6.00 (NAC) | 92-06 | 727505 | -35.4 | -35 | -51.6 | 39.7 | 31.7 | 32.9 | 32.5 | 32 | 32.3667 | 33 | 28.9 | 30.8 | 29.1 | 30 | 29.6 | 30 | 530 | United_StatesMinnesotaFOSSTON(AWOS)
United_States | Minnesota | M4 | GLENWOOD (ASOS) | GLENWOOD (ASOS), MN, USA | 45.65N | 95.32W | 425 | -6.00 (NAC) | 95-06 | 726547 | -29.5 | -30 | -39.6 | 39.7 | 32.9 | 36 | 33 | 34 | 33.9667 | 36 | 30.8 | 32.5 | 31 | 31 | 31.4333 | 31 | 531 | United_StatesMinnesotaGLENWOOD (ASOS)
United_States | Minnesota | M4 | GRAND MARAIS MUNI | GRAND MARAIS MUNI, MN, USA | 47.83N | 90.38W | 548 | -6.00 (NAC) | 97-06 | 727454 | -30.2 | -30 | -35.4 | 35.5 | 27.6 | 29.1 | 28.8 | 29 | 28.5 | 29 | 25.1 | 27.4 | 26.2 | 26 | 26.2333 | 26 | 532 | United_StatesMinnesotaGRAND MARAIS MUNI
United_States | Minnesota | M4 | GRAND RAPIDS(AWOS) | GRAND RAPIDS(AWOS), MN, USA | 47.22N | 93.52W | 413 | -6.00 (NAC) | 92-06 | 727458 | -32.3 | -32 | -41.7 | 36.5 | 31.6 | 32.2 | 30.9 | 32 | 31.5667 | 32 | 28.7 | 29.1 | 27.6 | 28 | 28.4667 | 28 | 533 | United_StatesMinnesotaGRAND RAPIDS(AWOS)
United_States | Minnesota | M4 | HALLOCK | HALLOCK, MN, USA | 48.78N | 96.95W | 250 | -6.00 (NAC) | 92-06 | 727478 | -34.1 | -34 | -45.3 | 39.8 | 33.3 | 32.9 | 33.7 | 33 | 33.3 | 33 | 30 | 31.1 | 31.2 | 31 | 30.7667 | 31 | 534 | United_StatesMinnesotaHALLOCK
United_States | Minnesota | M4 | HIBBING CHISHOLM-HIBBING AP | HIBBING CHISHOLM-HIBBING AP, MN, USA | 47.39N | 92.84W | 414 | -6.00 (NAC) | 82-06 | 727455 | -35.8 | -36 | -45.6 | 36.1 | 31.6 | 31.9 | 31.4 | 32 | 31.6333 | 32 | 28.5 | 29.8 | 28.7 | 29 | 29 | 29 | 535 | United_StatesMinnesotaHIBBING CHISHOLM-HIBBING AP
United_States | Minnesota | M4 | HUTCHINSON (AWOS) | HUTCHINSON (AWOS), MN, USA | 44.87N | 94.38W | 323 | -6.00 (NAC) | 92-06 | 726569 | -29.8 | -30 | -40.3 | 38.7 | 34 | 34.1 | 32.5 | 34 | 33.5333 | 34 | 32 | 32.4 | 30.2 | 32 | 31.5333 | 32 | 536 | United_StatesMinnesotaHUTCHINSON (AWOS)
United_States | Minnesota | M4 | INTERNATIONAL FALLS INTL AP | INTERNATIONAL FALLS INTL AP, MN, USA | 48.57N | 93.40W | 361 | -6.00 (NAC) | 82-06 | 727470 | -37.2 | -37 | -46 | 38.1 | 32.6 | 32.2 | 32 | 32 | 32.2667 | 32 | 29.3 | 29.6 | 29.1 | 29 | 29.3333 | 29 | 537 | United_StatesMinnesotaINTERNATIONAL FALLS INTL AP
United_States | Minnesota | M4 | LITCHFIELD MUNI | LITCHFIELD MUNI, MN, USA | 45.10N | 94.50W | 347 | -6.00 (NAC) | 92-06 | 726583 | -28.3 | -28 | -37.1 | 38.7 | 33.6 | 33.6 | 32.3 | 33 | 33.1667 | 34 | 31 | 32 | 29.5 | 31 | 30.8333 | 31 | 538 | United_StatesMinnesotaLITCHFIELD MUNI
United_States | Minnesota | M4 | LITTLE FALLS (AWOS) | LITTLE FALLS (AWOS), MN, USA | 45.95N | 94.35W | 342 | -6.00 (NAC) | 92-06 | 726578 | -32 | -32 | -43.9 | 39.2 | 34 | 34.8 | 33.7 | 34 | 34.1667 | 35 | 31.3 | 32.6 | 31.1 | 32 | 31.6667 | 32 | 539 | United_StatesMinnesotaLITTLE FALLS (AWOS)
United_States | Minnesota | M4 | MANKATO(AWOS) | MANKATO(AWOS), MN, USA | 44.22N | 93.92W | 311 | -6.00 (NAC) | 92-06 | 726585 | -26.1 | -26 | -34.1 | 39.2 | 33.8 | 33 | 32.2 | 33 | 33 | 33 | 31.3 | 32.1 | 29.4 | 31 | 30.9333 | 31 | 540 | United_StatesMinnesotaMANKATO(AWOS)
United_States | Minnesota | M4 | MARSHALL/RYAN(AWOS) | MARSHALL/RYAN(AWOS), MN, USA | 44.45N | 95.82W | 359 | -6.00 (NAC) | 92-06 | 726559 | -26.9 | -27 | -34.6 | 39.7 | 33.9 | 34.9 | 32.5 | 34 | 33.7667 | 35 | 31.4 | 32.4 | 30.9 | 32 | 31.5667 | 32 | 541 | United_StatesMinnesotaMARSHALL/RYAN(AWOS)
United_States | Minnesota | M4 | MINNEAPOLIS/BLAINE | MINNEAPOLIS/BLAINE, MN, USA | 45.15N | 93.22W | 278 | -6.00 (NAC) | 97-06 | 726577 | -26 | -26 | -34 | 39.4 | 32.8 | 35.1 | 33.7 | 34 | 33.8667 | 35 | 30.9 | 32.7 | 30.9 | 32 | 31.5 | 32 | 542 | United_StatesMinnesotaMINNEAPOLIS/BLAINE
United_States | Minnesota | M4 | MINNEAPOLIS/CRYSTAL | MINNEAPOLIS/CRYSTAL, MN, USA | 45.07N | 93.35W | 265 | -6.00 (NAC) | 97-06 | 726575 | -26.4 | -26 | -34 | 40 | 33 | 36.1 | 33.9 | 34 | 34.3333 | 36 | 30.9 | 32.8 | 31.3 | 32 | 31.6667 | 32 | 543 | United_StatesMinnesotaMINNEAPOLIS/CRYSTAL
United_States | Minnesota | M4 | MINNEAPOLIS-ST PAUL INT'L ARP | MINNEAPOLIS-ST PAUL INT'L ARP, MN, USA | 44.88N | 93.23W | 255 | -6.00 (NAC) | 82-06 | 726580 | -28.1 | -28 | -37.6 | 40.9 | 34.2 | 35.8 | 34.3 | 35 | 34.7667 | 36 | 31.6 | 33.2 | 31.4 | 32 | 32.0667 | 32 | 544 | United_StatesMinnesotaMINNEAPOLIS-ST PAUL INT'L ARP
United_States | Minnesota | M4 | MONTEVIDEO (AWOS) | MONTEVIDEO (AWOS), MN, USA | 44.97N | 95.72W | 315 | -6.00 (NAC) | 92-06 | 726553 | -28.1 | -28 | -38.1 | 39.2 | 34.1 | 33.9 | 32.9 | 34 | 33.6333 | 34 | 31.6 | 32.3 | 30.9 | 32 | 31.6 | 32 | 545 | United_StatesMinnesotaMONTEVIDEO (AWOS)
United_States | Minnesota | M4 | MORA MUNI (AWOS) | MORA MUNI (AWOS), MN, USA | 45.88N | 93.27W | 309 | -6.00 (NAC) | 92-06 | 727475 | -30.5 | -31 | -42.1 | 37.6 | 33 | 33.4 | 32.4 | 33 | 32.9333 | 33 | 30.2 | 32 | 30 | 31 | 30.7333 | 31 | 546 | United_StatesMinnesotaMORA MUNI (AWOS)
United_States | Minnesota | M4 | MORRIS MUNI (AWOS) | MORRIS MUNI (AWOS), MN, USA | 45.72N | 95.97W | 347 | -6.00 (NAC) | 92-06 | 726565 | -30.2 | -30 | -41.3 | 39.5 | 33 | 33 | 32.5 | 33 | 32.8333 | 33 | 31.1 | 31.3 | 29.4 | 31 | 30.6 | 31 | 547 | United_StatesMinnesotaMORRIS MUNI (AWOS)
United_States | Minnesota | M4 | NEW ULM MUNI (AWOS) | NEW ULM MUNI (AWOS), MN, USA | 44.32N | 94.50W | 308 | -6.00 (NAC) | 92-06 | 726567 | -27.4 | -27 | -35.7 | 39.5 | 34.1 | 34 | 32.7 | 34 | 33.6 | 34 | 32.1 | 32.3 | 30.8 | 32 | 31.7333 | 32 | 548 | United_StatesMinnesotaNEW ULM MUNI (AWOS)
United_States | Minnesota | M4 | ORR | ORR, MN, USA | 48.02N | 92.87W | 397 | -6.00 (NAC) | 93-06 | 726544 | -35.1 | -35 | -46.5 | 38.5 | 32.2 | 32.5 | 31 | 32 | 31.9 | 33 | 28.6 | 29.7 | 27.9 | 29 | 28.7333 | 29 | 549 | United_StatesMinnesotaORR
United_States | Minnesota | M4 | OWATONNA (AWOS) | OWATONNA (AWOS), MN, USA | 44.12N | 93.25W | 350 | -6.00 (NAC) | 92-06 | 726568 | -27.8 | -28 | -35.8 | 38.3 | 33 | 33 | 32.2 | 33 | 32.7333 | 33 | 31.2 | 32.1 | 30.1 | 31 | 31.1333 | 31 | 550 | United_StatesMinnesotaOWATONNA (AWOS)
United_States | Minnesota | M4 | PARK RAPIDS MUNICIPAL AP | PARK RAPIDS MUNICIPAL AP, MN, USA | 46.90N | 95.07W | 440 | -6.00 (NAC) | 95-06 | 727453 | -34.4 | -34 | -46.4 | 37.8 | 32.3 | 33 | 32.8 | 33 | 32.7 | 33 | 29 | 31.1 | 29.6 | 30 | 29.9 | 30 | 551 | United_StatesMinnesotaPARK RAPIDS MUNICIPAL AP
United_States | Minnesota | M4 | PEQUOT LAKE (AMOS) | PEQUOT LAKE (AMOS), MN, USA | 46.60N | 94.32W | 390 | -6.00 (NAC) | 82-95 | 727500 | -34.7 | -35 | -42.2 | 41.7 | 32.7 | 36.2 | 33 | 34 | 33.9667 | 36 | 30.1 | 32.3 | 30.6 | 31 | 31 | 31 | 552 | United_StatesMinnesotaPEQUOT LAKE (AMOS)
United_States | Minnesota | M4 | PIPESTONE (AWOS) | PIPESTONE (AWOS), MN, USA | 43.98N | 96.32W | 529 | -6.00 (NAC) | 92-06 | 726566 | -28 | -28 | -37.7 | 39.2 | 33 | 33.9 | 32.4 | 33 | 33.1 | 34 | 30.9 | 32.2 | 29.9 | 31 | 31 | 31 | 553 | United_StatesMinnesotaPIPESTONE (AWOS)
United_States | Minnesota | M4 | PRINCETON MUNI | PRINCETON MUNI, MN, USA | 45.55N | 93.60W | 306 | -6.00 (NAC) | 97-06 | 726682 | -29.2 | -29 | -40 | 39.3 | 32.8 | 35.2 | 33.7 | 34 | 33.9 | 35 | 29.9 | 32.6 | 31 | 31 | 31.1667 | 31 | 554 | United_StatesMinnesotaPRINCETON MUNI
United_States | Minnesota | M4 | RED WING | RED WING, MN, USA | 44.58N | 92.48W | 239 | -6.00 (NAC) | 92-06 | 726564 | -28.2 | -28 | -36.2 | 39.9 | 33.4 | 35.1 | 33.8 | 34 | 34.1 | 35 | 31.3 | 32.8 | 31.1 | 32 | 31.7333 | 32 | 555 | United_StatesMinnesotaRED WING
United_States | Minnesota | M4 | REDWOOD FALLS MUNI | REDWOOD FALLS MUNI, MN, USA | 44.55N | 95.08W | 314 | -6.00 (NAC) | 82-06 | 726556 | -28.7 | -29 | -37.3 | 40.7 | 35.1 | 36.2 | 34.4 | 35 | 35.2333 | 36 | 32.5 | 33.3 | 32 | 33 | 32.6 | 33 | 556 | United_StatesMinnesotaREDWOOD FALLS MUNI
United_States | Minnesota | M4 | ROCHESTER INTERNATIONAL ARPT | ROCHESTER INTERNATIONAL ARPT, MN, USA | 43.90N | 92.49W | 402 | -6.00 (NAC) | 82-06 | 726440 | -29 | -29 | -37.9 | 39.5 | 33 | 33.3 | 33.1 | 33 | 33.1333 | 33 | 30.6 | 31.3 | 30 | 31 | 30.6333 | 31 | 557 | United_StatesMinnesotaROCHESTER INTERNATIONAL ARPT
United_States | Minnesota | M4 | ROSEAU MUNI (AWOS) | ROSEAU MUNI (AWOS), MN, USA | 48.85N | 95.70W | 323 | -6.00 (NAC) | 92-06 | 727477 | -35.2 | -35 | -47.7 | 39.2 | 32.2 | 32.6 | 32.3 | 32 | 32.3667 | 33 | 28.9 | 30.2 | 29 | 29 | 29.3667 | 29 | 558 | United_StatesMinnesotaROSEAU MUNI (AWOS)
United_States | Minnesota | M4 | SILVER BAY | SILVER BAY, MN, USA | 47.20N | 91.40W | 331 | -6.00 (NAC) | 92-06 | 727556 | -33.9 | -34 | -45.7 | 38.2 | 30.3 | 32.4 | 30.1 | 31 | 30.9333 | 32 | 27.5 | 29.1 | 27.6 | 28 | 28.0667 | 28 | 559 | United_StatesMinnesotaSILVER BAY
United_States | Minnesota | M4 | SOUTH ST PAUL MUNI | SOUTH ST PAUL MUNI, MN, USA | 44.85N | 93.15W | 250 | -6.00 (NAC) | 95-06 | 726603 | -26.4 | -26 | -37.8 | 39 | 33.9 | 34.8 | 34 | 34 | 34.2333 | 35 | 31.3 | 32.8 | 31.2 | 32 | 31.7667 | 32 | 560 | United_StatesMinnesotaSOUTH ST PAUL MUNI
United_States | Minnesota | M4 | ST CLOUD REGIONAL ARPT | ST CLOUD REGIONAL ARPT, MN, USA | 45.55N | 94.05W | 312 | -6.00 (NAC) | 82-06 | 726550 | -32 | -32 | -42.5 | 39.6 | 34 | 35.3 | 33.7 | 34 | 34.3333 | 35 | 30.9 | 32.5 | 30.9 | 31 | 31.4333 | 31 | 561 | United_StatesMinnesotaST CLOUD REGIONAL ARPT
United_States | Minnesota | M4 | ST JAMES MUNI ARPT | ST JAMES MUNI ARPT, MN, USA | 43.98N | 94.55W | 325 | -6.00 (NAC) | 97-06 | 726554 | -25.3 | -25 | -30.8 | 38.3 | 33.9 | 33.8 | 32.4 | 33 | 33.3667 | 34 | 32.2 | 32.4 | 30.1 | 32 | 31.5667 | 32 | 562 | United_StatesMinnesotaST JAMES MUNI ARPT
United_States | Minnesota | M4 | ST PAUL DOWNTOWN AP | ST PAUL DOWNTOWN AP, MN, USA | 44.93N | 93.05W | 217 | -6.00 (NAC) | 92-06 | 726584 | -27.9 | -28 | -38.3 | 40 | 34.1 | 36.1 | 32.3 | 34 | 34.1667 | 36 | 31.3 | 32.9 | 29.6 | 31 | 31.2667 | 31 | 563 | United_StatesMinnesotaST PAUL DOWNTOWN AP
United_States | Minnesota | M4 | THIEF RIVER(AWOS) | THIEF RIVER(AWOS), MN, USA | 48.07N | 96.18W | 340 | -6.00 (NAC) | 92-06 | 727555 | -33.4 | -33 | -44 | 38.3 | 32.1 | 32.1 | 32.2 | 32 | 32.1333 | 32 | 28.9 | 29 | 28.9 | 29 | 28.9333 | 29 | 564 | United_StatesMinnesotaTHIEF RIVER(AWOS)
United_States | Minnesota | M4 | TOFTE (RAMOS) | TOFTE (RAMOS), MN, USA | 47.58N | 90.83W | 241 | -6.00 (NAC) | 82-96 | 727554 | -29.2 | -29 | -36.4 | 34.8 | 26.3 | 28.8 | 28.5 | 28 | 27.8667 | 29 | 22.2 | 26.3 | 25.2 | 25 | 24.5667 | 25 | 565 | United_StatesMinnesotaTOFTE (RAMOS)
United_States | Minnesota | M4 | TWO HARBORS | TWO HARBORS, MN, USA | 47.05N | 91.75W | 328 | -6.00 (NAC) | 92-06 | 727444 | -30.9 | -31 | -42.1 | 37.3 | 30.2 | 32.1 | 30.9 | 31 | 31.0667 | 32 | 27.3 | 29 | 27.6 | 28 | 27.9667 | 28 | 566 | United_StatesMinnesotaTWO HARBORS
United_States | Minnesota | M4 | WHEATON NDB (AWOS) | WHEATON NDB (AWOS), MN, USA | 45.70N | 96.50W | 313 | -6.00 (NAC) | 92-06 | 727533 | -30 | -30 | -41.6 | 39.4 | 33.5 | 33 | 32.9 | 33 | 33.1333 | 33 | 31.2 | 32 | 30.2 | 31 | 31.1333 | 31 | 567 | United_StatesMinnesotaWHEATON NDB (AWOS)
United_States | Minnesota | M4 | WILLMAR | WILLMAR, MN, USA | 45.12N | 95.08W | 344 | -6.00 (NAC) | 92-06 | 726576 | -31.1 | -31 | -40.2 | 37.9 | 33.6 | 33.7 | 31.2 | 33 | 32.8333 | 34 | 31.1 | 31.5 | 28.9 | 31 | 30.5 | 31 | 568 | United_StatesMinnesotaWILLMAR
United_States | Minnesota | M4 | WINONA MUNI (AWOS) | WINONA MUNI (AWOS), MN, USA | 44.08N | 91.70W | 200 | -6.00 (NAC) | 92-06 | 726588 | -27.6 | -28 | -41.6 | 48 | 33.8 | 36.1 | 35.2 | 35 | 35.0333 | 36 | 32.1 | 32.9 | 32.3 | 32 | 32.4333 | 32 | 569 | United_StatesMinnesotaWINONA MUNI (AWOS)
United_States | Minnesota | M4 | WORTHINGTON (AWOS) | WORTHINGTON (AWOS), MN, USA | 43.65N | 95.58W | 480 | -6.00 (NAC) | 92-06 | 726587 | -25.9 | -26 | -29.5 | 38.7 | 33 | 33.8 | 32.1 | 33 | 32.9667 | 34 | 31.1 | 31.3 | 29.1 | 31 | 30.5 | 31 | 570 | United_StatesMinnesotaWORTHINGTON (AWOS)
United_States | Mississippi | E1 | COLUMBUS AFB | COLUMBUS AFB, MS, USA | 33.65N | 88.45W | 68 | -6.00 (NAC) | 82-00 | 723306 | -10.8 | -11 | -19.7 | 41.9 | 36.4 | 37.4 | 37.9 | 37 | 37.2333 | 37 | 34.6 | 35.8 | 36 | 35 | 35.4667 | 35 | 571 | United_StatesMississippiCOLUMBUS AFB
United_States | Mississippi | E1 | GOLDEN TRI(AWOS) | GOLDEN TRI(AWOS), MS, USA | 33.45N | 88.58W | 80 | -6.00 (NAC) | 92-06 | 723307 | -10.4 | -10 | -16.7 | 42.4 | 35.1 | 37.3 | 37.9 | 37 | 36.7667 | 37 | 33.6 | 36 | 36.3 | 35 | 35.3 | 35 | 572 | United_StatesMississippiGOLDEN TRI(AWOS)
United_States | Mississippi | E1 | GREENWOOD LEFLORE ARPT | GREENWOOD LEFLORE ARPT, MS, USA | 33.50N | 90.08W | 41 | -6.00 (NAC) | 82-06 | 722359 | -10 | -10 | -18.6 | 42.7 | 35.2 | 36.8 | 37.4 | 36 | 36.4667 | 37 | 33.8 | 35.2 | 36 | 35 | 35 | 35 | 573 | United_StatesMississippiGREENWOOD LEFLORE ARPT
United_States | Mississippi | E1 | HATTIESBURG LAUREL | HATTIESBURG LAUREL, MS, USA | 31.47N | 89.33W | 93 | -6.00 (NAC) | 91-06 | 722348 | -7.8 | -8 | -13.4 | 41.9 | 36.1 | 37.6 | 37.4 | 37 | 37.0333 | 38 | 33.8 | 35.2 | 35.4 | 35 | 34.8 | 35 | 574 | United_StatesMississippiHATTIESBURG LAUREL
United_States | Mississippi | E1 | JACKSON INTERNATIONAL AP | JACKSON INTERNATIONAL AP, MS, USA | 32.32N | 90.08W | 101 | -6.00 (NAC) | 82-06 | 722350 | -9.3 | -9 | -17.9 | 41.5 | 35.6 | 36.8 | 37.6 | 37 | 36.6667 | 37 | 34 | 35 | 35.6 | 35 | 34.8667 | 35 | 575 | United_StatesMississippiJACKSON INTERNATIONAL AP
United_States | Mississippi | E1 | KEESLER AFB/BILOXI | KEESLER AFB/BILOXI, MS, USA | 30.42N | 88.92W | 8 | -6.00 (NAC) | 82-01 | 747686 | -5.8 | -6 | -16.9 | 40.5 | 34.1 | 36.2 | 36.3 | 36 | 35.5333 | 36 | 32.8 | 34.1 | 34.4 | 34 | 33.7667 | 34 | 576 | United_StatesMississippiKEESLER AFB/BILOXI
United_States | Mississippi | E1 | MCCOMB PIKE COUNTY AP | MCCOMB PIKE COUNTY AP, MS, USA | 31.18N | 90.47W | 129 | -6.00 (NAC) | 82-06 | 722358 | -8.1 | -8 | -16.7 | 40.3 | 35.2 | 36.2 | 36.5 | 36 | 35.9667 | 36 | 33.7 | 34.5 | 34.8 | 34 | 34.3333 | 34 | 577 | United_StatesMississippiMCCOMB PIKE COUNTY AP
United_States | Mississippi | E1 | MERIDIAN KEY FIELD | MERIDIAN KEY FIELD, MS, USA | 32.33N | 88.75W | 95 | -6.00 (NAC) | 82-06 | 722340 | -9.9 | -10 | -18.2 | 41.6 | 36 | 37 | 37.5 | 37 | 36.8333 | 37 | 34 | 35.2 | 35.4 | 35 | 34.8667 | 35 | 578 | United_StatesMississippiMERIDIAN KEY FIELD
United_States | Mississippi | E1 | MERIDIAN NAAS | MERIDIAN NAAS, MS, USA | 32.55N | 88.57W | 97 | -6.00 (NAC) | 82-98 | 722345 | -10.9 | -11 | -20.7 | 42.1 | 37.1 | 37.9 | 37.7 | 38 | 37.5667 | 38 | 35.3 | 36 | 35.9 | 36 | 35.7333 | 36 | 579 | United_StatesMississippiMERIDIAN NAAS
United_States | Mississippi | E1 | NATCHEZ/HARDY(AWOS) | NATCHEZ/HARDY(AWOS), MS, USA | 31.62N | 91.30W | 83 | -6.00 (NAC) | 92-06 | 722357 | -7 | -7 | -13 | 38.6 | 33.7 | 35.9 | 36.3 | 35 | 35.3 | 36 | 32.5 | 33.9 | 34.1 | 34 | 33.5 | 34 | 580 | United_StatesMississippiNATCHEZ/HARDY(AWOS)
United_States | Mississippi | E1 | TUPELO C D LEMONS ARPT | TUPELO C D LEMONS ARPT, MS, USA | 34.26N | 88.77W | 110 | -6.00 (NAC) | 83-06 | 723320 | -11.5 | -12 | -21 | 42.2 | 35.6 | 37.1 | 37.5 | 37 | 36.7333 | 37 | 33.8 | 35.2 | 35.8 | 35 | 34.9333 | 35 | 581 | United_StatesMississippiTUPELO C D LEMONS ARPT
United_States | Missouri | E3 | CAPE GIRARDEAU MUNICIPAL AP | CAPE GIRARDEAU MUNICIPAL AP, MO, USA | 37.23N | 89.57W | 107 | -6.00 (NAC) | 82-06 | 723489 | -18.4 | -18 | -29.5 | 40.8 | 35.3 | 36.9 | 36.5 | 36 | 36.2333 | 37 | 33.6 | 35 | 34.6 | 34 | 34.4 | 34 | 582 | United_StatesMissouriCAPE GIRARDEAU MUNICIPAL AP
United_States | Missouri | E3 | COLUMBIA REGIONAL AIRPORT | COLUMBIA REGIONAL AIRPORT, MO, USA | 38.82N | 92.22W | 274 | -6.00 (NAC) | 82-06 | 724450 | -21 | -21 | -30.8 | 43.5 | 34.2 | 37.1 | 37.7 | 36 | 36.3333 | 37 | 31.9 | 34.7 | 35.1 | 34 | 33.9 | 34 | 583 | United_StatesMissouriCOLUMBIA REGIONAL AIRPORT
United_States | Missouri | E3 | JEFFERSON CITY MEM | JEFFERSON CITY MEM, MO, USA | 38.58N | 92.15W | 167 | -6.00 (NAC) | 97-06 | 724458 | -18.6 | -19 | -24.4 | 41.2 | 33.7 | 37.6 | 37.4 | 36 | 36.2333 | 38 | 32.5 | 35.9 | 35.1 | 35 | 34.5 | 35 | 584 | United_StatesMissouriJEFFERSON CITY MEM
United_States | Missouri | E3 | JOPLIN MUNICIPAL AP | JOPLIN MUNICIPAL AP, MO, USA | 37.15N | 94.50W | 300 | -6.00 (NAC) | 82-06 | 723495 | -17.9 | -18 | -28.1 | 42.7 | 34.7 | 37.3 | 38 | 37 | 36.6667 | 37 | 32.9 | 35.5 | 36.3 | 35 | 34.9 | 35 | 585 | United_StatesMissouriJOPLIN MUNICIPAL AP
United_States | Missouri | E3 | KAISER MEM (AWOS) | KAISER MEM (AWOS), MO, USA | 38.10N | 92.55W | 265 | -6.00 (NAC) | 92-06 | 724459 | -18.2 | -18 | -26.9 | 44.1 | 33.6 | 37.8 | 38 | 36 | 36.4667 | 38 | 32.5 | 35.3 | 36.2 | 35 | 34.6667 | 35 | 586 | United_StatesMissouriKAISER MEM (AWOS)
United_States | Missouri | E3 | KANSAS CITY DOWNTOWN AP | KANSAS CITY DOWNTOWN AP, MO, USA | 39.12N | 94.59W | 229 | -6.00 (NAC) | 82-06 | 724463 | -19.1 | -19 | -29.9 | 43.7 | 35.7 | 38 | 38.5 | 37 | 37.4 | 38 | 33.5 | 36.5 | 36.1 | 35 | 35.3667 | 35 | 587 | United_StatesMissouriKANSAS CITY DOWNTOWN AP
United_States | Missouri | E3 | KANSAS CITY INT'L ARPT | KANSAS CITY INT'L ARPT, MO, USA | 39.30N | 94.72W | 312 | -6.00 (NAC) | 82-06 | 724460 | -21.2 | -21 | -31.5 | 43.5 | 34.9 | 37.5 | 38.6 | 37 | 37 | 38 | 32.7 | 35.6 | 35.8 | 35 | 34.7 | 35 | 588 | United_StatesMissouriKANSAS CITY INT'L ARPT
United_States | Missouri | E3 | KIRKSVILLE REGIONAL AP | KIRKSVILLE REGIONAL AP, MO, USA | 40.10N | 92.54W | 294 | -6.00 (NAC) | 82-06 | 724455 | -22 | -22 | -31.8 | 42 | 34 | 36.9 | 37 | 36 | 35.9667 | 37 | 32 | 34.9 | 34.3 | 34 | 33.7333 | 34 | 589 | United_StatesMissouriKIRKSVILLE REGIONAL AP
United_States | Missouri | E3 | POPLAR BLUFF(AMOS) | POPLAR BLUFF(AMOS), MO, USA | 36.77N | 90.47W | 146 | -6.00 (NAC) | 82-06 | 723300 | -16.2 | -16 | -26.6 | 42.3 | 34.6 | 36.2 | 36.4 | 36 | 35.7333 | 36 | 32.9 | 34.5 | 34.1 | 34 | 33.8333 | 34 | 590 | United_StatesMissouriPOPLAR BLUFF(AMOS)
United_States | Missouri | E3 | SEDALIA MEMORIAL | SEDALIA MEMORIAL, MO, USA | 38.70N | 93.18W | 277 | -6.00 (NAC) | 97-06 | 724453 | -18.3 | -18 | -23 | 43.1 | 33 | 37.7 | 38 | 36 | 36.2333 | 38 | 32.3 | 36.1 | 36.2 | 35 | 34.8667 | 35 | 591 | United_StatesMissouriSEDALIA MEMORIAL
United_States | Missouri | E3 | SPICKARD (AMOS) | SPICKARD (AMOS), MO, USA | 40.25N | 93.72W | 270 | -6.00 (NAC) | 82-96 | 725400 | -22 | N/A | N/A | N/A | 36.1 | 37.9 | 38.2 | 37 | 37.4 | 38 | 33.1 | 35.3 | 35.5 | 35 | 34.6333 | 35 | 592 | United_StatesMissouriSPICKARD (AMOS)
United_States | Missouri | E3 | SPRINGFIELD REGIONAL ARPT | SPRINGFIELD REGIONAL ARPT, MO, USA | 37.24N | 93.39W | 387 | -6.00 (NAC) | 82-06 | 724400 | -19.1 | -19 | -29.1 | 42.2 | 33.8 | 36.9 | 37.1 | 36 | 35.9333 | 37 | 32 | 34.8 | 35.3 | 34 | 34.0333 | 34 | 593 | United_StatesMissouriSPRINGFIELD REGIONAL ARPT
United_States | Missouri | E3 | ST LOUIS LAMBERT INT'L ARPT | ST LOUIS LAMBERT INT'L ARPT, MO, USA | 38.75N | 90.37W | 216 | -6.00 (NAC) | 82-06 | 724340 | -18.8 | -19 | -30.1 | 41.7 | 35 | 37.4 | 37.6 | 37 | 36.6667 | 37 | 33.4 | 35.6 | 35.3 | 35 | 34.7667 | 35 | 594 | United_StatesMissouriST LOUIS LAMBERT INT'L ARPT
United_States | Missouri | E3 | ST LOUIS SPIRIT OF ST LOUIS A | ST LOUIS SPIRIT OF ST LOUIS A, MO, USA | 38.66N | 90.66W | 141 | -6.00 (NAC) | 86-06 | 724345 | -19.5 | -20 | -30.9 | 41.5 | 35.3 | 37.3 | 37.4 | 37 | 36.6667 | 37 | 33.1 | 35.3 | 35 | 34 | 34.4667 | 34 | 595 | United_StatesMissouriST LOUIS SPIRIT OF ST LOUIS A
United_States | Missouri | E3 | VICHY ROLLA NATL ARPT | VICHY ROLLA NATL ARPT, MO, USA | 38.13N | 91.77W | 347 | -6.00 (NAC) | 82-06 | 724456 | -19 | -19 | -24.9 | 41.9 | 34.3 | 37.6 | 37.2 | 36 | 36.3667 | 38 | 32.1 | 35.4 | 35.4 | 34 | 34.3 | 34 | 596 | United_StatesMissouriVICHY ROLLA NATL ARPT
United_States | Missouri | E3 | WHITEMAN AFB | WHITEMAN AFB, MO, USA | 38.73N | 93.55W | 255 | -6.00 (NAC) | 82-06 | 724467 | -20.4 | -20 | -30.1 | 43 | 34.8 | 37.7 | 38.2 | 37 | 36.9 | 38 | 32.8 | 36.1 | 36.2 | 35 | 35.0333 | 35 | 597 | United_StatesMissouriWHITEMAN AFB
United_States | Montana | M4 | BILLINGS LOGAN INT'L ARPT | BILLINGS LOGAN INT'L ARPT, MT, USA | 45.81N | 108.54W | 1088 | -7.00 (NAM) | 82-06 | 726770 | -26.6 | -27 | -38.2 | 42.7 | 35.7 | 37.7 | 36.6 | 37 | 36.6667 | 38 | 32.4 | 35.4 | 34.4 | 34 | 34.0667 | 34 | 598 | United_StatesMontanaBILLINGS LOGAN INT'L ARPT
United_States | Montana | M4 | BOZEMAN GALLATIN FIELD | BOZEMAN GALLATIN FIELD, MT, USA | 45.79N | 111.15W | 1356 | -7.00 (NAM) | 82-06 | 726797 | -32.7 | -33 | -43.3 | 40.5 | 32.7 | 35.8 | 35 | 35 | 34.5 | 36 | 29.5 | 33.6 | 32.6 | 32 | 31.9 | 32 | 599 | United_StatesMontanaBOZEMAN GALLATIN FIELD
United_States | Montana | M4 | BUTTE BERT MOONEY ARPT | BUTTE BERT MOONEY ARPT, MT, USA | 45.95N | 112.51W | 1687 | -7.00 (NAM) | 82-06 | 726785 | -35.3 | -35 | -47.2 | 37.6 | 30.4 | 33.8 | 32.5 | 32 | 32.2333 | 34 | 27.8 | 31.6 | 30.3 | 30 | 29.9 | 30 | 600 | United_StatesMontanaBUTTE BERT MOONEY ARPT
United_States | Montana | M4 | CUT BANK MUNI AP | CUT BANK MUNI AP, MT, USA | 48.61N | 112.38W | 1170 | -7.00 (NAM) | 83-06 | 727796 | -33.4 | -33 | -45.3 | 39.8 | 29.2 | 33.9 | 34 | 32 | 32.3667 | 34 | 26.3 | 32 | 31.9 | 30 | 30.0667 | 30 | 601 | United_StatesMontanaCUT BANK MUNI AP
United_States | Montana | M4 | DILLON AIRPORT | DILLON AIRPORT, MT, USA | 45.26N | 112.55W | 1592 | -7.00 (NAM) | 97-06 | 726796 | -26.3 | -26 | -38 | 38.1 | 29.8 | 34 | 32.9 | 32 | 32.2333 | 34 | 27.5 | 32.5 | 31.2 | 30 | 30.4 | 30 | 602 | United_StatesMontanaDILLON AIRPORT
United_States | Montana | M4 | GLASGOW INTL ARPT | GLASGOW INTL ARPT, MT, USA | 48.21N | 106.62W | 699 | -7.00 (NAM) | 82-06 | 727680 | -33 | -33 | -43.8 | 42.3 | 36.6 | 37.2 | 37.1 | 37 | 36.9667 | 37 | 32.7 | 34.9 | 34.7 | 34 | 34.1 | 34 | 603 | United_StatesMontanaGLASGOW INTL ARPT
United_States | Montana | M4 | GLENDIVE(AWOS) | GLENDIVE(AWOS), MT, USA | 47.13N | 104.80W | 749 | -7.00 (NAM) | 92-06 | 726676 | -30.7 | -31 | -38.9 | 43 | 34 | 37.5 | 37.3 | 36 | 36.2667 | 38 | 31 | 35.2 | 34.7 | 34 | 33.6333 | 34 | 604 | United_StatesMontanaGLENDIVE(AWOS)
United_States | Montana | M4 | GREAT FALLS | GREAT FALLS, MT, USA | 47.45N | 111.38W | 1130 | -7.00 (NAM) | 94-06 | 727760 | -32 | N/A | N/A | N/A | 30.9 | 35.7 | 34.6 | 34 | 33.7333 | 36 | 27.4 | 33.1 | 32.3 | 31 | 30.9333 | 31 | 605 | United_StatesMontanaGREAT FALLS
United_States | Montana | M4 | GREAT FALLS INTL ARPT | GREAT FALLS INTL ARPT, MT, USA | 47.47N | 111.38W | 1115 | -7.00 (NAM) | 82-06 | 727750 | -31.2 | -31 | -42.5 | 40.7 | 33.1 | 36.3 | 35.7 | 35 | 35.0333 | 36 | 30.2 | 33.9 | 33.1 | 32 | 32.4 | 32 | 606 | United_StatesMontanaGREAT FALLS INTL ARPT
United_States | Montana | M4 | HAVRE CITY-COUNTY AP | HAVRE CITY-COUNTY AP, MT, USA | 48.56N | 109.78W | 792 | -7.00 (NAM) | 82-06 | 727770 | -35.1 | -35 | -47.7 | 42.9 | 35 | 37.4 | 37.4 | 37 | 36.6 | 37 | 31.4 | 35.1 | 34.6 | 34 | 33.7 | 34 | 607 | United_StatesMontanaHAVRE CITY-COUNTY AP
United_States | Montana | M4 | HELENA REGIONAL AIRPORT | HELENA REGIONAL AIRPORT, MT, USA | 46.61N | 111.96W | 1179 | -7.00 (NAM) | 82-06 | 727720 | -29.8 | -30 | -42.5 | 41 | 33.4 | 36.8 | 35.7 | 35 | 35.3 | 37 | 30.9 | 34.4 | 33.1 | 33 | 32.8 | 33 | 608 | United_StatesMontanaHELENA REGIONAL AIRPORT
United_States | Montana | M4 | JORDAN (RAMOS) | JORDAN (RAMOS), MT, USA | 47.33N | 106.93W | 811 | -7.00 (NAM) | 83-06 | 727684 | -36.8 | -37 | -47.3 | 43.6 | 37.4 | 37.8 | 37.3 | 38 | 37.5 | 38 | 33.7 | 35.9 | 35.3 | 35 | 34.9667 | 35 | 609 | United_StatesMontanaJORDAN (RAMOS)
United_States | Montana | M4 | KALISPELL GLACIER PK INT'L AR | KALISPELL GLACIER PK INT'L AR, MT, USA | 48.30N | 114.26W | 906 | -7.00 (NAM) | 82-06 | 727790 | -27.4 | -27 | -39.5 | 38.6 | 31 | 34.5 | 33.7 | 33 | 33.0667 | 35 | 28.5 | 32.5 | 31.9 | 31 | 30.9667 | 31 | 610 | United_StatesMontanaKALISPELL GLACIER PK INT'L AR
United_States | Montana | M4 | LEWISTOWN MUNICIPAL ARPT | LEWISTOWN MUNICIPAL ARPT, MT, USA | 47.05N | 109.47W | 1264 | -7.00 (NAM) | 82-06 | 726776 | -31.4 | -31 | -43.2 | 39.6 | 30.8 | 35 | 34.7 | 34 | 33.5 | 35 | 27.4 | 32.8 | 32.4 | 31 | 30.8667 | 31 | 611 | United_StatesMontanaLEWISTOWN MUNICIPAL ARPT
United_States | Montana | M4 | MALMSTROM AFB | MALMSTROM AFB, MT, USA | 47.52N | 111.18W | 1056 | -7.00 (NAM) | 82-06 | 727755 | -30.3 | -30 | -40.3 | 42 | 32.9 | 36.2 | 37 | 35 | 35.3667 | 36 | 30.3 | 33.9 | 34 | 33 | 32.7333 | 33 | 612 | United_StatesMontanaMALMSTROM AFB
United_States | Montana | M4 | MILES CITY MUNICIPAL ARPT | MILES CITY MUNICIPAL ARPT, MT, USA | 46.43N | 105.89W | 803 | -7.00 (NAM) | 82-06 | 742300 | -31.1 | -31 | -42.5 | 44.7 | 38 | 39.2 | 38.7 | 39 | 38.6333 | 39 | 34.1 | 37.2 | 36.4 | 36 | 35.9 | 36 | 613 | United_StatesMontanaMILES CITY MUNICIPAL ARPT
United_States | Montana | M4 | MISSOULA INTERNATIONAL AP | MISSOULA INTERNATIONAL AP, MT, USA | 46.92N | 114.09W | 972 | -7.00 (NAM) | 82-06 | 727730 | -25 | -25 | -37.9 | 40.5 | 33 | 36.9 | 35.4 | 35 | 35.1 | 37 | 30.3 | 34.3 | 33.2 | 33 | 32.6 | 33 | 614 | United_StatesMontanaMISSOULA INTERNATIONAL AP
United_States | Montana | M4 | SIDNEY-RICHLAND | SIDNEY-RICHLAND, MT, USA | 47.70N | 104.20W | 605 | -7.00 (NAM) | 92-06 | 727687 | -32.4 | -32 | -39.3 | 42.4 | 35.2 | 37.3 | 37 | 37 | 36.5 | 37 | 31.2 | 34.1 | 33.8 | 33 | 33.0333 | 33 | 615 | United_StatesMontanaSIDNEY-RICHLAND
United_States | Nebraska | M4 | AINSWORTH MUNICIPAL | AINSWORTH MUNICIPAL, NE, USA | 42.58N | 100.00W | 789 | -6.00 (NAC) | 95-06 | 725556 | -25.9 | -26 | -33.6 | 45.4 | 34.9 | 39.8 | 37.3 | 37 | 37.3333 | 40 | 31.6 | 37.1 | 34 | 34 | 34.2333 | 34 | 616 | United_StatesNebraskaAINSWORTH MUNICIPAL
United_States | Nebraska | M4 | ALLIANCE MUNICIPAL | ALLIANCE MUNICIPAL, NE, USA | 42.05N | 102.80W | 1198 | -7.00 (NAM) | 96-06 | 725635 | -29.8 | -30 | -41.6 | 43.8 | 37.3 | 39.1 | 37.3 | 38 | 37.9 | 39 | 33.9 | 37.3 | 35 | 35 | 35.4 | 35 | 617 | United_StatesNebraskaALLIANCE MUNICIPAL
United_States | Nebraska | M4 | BEATRICE MUNICIPAL | BEATRICE MUNICIPAL, NE, USA | 40.30N | 96.75W | 403 | -6.00 (NAC) | 95-06 | 725515 | -23.2 | -23 | -30.3 | 42.8 | 35.2 | 38.8 | 37.8 | 37 | 37.2667 | 39 | 33.7 | 37.1 | 35.6 | 35 | 35.4667 | 35 | 618 | United_StatesNebraskaBEATRICE MUNICIPAL
United_States | Nebraska | M4 | BREWSTER FIELD ARPT | BREWSTER FIELD ARPT, NE, USA | 40.45N | 99.33W | 704 | -6.00 (NAC) | 96-06 | 725628 | -21.7 | -22 | -26.9 | 41.9 | 36.1 | 37.9 | 37.1 | 37 | 37.0333 | 38 | 33.5 | 36.1 | 33.9 | 35 | 34.5 | 35 | 619 | United_StatesNebraskaBREWSTER FIELD ARPT
United_States | Nebraska | M4 | COLUMBUS MUNI | COLUMBUS MUNI, NE, USA | 41.45N | 97.33W | 451 | -6.00 (NAC) | 92-06 | 725565 | -24.9 | -25 | -30.6 | 40.7 | 34.1 | 37.2 | 36 | 36 | 35.7667 | 37 | 32.6 | 34.2 | 33 | 33 | 33.2667 | 33 | 620 | United_StatesNebraskaCOLUMBUS MUNI
United_States | Nebraska | M4 | FREMONT MUNI ARPT | FREMONT MUNI ARPT, NE, USA | 41.45N | 96.52W | 379 | -6.00 (NAC) | 96-06 | 725564 | -25 | N/A | N/A | N/A | 34.3 | 37.1 | 36 | 36 | 35.8 | 37 | 32.7 | 34.8 | 32.8 | 33 | 33.4333 | 33 | 621 | United_StatesNebraskaFREMONT MUNI ARPT
United_States | Nebraska | M4 | GRAND ISLAND CENTRAL NE REGIO | GRAND ISLAND CENTRAL NE REGIO, NE, USA | 40.96N | 98.31W | 566 | -6.00 (NAC) | 82-06 | 725520 | -24.7 | -25 | -32.7 | 44.9 | 36.7 | 38.8 | 37.3 | 38 | 37.6 | 39 | 33.9 | 36 | 34.9 | 35 | 34.9333 | 35 | 622 | United_StatesNebraskaGRAND ISLAND CENTRAL NE REGIO
United_States | Nebraska | M4 | HASTINGS MUNICIPAL | HASTINGS MUNICIPAL, NE, USA | 40.60N | 98.43W | 596 | -6.00 (NAC) | 95-06 | 725525 | -23 | -23 | -29.2 | 42.4 | 36.1 | 38.7 | 37.2 | 37 | 37.3333 | 39 | 33.6 | 36.9 | 34.1 | 35 | 34.8667 | 35 | 623 | United_StatesNebraskaHASTINGS MUNICIPAL
United_States | Nebraska | M4 | KEARNEY MUNI (AWOS) | KEARNEY MUNI (AWOS), NE, USA | 40.73N | 99.00W | 649 | -6.00 (NAC) | 92-06 | 725526 | -22.8 | -23 | -31.1 | 42.2 | 35.9 | 37.5 | 36.2 | 37 | 36.5333 | 38 | 32.9 | 35.1 | 33.7 | 34 | 33.9 | 34 | 624 | United_StatesNebraskaKEARNEY MUNI (AWOS)
United_States | Nebraska | M4 | LINCOLN MUNICIPAL ARPT | LINCOLN MUNICIPAL ARPT, NE, USA | 40.83N | 96.76W | 362 | -6.00 (NAC) | 82-06 | 725510 | -24.1 | -24 | -33.6 | 44.6 | 37 | 38.9 | 38.1 | 38 | 38 | 39 | 34.1 | 36.5 | 35.8 | 35 | 35.4667 | 35 | 625 | United_StatesNebraskaLINCOLN MUNICIPAL ARPT
United_States | Nebraska | M4 | MCCOOK MUNICIPAL | MCCOOK MUNICIPAL, NE, USA | 40.20N | 100.58W | 786 | -6.00 (NAC) | 96-06 | 725625 | -21.9 | -22 | -29.9 | 46.5 | 38.7 | 42.1 | 38.8 | 40 | 39.8667 | 42 | 37.2 | 38.8 | 37.1 | 38 | 37.7 | 38 | 626 | United_StatesNebraskaMCCOOK MUNICIPAL
United_States | Nebraska | M4 | NORFOLK KARL STEFAN MEM ARPT | NORFOLK KARL STEFAN MEM ARPT, NE, USA | 41.98N | 97.44W | 473 | -6.00 (NAC) | 82-06 | 725560 | -25.6 | -26 | -34 | 43.3 | 35.9 | 37.4 | 36.4 | 37 | 36.5667 | 37 | 33.3 | 35 | 34.2 | 34 | 34.1667 | 34 | 627 | United_StatesNebraskaNORFOLK KARL STEFAN MEM ARPT
United_States | Nebraska | M4 | NORTH PLATTE REGIONAL AP | NORTH PLATTE REGIONAL AP, NE, USA | 41.12N | 100.67W | 850 | -6.00 (NAC) | 82-06 | 725620 | -26.2 | -26 | -37.4 | 43.9 | 36.6 | 38.9 | 37.1 | 38 | 37.5333 | 39 | 33.7 | 36.1 | 34.8 | 35 | 34.8667 | 35 | 628 | United_StatesNebraskaNORTH PLATTE REGIONAL AP
United_States | Nebraska | M4 | O`NEILL/BAKER FIELD | O`NEILL/BAKER FIELD, NE, USA | 42.47N | 98.68W | 619 | -6.00 (NAC) | 95-06 | 725566 | -25.3 | -25 | -31.5 | 44.8 | 35.9 | 38.9 | 37.5 | 37 | 37.4333 | 39 | 32.3 | 36 | 34 | 34 | 34.1 | 34 | 629 | United_StatesNebraskaO`NEILL/BAKER FIELD
United_States | Nebraska | M4 | OFFUTT AFB/BELLEVUE | OFFUTT AFB/BELLEVUE, NE, USA | 41.12N | 95.92W | 319 | -6.00 (NAC) | 82-06 | 725540 | -22.4 | -22 | -29.4 | 44 | 36 | 38 | 37.1 | 37 | 37.0333 | 38 | 33 | 35.1 | 34.5 | 34 | 34.2 | 34 | 630 | United_StatesNebraskaOFFUTT AFB/BELLEVUE
United_States | Nebraska | M4 | OMAHA EPPLEY AIRFIELD | OMAHA EPPLEY AIRFIELD, NE, USA | 41.31N | 95.90W | 299 | -6.00 (NAC) | 82-06 | 725500 | -24.3 | -24 | -32.5 | 44 | 35.6 | 38.2 | 37.1 | 37 | 36.9667 | 38 | 33.3 | 35.2 | 34.5 | 34 | 34.3333 | 34 | 631 | United_StatesNebraskaOMAHA EPPLEY AIRFIELD
United_States | Nebraska | M4 | OMAHA WSFO | OMAHA WSFO, NE, USA | 41.37N | 96.02W | 399 | -6.00 (NAC) | 82-93 | 725530 | -24.5 | -25 | -33.1 | 42.7 | 36 | 36.1 | 36.5 | 36 | 36.2 | 36 | 33.1 | 34 | 33.7 | 34 | 33.6 | 34 | 632 | United_StatesNebraskaOMAHA WSFO
United_States | Nebraska | M4 | SCOTTSBLUFF W B HEILIG FIELD | SCOTTSBLUFF W B HEILIG FIELD, NE, USA | 41.87N | 103.60W | 1206 | -7.00 (NAM) | 82-06 | 725660 | -27.9 | -28 | -42.1 | 43.1 | 37.1 | 38.9 | 36.6 | 38 | 37.5333 | 39 | 33.9 | 36.7 | 34.6 | 35 | 35.0667 | 35 | 633 | United_StatesNebraskaSCOTTSBLUFF W B HEILIG FIELD
United_States | Nebraska | M4 | SIDNEY MUNICIPAL AP | SIDNEY MUNICIPAL AP, NE, USA | 41.10N | 102.99W | 1313 | -7.00 (NAM) | 82-06 | 725610 | -26.6 | -27 | -40 | 44.2 | 36.1 | 38.6 | 36.2 | 37 | 36.9667 | 39 | 32.9 | 36.2 | 34.2 | 34 | 34.4333 | 34 | 634 | United_StatesNebraskaSIDNEY MUNICIPAL AP
United_States | Nebraska | M4 | TEKAMAH (ASOS) | TEKAMAH (ASOS), NE, USA | 41.77N | 96.17W | 312 | -6.00 (NAC) | 95-06 | 725527 | -25.7 | -26 | -30.5 | 42.3 | 35.9 | 37.3 | 35.9 | 36 | 36.3667 | 37 | 33 | 34.8 | 32.8 | 34 | 33.5333 | 34 | 635 | United_StatesNebraskaTEKAMAH (ASOS)
United_States | Nebraska | M4 | VALENTINE MILLER FIELD | VALENTINE MILLER FIELD, NE, USA | 42.86N | 100.55W | 792 | -6.00 (NAC) | 82-06 | 725670 | -29.4 | -29 | -40.5 | 46 | 37.6 | 39.7 | 37.9 | 38 | 38.4 | 40 | 33.9 | 37.1 | 35.6 | 36 | 35.5333 | 36 | 636 | United_StatesNebraskaVALENTINE MILLER FIELD
United_States | Nevada-S | M2 | CALIENTE (AMOS) | CALIENTE (AMOS), NV, USA | 37.62N | 114.52W | 1335 | -8.00 (NAP) | 82-02 | 724870 | -22 | N/A | N/A | N/A | 37.7 | 39.1 | 37.8 | 38 | 38.2 | 39 | 36.2 | 37.4 | 36.4 | 37 | 36.6667 | 37 | 637 | United_StatesNevada-SCALIENTE (AMOS)
United_States | Nevada-N | M3 | ELKO MUNICIPAL ARPT | ELKO MUNICIPAL ARPT, NV, USA | 40.83N | 115.79W | 1547 | -8.00 (NAP) | 82-06 | 725825 | -23.8 | -24 | -36.2 | 41.7 | 34.2 | 37.5 | 35.6 | 36 | 35.7667 | 38 | 32.3 | 35.7 | 34.2 | 34 | 34.0667 | 34 | 638 | United_StatesNevada-NELKO MUNICIPAL ARPT
United_States | Nevada-N | M3 | ELY YELLAND FIELD | ELY YELLAND FIELD, NV, USA | 39.30N | 114.85W | 1909 | -8.00 (NAP) | 82-06 | 724860 | -25 | -25 | -35.8 | 38.9 | 32.4 | 35.3 | 33.3 | 34 | 33.6667 | 35 | 30.9 | 33.4 | 31.9 | 32 | 32.0667 | 32 | 639 | United_StatesNevada-NELY YELLAND FIELD
United_States | Nevada-N | M3 | EUREKA (RAMOS) | EUREKA (RAMOS), NV, USA | 39.52N | 115.97W | 1993 | -8.00 (NAP) | 83-06 | 725824 | -19.7 | -20 | -30.6 | 39.9 | 32.5 | 36.2 | 33.8 | 34 | 34.1667 | 36 | 30.6 | 33.7 | 32.3 | 32 | 32.2 | 32 | 640 | United_StatesNevada-NEUREKA (RAMOS)
United_States | Nevada-S | M2 | FALLON NAAS | FALLON NAAS, NV, USA | 39.42N | 118.70W | 1199 | -8.00 (NAP) | 90-06 | 724885 | -20 | N/A | N/A | N/A | 36.9 | 39.3 | 39.3 | 39 | 38.5 | 39 | 35 | 37.7 | 37.1 | 37 | 36.6 | 37 | 641 | United_StatesNevada-SFALLON NAAS
United_States | Nevada-S | M2 | LAS VEGAS MCCARRAN INTL AP | LAS VEGAS MCCARRAN INTL AP, NV, USA | 36.08N | 115.16W | 665 | -8.00 (NAP) | 82-06 | 723860 | -3.8 | -4 | -11 | 47.6 | 42.9 | 44.8 | 43 | 44 | 43.5667 | 45 | 41.2 | 43 | 41.7 | 42 | 41.9667 | 42 | 642 | United_StatesNevada-SLAS VEGAS MCCARRAN INTL AP
United_States | Nevada-N | M3 | LOVELOCK DERBY FIELD | LOVELOCK DERBY FIELD, NV, USA | 40.07N | 118.57W | 1190 | -8.00 (NAP) | 88-06 | 725805 | -19.3 | -19 | -32.7 | 44.1 | 36.6 | 40.3 | 38 | 38 | 38.3 | 40 | 34.7 | 37.9 | 36.7 | 36 | 36.4333 | 36 | 643 | United_StatesNevada-NLOVELOCK DERBY FIELD
United_States | Nevada-S | M2 | MERCURY DESERT ROCK AP | MERCURY DESERT ROCK AP, NV, USA | 36.62N | 116.03W | 1009 | -8.00 (NAP) | 83-06 | 723870 | -6.9 | -7 | -13.4 | 46.5 | 40.7 | 42.4 | 41.4 | 42 | 41.5 | 42 | 38.3 | 40.7 | 39.2 | 39 | 39.4 | 39 | 644 | United_StatesNevada-SMERCURY DESERT ROCK AP
United_States | Nevada-S | M2 | NELLIS AFB | NELLIS AFB, NV, USA | 36.23N | 115.03W | 573 | -8.00 (NAP) | 82-06 | 723865 | -5.6 | -6 | -14.2 | 49.1 | 43.8 | 45.9 | 43.9 | 45 | 44.5333 | 46 | 41.7 | 43.4 | 42.4 | 43 | 42.5 | 43 | 645 | United_StatesNevada-SNELLIS AFB
United_States | Nevada-N | M3 | RENO TAHOE INTERNATIONAL AP | RENO TAHOE INTERNATIONAL AP, NV, USA | 39.48N | 119.77W | 1341 | -8.00 (NAP) | 82-06 | 724880 | -14.7 | -15 | -26 | 40.8 | 34.9 | 37.9 | 36.5 | 36 | 36.4333 | 38 | 32.9 | 36 | 35 | 35 | 34.6333 | 35 | 646 | United_StatesNevada-NRENO TAHOE INTERNATIONAL AP
United_States | Nevada-S | M2 | TONOPAH AIRPORT | TONOPAH AIRPORT, NV, USA | 38.06N | 117.09W | 1656 | -8.00 (NAP) | 82-06 | 724855 | -16.9 | -17 | -25.5 | 40 | 35 | 37.3 | 36 | 36 | 36.1 | 37 | 33.4 | 36 | 34.6 | 35 | 34.6667 | 35 | 647 | United_StatesNevada-STONOPAH AIRPORT
United_States | Nevada-N | M3 | WINNEMUCCA MUNICIPAL ARPT | WINNEMUCCA MUNICIPAL ARPT, NV, USA | 40.90N | 117.81W | 1315 | -8.00 (NAP) | 82-06 | 725830 | -21.2 | -21 | -35.3 | 43.8 | 35.8 | 39 | 37.5 | 37 | 37.4333 | 39 | 33.9 | 37 | 35.8 | 36 | 35.5667 | 36 | 648 | United_StatesNevada-NWINNEMUCCA MUNICIPAL ARPT
United_States | New_Hampshire | E5 | BERLIN MUNICIPAL | BERLIN MUNICIPAL, NH, USA | 44.58N | 71.18W | 353 | -5.00 (NAE) | 95-06 | 726160 | -32 | -32 | -41.9 | 36.8 | 32.2 | 31.2 | 31.3 | 32 | 31.5667 | 31 | 28.8 | 28.9 | 28.6 | 29 | 28.7667 | 29 | 649 | United_StatesNew_HampshireBERLIN MUNICIPAL
United_States | New_Hampshire | E5 | CONCORD MUNICIPAL ARPT | CONCORD MUNICIPAL ARPT, NH, USA | 43.20N | 71.50W | 106 | -5.00 (NAE) | 82-06 | 726050 | -25.2 | -25 | -36.2 | 38.2 | 33.3 | 34.2 | 33.7 | 34 | 33.7333 | 34 | 31.1 | 32 | 31.4 | 32 | 31.5 | 32 | 650 | United_StatesNew_HampshireCONCORD MUNICIPAL ARPT
United_States | New_Hampshire | E5 | DILLANT HOPKINS | DILLANT HOPKINS, NH, USA | 42.90N | 72.27W | 153 | -5.00 (NAE) | 92-06 | 726165 | -25.1 | -25 | -35.1 | 37.7 | 32.7 | 32.9 | 32.8 | 33 | 32.8 | 33 | 30.9 | 31.2 | 30.2 | 31 | 30.7667 | 31 | 651 | United_StatesNew_HampshireDILLANT HOPKINS
United_States | New_Hampshire | E5 | ISLE OF SHOALS | ISLE OF SHOALS, NH, USA | 42.97N | 70.62W | 19 | -5.00 (NAE) | 85-06 | 994270 | -17.4 | -17 | -24.7 | 35.4 | 28.5 | 29.4 | 29.1 | 29 | 29 | 29 | 25.6 | 27.2 | 26.5 | 26 | 26.4333 | 26 | 652 | United_StatesNew_HampshireISLE OF SHOALS
United_States | New_Hampshire | E5 | JAFFREY MUNICIPAL | JAFFREY MUNICIPAL, NH, USA | 42.80N | 72.00W | 317 | -5.00 (NAE) | 97-06 | 726163 | -23 | -23 | -32.7 | 35.9 | 32.1 | 32.2 | 32.3 | 32 | 32.2 | 32 | 29.1 | 29.8 | 29.7 | 30 | 29.5333 | 30 | 653 | United_StatesNew_HampshireJAFFREY MUNICIPAL
United_States | New_Hampshire | E5 | LACONIA MUNI (AWOS) | LACONIA MUNI (AWOS), NH, USA | 43.57N | 71.42W | 166 | -5.00 (NAE) | 92-06 | 726155 | -23.6 | -24 | -34.1 | 37.7 | 32.8 | 32.8 | 32.5 | 33 | 32.7 | 33 | 30.9 | 31.1 | 29.9 | 31 | 30.6333 | 31 | 654 | United_StatesNew_HampshireLACONIA MUNI (AWOS)
United_States | New_Hampshire | E5 | LEBANON MUNICIPAL | LEBANON MUNICIPAL, NH, USA | 43.63N | 72.30W | 182 | -5.00 (NAE) | 82-03 | 726116 | -26.7 | -27 | -35.4 | 38 | 32.9 | 33.6 | 33 | 33 | 33.1667 | 34 | 30.3 | 31.3 | 31 | 31 | 30.8667 | 31 | 655 | United_StatesNew_HampshireLEBANON MUNICIPAL
United_States | New_Hampshire | E5 | MANCHESTER AIRPORT | MANCHESTER AIRPORT, NH, USA | 42.93N | 71.44W | 71 | -5.00 (NAE) | 84-06 | 743945 | -21 | -21 | -27.7 | 41.6 | 34.4 | 35.5 | 34 | 35 | 34.6333 | 36 | 32.4 | 33 | 32.1 | 33 | 32.5 | 33 | 656 | United_StatesNew_HampshireMANCHESTER AIRPORT
United_States | New_Hampshire | E5 | MOUNT WASHINGTON | MOUNT WASHINGTON, NH, USA | 44.27N | 71.30W | 1910 | -5.00 (NAE) | 82-06 | 726130 | -35.5 | -36 | -42 | 22.3 | 17.8 | 18 | 17.5 | 18 | 17.7667 | 18 | 15.6 | 16.1 | 15.7 | 16 | 15.8 | 16 | 657 | United_StatesNew_HampshireMOUNT WASHINGTON
United_States | New_Hampshire | E5 | PEASE INTL TRADEPOR | PEASE INTL TRADEPOR, NH, USA | 43.08N | 70.82W | 31 | -5.00 (NAE) | 82-06 | 726055 | -19.4 | -19 | -26.4 | 37.8 | 32.6 | 33.9 | 33.4 | 33 | 33.3 | 34 | 30.2 | 31.6 | 31.1 | 31 | 30.9667 | 31 | 658 | United_StatesNew_HampshirePEASE INTL TRADEPOR
United_States | New_Jersey | E4 | ATLANTIC CITY INTL AP | ATLANTIC CITY INTL AP, NJ, USA | 39.46N | 74.46W | 20 | -5.00 (NAE) | 82-06 | 724070 | -16.4 | -16 | -25.1 | 39.7 | 34.5 | 35.8 | 34.9 | 35 | 35.0667 | 36 | 32.1 | 33.8 | 32.6 | 33 | 32.8333 | 33 | 659 | United_StatesNew_JerseyATLANTIC CITY INTL AP
United_States | New_Jersey | E4 | BELMAR-FARMINGDALE | BELMAR-FARMINGDALE, NJ, USA | 40.18N | 74.13W | 26 | -5.00 (NAE) | 92-06 | 724084 | -14.3 | -14 | -23.8 | 39.6 | 32.9 | 35.8 | 34.8 | 35 | 34.5 | 36 | 31.4 | 32.9 | 32.1 | 32 | 32.1333 | 32 | 660 | United_StatesNew_JerseyBELMAR-FARMINGDALE
United_States | New_Jersey | E4 | CAPE MAY CO | CAPE MAY CO, NJ, USA | 39.00N | 74.90W | 7 | -5.00 (NAE) | 92-06 | 745966 | -12.7 | -13 | -19.7 | 37.1 | 32 | 34 | 32.9 | 33 | 32.9667 | 34 | 29.7 | 32.3 | 31.2 | 31 | 31.0667 | 31 | 661 | United_StatesNew_JerseyCAPE MAY CO
United_States | New_Jersey | E4 | MCGUIRE AFB | MCGUIRE AFB, NJ, USA | 40.02N | 74.60W | 45 | -5.00 (NAE) | 82-06 | 724096 | -15.8 | -16 | -23.3 | 41.2 | 34.1 | 36.2 | 35.9 | 35 | 35.4 | 36 | 32.5 | 34.1 | 32.9 | 33 | 33.1667 | 33 | 662 | United_StatesNew_JerseyMCGUIRE AFB
United_States | New_Jersey | E4 | MILLVILLE MUNICIPAL AP | MILLVILLE MUNICIPAL AP, NJ, USA | 39.37N | 75.08W | 23 | -5.00 (NAE) | 82-06 | 724075 | -17 | -17 | -25.6 | 39.4 | 34.1 | 35.8 | 34.3 | 35 | 34.7333 | 36 | 32 | 33.7 | 32.4 | 33 | 32.7 | 33 | 663 | United_StatesNew_JerseyMILLVILLE MUNICIPAL AP
United_States | New_Jersey | E4 | NEWARK INTERNATIONAL ARPT | NEWARK INTERNATIONAL ARPT, NJ, USA | 40.72N | 74.17W | 9 | -5.00 (NAE) | 82-06 | 725020 | -14.7 | -15 | -23.2 | 40.9 | 35.2 | 37 | 36.2 | 36 | 36.1333 | 37 | 33.2 | 34.8 | 33.5 | 34 | 33.8333 | 34 | 664 | United_StatesNew_JerseyNEWARK INTERNATIONAL ARPT
United_States | New_Jersey | E4 | TETERBORO AIRPORT | TETERBORO AIRPORT, NJ, USA | 40.85N | 74.06W | 2 | -5.00 (NAE) | 82-06 | 725025 | -15.8 | -16 | -24.5 | 40.5 | 34.1 | 36.3 | 35 | 35 | 35.1333 | 36 | 32.4 | 33.9 | 32.5 | 33 | 32.9333 | 33 | 665 | United_StatesNew_JerseyTETERBORO AIRPORT
United_States | New_Jersey | E4 | TRENTON MERCER COUNTY AP | TRENTON MERCER COUNTY AP, NJ, USA | 40.28N | 74.81W | 65 | -5.00 (NAE) | 84-06 | 724095 | -16 | N/A | N/A | N/A | 34 | 36.7 | 34.8 | 35 | 35.1667 | 37 | 32.4 | 34 | 32.5 | 33 | 32.9667 | 33 | 666 | United_StatesNew_JerseyTRENTON MERCER COUNTY AP
United_States | New_Mexico | M2 | ALAMOGORDO WHITE SA | ALAMOGORDO WHITE SA, NM, USA | 32.83N | 105.98W | 1313 | -7.00 (NAM) | 96-06 | 722693 | -13 | N/A | N/A | N/A | 39.2 | 39.1 | 37.9 | 39 | 38.7333 | 39 | 37.7 | 37.8 | 37 | 38 | 37.5 | 38 | 667 | United_StatesNew_MexicoALAMOGORDO WHITE SA
United_States | New_Mexico | M3 | ALBUQUERQUE INTL ARPT | ALBUQUERQUE INTL ARPT, NM, USA | 35.04N | 106.62W | 1620 | -7.00 (NAM) | 82-06 | 723650 | -12 | -12 | -20.2 | 40.8 | 37.3 | 36.9 | 35 | 36 | 36.4 | 37 | 34.9 | 35.4 | 33.5 | 35 | 34.6 | 35 | 668 | United_StatesNew_MexicoALBUQUERQUE INTL ARPT
United_States | New_Mexico | M3 | CANNON AFB/CLOVIS | CANNON AFB/CLOVIS, NM, USA | 34.38N | 103.32W | 1309 | -7.00 (NAM) | 82-02 | 722686 | -14 | -14 | -20.1 | 43.8 | 39.3 | 38.1 | 36.4 | 38 | 37.9333 | 38 | 36.4 | 36.2 | 34.8 | 36 | 35.8 | 36 | 669 | United_StatesNew_MexicoCANNON AFB/CLOVIS
United_States | New_Mexico | M2 | CARLSBAD CAVERN CITY AIR TERM | CARLSBAD CAVERN CITY AIR TERM, NM, USA | 32.34N | 104.26W | 994 | -7.00 (NAM) | 85-06 | 722687 | -10.6 | -11 | -18.4 | 46.4 | 42.2 | 41.1 | 38.9 | 41 | 40.7333 | 41 | 39.6 | 38.7 | 37.3 | 39 | 38.5333 | 39 | 670 | United_StatesNew_MexicoCARLSBAD CAVERN CITY AIR TERM
United_States | New_Mexico | M3 | CLAYTON MUNICIPAL AIRPARK | CLAYTON MUNICIPAL AIRPARK, NM, USA | 36.45N | 103.15W | 1516 | -7.00 (NAM) | 82-06 | 723600 | -18.7 | -19 | -29 | 40.4 | 36.6 | 36.2 | 35.1 | 36 | 35.9667 | 36 | 34.1 | 34.7 | 33.5 | 34 | 34.1 | 34 | 671 | United_StatesNew_MexicoCLAYTON MUNICIPAL AIRPARK
United_States | New_Mexico | M3 | CLOVIS MUNI (AWOS) | CLOVIS MUNI (AWOS), NM, USA | 34.43N | 103.08W | 1284 | -7.00 (NAM) | 92-06 | 722689 | -14.3 | -14 | -22.8 | 42 | 38.2 | 37.4 | 36.1 | 37 | 37.2333 | 37 | 36.3 | 36.1 | 33.8 | 35 | 35.4 | 35 | 672 | United_StatesNew_MexicoCLOVIS MUNI (AWOS)
United_States | New_Mexico | M3 | FARMINGTON FOUR CORNERS REGL | FARMINGTON FOUR CORNERS REGL, NM, USA | 36.74N | 108.23W | 1677 | -7.00 (NAM) | 82-06 | 723658 | -16.8 | -17 | -26.1 | 42 | 36.4 | 37.3 | 35.5 | 36 | 36.4 | 37 | 34 | 35.7 | 33.5 | 34 | 34.4 | 34 | 673 | United_StatesNew_MexicoFARMINGTON FOUR CORNERS REGL
United_States | New_Mexico | M3 | GALLUP SEN CLARKE FLD | GALLUP SEN CLARKE FLD, NM, USA | 35.51N | 108.79W | 1971 | -7.00 (NAM) | 82-06 | 723627 | -22.8 | -23 | -32.9 | 38.9 | 34.4 | 35.1 | 33.6 | 34 | 34.3667 | 35 | 32.4 | 33.4 | 31.6 | 32 | 32.4667 | 32 | 674 | United_StatesNew_MexicoGALLUP SEN CLARKE FLD
United_States | New_Mexico | M2 | HOLLOMAN AFB | HOLLOMAN AFB, NM, USA | 32.85N | 106.10W | 1248 | -7.00 (NAM) | 82-01 | 747320 | -10.7 | -11 | -16.6 | 44 | 39.6 | 38.9 | 36.8 | 38 | 38.4333 | 39 | 37.6 | 37.1 | 35.1 | 37 | 36.6 | 37 | 675 | United_StatesNew_MexicoHOLLOMAN AFB
United_States | New_Mexico | M2 | ROSWELL INDUSTRIAL AIR PARK | ROSWELL INDUSTRIAL AIR PARK, NM, USA | 33.31N | 104.54W | 1118 | -7.00 (NAM) | 82-06 | 722680 | -13.1 | -13 | -21.8 | 44.3 | 40.1 | 39.1 | 37.5 | 39 | 38.9 | 39 | 38.1 | 37.3 | 36 | 37 | 37.1333 | 37 | 676 | United_StatesNew_MexicoROSWELL INDUSTRIAL AIR PARK
United_States | New_Mexico | M2 | SIERRA BLANCA RGNL | SIERRA BLANCA RGNL, NM, USA | 33.47N | 105.53W | 2078 | -7.00 (NAM) | 96-06 | 722683 | -13 | -13 | -19.9 | 37 | 33 | 32.5 | 31.2 | 32 | 32.2333 | 33 | 32 | 31 | 28.9 | 31 | 30.6333 | 31 | 677 | United_StatesNew_MexicoSIERRA BLANCA RGNL
United_States | New_Mexico | M3 | TAOS MUNI APT(AWOS) | TAOS MUNI APT(AWOS), NM, USA | 36.45N | 105.67W | 2161 | -7.00 (NAM) | 92-06 | 723663 | -22.7 | -23 | -29.7 | 36.8 | 32.7 | 32.9 | 31.4 | 32 | 32.3333 | 33 | 31.1 | 31.4 | 29.1 | 31 | 30.5333 | 31 | 678 | United_StatesNew_MexicoTAOS MUNI APT(AWOS)
United_States | New_Mexico | M2 | TRUTH OR CONSEQUENCES MUNI AP | TRUTH OR CONSEQUENCES MUNI AP, NM, USA | 33.24N | 107.27W | 1481 | -7.00 (NAM) | 82-06 | 722710 | -10.4 | -10 | -30.4 | 43.5 | 39.5 | 38.1 | 36.1 | 38 | 37.9 | 38 | 37.2 | 36.5 | 34.4 | 36 | 36.0333 | 36 | 679 | United_StatesNew_MexicoTRUTH OR CONSEQUENCES MUNI AP
United_States | New_Mexico | M2 | WHITE SANDS | WHITE SANDS, NM, USA | 32.38N | 106.48W | 1244 | -7.00 (NAM) | 82-93 | 722690 | -12 | -12 | -20.1 | 43 | 39.6 | 38.7 | 36.3 | 38 | 38.2 | 39 | 37.9 | 36.9 | 35 | 37 | 36.6 | 37 | 680 | United_StatesNew_MexicoWHITE SANDS
United_States | New_York | E5 | ALBANY COUNTY AP | ALBANY COUNTY AP, NY, USA | 42.75N | 73.80W | 89 | -5.00 (NAE) | 82-06 | 725180 | -22.8 | -23 | -33 | 38.2 | 33 | 33.6 | 33 | 33 | 33.2 | 34 | 30.6 | 31.8 | 30.8 | 31 | 31.0667 | 31 | 681 | United_StatesNew_YorkALBANY COUNTY AP
United_States | New_York | E5 | AMBROSE LIGHT | AMBROSE LIGHT, NY, USA | 40.45N | 73.80W | 21 | -5.00 (NAE) | 85-06 | 994100 | -12.8 | -13 | -18.7 | 35.7 | 29.4 | 31.5 | 30.4 | 30 | 30.4333 | 32 | 26.8 | 29.2 | 27.6 | 28 | 27.8667 | 28 | 682 | United_StatesNew_YorkAMBROSE LIGHT
United_States | New_York | E5 | BINGHAMTON EDWIN A LINK FIELD | BINGHAMTON EDWIN A LINK FIELD, NY, USA | 42.21N | 75.98W | 499 | -5.00 (NAE) | 82-06 | 725150 | -21.6 | -22 | -29.1 | 37 | 30.6 | 32.1 | 31.5 | 31 | 31.4 | 32 | 28.3 | 29.8 | 29.2 | 29 | 29.1 | 29 | 683 | United_StatesNew_YorkBINGHAMTON EDWIN A LINK FIELD
United_States | New_York | E5 | BUFFALO NIAGARA INTL AP | BUFFALO NIAGARA INTL AP, NY, USA | 42.94N | 78.74W | 215 | -5.00 (NAE) | 82-06 | 725280 | -19.5 | -20 | -28.1 | 36.9 | 31.7 | 32.4 | 31.7 | 32 | 31.9333 | 32 | 29.3 | 30.3 | 29.6 | 30 | 29.7333 | 30 | 684 | United_StatesNew_YorkBUFFALO NIAGARA INTL AP
United_States | New_York | E5 | DUNKIRK | DUNKIRK, NY, USA | 42.48N | 79.35W | 197 | -5.00 (NAE) | 85-06 | 994250 | -15.6 | -16 | -24.9 | 36.2 | 28.7 | 29.1 | 29 | 29 | 28.9333 | 29 | 26.3 | 27.4 | 27.4 | 27 | 27.0333 | 27 | 685 | United_StatesNew_YorkDUNKIRK
United_States | New_York | E5 | ELMIRA CORNING REGIONAL AP | ELMIRA CORNING REGIONAL AP, NY, USA | 42.16N | 76.89W | 291 | -5.00 (NAE) | 82-06 | 725156 | -23.4 | -23 | -32.2 | 39.6 | 32.9 | 35 | 33.2 | 34 | 33.7 | 35 | 30.9 | 32.4 | 31.2 | 32 | 31.5 | 32 | 686 | United_StatesNew_YorkELMIRA CORNING REGIONAL AP
United_States | New_York | E5 | FORT DRUM/WHEELER-S | FORT DRUM/WHEELER-S, NY, USA | 44.05N | 75.73W | 207 | -5.00 (NAE) | 89-06 | 743700 | -28.1 | -28 | -38.2 | 36.6 | 31.4 | 32.1 | 31.4 | 32 | 31.6333 | 32 | 29.2 | 30 | 29.1 | 29 | 29.4333 | 29 | 687 | United_StatesNew_YorkFORT DRUM/WHEELER-S
United_States | New_York | E5 | GALLOO ISLAND | GALLOO ISLAND, NY, USA | 43.88N | 76.43W | 76 | -5.00 (NAE) | 85-02 | 994320 | -22 | -22 | -29.7 | 32.4 | 25.3 | 27.2 | 27.9 | 27 | 26.8 | 27 | 23.2 | 25.6 | 26.1 | 25 | 24.9667 | 25 | 688 | United_StatesNew_YorkGALLOO ISLAND
United_States | New_York | E5 | GLENS FALLS AP | GLENS FALLS AP, NY, USA | 43.34N | 73.61W | 102 | -5.00 (NAE) | 82-06 | 725185 | -28.5 | -29 | -38.7 | 37.7 | 32.8 | 33.3 | 32.4 | 33 | 32.8333 | 33 | 30.2 | 31.2 | 30.1 | 31 | 30.5 | 31 | 689 | United_StatesNew_YorkGLENS FALLS AP
United_States | New_York | E5 | GRIFFISS AFB | GRIFFISS AFB, NY, USA | 43.23N | 75.40W | 158 | -5.00 (NAE) | 82-94 | 725196 | -25.8 | -26 | -31.3 | 37.7 | 32.9 | 34.1 | 33.1 | 33 | 33.3667 | 34 | 30.2 | 31.8 | 30.5 | 31 | 30.8333 | 31 | 690 | United_StatesNew_YorkGRIFFISS AFB
United_States | New_York | E5 | ISLIP LONG ISL MACARTHUR AP | ISLIP LONG ISL MACARTHUR AP, NY, USA | 40.79N | 73.10W | 33 | -5.00 (NAE) | 82-06 | 725035 | -15.3 | -15 | -22.6 | 39.9 | 32.4 | 34.2 | 32.5 | 33 | 33.0333 | 34 | 29.9 | 31.8 | 30.5 | 31 | 30.7333 | 31 | 691 | United_StatesNew_YorkISLIP LONG ISL MACARTHUR AP
United_States | New_York | E5 | JAMESTOWN (AWOS) | JAMESTOWN (AWOS), NY, USA | 42.15N | 79.27W | 525 | -5.00 (NAE) | 91-06 | 725235 | -20.1 | -20 | -31.5 | 36.7 | 29.1 | 30.9 | 29.7 | 30 | 29.9 | 31 | 27.7 | 28 | 27.6 | 28 | 27.7667 | 28 | 692 | United_StatesNew_YorkJAMESTOWN (AWOS)
United_States | New_York | E5 | MASSENA AP | MASSENA AP, NY, USA | 44.94N | 74.85W | 65 | -5.00 (NAE) | 82-06 | 726223 | -30.4 | -30 | -39.8 | 37 | 32.2 | 32.8 | 32.3 | 32 | 32.4333 | 33 | 30 | 31 | 30.1 | 30 | 30.3667 | 30 | 693 | United_StatesNew_YorkMASSENA AP
United_States | New_York | E5 | MONTICELLO(AWOS) | MONTICELLO(AWOS), NY, USA | 41.70N | 74.80W | 428 | -5.00 (NAE) | 92-06 | 725145 | -20 | N/A | N/A | N/A | 30.1 | 32.3 | 32.4 | 32 | 31.6 | 32 | 28 | 30.2 | 29.3 | 29 | 29.1667 | 29 | 694 | United_StatesNew_YorkMONTICELLO(AWOS)
United_States | New_York | E5 | NEW YORK J F KENNEDY INT'L AR | NEW YORK J F KENNEDY INT'L AR, NY, USA | 40.66N | 73.80W | 7 | -5.00 (NAE) | 82-06 | 744860 | -13.7 | -14 | -21.3 | 39.9 | 33.3 | 35.3 | 33.7 | 34 | 34.1 | 35 | 30.6 | 32.3 | 31.1 | 31 | 31.3333 | 31 | 695 | United_StatesNew_YorkNEW YORK J F KENNEDY INT'L AR
United_States | New_York | E5 | NEW YORK LAGUARDIA ARPT | NEW YORK LAGUARDIA ARPT, NY, USA | 40.78N | 73.88W | 9 | -5.00 (NAE) | 82-06 | 725030 | -13.7 | -14 | -22 | 40.2 | 34.3 | 35.9 | 35 | 35 | 35.0667 | 36 | 32.1 | 33.7 | 32.6 | 33 | 32.8 | 33 | 696 | United_StatesNew_YorkNEW YORK LAGUARDIA ARPT
United_States | New_York | E5 | NEWBURGH/STEWART | NEWBURGH/STEWART, NY, USA | 41.50N | 74.10W | 177 | -5.00 (NAE) | 82-06 | 725038 | -20 | -20 | -30.5 | 39.9 | 32.6 | 34.9 | 33.9 | 34 | 33.8 | 35 | 30.8 | 32.3 | 31.2 | 31 | 31.4333 | 31 | 697 | United_StatesNew_YorkNEWBURGH/STEWART
United_States | New_York | E5 | NIAGARA FALLS AF | NIAGARA FALLS AF, NY, USA | 43.11N | 78.95W | 179 | -5.00 (NAE) | 82-06 | 725287 | -20.3 | -20 | -29.9 | 37.5 | 32.3 | 33.3 | 32.4 | 33 | 32.6667 | 33 | 30 | 31.2 | 30.2 | 30 | 30.4667 | 30 | 698 | United_StatesNew_YorkNIAGARA FALLS AF
United_States | New_York | E5 | PLATTSBURGH AFB | PLATTSBURGH AFB, NY, USA | 44.65N | 73.47W | 72 | -5.00 (NAE) | 82-95 | 726225 | -28 | -28 | -36.8 | 37.5 | 32.8 | 32.4 | 31.7 | 32 | 32.3 | 32 | 29.2 | 30.2 | 29.1 | 30 | 29.5 | 30 | 699 | United_StatesNew_YorkPLATTSBURGH AFB
United_States | New_York | E5 | POUGHKEEPSIE DUTCHESS CO AP | POUGHKEEPSIE DUTCHESS CO AP, NY, USA | 41.63N | 73.88W | 49 | -5.00 (NAE) | 82-06 | 725036 | -22.3 | -22 | -31.6 | 41 | 33.9 | 36.3 | 34.6 | 35 | 34.9333 | 36 | 31.8 | 33.4 | 32.3 | 33 | 32.5 | 33 | 700 | United_StatesNew_YorkPOUGHKEEPSIE DUTCHESS CO AP
United_States | New_York | E5 | REPUBLIC | REPUBLIC, NY, USA | 40.72N | 73.40W | 26 | -5.00 (NAE) | 96-06 | 744864 | -13 | -13 | -21.2 | 40.8 | 32.8 | 35 | 33.9 | 34 | 33.9 | 35 | 31 | 32.6 | 32 | 32 | 31.8667 | 32 | 701 | United_StatesNew_YorkREPUBLIC
United_States | New_York | E5 | ROCHESTER GREATER ROCHESTER I | ROCHESTER GREATER ROCHESTER I, NY, USA | 43.12N | 77.68W | 169 | -5.00 (NAE) | 82-06 | 725290 | -20 | -20 | -29.3 | 38.2 | 32.4 | 33.7 | 33 | 33 | 33.0333 | 34 | 30.1 | 31.5 | 30.4 | 31 | 30.6667 | 31 | 702 | United_StatesNew_YorkROCHESTER GREATER ROCHESTER I
United_States | New_York | E5 | SUPERIOR SHOALS | SUPERIOR SHOALS, NY, USA | 44.48N | 75.80W | 79 | -5.00 (NAE) | 94-06 | 994580 | -23.1 | -23 | -34.3 | 32.8 | 28.3 | 28.6 | 28.9 | 29 | 28.6 | 29 | 26.2 | 27.4 | 27.2 | 27 | 26.9333 | 27 | 703 | United_StatesNew_YorkSUPERIOR SHOALS
United_States | New_York | E5 | SYRACUSE HANCOCK INT'L ARPT | SYRACUSE HANCOCK INT'L ARPT, NY, USA | 43.11N | 76.10W | 127 | -5.00 (NAE) | 82-06 | 725190 | -23.6 | -24 | -34 | 38.9 | 32.9 | 33.4 | 33.6 | 33 | 33.3 | 33 | 30.7 | 31.6 | 30.9 | 31 | 31.0667 | 31 | 704 | United_StatesNew_YorkSYRACUSE HANCOCK INT'L ARPT
United_States | New_York | E5 | UTICA ONEIDA COUNTY AP | UTICA ONEIDA COUNTY AP, NY, USA | 43.15N | 75.38W | 227 | -5.00 (NAE) | 82-06 | 725197 | -24.4 | -24 | -32.2 | 37 | 31.9 | 32.8 | 32.4 | 32 | 32.3667 | 33 | 30 | 30.9 | 29.9 | 30 | 30.2667 | 30 | 705 | United_StatesNew_YorkUTICA ONEIDA COUNTY AP
United_States | New_York | E5 | WATERTOWN AP | WATERTOWN AP, NY, USA | 43.99N | 76.02W | 102 | -5.00 (NAE) | 82-06 | 726227 | -32 | -32 | -42.1 | 36.4 | 30.5 | 31.2 | 31.5 | 31 | 31.0667 | 31 | 28.4 | 29.4 | 29.3 | 29 | 29.0333 | 29 | 706 | United_StatesNew_YorkWATERTOWN AP
United_States | New_York | E5 | WHITE PLAINS WESTCHESTER CO A | WHITE PLAINS WESTCHESTER CO A, NY, USA | 41.07N | 73.71W | 121 | -5.00 (NAE) | 82-06 | 725037 | -16.7 | -17 | -25.4 | 39.4 | 32.8 | 34.7 | 33.7 | 34 | 33.7333 | 35 | 30.9 | 32.4 | 31.2 | 32 | 31.5 | 32 | 707 | United_StatesNew_YorkWHITE PLAINS WESTCHESTER CO A
United_States | North_Carolina | E2 | ASHEVILLE REGIONAL ARPT | ASHEVILLE REGIONAL ARPT, NC, USA | 35.43N | 82.54W | 661 | -5.00 (NAE) | 82-06 | 723150 | -15.2 | -15 | -26.1 | 36.9 | 31.6 | 33.2 | 32.7 | 33 | 32.5 | 33 | 29.8 | 31.5 | 30.8 | 31 | 30.7 | 31 | 708 | United_StatesNorth_CarolinaASHEVILLE REGIONAL ARPT
United_States | North_Carolina | E2 | CAPE HATTERAS | CAPE HATTERAS, NC, USA | 35.27N | 75.55W | 3 | -5.00 (NAE) | 96-06 | 723040 | -4.1 | -4 | -11 | 34.5 | 30 | 31.5 | 31.6 | 31 | 31.0333 | 32 | 29 | 30.2 | 30.5 | 30 | 29.9 | 30 | 709 | United_StatesNorth_CarolinaCAPE HATTERAS
United_States | North_Carolina | E2 | CAPE LOOKOUT | CAPE LOOKOUT, NC, USA | 34.62N | 76.52W | 11 | -5.00 (NAE) | 85-06 | 994160 | -6 | -6 | -13.3 | 32.9 | 28.7 | 30.6 | 30.2 | 30 | 29.8333 | 31 | 27.9 | 29.7 | 29.3 | 29 | 28.9667 | 29 | 710 | United_StatesNorth_CarolinaCAPE LOOKOUT
United_States | North_Carolina | E2 | CHARLOTTE DOUGLAS INTL ARPT | CHARLOTTE DOUGLAS INTL ARPT, NC, USA | 35.21N | 80.94W | 234 | -5.00 (NAE) | 82-06 | 723140 | -11.1 | -11 | -20.3 | 40.7 | 35 | 36.8 | 35.7 | 36 | 35.8333 | 37 | 33.1 | 34.9 | 34 | 34 | 34 | 34 | 711 | United_StatesNorth_CarolinaCHARLOTTE DOUGLAS INTL ARPT
United_States | North_Carolina | E2 | CHERRY POINT MCAS | CHERRY POINT MCAS, NC, USA | 34.90N | 76.88W | 9 | -5.00 (NAE) | 82-06 | 723090 | -9.3 | -9 | -18.7 | 40.7 | 34.7 | 36.3 | 35.1 | 35 | 35.3667 | 36 | 32.7 | 34.2 | 33 | 33 | 33.3 | 33 | 712 | United_StatesNorth_CarolinaCHERRY POINT MCAS
United_States | North_Carolina | E2 | DIAMOND SHOALS (LS) | DIAMOND SHOALS (LS), NC, USA | 35.15N | 75.30W | 0 | -5.00 (NAE) | 89-03 | 994030 | -3 | -3 | -11.2 | 32.3 | 28.5 | 29.6 | 29.1 | 29 | 29.0667 | 30 | 27.5 | 28.7 | 28.5 | 28 | 28.2333 | 28 | 713 | United_StatesNorth_CarolinaDIAMOND SHOALS (LS)
United_States | North_Carolina | E2 | FAYETTEVILLE RGNL G | FAYETTEVILLE RGNL G, NC, USA | 34.98N | 78.88W | 59 | -5.00 (NAE) | 82-06 | 723035 | -10.2 | -10 | -19.8 | 42.2 | 36.4 | 37.5 | 37.3 | 37 | 37.0667 | 38 | 34.1 | 35.7 | 34.8 | 35 | 34.8667 | 35 | 714 | United_StatesNorth_CarolinaFAYETTEVILLE RGNL G
United_States | North_Carolina | E2 | FORT BRAGG/SIMMONS | FORT BRAGG/SIMMONS, NC, USA | 35.13N | 78.93W | 93 | -5.00 (NAE) | 82-01 | 746930 | -10.4 | -10 | -21.5 | 43 | 37.2 | 37.8 | 37 | 37 | 37.3333 | 38 | 34.9 | 36.2 | 34.8 | 35 | 35.3 | 35 | 715 | United_StatesNorth_CarolinaFORT BRAGG/SIMMONS
United_States | North_Carolina | E2 | FRYING PAN SHOALS | FRYING PAN SHOALS, NC, USA | 33.48N | 77.58W | 24 | -5.00 (NAE) | 89-05 | 994040 | -1.7 | -2 | -10.5 | 31.7 | 29.1 | 30.1 | 30.1 | 30 | 29.7667 | 30 | 27.8 | 29.1 | 29.2 | 29 | 28.7 | 29 | 716 | United_StatesNorth_CarolinaFRYING PAN SHOALS
United_States | North_Carolina | E2 | GREENSBORO PIEDMONT TRIAD INT | GREENSBORO PIEDMONT TRIAD INT, NC, USA | 36.10N | 79.94W | 270 | -5.00 (NAE) | 82-06 | 723170 | -13 | -13 | -21.5 | 39.7 | 33.8 | 35.3 | 34.9 | 35 | 34.6667 | 35 | 32.1 | 33.7 | 33 | 33 | 32.9333 | 33 | 717 | United_StatesNorth_CarolinaGREENSBORO PIEDMONT TRIAD INT
United_States | North_Carolina | E2 | HATTERAS BILLY MITCHELL AP | HATTERAS BILLY MITCHELL AP, NC, USA | 35.23N | 75.62W | 3 | -5.00 (NAE) | 82-06 | 723139 | -5.8 | -6 | -14.1 | 36 | 31 | 32.6 | 31.9 | 32 | 31.8333 | 33 | 29.7 | 31.3 | 31 | 31 | 30.6667 | 31 | 718 | United_StatesNorth_CarolinaHATTERAS BILLY MITCHELL AP
United_States | North_Carolina | E2 | HICKORY REGIONAL AP | HICKORY REGIONAL AP, NC, USA | 35.74N | 81.39W | 362 | -5.00 (NAE) | 82-06 | 723145 | -12.5 | -13 | -21.2 | 40.5 | 33.8 | 35.9 | 35.4 | 35 | 35.0333 | 36 | 32.2 | 34.1 | 33 | 33 | 33.1 | 33 | 719 | United_StatesNorth_CarolinaHICKORY REGIONAL AP
United_States | North_Carolina | E2 | JACKSONVILLE (AWOS) | JACKSONVILLE (AWOS), NC, USA | 34.83N | 77.62W | 29 | -5.00 (NAE) | 92-06 | 723069 | -10.5 | -11 | -15.3 | 40.8 | 35.9 | 36.8 | 35.9 | 36 | 36.2 | 37 | 33.2 | 34.9 | 33.7 | 34 | 33.9333 | 34 | 720 | United_StatesNorth_CarolinaJACKSONVILLE (AWOS)
United_States | North_Carolina | E2 | NEW BERN CRAVEN CO REGL AP | NEW BERN CRAVEN CO REGL AP, NC, USA | 35.07N | 77.05W | 7 | -5.00 (NAE) | 82-06 | 723095 | -9.4 | -9 | -19.3 | 39.8 | 35.3 | 36.1 | 35.3 | 36 | 35.5667 | 36 | 33.3 | 34.4 | 33.6 | 34 | 33.7667 | 34 | 721 | United_StatesNorth_CarolinaNEW BERN CRAVEN CO REGL AP
United_States | North_Carolina | E2 | NEW RIVER MCAF | NEW RIVER MCAF, NC, USA | 34.70N | 77.43W | 8 | -5.00 (NAE) | 82-06 | 723096 | -9.3 | -9 | -19.1 | 39.7 | 35 | 36.2 | 35 | 35 | 35.4 | 36 | 33 | 34.3 | 33.3 | 34 | 33.5333 | 34 | 722 | United_StatesNorth_CarolinaNEW RIVER MCAF
United_States | North_Carolina | E2 | PITT GREENVILLE ARP | PITT GREENVILLE ARP, NC, USA | 35.63N | 77.40W | 8 | -5.00 (NAE) | 94-06 | 723065 | -9.5 | -10 | -15.8 | 40.5 | 37 | 37.3 | 37.2 | 37 | 37.1667 | 37 | 34.1 | 35.2 | 34.2 | 35 | 34.5 | 35 | 723 | United_StatesNorth_CarolinaPITT GREENVILLE ARP
United_States | North_Carolina | E2 | POPE AFB | POPE AFB, NC, USA | 35.17N | 79.02W | 66 | -5.00 (NAE) | 82-06 | 723030 | -10.4 | -10 | -18.8 | 42.7 | 37.4 | 37.9 | 37.5 | 38 | 37.6 | 38 | 35 | 36.3 | 35.2 | 36 | 35.5 | 36 | 724 | United_StatesNorth_CarolinaPOPE AFB
United_States | North_Carolina | E2 | RALEIGH DURHAM INTERNATIONAL | RALEIGH DURHAM INTERNATIONAL, NC, USA | 35.87N | 78.79W | 133 | -5.00 (NAE) | 82-06 | 723060 | -11.9 | -12 | -20.9 | 40.9 | 34.9 | 36.4 | 36.4 | 36 | 35.9 | 36 | 33.1 | 34.8 | 33.9 | 34 | 33.9333 | 34 | 725 | United_StatesNorth_CarolinaRALEIGH DURHAM INTERNATIONAL
United_States | North_Carolina | E2 | RICHMOND INTERNATIONAL AP | RICHMOND INTERNATIONAL AP, NC, USA | 37.51N | 77.32W | 50 | -5.00 (NAE) | 82-06 | 724010 | -13.2 | -13 | -22.2 | 40.9 | 35.6 | 36.6 | 36.1 | 36 | 36.1 | 37 | 33.5 | 35.1 | 34.1 | 34 | 34.2333 | 34 | 726 | United_StatesNorth_CarolinaRICHMOND INTERNATIONAL AP
United_States | North_Carolina | E2 | SEYMOUR-JOHNSON AFB | SEYMOUR-JOHNSON AFB, NC, USA | 35.33N | 77.97W | 33 | -5.00 (NAE) | 82-05 | 723066 | -10.1 | -10 | -20.1 | 42.1 | 36.4 | 37.7 | 37.3 | 37 | 37.1333 | 38 | 34.6 | 36.1 | 34.8 | 35 | 35.1667 | 35 | 727 | United_StatesNorth_CarolinaSEYMOUR-JOHNSON AFB
United_States | North_Carolina | E2 | SOUTHERN PINES AWOS | SOUTHERN PINES AWOS, NC, USA | 35.23N | 79.40W | 141 | -5.00 (NAE) | 92-06 | 723143 | -12.5 | -13 | -17.9 | 48.7 | 36.2 | 36.4 | 36.2 | 36 | 36.2667 | 36 | 33.8 | 34.9 | 34 | 34 | 34.2333 | 34 | 728 | United_StatesNorth_CarolinaSOUTHERN PINES AWOS
United_States | North_Carolina | E2 | WILMINGTON INTERNATIONAL ARPT | WILMINGTON INTERNATIONAL ARPT, NC, USA | 34.27N | 77.91W | 12 | -5.00 (NAE) | 82-06 | 723013 | -8.7 | -9 | -17 | 39.5 | 35 | 36.1 | 35 | 35 | 35.3667 | 36 | 32.9 | 34.4 | 33.2 | 34 | 33.5 | 34 | 729 | United_StatesNorth_CarolinaWILMINGTON INTERNATIONAL ARPT
United_States | North_Carolina | E2 | WINSTON-SALEM REYNOLDS AP | WINSTON-SALEM REYNOLDS AP, NC, USA | 36.13N | 80.22W | 296 | -5.00 (NAE) | 82-06 | 723193 | -12.5 | -13 | -21.7 | 39.1 | 33.7 | 35.7 | 34.8 | 35 | 34.7333 | 36 | 32.2 | 34 | 32.8 | 33 | 33 | 33 | 730 | United_StatesNorth_CarolinaWINSTON-SALEM REYNOLDS AP
United_States | North_Dakota | M4 | BISMARCK MUNICIPAL ARPT | BISMARCK MUNICIPAL ARPT, ND, USA | 46.77N | 100.75W | 506 | -6.00 (NAC) | 82-06 | 727640 | -33.1 | -33 | -43.9 | 44.8 | 35.8 | 38 | 36.8 | 37 | 36.8667 | 38 | 31.9 | 34.6 | 33.9 | 33 | 33.4667 | 33 | 731 | United_StatesNorth_DakotaBISMARCK MUNICIPAL ARPT
United_States | North_Dakota | M4 | DEVILS LAKE (AMOS) | DEVILS LAKE (AMOS), ND, USA | 48.10N | 98.87W | 443 | -6.00 (NAC) | 82-92 | 727580 | -33.3 | -33 | -40.4 | 40.4 | 35.4 | 35.4 | 35.5 | 35 | 35.4333 | 35 | 31 | 32.3 | 32.8 | 32 | 32.0333 | 32 | 732 | United_StatesNorth_DakotaDEVILS LAKE (AMOS)
United_States | North_Dakota | M4 | DEVILS LAKE(AWOS) | DEVILS LAKE(AWOS), ND, USA | 48.12N | 98.92W | 443 | -6.00 (NAC) | 91-06 | 727573 | -32.8 | -33 | -42.4 | 38.1 | 31.4 | 32.5 | 32.4 | 32 | 32.1 | 33 | 28.5 | 29.8 | 29.6 | 29 | 29.3 | 29 | 733 | United_StatesNorth_DakotaDEVILS LAKE(AWOS)
United_States | North_Dakota | M4 | DICKINSON MUNICIPAL AP | DICKINSON MUNICIPAL AP, ND, USA | 46.80N | 102.80W | 787 | -7.00 (NAM) | 82-06 | 727645 | -31.2 | -31 | -38.2 | 42.9 | 33.3 | 37.5 | 36.4 | 36 | 35.7333 | 38 | 30.7 | 33.9 | 34 | 33 | 32.8667 | 33 | 734 | United_StatesNorth_DakotaDICKINSON MUNICIPAL AP
United_States | North_Dakota | M4 | FARGO HECTOR INTERNATIONAL AP | FARGO HECTOR INTERNATIONAL AP, ND, USA | 46.93N | 96.81W | 274 | -6.00 (NAC) | 82-06 | 727530 | -31.5 | -32 | -40.1 | 41.5 | 34.1 | 35.5 | 34.9 | 35 | 34.8333 | 36 | 31.5 | 32.4 | 32.2 | 32 | 32.0333 | 32 | 735 | United_StatesNorth_DakotaFARGO HECTOR INTERNATIONAL AP
United_States | North_Dakota | M4 | GRAND FORKS AFB | GRAND FORKS AFB, ND, USA | 47.97N | 97.40W | 276 | -6.00 (NAC) | 82-06 | 727575 | -31.8 | -32 | -41.1 | 42.3 | 34.5 | 34.9 | 35.2 | 35 | 34.8667 | 35 | 31.3 | 32.2 | 32.4 | 32 | 31.9667 | 32 | 736 | United_StatesNorth_DakotaGRAND FORKS AFB
United_States | North_Dakota | M4 | GRAND FORKS INTERNATIONAL AP | GRAND FORKS INTERNATIONAL AP, ND, USA | 47.95N | 97.18W | 254 | -6.00 (NAC) | 82-06 | 727576 | -33 | -33 | -42.3 | 42 | 33.9 | 34 | 34.6 | 34 | 34.1667 | 34 | 30.9 | 31.4 | 32 | 31 | 31.4333 | 31 | 737 | United_StatesNorth_DakotaGRAND FORKS INTERNATIONAL AP
United_States | North_Dakota | M4 | JAMESTOWN MUNICIPAL ARPT | JAMESTOWN MUNICIPAL ARPT, ND, USA | 46.93N | 98.68W | 455 | -6.00 (NAC) | 82-06 | 727535 | -30.6 | -31 | -39.6 | 42.2 | 34.4 | 36.3 | 36.1 | 36 | 35.6 | 36 | 31.2 | 32.7 | 33.1 | 32 | 32.3333 | 32 | 738 | United_StatesNorth_DakotaJAMESTOWN MUNICIPAL ARPT
United_States | North_Dakota | M4 | LIDGERWOOD (RAMOS) | LIDGERWOOD (RAMOS), ND, USA | 46.10N | 97.15W | 351 | -6.00 (NAC) | 83-96 | 727534 | -30.8 | -31 | -38.2 | 44.2 | 34.8 | 37.9 | 36.2 | 36 | 36.3 | 38 | 32.4 | 33.7 | 32.5 | 33 | 32.8667 | 33 | 739 | United_StatesNorth_DakotaLIDGERWOOD (RAMOS)
United_States | North_Dakota | M4 | MINOT AFB | MINOT AFB, ND, USA | 48.42N | 101.35W | 497 | -6.00 (NAC) | 82-06 | 727675 | -32.5 | -33 | -43.1 | 42.8 | 36.1 | 35.7 | 37.2 | 36 | 36.3333 | 36 | 32.4 | 32.4 | 34.1 | 33 | 32.9667 | 33 | 740 | United_StatesNorth_DakotaMINOT AFB
United_States | North_Dakota | M4 | MINOT FAA AP | MINOT FAA AP, ND, USA | 48.26N | 101.28W | 522 | -6.00 (NAC) | 82-06 | 727676 | -30.6 | -31 | -40.3 | 41.1 | 34.8 | 35.1 | 35.9 | 35 | 35.2667 | 35 | 31.2 | 32.3 | 33.2 | 32 | 32.2333 | 32 | 741 | United_StatesNorth_DakotaMINOT FAA AP
United_States | North_Dakota | M4 | WILLISTON SLOULIN INTL AP | WILLISTON SLOULIN INTL AP, ND, USA | 48.20N | 103.64W | 581 | -6.00 (NAC) | 82-06 | 727670 | -34 | -34 | -44 | 43 | 36.3 | 37.4 | 37.6 | 37 | 37.1 | 37 | 32.7 | 34.7 | 34.8 | 34 | 34.0667 | 34 | 742 | United_StatesNorth_DakotaWILLISTON SLOULIN INTL AP
United_States | Ohio | E4 | AKRON AKRON-CANTON REG AP | AKRON AKRON-CANTON REG AP, OH, USA | 40.92N | 81.44W | 377 | -5.00 (NAE) | 82-06 | 725210 | -21 | -21 | -33.6 | 37.8 | 32.3 | 33.7 | 33 | 33 | 33 | 34 | 30.4 | 31.7 | 30.9 | 31 | 31 | 31 | 743 | United_StatesOhioAKRON AKRON-CANTON REG AP
United_States | Ohio | E4 | CINCINNATI MUNICIPAL AP LUNKI | CINCINNATI MUNICIPAL AP LUNKI, OH, USA | 39.10N | 84.42W | 152 | -5.00 (NAE) | 82-06 | 724297 | -18.8 | -19 | -31.9 | 40.3 | 33.9 | 36.1 | 35.3 | 35 | 35.1 | 36 | 32.2 | 34 | 33.3 | 33 | 33.1667 | 33 | 744 | United_StatesOhioCINCINNATI MUNICIPAL AP LUNKI
United_States | Ohio | E4 | CLEVELAND HOPKINS INTL AP | CLEVELAND HOPKINS INTL AP, OH, USA | 41.41N | 81.85W | 245 | -5.00 (NAE) | 82-06 | 725240 | -20 | -20 | -31.4 | 38.9 | 33 | 34.2 | 33.1 | 33 | 33.4333 | 34 | 31.1 | 32.1 | 31.1 | 31 | 31.4333 | 31 | 745 | United_StatesOhioCLEVELAND HOPKINS INTL AP
United_States | Ohio | E4 | COLUMBUS PORT COLUMBUS INTL A | COLUMBUS PORT COLUMBUS INTL A, OH, USA | 39.99N | 82.88W | 249 | -5.00 (NAE) | 82-06 | 724280 | -19.6 | -20 | -32.5 | 39 | 33.8 | 35.1 | 34.1 | 34 | 34.3333 | 35 | 31.8 | 32.9 | 32.3 | 32 | 32.3333 | 32 | 746 | United_StatesOhioCOLUMBUS PORT COLUMBUS INTL A
United_States | Ohio | E4 | DAYTON INTERNATIONAL AIRPORT | DAYTON INTERNATIONAL AIRPORT, OH, USA | 39.91N | 84.22W | 306 | -5.00 (NAE) | 82-06 | 724290 | -21.4 | -21 | -34.3 | 39.2 | 33.5 | 34.8 | 33.9 | 34 | 34.0667 | 35 | 31.3 | 32.5 | 31.9 | 32 | 31.9 | 32 | 747 | United_StatesOhioDAYTON INTERNATIONAL AIRPORT
United_States | Ohio | E4 | FINDLAY AIRPORT | FINDLAY AIRPORT, OH, USA | 41.01N | 83.67W | 248 | -5.00 (NAE) | 82-06 | 725366 | -21.5 | -22 | -33.3 | 39 | 33.8 | 34.9 | 33.6 | 34 | 34.1 | 35 | 31.8 | 32.5 | 31.4 | 32 | 31.9 | 32 | 748 | United_StatesOhioFINDLAY AIRPORT
United_States | Ohio | E4 | LANCASTER\FAIRFIEL | LANCASTER\FAIRFIEL, OH, USA | 39.75N | 82.65W | 264 | -5.00 (NAE) | 99-06 | 724294 | -21.4 | -21 | -34.9 | 39 | 32.8 | 33.9 | 33.9 | 34 | 33.5333 | 34 | 31.3 | 32.4 | 32.4 | 32 | 32.0333 | 32 | 749 | United_StatesOhioLANCASTER\FAIRFIEL
United_States | Ohio | E4 | MANSFIELD LAHM MUNICIPAL ARPT | MANSFIELD LAHM MUNICIPAL ARPT, OH, USA | 40.82N | 82.52W | 400 | -5.00 (NAE) | 82-06 | 725246 | -21.8 | -22 | -33 | 37.3 | 32.3 | 33.3 | 32.2 | 33 | 32.6 | 33 | 30.3 | 31.2 | 30.5 | 31 | 30.6667 | 31 | 750 | United_StatesOhioMANSFIELD LAHM MUNICIPAL ARPT
United_States | Ohio | E4 | OHIO STATE UNIVERSI | OHIO STATE UNIVERSI, OH, USA | 40.07N | 83.07W | 283 | -5.00 (NAE) | 97-06 | 724288 | -17.9 | -18 | -28 | 36.6 | 32.8 | 33.6 | 33.1 | 33 | 33.1667 | 34 | 32 | 32.4 | 32.2 | 32 | 32.2 | 32 | 751 | United_StatesOhioOHIO STATE UNIVERSI
United_States | Ohio | E4 | RICKENBACKER ANGB | RICKENBACKER ANGB, OH, USA | 39.82N | 82.93W | 230 | -5.00 (NAE) | 82-06 | 724285 | -19.2 | -19 | -31 | 45.6 | 34.1 | 36 | 35 | 35 | 35.0333 | 36 | 32.4 | 33.7 | 32.8 | 33 | 32.9667 | 33 | 752 | United_StatesOhioRICKENBACKER ANGB
United_States | Ohio | E4 | SOUTH BASS ISLAND | SOUTH BASS ISLAND, OH, USA | 41.62N | 82.83W | 178 | -5.00 (NAE) | 85-06 | 994340 | -17 | -17 | -25 | 35.9 | 29.7 | 31 | 30.7 | 30 | 30.4667 | 31 | 27.7 | 29.4 | 29 | 29 | 28.7 | 29 | 753 | United_StatesOhioSOUTH BASS ISLAND
United_States | Ohio | E4 | TOLEDO EXPRESS AIRPORT | TOLEDO EXPRESS AIRPORT, OH, USA | 41.59N | 83.80W | 211 | -5.00 (NAE) | 82-06 | 725360 | -21.2 | -21 | -32.6 | 40.1 | 34.6 | 35.4 | 34.1 | 35 | 34.7 | 35 | 32.3 | 32.9 | 31.8 | 32 | 32.3333 | 32 | 754 | United_StatesOhioTOLEDO EXPRESS AIRPORT
United_States | Ohio | E4 | WRIGHT-PATERSON AFB | WRIGHT-PATERSON AFB, OH, USA | 39.83N | 84.05W | 250 | -5.00 (NAE) | 82-06 | 745700 | -20.9 | -21 | -32.4 | 39.4 | 34 | 35.5 | 34.1 | 35 | 34.5333 | 36 | 32.2 | 33.2 | 32.4 | 33 | 32.6 | 33 | 755 | United_StatesOhioWRIGHT-PATERSON AFB
United_States | Ohio | E4 | YOUNGSTOWN REGIONAL AIRPORT | YOUNGSTOWN REGIONAL AIRPORT, OH, USA | 41.25N | 80.67W | 362 | -5.00 (NAE) | 82-06 | 725250 | -20.6 | -21 | -32.2 | 37.7 | 32.5 | 33.8 | 33 | 33 | 33.1 | 34 | 30.2 | 31.6 | 30.9 | 31 | 30.9 | 31 | 756 | United_StatesOhioYOUNGSTOWN REGIONAL AIRPORT
United_States | Ohio | E4 | ZANESVILLE MUNICIPAL AP | ZANESVILLE MUNICIPAL AP, OH, USA | 39.94N | 81.89W | 275 | -5.00 (NAE) | 82-06 | 724286 | -20.7 | -21 | -33 | 39.3 | 32.8 | 34.4 | 33.9 | 34 | 33.7 | 34 | 31.1 | 32.4 | 32.1 | 32 | 31.8667 | 32 | 757 | United_StatesOhioZANESVILLE MUNICIPAL AP
United_States | Oklahoma | M2 | ALTUS AFB | ALTUS AFB, OK, USA | 34.67N | 99.27W | 414 | -6.00 (NAC) | 82-00 | 723520 | -13 | -13 | -21.3 | 47.1 | 42 | 41.4 | 40.8 | 41 | 41.4 | 41 | 38.1 | 39.7 | 39 | 39 | 38.9333 | 39 | 758 | United_StatesOklahomaALTUS AFB
United_States | Oklahoma | M2 | CLINTON-SHERMAN | CLINTON-SHERMAN, OK, USA | 35.33N | 99.20W | 586 | -6.00 (NAC) | 96-06 | 723526 | -13.2 | -13 | -18.7 | 44.7 | 38 | 40.9 | 39 | 39 | 39.3 | 41 | 36.2 | 38.8 | 37.8 | 38 | 37.6 | 38 | 759 | United_StatesOklahomaCLINTON-SHERMAN
United_States | Oklahoma | M2 | FORT SILL | FORT SILL, OK, USA | 34.65N | 98.40W | 369 | -6.00 (NAC) | 82-99 | 723550 | -13.2 | -13 | -22.8 | 45 | 38.7 | 40.9 | 39.4 | 40 | 39.6667 | 41 | 36.1 | 38.6 | 37.7 | 37 | 37.4667 | 37 | 760 | United_StatesOklahomaFORT SILL
United_States | Oklahoma | M2 | GAGE AIRPORT | GAGE AIRPORT, OK, USA | 36.30N | 99.78W | 671 | -6.00 (NAC) | 87-06 | 723527 | -18.5 | -19 | -27.5 | 43.3 | 38 | 39.1 | 39 | 39 | 38.7 | 39 | 35.9 | 37.6 | 37.5 | 37 | 37 | 37 | 761 | United_StatesOklahomaGAGE AIRPORT
United_States | Oklahoma | M2 | HOBART MUNICIPAL AP | HOBART MUNICIPAL AP, OK, USA | 35.01N | 99.05W | 479 | -6.00 (NAC) | 87-06 | 723525 | -13.8 | -14 | -23.6 | 45.8 | 39.7 | 41 | 39.9 | 40 | 40.2 | 41 | 37 | 39.1 | 38.3 | 38 | 38.1333 | 38 | 762 | United_StatesOklahomaHOBART MUNICIPAL AP
United_States | Oklahoma | M2 | LAWTON MUNICIPAL | LAWTON MUNICIPAL, OK, USA | 34.57N | 98.42W | 338 | -6.00 (NAC) | 96-06 | 723575 | -11.6 | -12 | -14.7 | 45.4 | 38.3 | 41.2 | 41 | 40 | 40.1667 | 41 | 36.2 | 39.1 | 38.9 | 38 | 38.0667 | 38 | 763 | United_StatesOklahomaLAWTON MUNICIPAL
United_States | Oklahoma | M2 | MCALESTER MUNICIPAL AP | MCALESTER MUNICIPAL AP, OK, USA | 34.90N | 95.78W | 235 | -6.00 (NAC) | 82-06 | 723566 | -13.8 | -14 | -23.5 | 44.5 | 35.4 | 39.7 | 39.1 | 38 | 38.0667 | 40 | 33.7 | 37.4 | 37.5 | 36 | 36.2 | 36 | 764 | United_StatesOklahomaMCALESTER MUNICIPAL AP
United_States | Oklahoma | M2 | OKLAHOMA CITY WILL ROGERS WOR | OKLAHOMA CITY WILL ROGERS WOR, OK, USA | 35.39N | 97.60W | 398 | -6.00 (NAC) | 82-06 | 723530 | -14.4 | -14 | -22.9 | 44.4 | 36.3 | 40 | 39 | 38 | 38.4333 | 40 | 34.3 | 37.7 | 37.4 | 36 | 36.4667 | 36 | 765 | United_StatesOklahomaOKLAHOMA CITY WILL ROGERS WOR
United_States | Oklahoma | M2 | OKLAHOMA CITY/WILEY | OKLAHOMA CITY/WILEY, OK, USA | 35.53N | 97.65W | 396 | -6.00 (NAC) | 85-06 | 723544 | -14.7 | -15 | -22.9 | 44.3 | 36.4 | 40 | 38.6 | 38 | 38.3333 | 40 | 34.5 | 37.7 | 37.3 | 37 | 36.5 | 37 | 766 | United_StatesOklahomaOKLAHOMA CITY/WILEY
United_States | Oklahoma | M2 | PONCA CITY MUNICIPAL AP | PONCA CITY MUNICIPAL AP, OK, USA | 36.73N | 97.10W | 304 | -6.00 (NAC) | 82-06 | 723546 | -15.7 | -16 | -24.1 | 46.2 | 37.2 | 40.1 | 39.7 | 39 | 39 | 40 | 35.1 | 37.9 | 37.9 | 37 | 36.9667 | 37 | 767 | United_StatesOklahomaPONCA CITY MUNICIPAL AP
United_States | Oklahoma | M2 | STILLWATER RGNL | STILLWATER RGNL, OK, USA | 36.15N | 97.08W | 308 | -6.00 (NAC) | 96-06 | 723545 | -14.8 | -15 | -17.9 | 47 | 37.1 | 41.1 | 41.2 | 40 | 39.8 | 41 | 34.8 | 38.8 | 38.7 | 37 | 37.4333 | 37 | 768 | United_StatesOklahomaSTILLWATER RGNL
United_States | Oklahoma | M2 | TINKER AFB | TINKER AFB, OK, USA | 35.42N | 97.38W | 384 | -6.00 (NAC) | 82-06 | 723540 | -13.8 | -14 | -21.2 | 44.2 | 36.1 | 39.1 | 38.9 | 38 | 38.0333 | 39 | 34.1 | 37.4 | 37.4 | 36 | 36.3 | 36 | 769 | United_StatesOklahomaTINKER AFB
United_States | Oklahoma | M2 | TULSA INTERNATIONAL AIRPORT | TULSA INTERNATIONAL AIRPORT, OK, USA | 36.20N | 95.89W | 206 | -6.00 (NAC) | 82-06 | 723560 | -15 | -15 | -24.8 | 44.8 | 35.9 | 39 | 39.1 | 38 | 38 | 39 | 34.1 | 37.2 | 37.7 | 36 | 36.3333 | 36 | 770 | United_StatesOklahomaTULSA INTERNATIONAL AIRPORT
United_States | Oklahoma | M2 | TULSA/LLOYD JONES | TULSA/LLOYD JONES, OK, USA | 36.03N | 95.98W | 193 | -6.00 (NAC) | 97-06 | 723564 | -14.4 | -14 | -20.9 | 45.2 | 36.3 | 38.9 | 40 | 38 | 38.4 | 39 | 33.9 | 37.7 | 37.9 | 37 | 36.5 | 37 | 771 | United_StatesOklahomaTULSA/LLOYD JONES
United_States | Oklahoma | M2 | VANCE AFB | VANCE AFB, OK, USA | 36.33N | 97.92W | 408 | -6.00 (NAC) | 82-01 | 723535 | -16.4 | -16 | -25.9 | 45.1 | 38.2 | 40.1 | 39.6 | 39 | 39.3 | 40 | 36 | 38.3 | 38 | 37 | 37.4333 | 37 | 772 | United_StatesOklahomaVANCE AFB
United_States | Oregon | W2 | ASTORIA REGIONAL AIRPORT | ASTORIA REGIONAL AIRPORT, OR, USA | 46.16N | 123.88W | 7 | -8.00 (NAP) | 82-06 | 727910 | -5.4 | -5 | -13.9 | 36 | 27.2 | 26.5 | 27 | 27 | 26.9 | 27 | 21.8 | 22.7 | 23 | 23 | 22.5 | 23 | 773 | United_StatesOregonASTORIA REGIONAL AIRPORT
United_States | Oregon | W2 | AURORA STATE | AURORA STATE, OR, USA | 45.25N | 122.77W | 60 | -8.00 (NAP) | 97-06 | 726959 | -5.4 | -5 | -11.4 | 42 | 35 | 37.3 | 35 | 36 | 35.7667 | 37 | 30.9 | 32.8 | 32.6 | 32 | 32.1 | 32 | 774 | United_StatesOregonAURORA STATE
United_States | Oregon | W2 | BAKER MUNICIPAL AP | BAKER MUNICIPAL AP, OR, USA | 44.84N | 117.81W | 1028 | -8.00 (NAP) | 88-06 | 726886 | -23.1 | -23 | -34.3 | 42.2 | 32.7 | 36.4 | 36.1 | 35 | 35.0667 | 36 | 29.8 | 34 | 33.9 | 33 | 32.5667 | 33 | 775 | United_StatesOregonBAKER MUNICIPAL AP
United_States | Oregon | W2 | BURNS MUNICIPAL ARPT | BURNS MUNICIPAL ARPT, OR, USA | 43.59N | 118.95W | 1271 | -8.00 (NAP) | 91-06 | 726830 | -22.8 | -23 | -31.1 | 42.1 | 33 | 37.5 | 35.4 | 35 | 35.3 | 38 | 30.2 | 34.4 | 33.6 | 33 | 32.7333 | 33 | 776 | United_StatesOregonBURNS MUNICIPAL ARPT
United_States | Oregon | W2 | CAPE ARAGO (LS) | CAPE ARAGO (LS), OR, USA | 43.33N | 124.37W | 23 | -8.00 (NAP) | 85-06 | 994240 | -0.3 | 0 | -8.6 | 30.1 | 17.3 | 18.7 | 20.5 | 19 | 18.8333 | 19 | 16.2 | 17.4 | 18.7 | 17 | 17.4333 | 17 | 777 | United_StatesOregonCAPE ARAGO (LS)
United_States | Oregon | W2 | CORVALLIS MUNI | CORVALLIS MUNI, OR, USA | 44.48N | 123.28W | 77 | -8.00 (NAP) | 90-06 | 726945 | -7.8 | -8 | -16.2 | 43.1 | 35 | 37.5 | 37 | 37 | 36.5 | 38 | 31.1 | 33.7 | 33.7 | 33 | 32.8333 | 33 | 778 | United_StatesOregonCORVALLIS MUNI
United_States | Oregon | W2 | EUGENE MAHLON SWEET ARPT | EUGENE MAHLON SWEET ARPT, OR, USA | 44.13N | 123.21W | 114 | -8.00 (NAP) | 82-06 | 726930 | -8 | -8 | -15.6 | 42 | 33.4 | 36.5 | 35.3 | 35 | 35.0667 | 37 | 29.2 | 33 | 32.7 | 32 | 31.6333 | 32 | 779 | United_StatesOregonEUGENE MAHLON SWEET ARPT
United_States | Oregon | W2 | KLAMATH FALLS INTL AP | KLAMATH FALLS INTL AP, OR, USA | 42.15N | 121.72W | 1247 | -8.00 (NAP) | 82-06 | 725895 | -17.7 | -18 | -27.6 | 40.9 | 32.4 | 35.3 | 34.8 | 34 | 34.1667 | 35 | 29.7 | 33.1 | 32.5 | 32 | 31.7667 | 32 | 780 | United_StatesOregonKLAMATH FALLS INTL AP
United_States | Oregon | W2 | LA GRANDE MUNI AP | LA GRANDE MUNI AP, OR, USA | 45.29N | 118.01W | 828 | -8.00 (NAP) | 92-06 | 726884 | -16.9 | -17 | -24.2 | 41.5 | 32.3 | 37.3 | 36.3 | 35 | 35.3 | 37 | 28.8 | 34 | 33.9 | 32 | 32.2333 | 32 | 781 | United_StatesOregonLA GRANDE MUNI AP
United_States | Oregon | W2 | LAKEVIEW (AWOS) | LAKEVIEW (AWOS), OR, USA | 42.17N | 120.40W | 1441 | -8.00 (NAP) | 92-06 | 725976 | -20.6 | -21 | -27.9 | 39 | 31.1 | 34.4 | 33 | 33 | 32.8333 | 34 | 27.9 | 32.5 | 32 | 31 | 30.8 | 31 | 782 | United_StatesOregonLAKEVIEW (AWOS)
United_States | Oregon | W2 | MC MINNVILLE MUNI | MC MINNVILLE MUNI, OR, USA | 45.18N | 123.13W | 51 | -8.00 (NAP) | 97-06 | 726881 | -5.3 | -5 | -9.8 | 43.2 | 34.1 | 37.4 | 36 | 36 | 35.8333 | 37 | 30.9 | 33 | 32.8 | 32 | 32.2333 | 32 | 783 | United_StatesOregonMC MINNVILLE MUNI
United_States | Oregon | W2 | MEACHAM | MEACHAM, OR, USA | 45.51N | 118.43W | 1136 | -8.00 (NAP) | 82-06 | 726885 | -27.7 | -28 | -45.1 | 38.6 | 29.3 | 33.3 | 32.7 | 32 | 31.7667 | 33 | 27 | 31 | 30.5 | 30 | 29.5 | 30 | 784 | United_StatesOregonMEACHAM
United_States | Oregon | W2 | MEDFORD ROGUE VALLEY INTL AP | MEDFORD ROGUE VALLEY INTL AP, OR, USA | 42.39N | 122.87W | 405 | -8.00 (NAP) | 82-06 | 725970 | -7.7 | -8 | -16.1 | 44.8 | 37 | 39.9 | 39.4 | 39 | 38.7667 | 40 | 34 | 37.4 | 36.8 | 36 | 36.0667 | 36 | 785 | United_StatesOregonMEDFORD ROGUE VALLEY INTL AP
United_States | Oregon | W2 | NEWPORT STATE BEACH | NEWPORT STATE BEACH, OR, USA | 44.62N | 124.07W | 11 | -8.00 (NAP) | 85-06 | 994280 | -2 | -2 | -10 | 36.9 | 18.5 | 18.1 | 18.9 | 19 | 18.5 | 18 | 15.9 | 16.8 | 17.3 | 17 | 16.6667 | 17 | 786 | United_StatesOregonNEWPORT STATE BEACH
United_States | Oregon | W2 | NORTH BEND MUNI AIRPORT | NORTH BEND MUNI AIRPORT, OR, USA | 43.42N | 124.25W | 5 | -8.00 (NAP) | 82-06 | 726917 | -3.5 | -4 | -11.3 | 34.8 | 21.5 | 22.2 | 22.7 | 22 | 22.1333 | 22 | 18.9 | 20.5 | 21.2 | 20 | 20.2 | 20 | 787 | United_StatesOregonNORTH BEND MUNI AIRPORT
United_States | Oregon | W2 | PENDLETON E OR REGIONAL AP | PENDLETON E OR REGIONAL AP, OR, USA | 45.70N | 118.83W | 462 | -8.00 (NAP) | 82-06 | 726880 | -16.1 | -16 | -33.6 | 43.8 | 35.5 | 38.9 | 37.4 | 37 | 37.2667 | 39 | 32.5 | 36.3 | 35.2 | 35 | 34.6667 | 35 | 788 | United_StatesOregonPENDLETON E OR REGIONAL AP
United_States | Oregon | W2 | PORTLAND INTERNATIONAL AP | PORTLAND INTERNATIONAL AP, OR, USA | 45.59N | 122.60W | 33 | -8.00 (NAP) | 82-06 | 726980 | -6.4 | -6 | -14.9 | 41.9 | 34.3 | 36.4 | 35.4 | 35 | 35.3667 | 36 | 30 | 32.8 | 32.3 | 32 | 31.7 | 32 | 789 | United_StatesOregonPORTLAND INTERNATIONAL AP
United_States | Oregon | W2 | PORTLAND/HILLSBORO | PORTLAND/HILLSBORO, OR, USA | 45.53N | 122.95W | 62 | -8.00 (NAP) | 82-06 | 726986 | -8.4 | -8 | -16.8 | 42.3 | 34.2 | 37.2 | 36.1 | 36 | 35.8333 | 37 | 30.2 | 33.3 | 32.7 | 32 | 32.0667 | 32 | 790 | United_StatesOregonPORTLAND/HILLSBORO
United_States | Oregon | W2 | REDMOND ROBERTS FIELD | REDMOND ROBERTS FIELD, OR, USA | 44.25N | 121.15W | 940 | -8.00 (NAP) | 82-06 | 726835 | -19.2 | -19 | -31.2 | 41.4 | 33.6 | 36.9 | 35.6 | 35 | 35.3667 | 37 | 30.9 | 34.1 | 33.2 | 33 | 32.7333 | 33 | 791 | United_StatesOregonREDMOND ROBERTS FIELD
United_States | Oregon | W2 | SALEM MCNARY FIELD | SALEM MCNARY FIELD, OR, USA | 44.91N | 123.00W | 61 | -8.00 (NAP) | 82-06 | 726940 | -8.4 | -8 | -15.9 | 42 | 34.8 | 37 | 35.5 | 36 | 35.7667 | 37 | 30.5 | 33.3 | 32.7 | 32 | 32.1667 | 32 | 792 | United_StatesOregonSALEM MCNARY FIELD
United_States | Oregon | W2 | SEXTON SUMMIT | SEXTON SUMMIT, OR, USA | 42.62N | 123.38W | 1171 | -8.00 (NAP) | 82-06 | 725975 | -7.8 | -8 | -17.6 | 36.8 | 29.1 | 31.5 | 31.1 | 31 | 30.5667 | 32 | 26 | 28.4 | 28.3 | 28 | 27.5667 | 28 | 793 | United_StatesOregonSEXTON SUMMIT
United_States | Pennsylvania | E4 | ALLENTOWN LEHIGH VALLEY INTL | ALLENTOWN LEHIGH VALLEY INTL, PA, USA | 40.65N | 75.45W | 117 | -5.00 (NAE) | 82-06 | 725170 | -17.4 | -17 | -26.9 | 38.7 | 33.5 | 35.1 | 34.2 | 34 | 34.2667 | 35 | 31.5 | 33 | 32 | 32 | 32.1667 | 32 | 794 | United_StatesPennsylvaniaALLENTOWN LEHIGH VALLEY INTL
United_States | Pennsylvania | E4 | ALTOONA BLAIR CO ARPT | ALTOONA BLAIR CO ARPT, PA, USA | 40.30N | 78.32W | 448 | -5.00 (NAE) | 82-06 | 725126 | -19.2 | -19 | -30.9 | 38.7 | 32.1 | 33.5 | 33 | 33 | 32.8667 | 34 | 30 | 31.5 | 30.9 | 31 | 30.8 | 31 | 795 | United_StatesPennsylvaniaALTOONA BLAIR CO ARPT
United_States | Pennsylvania | E4 | BRADFORD REGIONAL AP | BRADFORD REGIONAL AP, PA, USA | 41.80N | 78.64W | 655 | -5.00 (NAE) | 82-06 | 725266 | -24.7 | -25 | -35.5 | 34.6 | 29.1 | 30.8 | 30 | 30 | 29.9667 | 31 | 27.6 | 28.8 | 27.8 | 28 | 28.0667 | 28 | 796 | United_StatesPennsylvaniaBRADFORD REGIONAL AP
United_States | Pennsylvania | E4 | BUTLER CO. (AWOS) | BUTLER CO. (AWOS), PA, USA | 40.78N | 79.95W | 380 | -5.00 (NAE) | 92-06 | 725124 | -19.1 | -19 | -30.5 | 37.1 | 31.4 | 32.6 | 32.6 | 32 | 32.2 | 33 | 29.8 | 31.1 | 30.9 | 31 | 30.6 | 31 | 797 | United_StatesPennsylvaniaBUTLER CO. (AWOS)
United_States | Pennsylvania | E4 | DUBOIS FAA AP | DUBOIS FAA AP, PA, USA | 41.18N | 78.90W | 556 | -5.00 (NAE) | 82-06 | 725125 | -22.1 | -22 | -33 | 36.5 | 30.4 | 32.2 | 31.3 | 31 | 31.3 | 32 | 28.6 | 29.9 | 29 | 29 | 29.1667 | 29 | 798 | United_StatesPennsylvaniaDUBOIS FAA AP
United_States | Pennsylvania | E4 | ERIE INTERNATIONAL AP | ERIE INTERNATIONAL AP, PA, USA | 42.08N | 80.18W | 225 | -5.00 (NAE) | 82-06 | 725260 | -18 | -18 | -30.3 | 37.5 | 31.3 | 32.4 | 31.4 | 32 | 31.7 | 32 | 29.5 | 30.1 | 29.6 | 30 | 29.7333 | 30 | 799 | United_StatesPennsylvaniaERIE INTERNATIONAL AP
United_States | Pennsylvania | E4 | FRANKLIN | FRANKLIN, PA, USA | 41.44N | 79.85W | 469 | -5.00 (NAE) | 92-06 | 725267 | -20.1 | -20 | -28.1 | 34.8 | 30.9 | 31.4 | 31.2 | 31 | 31.1667 | 31 | 28.9 | 29.1 | 28.9 | 29 | 28.9667 | 29 | 800 | United_StatesPennsylvaniaFRANKLIN
United_States | Pennsylvania | E4 | HARRISBURG CAPITAL CITY ARPT | HARRISBURG CAPITAL CITY ARPT, PA, USA | 40.22N | 76.85W | 106 | -5.00 (NAE) | 82-06 | 725118 | -16.9 | -17 | -26.2 | 41.1 | 34.1 | 36.7 | 35 | 35 | 35.2667 | 37 | 32.1 | 34.1 | 32.6 | 33 | 32.9333 | 33 | 801 | United_StatesPennsylvaniaHARRISBURG CAPITAL CITY ARPT
United_States | Pennsylvania | E4 | JOHNSTOWN CAMBRIA COUNTY AP | JOHNSTOWN CAMBRIA COUNTY AP, PA, USA | 40.30N | 78.83W | 696 | -5.00 (NAE) | 89-06 | 725127 | -19.9 | -20 | -29.7 | 37.2 | 30.3 | 32.4 | 31.1 | 31 | 31.2667 | 32 | 28.4 | 29.6 | 28.8 | 29 | 28.9333 | 29 | 802 | United_StatesPennsylvaniaJOHNSTOWN CAMBRIA COUNTY AP
United_States | Pennsylvania | E4 | MIDDLETOWN HARRISBURG INTL AP | MIDDLETOWN HARRISBURG INTL AP, PA, USA | 40.19N | 76.76W | 95 | -5.00 (NAE) | 82-06 | 725115 | -15.4 | -15 | -26.3 | 41.8 | 34.6 | 36.8 | 35 | 35 | 35.4667 | 37 | 32.4 | 34.1 | 32.7 | 33 | 33.0667 | 33 | 803 | United_StatesPennsylvaniaMIDDLETOWN HARRISBURG INTL AP
United_States | Pennsylvania | E4 | PHILADELPHIA INTERNATIONAL AP | PHILADELPHIA INTERNATIONAL AP, PA, USA | 39.87N | 75.23W | 9 | -5.00 (NAE) | 82-06 | 724080 | -14.1 | -14 | -24.4 | 40.5 | 34.6 | 36.4 | 35.5 | 36 | 35.5 | 36 | 32.8 | 34.4 | 33.3 | 34 | 33.5 | 34 | 804 | United_StatesPennsylvaniaPHILADELPHIA INTERNATIONAL AP
United_States | Pennsylvania | E4 | PHILADELPHIA NE PHILADELPHIA | PHILADELPHIA NE PHILADELPHIA, PA, USA | 40.08N | 75.01W | 36 | -5.00 (NAE) | 82-06 | 724085 | -15.3 | -15 | -24.2 | 40.3 | 34.6 | 36.5 | 35 | 35 | 35.3667 | 37 | 32.5 | 34.5 | 32.8 | 33 | 33.2667 | 33 | 805 | United_StatesPennsylvaniaPHILADELPHIA NE PHILADELPHIA
United_States | Pennsylvania | E4 | PITTSBURGH ALLEGHENY CO AP | PITTSBURGH ALLEGHENY CO AP, PA, USA | 40.36N | 79.92W | 388 | -5.00 (NAE) | 82-06 | 725205 | -19.5 | -20 | -32.2 | 38.8 | 32.7 | 34 | 33.5 | 33 | 33.4 | 34 | 30.9 | 32.3 | 31.7 | 32 | 31.6333 | 32 | 806 | United_StatesPennsylvaniaPITTSBURGH ALLEGHENY CO AP
United_States | Pennsylvania | E4 | PITTSBURGH INTERNATIONAL AP | PITTSBURGH INTERNATIONAL AP, PA, USA | 40.50N | 80.23W | 367 | -5.00 (NAE) | 82-06 | 725200 | -19.5 | -20 | -31.2 | 38.9 | 32.7 | 34.1 | 33.7 | 34 | 33.5 | 34 | 30.5 | 32 | 31.7 | 31 | 31.4 | 31 | 807 | United_StatesPennsylvaniaPITTSBURGH INTERNATIONAL AP
United_States | Pennsylvania | E4 | READING SPAATZ FIELD | READING SPAATZ FIELD, PA, USA | 40.37N | 75.96W | 108 | -5.00 (NAE) | 85-06 | 725103 | -16 | N/A | N/A | N/A | 33.8 | 37.2 | 34.8 | 35 | 35.2667 | 37 | 32.1 | 34.3 | 32.2 | 33 | 32.8667 | 33 | 808 | United_StatesPennsylvaniaREADING SPAATZ FIELD
United_States | Pennsylvania | E4 | WASHINGTON (AWOS) | WASHINGTON (AWOS), PA, USA | 40.13N | 80.28W | 361 | -5.00 (NAE) | 92-06 | 725117 | -20 | N/A | N/A | N/A | 32.2 | 32.8 | 32.8 | 33 | 32.6 | 33 | 30.1 | 31.3 | 31.3 | 31 | 30.9 | 31 | 809 | United_StatesPennsylvaniaWASHINGTON (AWOS)
United_States | Pennsylvania | E4 | WILKES-BARRE SCRANTON INTL AP | WILKES-BARRE SCRANTON INTL AP, PA, USA | 41.34N | 75.73W | 293 | -5.00 (NAE) | 82-06 | 725130 | -19.3 | -19 | -28.9 | 38.4 | 32.2 | 34 | 33.2 | 33 | 33.1333 | 34 | 30.2 | 31.8 | 31 | 31 | 31 | 31 | 810 | United_StatesPennsylvaniaWILKES-BARRE SCRANTON INTL AP
United_States | Pennsylvania | E4 | WILLIAMSPORT REGIONAL AP | WILLIAMSPORT REGIONAL AP, PA, USA | 41.24N | 76.92W | 160 | -5.00 (NAE) | 82-06 | 725140 | -19.1 | -19 | -29.1 | 39.6 | 33.5 | 35.6 | 34.4 | 35 | 34.5 | 36 | 31.2 | 33 | 31.8 | 32 | 32 | 32 | 811 | United_StatesPennsylvaniaWILLIAMSPORT REGIONAL AP
United_States | Pennsylvania | E4 | WILLOW GROVE NAS | WILLOW GROVE NAS, PA, USA | 40.20N | 75.15W | 110 | -5.00 (NAE) | 82-98 | 724086 | -16.7 | -17 | -24.8 | 39.3 | 34.8 | 36 | 34.5 | 35 | 35.1 | 36 | 32.8 | 34.1 | 32.5 | 33 | 33.1333 | 33 | 812 | United_StatesPennsylvaniaWILLOW GROVE NAS
United_States | Rhode_Island | E4 | BLOCK ISLAND STATE ARPT | BLOCK ISLAND STATE ARPT, RI, USA | 41.17N | 71.58W | 33 | -5.00 (NAE) | 90-06 | 725058 | -14.2 | -14 | -19.2 | 34.4 | 27.8 | 30.6 | 29.8 | 29 | 29.4 | 31 | 25.1 | 28 | 27.3 | 27 | 26.8 | 27 | 813 | United_StatesRhode_IslandBLOCK ISLAND STATE ARPT
United_States | Rhode_Island | E4 | PAWTUCKET (AWOS) | PAWTUCKET (AWOS), RI, USA | 41.92N | 71.50W | 134 | -5.00 (NAE) | 92-06 | 725054 | -18 | N/A | N/A | N/A | 32.1 | 32.8 | 33.7 | 33 | 32.8667 | 33 | 29.1 | 31.1 | 31 | 30 | 30.4 | 30 | 814 | United_StatesRhode_IslandPAWTUCKET (AWOS)
United_States | Rhode_Island | E4 | PROVIDENCE T F GREEN STATE AR | PROVIDENCE T F GREEN STATE AR, RI, USA | 41.72N | 71.43W | 19 | -5.00 (NAE) | 82-06 | 725070 | -17 | -17 | -24.8 | 40.2 | 33.1 | 35 | 33.9 | 34 | 34 | 35 | 30.7 | 32.4 | 31.4 | 32 | 31.5 | 32 | 815 | United_StatesRhode_IslandPROVIDENCE T F GREEN STATE AR
United_States | South_Carolina | E2 | ANDERSON COUNTY AP | ANDERSON COUNTY AP, SC, USA | 34.50N | 82.71W | 236 | -5.00 (NAE) | 87-06 | 723125 | -9.9 | -10 | -15.4 | 41.3 | 35.2 | 36.8 | 36.3 | 36 | 36.1 | 37 | 33.7 | 35.2 | 34.5 | 34 | 34.4667 | 34 | 816 | United_StatesSouth_CarolinaANDERSON COUNTY AP
United_States | South_Carolina | E2 | BEAUFORT MCAS | BEAUFORT MCAS, SC, USA | 32.48N | 80.72W | 12 | -5.00 (NAE) | 82-06 | 722085 | -6.4 | -6 | -14.7 | 42.2 | 36.2 | 37.2 | 36 | 36 | 36.4667 | 37 | 33.9 | 35.2 | 34.1 | 34 | 34.4 | 34 | 817 | United_StatesSouth_CarolinaBEAUFORT MCAS
United_States | South_Carolina | E2 | CHARLESTON INTL ARPT | CHARLESTON INTL ARPT, SC, USA | 32.90N | 80.04W | 15 | -5.00 (NAE) | 82-06 | 722080 | -7 | -7 | -14.7 | 40.2 | 35.5 | 36.6 | 35.5 | 36 | 35.8667 | 37 | 33.6 | 34.9 | 33.9 | 34 | 34.1333 | 34 | 818 | United_StatesSouth_CarolinaCHARLESTON INTL ARPT
United_States | South_Carolina | E2 | COLUMBIA METRO ARPT | COLUMBIA METRO ARPT, SC, USA | 33.94N | 81.12W | 69 | -5.00 (NAE) | 82-06 | 723100 | -9.5 | -10 | -17 | 42.5 | 36.9 | 38.4 | 37.4 | 38 | 37.5667 | 38 | 35 | 36.5 | 35.4 | 36 | 35.6333 | 36 | 819 | United_StatesSouth_CarolinaCOLUMBIA METRO ARPT
United_States | South_Carolina | E2 | FLORENCE REGIONAL AP | FLORENCE REGIONAL AP, SC, USA | 34.19N | 79.73W | 46 | -5.00 (NAE) | 82-06 | 723106 | -9.3 | -9 | -17.3 | 41.7 | 36.5 | 37.7 | 37 | 37 | 37.0667 | 38 | 34.3 | 36 | 34.6 | 35 | 34.9667 | 35 | 820 | United_StatesSouth_CarolinaFLORENCE REGIONAL AP
United_States | South_Carolina | E2 | FOLLY ISLAND | FOLLY ISLAND, SC, USA | 32.68N | 79.88W | 5 | -5.00 (NAE) | 85-06 | 994230 | -3.4 | -3 | -10.5 | 36.6 | 31.2 | 32.8 | 31.9 | 32 | 31.9667 | 33 | 29.4 | 31.2 | 30.6 | 30 | 30.4 | 30 | 821 | United_StatesSouth_CarolinaFOLLY ISLAND
United_States | South_Carolina | E2 | GREER GREENV'L-SPARTANBRG AP | GREER GREENV'L-SPARTANBRG AP, SC, USA | 34.90N | 82.22W | 296 | -5.00 (NAE) | 82-06 | 723120 | -11.1 | -11 | -19.5 | 41 | 34.9 | 36.6 | 36.2 | 36 | 35.9 | 37 | 33.1 | 34.8 | 33.9 | 34 | 33.9333 | 34 | 822 | United_StatesSouth_CarolinaGREER GREENV'L-SPARTANBRG AP
United_States | South_Carolina | E2 | MYRTLE BEACH AFB | MYRTLE BEACH AFB, SC, USA | 33.68N | 78.92W | 8 | -5.00 (NAE) | 82-06 | 747910 | -8.3 | -8 | -17 | 40.9 | 34.1 | 36 | 35.1 | 35 | 35.0667 | 36 | 32.2 | 33.8 | 33 | 33 | 33 | 33 | 823 | United_StatesSouth_CarolinaMYRTLE BEACH AFB
United_States | South_Carolina | E2 | SHAW AFB/SUMTER | SHAW AFB/SUMTER, SC, USA | 33.97N | 80.47W | 74 | -5.00 (NAE) | 82-06 | 747900 | -8.9 | -9 | -16 | 42 | 36 | 37.6 | 37.2 | 37 | 36.9333 | 38 | 33.8 | 35.8 | 34.8 | 35 | 34.8 | 35 | 824 | United_StatesSouth_CarolinaSHAW AFB/SUMTER
United_States | South_Dakota | M4 | ABERDEEN REGIONAL ARPT | ABERDEEN REGIONAL ARPT, SD, USA | 45.45N | 98.42W | 396 | -6.00 (NAC) | 82-06 | 726590 | -32.3 | -32 | -43.5 | 44.2 | 34.8 | 37.6 | 35.3 | 36 | 35.9 | 38 | 31.6 | 33.8 | 32.5 | 33 | 32.6333 | 33 | 825 | United_StatesSouth_DakotaABERDEEN REGIONAL ARPT
United_States | South_Dakota | M4 | BROOKINGS (AWOS) | BROOKINGS (AWOS), SD, USA | 44.30N | 96.82W | 502 | -6.00 (NAC) | 92-06 | 726515 | -29.5 | -30 | -37.3 | 38.9 | 32.4 | 34.1 | 32.6 | 33 | 33.0333 | 34 | 29.9 | 32.2 | 30.3 | 31 | 30.8 | 31 | 826 | United_StatesSouth_DakotaBROOKINGS (AWOS)
United_States | South_Dakota | M4 | BUFFALO (AMOS) | BUFFALO (AMOS), SD, USA | 45.60N | 103.55W | 915 | -7.00 (NAM) | 89-06 | 726627 | -28.8 | -29 | -36.7 | 47.6 | 36 | 40.2 | 37.8 | 38 | 38 | 40 | 31.3 | 36.7 | 35.2 | 34 | 34.4 | 34 | 827 | United_StatesSouth_DakotaBUFFALO (AMOS)
United_States | South_Dakota | M4 | CHAMBERLAIN (AMOS) | CHAMBERLAIN (AMOS), SD, USA | 43.80N | 99.32W | 530 | -6.00 (NAC) | 82-06 | 726530 | -26.9 | -27 | -34.4 | 47.4 | 35.9 | 41 | 38 | 38 | 38.3 | 41 | 32.8 | 37 | 35.4 | 35 | 35.0667 | 35 | 828 | United_StatesSouth_DakotaCHAMBERLAIN (AMOS)
United_States | South_Dakota | M4 | CHAN GURNEY MUNI | CHAN GURNEY MUNI, SD, USA | 42.92N | 97.38W | 408 | -6.00 (NAC) | 92-06 | 726525 | -25.3 | -25 | -33 | 42.2 | 35 | 37.5 | 35 | 36 | 35.8333 | 38 | 32.3 | 34 | 32.4 | 33 | 32.9 | 33 | 829 | United_StatesSouth_DakotaCHAN GURNEY MUNI
United_States | South_Dakota | M4 | CUSTER (RAMOS) | CUSTER (RAMOS), SD, USA | 43.73N | 103.62W | 1707 | -7.00 (NAM) | 85-06 | 726514 | -28.1 | -28 | -37.8 | 37.6 | 31.2 | 33.9 | 32.2 | 32 | 32.4333 | 34 | 27.7 | 31.8 | 30 | 30 | 29.8333 | 30 | 830 | United_StatesSouth_DakotaCUSTER (RAMOS)
United_States | South_Dakota | M4 | ELLSWORTH AFB | ELLSWORTH AFB, SD, USA | 44.15N | 103.10W | 980 | -7.00 (NAM) | 82-06 | 726625 | -25.9 | -26 | -37.2 | 44.8 | 37.5 | 38.8 | 37.9 | 38 | 38.0667 | 39 | 32.8 | 35.9 | 35.1 | 35 | 34.6 | 35 | 831 | United_StatesSouth_DakotaELLSWORTH AFB
United_States | South_Dakota | M4 | HURON REGIONAL ARPT | HURON REGIONAL ARPT, SD, USA | 44.39N | 98.23W | 393 | -6.00 (NAC) | 82-06 | 726540 | -30.4 | -30 | -41.4 | 45.3 | 35.5 | 37.8 | 36.6 | 37 | 36.6333 | 38 | 32.3 | 35 | 34 | 34 | 33.7667 | 34 | 832 | United_StatesSouth_DakotaHURON REGIONAL ARPT
United_States | South_Dakota | M4 | MITCHELL (AWOS) | MITCHELL (AWOS), SD, USA | 43.77N | 98.03W | 397 | -6.00 (NAC) | 92-06 | 726545 | -26.9 | -27 | -38 | 46 | 35.1 | 39 | 36 | 37 | 36.7 | 39 | 32.3 | 35.8 | 32.6 | 34 | 33.5667 | 34 | 833 | United_StatesSouth_DakotaMITCHELL (AWOS)
United_States | South_Dakota | M4 | MOBRIDGE | MOBRIDGE, SD, USA | 45.53N | 100.43W | 508 | -6.00 (NAC) | 82-06 | 726685 | -29.7 | -30 | -40.3 | 46.5 | 35.1 | 38.8 | 37.4 | 37 | 37.1 | 39 | 32.4 | 35.7 | 34.1 | 34 | 34.0667 | 34 | 834 | United_StatesSouth_DakotaMOBRIDGE
United_States | South_Dakota | M4 | PIERRE MUNICIPAL AP | PIERRE MUNICIPAL AP, SD, USA | 44.38N | 100.29W | 526 | -6.00 (NAC) | 82-06 | 726686 | -27.8 | -28 | -38.5 | 47.4 | 37.7 | 41.2 | 39.6 | 40 | 39.5 | 41 | 33.5 | 37.7 | 36.6 | 36 | 35.9333 | 36 | 835 | United_StatesSouth_DakotaPIERRE MUNICIPAL AP
United_States | South_Dakota | M4 | RAPID CITY REGIONAL ARPT | RAPID CITY REGIONAL ARPT, SD, USA | 44.05N | 103.05W | 966 | -7.00 (NAM) | 82-06 | 726620 | -27.4 | -27 | -37.2 | 45 | 37.1 | 39.7 | 37.7 | 38 | 38.1667 | 40 | 32.8 | 36.6 | 35.3 | 35 | 34.9 | 35 | 836 | United_StatesSouth_DakotaRAPID CITY REGIONAL ARPT
United_States | South_Dakota | M4 | SIOUX FALLS FOSS FIELD | SIOUX FALLS FOSS FIELD, SD, USA | 43.58N | 96.75W | 435 | -6.00 (NAC) | 82-06 | 726510 | -28.6 | -29 | -37 | 44 | 35.5 | 37.1 | 35.3 | 36 | 35.9667 | 37 | 32.3 | 34.1 | 32.7 | 33 | 33.0333 | 33 | 837 | United_StatesSouth_DakotaSIOUX FALLS FOSS FIELD
United_States | South_Dakota | M4 | WATERTOWN MUNICIPAL AP | WATERTOWN MUNICIPAL AP, SD, USA | 44.93N | 97.15W | 530 | -6.00 (NAC) | 82-06 | 726546 | -29.3 | -29 | -37.8 | 40.9 | 34.8 | 35.9 | 33.5 | 35 | 34.7333 | 36 | 31.1 | 32.7 | 31 | 32 | 31.6 | 32 | 838 | United_StatesSouth_DakotaWATERTOWN MUNICIPAL AP
United_States | Tennessee | E2 | BRISTOL TRI CITY AIRPORT | BRISTOL TRI CITY AIRPORT, TN, USA | 36.48N | 82.40W | 465 | -5.00 (NAE) | 82-06 | 723183 | -16.5 | -17 | -28.3 | 38.4 | 32.1 | 34 | 34 | 33 | 33.3667 | 34 | 30.7 | 32.2 | 32.1 | 32 | 31.6667 | 32 | 839 | United_StatesTennesseeBRISTOL TRI CITY AIRPORT
United_States | Tennessee | E2 | CHATTANOOGA LOVELL FIELD AP | CHATTANOOGA LOVELL FIELD AP, TN, USA | 35.03N | 85.20W | 210 | -5.00 (NAE) | 82-06 | 723240 | -12.2 | -12 | -23.2 | 40.6 | 34.9 | 36.7 | 36.2 | 36 | 35.9333 | 37 | 33.2 | 34.8 | 34.5 | 34 | 34.1667 | 34 | 840 | United_StatesTennesseeCHATTANOOGA LOVELL FIELD AP
United_States | Tennessee | E2 | CROSSVILLE MEMORIAL AP | CROSSVILLE MEMORIAL AP, TN, USA | 35.95N | 85.09W | 570 | -6.00 (NAC) | 82-06 | 723265 | -17.9 | -18 | -30.2 | 38.2 | 31.6 | 33.3 | 32.8 | 33 | 32.5667 | 33 | 29.8 | 31.6 | 31.1 | 31 | 30.8333 | 31 | 841 | United_StatesTennesseeCROSSVILLE MEMORIAL AP
United_States | Tennessee | E2 | DYERSBURG MUNICIPAL AP | DYERSBURG MUNICIPAL AP, TN, USA | 36.02N | 89.32W | 103 | -6.00 (NAC) | 92-06 | 723347 | -11.9 | -12 | -18.3 | 39 | 34.1 | 36.2 | 36.3 | 36 | 35.5333 | 36 | 33 | 34.1 | 34.4 | 34 | 33.8333 | 34 | 842 | United_StatesTennesseeDYERSBURG MUNICIPAL AP
United_States | Tennessee | E2 | JACKSON MCKELLAR-SIPES REGL A | JACKSON MCKELLAR-SIPES REGL A, TN, USA | 35.59N | 88.92W | 129 | -6.00 (NAC) | 82-06 | 723346 | -14.6 | -15 | -24.8 | 40 | 34.8 | 36.1 | 36.7 | 36 | 35.8667 | 36 | 33.3 | 34.7 | 35 | 34 | 34.3333 | 34 | 843 | United_StatesTennesseeJACKSON MCKELLAR-SIPES REGL A
United_States | Tennessee | E2 | KNOXVILLE MCGHEE TYSON AP | KNOXVILLE MCGHEE TYSON AP, TN, USA | 35.82N | 83.99W | 299 | -5.00 (NAE) | 82-06 | 723260 | -14.5 | -15 | -27.8 | 39.8 | 34 | 35.6 | 35.2 | 35 | 34.9333 | 36 | 32.1 | 33.9 | 33.3 | 33 | 33.1 | 33 | 844 | United_StatesTennesseeKNOXVILLE MCGHEE TYSON AP
United_States | Tennessee | E2 | MEMPHIS INTERNATIONAL AP | MEMPHIS INTERNATIONAL AP, TN, USA | 35.06N | 89.99W | 101 | -6.00 (NAC) | 82-06 | 723340 | -11.8 | -12 | -21.5 | 41 | 35.7 | 36.8 | 37.4 | 37 | 36.6333 | 37 | 34.1 | 35.4 | 35.7 | 35 | 35.0667 | 35 | 845 | United_StatesTennesseeMEMPHIS INTERNATIONAL AP
United_States | Tennessee | E2 | MILLINGTON MUNI ARP | MILLINGTON MUNI ARP, TN, USA | 35.35N | 89.87W | 98 | -6.00 (NAC) | 82-06 | 723284 | -13.6 | -14 | -26.5 | 41.9 | 36.3 | 37.7 | 37.8 | 37 | 37.2667 | 38 | 34.9 | 36.2 | 36.4 | 36 | 35.8333 | 36 | 846 | United_StatesTennesseeMILLINGTON MUNI ARP
United_States | Tennessee | E2 | NASHVILLE INTERNATIONAL AP | NASHVILLE INTERNATIONAL AP, TN, USA | 36.12N | 86.69W | 184 | -6.00 (NAC) | 82-06 | 723270 | -15.2 | -15 | -27.7 | 40.8 | 34.6 | 36.6 | 36.6 | 36 | 35.9333 | 37 | 33 | 34.6 | 34.7 | 34 | 34.1 | 34 | 847 | United_StatesTennesseeNASHVILLE INTERNATIONAL AP
United_States | Territory or Island |  | GUAM ANDERSEN AFB | ANDERSEN AFB, Guam | 13.57N | 144.92E | 162 | 10.00 (PCW) | 82-06 | 912180 | 21.8 |  | 20.1 | 34.2 | 31.2 | 31.2 | 31.1 | 31 | 31.1667 |  | 30.8 | 30.5 | 30.2 | 31 | 30.5 |  | 848 | United_StatesTerritory or IslandGUAM ANDERSEN AFB
United_States | Territory or Island |  | GUAM WFO | GUAM WFO, Guam | 13.48N | 144.80E | 77 | 10.00 (PCW) | 82-06 | 912120 | 21.4 |  | 18.9 | 37.8 | 32.9 | 32.2 | 32.2 | 32 | 32.4333 |  | 31.9 | 31.6 | 31.5 | 32 | 31.6667 |  | 849 | United_StatesTerritory or IslandGUAM WFO
United_States | Territory or Island |  | MIDWAY ISLAND NAS | MIDWAY ISLAND NAS, United States Minor Outlying Islands | 28.20N | 177.38W | 4 | -11.00 (PCM) | 82-99 | 910660 | 13 |  | 10.3 | 36.6 | 30.6 | 31.2 | 31.7 | 31 | 31.1667 |  | 29.7 | 30.4 | 30.9 | 30 | 30.3333 |  | 850 | United_StatesTerritory or IslandMIDWAY ISLAND NAS
United_States | Territory or Island |  | PAGO PAGO WSO AP | PAGO PAGO WSO AP, American Samoa | 14.33S | 170.71W | 3 | -11.00 (PCM) | 82-06 | 917650 | 21.1 |  | 18.2 | 37 | 31 | 30.8 | 30.8 | 31 | 30.8667 |  | 30.2 | 30.1 | 30.1 | 30 | 30.1333 |  | 851 | United_StatesTerritory or IslandPAGO PAGO WSO AP
United_States | Territory or Island |  | WAKE ISLAND | WAKE ISLAND, United States Minor Outlying Islands | 19.28N | 166.64E | 4 | 12.00 (FJI) | 82-06 | 912450 | 20.4 |  | 18.4 | 34.2 | 32.2 | 32.3 | 32.6 | 32 | 32.3667 |  | 31.3 | 31.8 | 32.1 | 32 | 31.7333 |  | 852 | United_StatesTerritory or IslandWAKE ISLAND
United_States | Texas | M2 | ABILENE DYESS AFB | ABILENE DYESS AFB, TX, USA | 32.43N | 99.85W | 545 | -6.00 (NAC) | 82-06 | 690190 | -12.2 | -12 | -22.8 | 44.9 | 40.4 | 40.4 | 39.4 | 40 | 40.0667 | 40 | 37.7 | 38.5 | 37.9 | 38 | 38.0333 | 38 | 853 | United_StatesTexasABILENE DYESS AFB
United_States | Texas | M2 | ABILENE REGIONAL AP | ABILENE REGIONAL AP, TX, USA | 32.41N | 99.68W | 546 | -6.00 (NAC) | 82-06 | 722660 | -10.9 | -11 | -21.5 | 43.3 | 38.1 | 38.9 | 38.5 | 39 | 38.5 | 39 | 35.9 | 37.2 | 37.1 | 37 | 36.7333 | 37 | 854 | United_StatesTexasABILENE REGIONAL AP
United_States | Texas | M1 | ALICE INTL AP | ALICE INTL AP, TX, USA | 27.74N | 98.03W | 55 | -6.00 (NAC) | 82-06 | 722517 | -2 | -2 | -7.9 | 45.6 | 37.9 | 38.9 | 38.9 | 39 | 38.5667 | 39 | 36.3 | 37.5 | 37.6 | 37 | 37.1333 | 37 | 855 | United_StatesTexasALICE INTL AP
United_States | Texas | M3 | AMARILLO INTERNATIONAL AP | AMARILLO INTERNATIONAL AP, TX, USA | 35.22N | 101.71W | 1099 | -6.00 (NAC) | 82-06 | 723630 | -17.3 | -17 | -26.5 | 42.7 | 38.8 | 37.9 | 36.8 | 38 | 37.8333 | 38 | 35.9 | 36.2 | 35.1 | 36 | 35.7333 | 36 | 856 | United_StatesTexasAMARILLO INTERNATIONAL AP
United_States | Texas | M2 | AUSTIN/BERGSTROM | AUSTIN/BERGSTROM, TX, USA | 30.18N | 97.68W | 151 | -6.00 (NAC) | 82-06 | 722540 | -7.1 | -7 | -15.7 | 44 | 37.4 | 38.6 | 39.1 | 38 | 38.3667 | 39 | 35.6 | 37.3 | 37.8 | 37 | 36.9 | 37 | 857 | United_StatesTexasAUSTIN/BERGSTROM
United_States | Texas | M1 | BEEVILLE CHASE NAAS | BEEVILLE CHASE NAAS, TX, USA | 28.37N | 97.67W | 58 | -6.00 (NAC) | 82-92 | 722556 | -5 | -5 | -15.1 | 44 | 38.4 | 38.9 | 39.2 | 39 | 38.8333 | 39 | 36.6 | 37.4 | 38 | 37 | 37.3333 | 37 | 858 | United_StatesTexasBEEVILLE CHASE NAAS
United_States | Texas | M1 | BROWNSVILLE S PADRE ISL INTL | BROWNSVILLE S PADRE ISL INTL, TX, USA | 25.91N | 97.43W | 7 | -6.00 (NAC) | 82-06 | 722500 | 0.2 | 0 | -7.7 | 40.8 | 35.2 | 35.9 | 36.3 | 36 | 35.8 | 36 | 34.4 | 35.1 | 35.4 | 35 | 34.9667 | 35 | 859 | United_StatesTexasBROWNSVILLE S PADRE ISL INTL
United_States | Texas | M2 | BURNET MUNI. | BURNET MUNI., TX, USA | 30.73N | 98.23W | 391 | -6.00 (NAC) | 97-06 | 722542 | -5.5 | -6 | -9.2 | 45.7 | 37 | 37.5 | 37.7 | 37 | 37.4 | 38 | 34.1 | 36.3 | 37.1 | 36 | 35.8333 | 36 | 860 | United_StatesTexasBURNET MUNI.
United_States | Texas | M2 | CAMP MABRY | CAMP MABRY, TX, USA | 30.32N | 97.77W | 201 | -6.00 (NAC) | 82-06 | 722544 | -5.4 | -5 | -14.9 | 43.8 | 37.3 | 38.5 | 39 | 38 | 38.2667 | 39 | 35.3 | 37.2 | 37.5 | 37 | 36.6667 | 37 | 861 | United_StatesTexasCAMP MABRY
United_States | Texas | M3 | CHILDRESS MUNICIPAL AP | CHILDRESS MUNICIPAL AP, TX, USA | 34.43N | 100.29W | 595 | -6.00 (NAC) | 88-06 | 723604 | -12.2 | -12 | -21.2 | 47.2 | 40.7 | 40.1 | 38.7 | 40 | 39.8333 | 40 | 37.5 | 38 | 37.4 | 38 | 37.6333 | 38 | 862 | United_StatesTexasCHILDRESS MUNICIPAL AP
United_States | Texas | M2 | COLLEGE STATION EASTERWOOD FL | COLLEGE STATION EASTERWOOD FL, TX, USA | 30.59N | 96.36W | 100 | -6.00 (NAC) | 82-06 | 722445 | -6.4 | -6 | -15.4 | 43.8 | 37.2 | 38 | 38.9 | 38 | 38.0333 | 38 | 35.3 | 37.1 | 37.4 | 37 | 36.6 | 37 | 863 | United_StatesTexasCOLLEGE STATION EASTERWOOD FL
United_States | Texas | M1 | CORPUS CHRISTI INTL ARPT | CORPUS CHRISTI INTL ARPT, TX, USA | 27.77N | 97.51W | 13 | -6.00 (NAC) | 82-06 | 722510 | -2.8 | -3 | -10.9 | 41.8 | 34.9 | 36.1 | 36.7 | 36 | 35.9 | 36 | 33.8 | 35.1 | 35.6 | 35 | 34.8333 | 35 | 864 | United_StatesTexasCORPUS CHRISTI INTL ARPT
United_States | Texas | M1 | CORPUS CHRISTI NAS | CORPUS CHRISTI NAS, TX, USA | 27.70N | 97.28W | 6 | -6.00 (NAC) | 82-06 | 722515 | -0.9 | -1 | -10.8 | 41.2 | 34 | 34.1 | 34.9 | 34 | 34.3333 | 34 | 33 | 33.5 | 34.1 | 34 | 33.5333 | 34 | 865 | United_StatesTexasCORPUS CHRISTI NAS
United_States | Texas | M1 | COTULLA FAA AP | COTULLA FAA AP, TX, USA | 28.46N | 99.22W | 146 | -6.00 (NAC) | 82-06 | 722526 | -4.1 | -4 | -11.6 | 44.5 | 39.5 | 40.5 | 40.3 | 40 | 40.1 | 41 | 38.1 | 38.8 | 38.9 | 39 | 38.6 | 39 | 866 | United_StatesTexasCOTULLA FAA AP
United_States | Texas | M2 | COX FLD | COX FLD, TX, USA | 33.63N | 95.45W | 171 | -6.00 (NAC) | 93-06 | 722587 | -9.9 | -10 | -15.5 | 43.5 | 36.1 | 38 | 38.9 | 38 | 37.6667 | 38 | 33.9 | 37.1 | 37.5 | 36 | 36.1667 | 36 | 867 | United_StatesTexasCOX FLD
United_States | Texas | M3 | DALHART MUNICIPAL AP | DALHART MUNICIPAL AP, TX, USA | 36.02N | 102.55W | 1217 | -6.00 (NAC) | 88-06 | 722636 | -17.3 | -17 | -25.3 | 42.2 | 38.3 | 37.9 | 37 | 38 | 37.7333 | 38 | 36.3 | 36.3 | 35.1 | 36 | 35.9 | 36 | 868 | United_StatesTexasDALHART MUNICIPAL AP
United_States | Texas | M2 | DALLAS HENSLEY FIELD NAS | DALLAS HENSLEY FIELD NAS, TX, USA | 32.73N | 96.97W | 151 | -6.00 (NAC) | 82-96 | 722585 | -9.2 | -9 | -20.3 | 43.1 | 37 | 38.9 | 39.2 | 38 | 38.3667 | 39 | 35.2 | 37.3 | 38 | 37 | 36.8333 | 37 | 869 | United_StatesTexasDALLAS HENSLEY FIELD NAS
United_States | Texas | M2 | DALLAS LOVE FIELD | DALLAS LOVE FIELD, TX, USA | 32.85N | 96.85W | 149 | -6.00 (NAC) | 82-06 | 722583 | -8.2 | -8 | -17.7 | 44.2 | 37.3 | 39.4 | 39.6 | 39 | 38.7667 | 39 | 35.7 | 37.9 | 38.1 | 37 | 37.2333 | 37 | 870 | United_StatesTexasDALLAS LOVE FIELD
United_States | Texas | M2 | DALLAS/REDBIRD ARPT | DALLAS/REDBIRD ARPT, TX, USA | 32.68N | 96.87W | 201 | -6.00 (NAC) | 97-06 | 722599 | -7.6 | -8 | -11.2 | 45.5 | 37.4 | 39.8 | 39.1 | 39 | 38.7667 | 40 | 36 | 37.9 | 37.9 | 37 | 37.2667 | 37 | 871 | United_StatesTexasDALLAS/REDBIRD ARPT
United_States | Texas | M2 | DALLAS-FORT WORTH INTL AP | DALLAS-FORT WORTH INTL AP, TX, USA | 32.90N | 97.04W | 182 | -6.00 (NAC) | 82-06 | 722590 | -9.1 | -9 | -18.3 | 44.7 | 37.1 | 39.3 | 39.9 | 39 | 38.7667 | 39 | 35.4 | 37.8 | 38.3 | 37 | 37.1667 | 37 | 872 | United_StatesTexasDALLAS-FORT WORTH INTL AP
United_States | Texas | M2 | DEL RIO INTERNATIONAL AP | DEL RIO INTERNATIONAL AP, TX, USA | 29.37N | 100.92W | 313 | -6.00 (NAC) | 82-06 | 722610 | -3.5 | -4 | -8.7 | 43.7 | 40.1 | 40.1 | 39.2 | 40 | 39.8 | 40 | 37.8 | 38.4 | 37.9 | 38 | 38.0333 | 38 | 873 | United_StatesTexasDEL RIO INTERNATIONAL AP
United_States | Texas | M2 | DRAUGHON MILLER CEN | DRAUGHON MILLER CEN, TX, USA | 31.15N | 97.40W | 213 | -6.00 (NAC) | 85-06 | 722577 | -6.8 | -7 | -12.5 | 43.1 | 37.3 | 38.8 | 38.8 | 38 | 38.3 | 39 | 35.3 | 37.4 | 37.6 | 37 | 36.7667 | 37 | 874 | United_StatesTexasDRAUGHON MILLER CEN
United_States | Texas | M2 | EL PASO INTERNATIONAL AP | EL PASO INTERNATIONAL AP, TX, USA | 31.81N | 106.38W | 1194 | -7.00 (NAM) | 82-06 | 722700 | -8.9 | -9 | -16.4 | 44.5 | 40.6 | 39.8 | 37.8 | 39 | 39.4 | 40 | 38.6 | 37.8 | 36.1 | 38 | 37.5 | 38 | 875 | United_StatesTexasEL PASO INTERNATIONAL AP
United_States | Texas | M2 | FORT HOOD/GRAY AAF | FORT HOOD/GRAY AAF, TX, USA | 31.07N | 97.83W | 312 | -6.00 (NAC) | 82-06 | 722576 | -7.5 | -8 | -17.8 | 43.5 | 37.6 | 39 | 39.2 | 39 | 38.6 | 39 | 35.3 | 37.6 | 37.8 | 37 | 36.9 | 37 | 876 | United_StatesTexasFORT HOOD/GRAY AAF
United_States | Texas | M2 | FORT STOCKTON PECOS | FORT STOCKTON PECOS, TX, USA | 30.92N | 102.92W | 941 | -6.00 (NAC) | 98-06 | 722618 | -7.6 | -8 | -12.4 | 43.6 | 40.9 | 38.9 | 38 | 39 | 39.2667 | 39 | 38 | 37.6 | 37.1 | 38 | 37.5667 | 38 | 877 | United_StatesTexasFORT STOCKTON PECOS
United_States | Texas | M2 | FORT WORTH ALLIANCE | FORT WORTH ALLIANCE, TX, USA | 32.98N | 97.32W | 226 | -6.00 (NAC) | 92-06 | 722594 | -8.6 | -9 | -14.2 | 46 | 37.7 | 39.9 | 40.9 | 40 | 39.5 | 40 | 36.1 | 38.1 | 38.8 | 38 | 37.6667 | 38 | 878 | United_StatesTexasFORT WORTH ALLIANCE
United_States | Texas | M2 | FORT WORTH MEACHAM | FORT WORTH MEACHAM, TX, USA | 32.82N | 97.36W | 215 | -6.00 (NAC) | 82-06 | 722596 | -9.5 | -10 | -18.6 | 44.7 | 37.5 | 39.8 | 39.9 | 39 | 39.0667 | 40 | 35.8 | 38 | 38.5 | 37 | 37.4333 | 37 | 879 | United_StatesTexasFORT WORTH MEACHAM
United_States | Texas | M2 | FORT WORTH NAS | FORT WORTH NAS, TX, USA | 32.77N | 97.44W | 198 | -6.00 (NAC) | 82-05 | 722595 | -9.8 | -10 | -20.7 | 43.3 | 37.6 | 39.7 | 39.3 | 39 | 38.8667 | 40 | 35.8 | 37.9 | 37.9 | 37 | 37.2 | 37 | 880 | United_StatesTexasFORT WORTH NAS
United_States | Texas | M1 | GALVESTON/SCHOLES | GALVESTON/SCHOLES, TX, USA | 29.27N | 94.86W | 3 | -6.00 (NAC) | 82-06 | 722420 | -1.6 | -2 | -12.2 | 39 | 32.9 | 33.5 | 34.1 | 34 | 33.5 | 34 | 32.2 | 32.8 | 33.2 | 33 | 32.7333 | 33 | 881 | United_StatesTexasGALVESTON/SCHOLES
United_States | Texas | M2 | GEORGETOWN (AWOS) | GEORGETOWN (AWOS), TX, USA | 30.68N | 97.68W | 240 | -6.00 (NAC) | 92-06 | 722547 | -6.6 | -7 | -9.7 | 44.4 | 36.1 | 37.9 | 38.7 | 38 | 37.5667 | 38 | 34 | 36.8 | 37.4 | 36 | 36.0667 | 36 | 882 | United_StatesTexasGEORGETOWN (AWOS)
United_States | Texas | M1 | HARLINGEN RIO GRANDE VALLEY I | HARLINGEN RIO GRANDE VALLEY I, TX, USA | 26.23N | 97.65W | 11 | -6.00 (NAC) | 86-06 | 722505 | -0.1 | 0 | -8.4 | 39.7 | 37.3 | 37.7 | 37.9 | 38 | 37.6333 | 38 | 36.1 | 37 | 37.1 | 37 | 36.7333 | 37 | 883 | United_StatesTexasHARLINGEN RIO GRANDE VALLEY I
United_States | Texas | M2 | HONDO MUNICIPAL AP | HONDO MUNICIPAL AP, TX, USA | 29.36N | 99.17W | 284 | -6.00 (NAC) | 83-06 | 722533 | -6.9 | -7 | -14.3 | 43.1 | 37.8 | 38.3 | 38 | 38 | 38.0333 | 38 | 36.2 | 37.2 | 37.3 | 37 | 36.9 | 37 | 884 | United_StatesTexasHONDO MUNICIPAL AP
United_States | Texas | M2 | HOUSTON BUSH INTERCONTINENTAL | HOUSTON BUSH INTERCONTINENTAL, TX, USA | 29.99N | 95.36W | 32 | -6.00 (NAC) | 82-06 | 722430 | -4.4 | -4 | -13.5 | 42.4 | 35.7 | 37.3 | 37.5 | 37 | 36.8333 | 37 | 34.4 | 35.7 | 36.2 | 35 | 35.4333 | 35 | 885 | United_StatesTexasHOUSTON BUSH INTERCONTINENTAL
United_States | Texas | M2 | HOUSTON WILLIAM P HOBBY AP | HOUSTON WILLIAM P HOBBY AP, TX, USA | 29.65N | 95.28W | 14 | -6.00 (NAC) | 82-06 | 722435 | -3.1 | -3 | -12.3 | 41 | 35.2 | 36.3 | 36.4 | 36 | 35.9667 | 36 | 33.8 | 34.7 | 35.1 | 35 | 34.5333 | 35 | 886 | United_StatesTexasHOUSTON WILLIAM P HOBBY AP
United_States | Texas | M2 | HOUSTON/D.W. HOOKS | HOUSTON/D.W. HOOKS, TX, USA | 30.07N | 95.55W | 46 | -6.00 (NAC) | 98-06 | 722429 | -4.1 | -4 | -9.8 | 47 | 36.3 | 37.9 | 37.9 | 37 | 37.3667 | 38 | 34 | 37 | 36.3 | 36 | 35.7667 | 36 | 887 | United_StatesTexasHOUSTON/D.W. HOOKS
United_States | Texas | M2 | HOUSTON/ELLINGTON | HOUSTON/ELLINGTON, TX, USA | 29.60N | 95.17W | 12 | -6.00 (NAC) | 82-06 | 722436 | -2.6 | -3 | -11 | 42 | 35.4 | 37 | 37.2 | 37 | 36.5333 | 37 | 34.1 | 35.2 | 35.7 | 35 | 35 | 35 | 888 | United_StatesTexasHOUSTON/ELLINGTON
United_States | Texas | M2 | JUNCTION KIMBLE COUNTY AP | JUNCTION KIMBLE COUNTY AP, TX, USA | 30.51N | 99.77W | 533 | -6.00 (NAC) | 82-06 | 747400 | -9.9 | -10 | -18.4 | 42.6 | 38.5 | 38.7 | 38.8 | 39 | 38.6667 | 39 | 36.3 | 37.2 | 37.3 | 37 | 36.9333 | 37 | 889 | United_StatesTexasJUNCTION KIMBLE COUNTY AP
United_States | Texas | M2 | KELLY AFB | KELLY AFB, TX, USA | 29.38N | 98.58W | 208 | -6.00 (NAC) | 82-05 | 722535 | -6.4 | -6 | -17.5 | 44 | 38.8 | 39.1 | 38.9 | 39 | 38.9333 | 39 | 36.4 | 37.8 | 37.6 | 37 | 37.2667 | 37 | 890 | United_StatesTexasKELLY AFB
United_States | Texas | M2 | KILLEEN MUNI (AWOS) | KILLEEN MUNI (AWOS), TX, USA | 31.08N | 97.68W | 258 | -6.00 (NAC) | 87-06 | 722575 | -6.3 | -6 | -12.4 | 43.4 | 37.3 | 38.7 | 38.9 | 38 | 38.3 | 39 | 35.2 | 37.3 | 37.6 | 37 | 36.7 | 37 | 891 | United_StatesTexasKILLEEN MUNI (AWOS)
United_States | Texas | M1 | KINGSVILLE | KINGSVILLE, TX, USA | 27.50N | 97.82W | 18 | -6.00 (NAC) | 82-06 | 722516 | -2.6 | -3 | -11.6 | 41.3 | 36.8 | 37.4 | 37.8 | 37 | 37.3333 | 37 | 35.5 | 36.2 | 36.5 | 36 | 36.0667 | 36 | 892 | United_StatesTexasKINGSVILLE
United_States | Texas | M1 | LAREDO INTL AIRPORT | LAREDO INTL AIRPORT, TX, USA | 27.55N | 99.47W | 155 | -6.00 (NAC) | 82-06 | 722520 | -1.6 | -2 | -9.1 | 45 | 41 | 40.4 | 40.3 | 41 | 40.5667 | 40 | 38.9 | 38.9 | 38.9 | 39 | 38.9 | 39 | 893 | United_StatesTexasLAREDO INTL AIRPORT
United_States | Texas | M2 | LAUGHLIN AFB | LAUGHLIN AFB, TX, USA | 29.37N | 100.78W | 327 | -6.00 (NAC) | 82-01 | 722615 | -5.1 | -5 | -14 | 46.7 | 41.4 | 42.2 | 41.1 | 42 | 41.5667 | 42 | 39 | 40 | 39.2 | 39 | 39.4 | 39 | 894 | United_StatesTexasLAUGHLIN AFB
United_States | Texas | M2 | LONGVIEW GREGG COUNTY AP | LONGVIEW GREGG COUNTY AP, TX, USA | 32.39N | 94.71W | 114 | -6.00 (NAC) | 83-06 | 722470 | -8.2 | -8 | -17.3 | 43.4 | 37.1 | 38.7 | 38.9 | 38 | 38.2333 | 39 | 34.6 | 37.1 | 37.4 | 36 | 36.3667 | 36 | 895 | United_StatesTexasLONGVIEW GREGG COUNTY AP
United_States | Texas | M2 | LUBBOCK INTERNATIONAL AP | LUBBOCK INTERNATIONAL AP, TX, USA | 33.67N | 101.82W | 988 | -6.00 (NAC) | 82-06 | 722670 | -13.5 | -14 | -21 | 44.7 | 39.3 | 38.7 | 37.1 | 38 | 38.3667 | 39 | 36.9 | 36.9 | 35.6 | 36 | 36.4667 | 36 | 896 | United_StatesTexasLUBBOCK INTERNATIONAL AP
United_States | Texas | M2 | LUFKIN ANGELINA CO | LUFKIN ANGELINA CO, TX, USA | 31.23N | 94.75W | 96 | -6.00 (NAC) | 82-06 | 722446 | -7.1 | -7 | -13.9 | 43.2 | 36.4 | 37.9 | 38.3 | 38 | 37.5333 | 38 | 34.2 | 36.1 | 36.7 | 36 | 35.6667 | 36 | 897 | United_StatesTexasLUFKIN ANGELINA CO
United_States | Texas | M2 | MARFA AP | MARFA AP, TX, USA | 30.37N | 104.02W | 1478 | -7.00 (NAM) | 82-06 | 722640 | -13.7 | -14 | -21.2 | 40.8 | 37.3 | 35.7 | 34 | 36 | 35.6667 | 36 | 35 | 33.7 | 32.4 | 34 | 33.7 | 34 | 898 | United_StatesTexasMARFA AP
United_States | Texas | M2 | MC GREGOR (AWOS) | MC GREGOR (AWOS), TX, USA | 31.48N | 97.32W | 180 | -6.00 (NAC) | 92-06 | 722563 | -6.7 | -7 | -11.8 | 43.8 | 37.4 | 39 | 39 | 38 | 38.4667 | 39 | 36.1 | 37.7 | 37.8 | 37 | 37.2 | 37 | 899 | United_StatesTexasMC GREGOR (AWOS)
United_States | Texas | M1 | MCALLEN MILLER INTL AP | MCALLEN MILLER INTL AP, TX, USA | 26.18N | 98.24W | 34 | -6.00 (NAC) | 82-06 | 722506 | -0.4 | 0 | -7.9 | 43.6 | 37.9 | 38.8 | 38.9 | 39 | 38.5333 | 39 | 37 | 37.6 | 37.8 | 37 | 37.4667 | 37 | 900 | United_StatesTexasMCALLEN MILLER INTL AP
United_States | Texas | M2 | MCKINNEY MUNI ARPT | MCKINNEY MUNI ARPT, TX, USA | 33.18N | 96.58W | 176 | -6.00 (NAC) | 98-06 | 722541 | -9.5 | -10 | -15.5 | 47 | 37.1 | 39.2 | 40.2 | 39 | 38.8333 | 39 | 35.2 | 37.9 | 38 | 37 | 37.0333 | 37 | 901 | United_StatesTexasMCKINNEY MUNI ARPT
United_States | Texas | M2 | MIDLAND INTERNATIONAL AP | MIDLAND INTERNATIONAL AP, TX, USA | 31.93N | 102.21W | 872 | -6.00 (NAC) | 82-06 | 722650 | -11.4 | -11 | -20.6 | 45.5 | 40.7 | 39.7 | 38.4 | 40 | 39.6 | 40 | 37.9 | 37.5 | 36.8 | 37 | 37.4 | 37 | 902 | United_StatesTexasMIDLAND INTERNATIONAL AP
United_States | Texas | M2 | NACOGDOCHES (AWOS) | NACOGDOCHES (AWOS), TX, USA | 31.58N | 94.72W | 108 | -6.00 (NAC) | 92-06 | 722499 | -7.4 | -7 | -12.7 | 42.8 | 37 | 37.9 | 37.7 | 38 | 37.5333 | 38 | 34 | 36.3 | 36.3 | 36 | 35.5333 | 36 | 903 | United_StatesTexasNACOGDOCHES (AWOS)
United_States | Texas | M1 | PALACIOS MUNICIPAL AP | PALACIOS MUNICIPAL AP, TX, USA | 28.73N | 96.25W | 5 | -6.00 (NAC) | 87-06 | 722555 | -2.7 | -3 | -10.4 | 39.9 | 33.1 | 34 | 34.8 | 34 | 33.9667 | 34 | 32.4 | 32.9 | 33.7 | 33 | 33 | 33 | 904 | United_StatesTexasPALACIOS MUNICIPAL AP
United_States | Texas | M2 | PINE SPRINGS GUADALUPE MOUNTA | PINE SPRINGS GUADALUPE MOUNTA, TX, USA | 31.83N | 104.81W | 1663 | -7.00 (NAM) | 82-06 | 722620 | -11.9 | -12 | -21.7 | 41.4 | 37.1 | 36.2 | 34 | 36 | 35.7667 | 36 | 34.6 | 33.6 | 32 | 33 | 33.4 | 33 | 905 | United_StatesTexasPINE SPRINGS GUADALUPE MOUNTA
United_States | Texas | M1 | PORT ARANSAS | PORT ARANSAS, TX, USA | 27.82N | 97.05W | 6 | -6.00 (NAC) | 85-06 | 994110 | -0.1 | 0 | -8.8 | 35.5 | 29.6 | 29.9 | 30.6 | 30 | 30.0333 | 30 | 29 | 29.5 | 30 | 30 | 29.5 | 30 | 906 | United_StatesTexasPORT ARANSAS
United_States | Texas | M2 | PORT ARTHUR JEFFERSON COUNTY | PORT ARTHUR JEFFERSON COUNTY, TX, USA | 29.95N | 94.02W | 5 | -6.00 (NAC) | 82-06 | 722410 | -3.9 | -4 | -10.8 | 40.4 | 34.5 | 35.4 | 36.2 | 35 | 35.3667 | 35 | 33.3 | 34.1 | 34.7 | 34 | 34.0333 | 34 | 907 | United_StatesTexasPORT ARTHUR JEFFERSON COUNTY
United_States | Texas | M2 | RANDOLPH AFB | RANDOLPH AFB, TX, USA | 29.53N | 98.28W | 232 | -6.00 (NAC) | 82-01 | 722536 | -5.8 | -6 | -13.6 | 44 | 38.2 | 38.8 | 38.7 | 39 | 38.5667 | 39 | 36 | 37.4 | 37.3 | 37 | 36.9 | 37 | 908 | United_StatesTexasRANDOLPH AFB
United_States | Texas | M2 | REESE AFB | REESE AFB, TX, USA | 33.60N | 102.05W | 1014 | -6.00 (NAC) | 82-97 | 722675 | -13.9 | -14 | -20.9 | 46.9 | 40.1 | 40.1 | 37.5 | 39 | 39.2333 | 40 | 37.1 | 37.8 | 36 | 37 | 36.9667 | 37 | 909 | United_StatesTexasREESE AFB
United_States | Texas | M1 | ROCKPORT/ARANSAS CO | ROCKPORT/ARANSAS CO, TX, USA | 28.08N | 97.05W | 8 | -6.00 (NAC) | 96-06 | 722524 | -0.2 | 0 | -4.9 | 42.4 | 33.8 | 33.9 | 34.9 | 34 | 34.2 | 34 | 32.8 | 32.9 | 33.9 | 33 | 33.2 | 33 | 910 | United_StatesTexasROCKPORT/ARANSAS CO
United_States | Texas | M2 | SABINE | SABINE, TX, USA | 29.67N | 94.05W | 6 | -6.00 (NAC) | 85-06 | 994260 | -2.9 | -3 | -10.6 | 37.5 | 31.4 | 31.8 | 32.9 | 32 | 32.0333 | 32 | 30.1 | 30.7 | 31.4 | 31 | 30.7333 | 31 | 911 | United_StatesTexasSABINE
United_States | Texas | M2 | SAN ANGELO MATHIS FIELD | SAN ANGELO MATHIS FIELD, TX, USA | 31.35N | 100.49W | 577 | -6.00 (NAC) | 82-06 | 722630 | -10.2 | -10 | -20 | 44.3 | 39.3 | 39.7 | 38.6 | 39 | 39.2 | 40 | 36.9 | 37.8 | 37.3 | 37 | 37.3333 | 37 | 912 | United_StatesTexasSAN ANGELO MATHIS FIELD
United_States | Texas | M2 | SAN ANTONIO INTL AP | SAN ANTONIO INTL AP, TX, USA | 29.53N | 98.46W | 247 | -6.00 (NAC) | 82-06 | 722530 | -5.8 | -6 | -14.1 | 42.8 | 37.3 | 38 | 37.9 | 38 | 37.7333 | 38 | 35.7 | 36.8 | 36.9 | 36 | 36.4667 | 36 | 913 | United_StatesTexasSAN ANTONIO INTL AP
United_States | Texas | M2 | SAN ANTONIO/STINSON | SAN ANTONIO/STINSON, TX, USA | 29.34N | 98.47W | 176 | -6.00 (NAC) | 98-06 | 722523 | -3.8 | -4 | -7.9 | 43.8 | 38.7 | 38.9 | 38.7 | 39 | 38.7667 | 39 | 36.4 | 37.7 | 37.6 | 37 | 37.2333 | 37 | 914 | United_StatesTexasSAN ANTONIO/STINSON
United_States | Texas | M2 | SAN MARCOS MUNI | SAN MARCOS MUNI, TX, USA | 29.88N | 97.87W | 182 | -6.00 (NAC) | 92-06 | 722539 | -5.1 | -5 | -9.2 | 44.2 | 37.4 | 37.7 | 38 | 38 | 37.7 | 38 | 35.8 | 37.1 | 37.3 | 37 | 36.7333 | 37 | 915 | United_StatesTexasSAN MARCOS MUNI
United_States | Texas | M2 | SANDERSON (RAMOS) | SANDERSON (RAMOS), TX, USA | 30.17N | 102.42W | 865 | -6.00 (NAC) | 82-96 | 747300 | -8.2 | -8 | -19.4 | 44.5 | 39.9 | 39 | 36.7 | 39 | 38.5333 | 39 | 36.8 | 36.5 | 35.4 | 36 | 36.2333 | 36 | 916 | United_StatesTexasSANDERSON (RAMOS)
United_States | Texas | M2 | STEPHENVILLE CLARK FIELD | STEPHENVILLE CLARK FIELD, TX, USA | 32.22N | 98.18W | 403 | -6.00 (NAC) | 84-06 | 722600 | -10.2 | -10 | -22.5 | 41.9 | 36.3 | 37.7 | 37.9 | 37 | 37.3 | 38 | 34.2 | 36.1 | 36.9 | 36 | 35.7333 | 36 | 917 | United_StatesTexasSTEPHENVILLE CLARK FIELD
United_States | Texas | M1 | VICTORIA REGIONAL AP | VICTORIA REGIONAL AP, TX, USA | 28.86N | 96.93W | 36 | -6.00 (NAC) | 82-06 | 722550 | -4.2 | -4 | -12.3 | 42.1 | 35.7 | 36.8 | 37.4 | 37 | 36.6333 | 37 | 34.4 | 35.6 | 36 | 35 | 35.3333 | 35 | 918 | United_StatesTexasVICTORIA REGIONAL AP
United_States | Texas | M2 | WACO REGIONAL AP | WACO REGIONAL AP, TX, USA | 31.61N | 97.23W | 155 | -6.00 (NAC) | 82-06 | 722560 | -8 | -8 | -18.2 | 44.3 | 37.7 | 39.3 | 39.9 | 39 | 38.9667 | 39 | 35.9 | 38 | 38.4 | 37 | 37.4333 | 37 | 919 | United_StatesTexasWACO REGIONAL AP
United_States | Texas | M3 | WICHITA FALLS MUNICIPAL ARPT | WICHITA FALLS MUNICIPAL ARPT, TX, USA | 33.98N | 98.49W | 314 | -6.00 (NAC) | 82-06 | 723510 | -12.2 | -12 | -22.4 | 45.1 | 38.8 | 41.2 | 40.7 | 40 | 40.2333 | 41 | 36.5 | 39.4 | 39.1 | 38 | 38.3333 | 38 | 920 | United_StatesTexasWICHITA FALLS MUNICIPAL ARPT
United_States | Texas | M2 | WINK WINKLER COUNTY AP | WINK WINKLER COUNTY AP, TX, USA | 31.78N | 103.20W | 860 | -6.00 (NAC) | 88-06 | 722656 | -11 | -11 | -17.5 | 47.8 | 42.6 | 42.2 | 41.3 | 42 | 42.0333 | 42 | 40.7 | 39.9 | 38.3 | 40 | 39.6333 | 40 | 921 | United_StatesTexasWINK WINKLER COUNTY AP
United_States | Utah | M3 | CEDAR CITY MUNICIPAL AP | CEDAR CITY MUNICIPAL AP, UT, USA | 37.70N | 113.10W | 1712 | -7.00 (NAM) | 82-06 | 724755 | -20.9 | -21 | -31.8 | 39.7 | 34.7 | 36.5 | 34.7 | 35 | 35.3 | 37 | 32.9 | 34.8 | 33.2 | 34 | 33.6333 | 34 | 922 | United_StatesUtahCEDAR CITY MUNICIPAL AP
United_States | Utah | M3 | HILL AFB/OGDEN | HILL AFB/OGDEN, UT, USA | 41.12N | 111.97W | 1459 | -7.00 (NAM) | 82-06 | 725755 | -16.1 | -16 | -24.5 | 40.8 | 35 | 37.1 | 35 | 36 | 35.7 | 37 | 32.1 | 34.9 | 33.3 | 33 | 33.4333 | 33 | 923 | United_StatesUtahHILL AFB/OGDEN
United_States | Utah | M3 | LOGAN-CACHE AIRPORT | LOGAN-CACHE AIRPORT, UT, USA | 41.79N | 111.85W | 1358 | -7.00 (NAM) | 98-06 | 724796 | -23.6 | -24 | -37.1 | 41.1 | 33.8 | 37.6 | 36.1 | 36 | 35.8333 | 38 | 32.2 | 36.2 | 33.9 | 34 | 34.1 | 34 | 924 | United_StatesUtahLOGAN-CACHE AIRPORT
United_States | Utah | M3 | MILFORD MUNICIPAL AP | MILFORD MUNICIPAL AP, UT, USA | 38.44N | 113.03W | 1534 | -7.00 (NAM) | 82-06 | 724797 | -22.1 | -22 | -33 | 41.8 | 36.1 | 38.7 | 36.3 | 37 | 37.0333 | 39 | 34 | 37.1 | 34.4 | 35 | 35.1667 | 35 | 925 | United_StatesUtahMILFORD MUNICIPAL AP
United_States | Utah | M3 | PRICE/CARBON COUNTY | PRICE/CARBON COUNTY, UT, USA | 39.62N | 110.75W | 1799 | -7.00 (NAM) | 82-06 | 724700 | -18.7 | -19 | -28.4 | 38.8 | 34.1 | 36.4 | 33.9 | 35 | 34.8 | 36 | 32.4 | 34.3 | 32.4 | 33 | 33.0333 | 33 | 926 | United_StatesUtahPRICE/CARBON COUNTY
United_States | Utah | M3 | PROVO MUNI (AWOS) | PROVO MUNI (AWOS), UT, USA | 40.22N | 111.72W | 1369 | -7.00 (NAM) | 92-06 | 725724 | -15 | -15 | -26.9 | 41.5 | 35.2 | 37.7 | 35.3 | 36 | 36.0667 | 38 | 32.7 | 36 | 33.1 | 34 | 33.9333 | 34 | 927 | United_StatesUtahPROVO MUNI (AWOS)
United_States | Utah | M3 | SAINT GEORGE (AWOS) | SAINT GEORGE (AWOS), UT, USA | 37.08N | 113.60W | 896 | -7.00 (NAM) | 92-06 | 724754 | -5.8 | -6 | -8.9 | 46.4 | 42 | 43.7 | 42.1 | 43 | 42.6 | 44 | 39.1 | 42.1 | 40.9 | 41 | 40.7 | 41 | 928 | United_StatesUtahSAINT GEORGE (AWOS)
United_States | Utah | M3 | SALT LAKE CITY INT'L ARPT | SALT LAKE CITY INT'L ARPT, UT, USA | 40.79N | 111.97W | 1288 | -7.00 (NAM) | 82-06 | 725720 | -16.3 | -16 | -27.3 | 42.6 | 36.8 | 38.7 | 37.2 | 38 | 37.5667 | 39 | 34.5 | 37.1 | 35.4 | 36 | 35.6667 | 36 | 929 | United_StatesUtahSALT LAKE CITY INT'L ARPT
United_States | Utah | M3 | VERNAL | VERNAL, UT, USA | 40.43N | 109.52W | 1608 | -7.00 (NAM) | 98-06 | 725705 | -20.2 | -20 | -29.5 | 39.4 | 34.1 | 37 | 33.9 | 35 | 35 | 37 | 32.4 | 35.2 | 32.5 | 33 | 33.3667 | 33 | 930 | United_StatesUtahVERNAL
United_States | Utah | M3 | WENDOVER USAF AUXILIARY FIELD | WENDOVER USAF AUXILIARY FIELD, UT, USA | 40.72N | 114.02W | 1291 | -7.00 (NAM) | 82-06 | 725810 | -16.1 | -16 | -27.5 | 41.8 | 36.3 | 38 | 36.4 | 37 | 36.9 | 38 | 33.8 | 36.5 | 34.8 | 35 | 35.0333 | 35 | 931 | United_StatesUtahWENDOVER USAF AUXILIARY FIELD
United_States | Vermont | E5 | BURLINGTON INTERNATIONAL AP | BURLINGTON INTERNATIONAL AP, VT, USA | 44.47N | 73.15W | 104 | -5.00 (NAE) | 82-06 | 726170 | -26.1 | -26 | -35.8 | 38.8 | 33 | 33.7 | 32.7 | 33 | 33.1333 | 34 | 30.5 | 31.3 | 30.4 | 31 | 30.7333 | 31 | 932 | United_StatesVermontBURLINGTON INTERNATIONAL AP
United_States | Vermont | E5 | MONTPELIER AP | MONTPELIER AP, VT, USA | 44.20N | 72.58W | 342 | -5.00 (NAE) | 82-06 | 726145 | -27.9 | -28 | -36.8 | 37.2 | 31.3 | 31.7 | 30.8 | 31 | 31.2667 | 32 | 28.9 | 29.5 | 28.5 | 29 | 28.9667 | 29 | 933 | United_StatesVermontMONTPELIER AP
United_States | Vermont | E5 | MORRISVILLE\STONE | MORRISVILLE\STONE, VT, USA | 44.53N | 72.62W | 223 | -5.00 (NAE) | 97-06 | 726114 | -28.3 | -28 | -39 | 37.8 | 32.4 | 31.4 | 32.2 | 32 | 32 | 31 | 29.2 | 29.1 | 29 | 29 | 29.1 | 29 | 934 | United_StatesVermontMORRISVILLE\STONE
United_States | Vermont | E5 | RUTLAND STATE | RUTLAND STATE, VT, USA | 43.52N | 72.95W | 246 | -5.00 (NAE) | 92-06 | 725165 | -25.8 | -26 | -36.8 | 36.2 | 31.3 | 31.3 | 31.2 | 31 | 31.2667 | 31 | 28.8 | 29.1 | 28.7 | 29 | 28.8667 | 29 | 935 | United_StatesVermontRUTLAND STATE
United_States | Vermont | E5 | SPRINGFIELD/HARTNES | SPRINGFIELD/HARTNES, VT, USA | 43.35N | 72.52W | 176 | -5.00 (NAE) | 96-06 | 726115 | -24.5 | -25 | -33.6 | 40.9 | 32.5 | 32.8 | 32.7 | 33 | 32.6667 | 33 | 30.9 | 31.2 | 30 | 31 | 30.7 | 31 | 936 | United_StatesVermontSPRINGFIELD/HARTNES
United_States | Virginia | E3 | ABINGTON | ABINGTON, VA, USA | 36.68N | 82.03W | 631 | -5.00 (NAE) | 95-06 | 724058 | -15.8 | -16 | -24.4 | 35 | 32.2 | 32.4 | 33.7 | 33 | 32.7667 | 32 | 30.9 | 31.1 | 32.2 | 31 | 31.4 | 31 | 937 | United_StatesVirginiaABINGTON
United_States | Virginia | E3 | CHESAPEAKE | CHESAPEAKE, VA, USA | 36.90N | 75.72W | 23 | -5.00 (NAE) | 89-06 | 994020 | -7.7 | -8 | -15 | 33.9 | 28.9 | 30.7 | 30.2 | 30 | 29.9333 | 31 | 27.1 | 29.3 | 28.6 | 28 | 28.3333 | 28 | 938 | United_StatesVirginiaCHESAPEAKE
United_States | Virginia | E3 | DANVILLE FAA AP | DANVILLE FAA AP, VA, USA | 36.57N | 79.34W | 180 | -5.00 (NAE) | 94-06 | 724106 | -11.8 | -12 | -19 | 40.6 | 34.2 | 36.2 | 36 | 35 | 35.4667 | 36 | 32.6 | 34 | 34 | 34 | 33.5333 | 34 | 939 | United_StatesVirginiaDANVILLE FAA AP
United_States | Virginia | E3 | DINWIDDIE CO | DINWIDDIE CO, VA, USA | 37.18N | 77.50W | 60 | -5.00 (NAE) | 92-06 | 724014 | -14.3 | -14 | -22.7 | 43.2 | 37.2 | 38 | 37.6 | 38 | 37.6 | 38 | 35 | 36.9 | 36.1 | 36 | 36 | 36 | 940 | United_StatesVirginiaDINWIDDIE CO
United_States | Virginia | E3 | FARMVILLE | FARMVILLE, VA, USA | 37.35N | 78.43W | 125 | -5.00 (NAE) | 94-06 | 724017 | -16 | -16 | -27.1 | 41.1 | 34.7 | 37 | 37.1 | 36 | 36.2667 | 37 | 32.9 | 34.9 | 34.9 | 34 | 34.2333 | 34 | 941 | United_StatesVirginiaFARMVILLE
United_States | Virginia | E3 | FORT BELVOIR/DAVISO | FORT BELVOIR/DAVISO, VA, USA | 38.72N | 77.18W | 27 | -5.00 (NAE) | 82-01 | 724037 | -16.5 | -17 | -27.6 | 42.1 | 36.1 | 37.8 | 37.2 | 37 | 37.0333 | 38 | 33.9 | 36 | 34.7 | 35 | 34.8667 | 35 | 942 | United_StatesVirginiaFORT BELVOIR/DAVISO
United_States | Virginia | E3 | HILLSVILLE | HILLSVILLE, VA, USA | 36.77N | 80.82W | 834 | -5.00 (NAE) | 95-06 | 724107 | -14.5 | -15 | -19.6 | 35 | 29.9 | 31.4 | 31.3 | 31 | 30.8667 | 31 | 28 | 29.1 | 29.5 | 29 | 28.8667 | 29 | 943 | United_StatesVirginiaHILLSVILLE
United_States | Virginia | E3 | HOT SPRINGS/INGALLS | HOT SPRINGS/INGALLS, VA, USA | 37.95N | 79.83W | 1156 | -5.00 (NAE) | 94-06 | 724115 | -19.3 | -19 | -28.5 | 35.2 | 27.9 | 30.5 | 29.7 | 29 | 29.3667 | 31 | 26.6 | 28.5 | 27.8 | 28 | 27.6333 | 28 | 944 | United_StatesVirginiaHOT SPRINGS/INGALLS
United_States | Virginia | E3 | LANGLEY AFB/HAMPTON | LANGLEY AFB/HAMPTON, VA, USA | 37.08N | 76.37W | 3 | -5.00 (NAE) | 82-06 | 745980 | -10.2 | -10 | -18.5 | 40 | 34.4 | 36 | 35.1 | 35 | 35.1667 | 36 | 32.6 | 34.1 | 32.9 | 33 | 33.2 | 33 | 945 | United_StatesVirginiaLANGLEY AFB/HAMPTON
United_States | Virginia | E3 | LEESBURG/GODFREY | LEESBURG/GODFREY, VA, USA | 39.08N | 77.57W | 119 | -5.00 (NAE) | 95-06 | 724055 | -14.4 | -14 | -19.6 | 39.7 | 35 | 37.1 | 37.1 | 36 | 36.4 | 37 | 33.2 | 35 | 34.8 | 34 | 34.3333 | 34 | 946 | United_StatesVirginiaLEESBURG/GODFREY
United_States | Virginia | E3 | LYNCHBURG REGIONAL ARPT | LYNCHBURG REGIONAL ARPT, VA, USA | 37.34N | 79.21W | 286 | -5.00 (NAE) | 82-06 | 724100 | -15.1 | -15 | -24.5 | 39.3 | 33.3 | 35.2 | 35.1 | 35 | 34.5333 | 35 | 31.8 | 33.7 | 33 | 33 | 32.8333 | 33 | 947 | United_StatesVirginiaLYNCHBURG REGIONAL ARPT
United_States | Virginia | E3 | MANASSAS MUNI(AWOS) | MANASSAS MUNI(AWOS), VA, USA | 38.72N | 77.52W | 59 | -5.00 (NAE) | 92-06 | 724036 | -16.4 | -16 | -25.7 | 39.5 | 33.9 | 35.9 | 35.8 | 35 | 35.2 | 36 | 32.4 | 33.8 | 33.7 | 33 | 33.3 | 33 | 948 | United_StatesVirginiaMANASSAS MUNI(AWOS)
United_States | Virginia | E3 | MARION / WYTHEVILLE | MARION / WYTHEVILLE, VA, USA | 36.90N | 81.35W | 780 | -5.00 (NAE) | 95-06 | 724056 | -17.1 | -17 | -26.4 | 38.2 | 32.3 | 33 | 32.9 | 33 | 32.7333 | 33 | 30.3 | 32.1 | 32.1 | 32 | 31.5 | 32 | 949 | United_StatesVirginiaMARION / WYTHEVILLE
United_States | Virginia | E3 | MARTINSVILLE | MARTINSVILLE, VA, USA | 36.63N | 80.02W | 287 | -5.00 (NAE) | 95-06 | 745985 | -14.8 | -15 | -23.2 | 39.6 | 35.2 | 36.2 | 36.3 | 36 | 35.9 | 36 | 32.9 | 34.1 | 34.1 | 34 | 33.7 | 34 | 950 | United_StatesVirginiaMARTINSVILLE
United_States | Virginia | E3 | MECKLENBURG\BRUNS. | MECKLENBURG\BRUNS., VA, USA | 36.70N | 78.05W | 430 | -5.00 (NAE) | 97-06 | 724118 | -15 | N/A | N/A | N/A | 35.3 | 37.3 | 37 | 37 | 36.5333 | 37 | 33 | 35.1 | 34.9 | 34 | 34.3333 | 34 | 951 | United_StatesVirginiaMECKLENBURG\BRUNS.
United_States | Virginia | E3 | MELFA/ACCOMACK ARPT | MELFA/ACCOMACK ARPT, VA, USA | 37.65N | 75.77W | 15 | -5.00 (NAE) | 82-06 | 724026 | -11 | N/A | N/A | N/A | 35 | 36.4 | 35.2 | 36 | 35.5333 | 36 | 32.9 | 34.3 | 33.7 | 34 | 33.6333 | 34 | 952 | United_StatesVirginiaMELFA/ACCOMACK ARPT
United_States | Virginia | E3 | NEWPORT NEWS | NEWPORT NEWS, VA, USA | 37.13N | 76.49W | 16 | -5.00 (NAE) | 82-06 | 723086 | -11.4 | -11 | -19.4 | 42.4 | 35.1 | 36.9 | 36.1 | 36 | 36.0333 | 37 | 33.1 | 35.1 | 33.8 | 34 | 34 | 34 | 953 | United_StatesVirginiaNEWPORT NEWS
United_States | Virginia | E3 | NORFOLK INTERNATIONAL AP | NORFOLK INTERNATIONAL AP, VA, USA | 36.90N | 76.19W | 9 | -5.00 (NAE) | 82-06 | 723080 | -9.1 | -9 | -18.1 | 39.9 | 35 | 36.4 | 35.3 | 36 | 35.5667 | 36 | 33.1 | 34.6 | 33.4 | 34 | 33.7 | 34 | 954 | United_StatesVirginiaNORFOLK INTERNATIONAL AP
United_States | Virginia | E3 | NORFOLK NAS | NORFOLK NAS, VA, USA | 36.93N | 76.28W | 5 | -5.00 (NAE) | 82-06 | 723085 | -8.5 | -9 | -17.4 | 40.2 | 35 | 36.7 | 35.9 | 36 | 35.8667 | 37 | 32.9 | 34.9 | 33.3 | 34 | 33.7 | 34 | 955 | United_StatesVirginiaNORFOLK NAS
United_States | Virginia | E3 | OCEANA NAS | OCEANA NAS, VA, USA | 36.82N | 76.03W | 7 | -5.00 (NAE) | 82-06 | 723075 | -9.5 | -10 | -17.7 | 39.3 | 34.1 | 35.9 | 34.9 | 35 | 34.9667 | 36 | 32.4 | 34.1 | 32.9 | 33 | 33.1333 | 33 | 956 | United_StatesVirginiaOCEANA NAS
United_States | Virginia | E3 | QUANTICO MCAS | QUANTICO MCAS, VA, USA | 38.50N | 77.30W | 4 | -5.00 (NAE) | 84-06 | 724035 | -13.1 | -13 | -22.8 | 40.7 | 34.3 | 36.2 | 34.8 | 35 | 35.1 | 36 | 32.3 | 34 | 32.9 | 33 | 33.0667 | 33 | 957 | United_StatesVirginiaQUANTICO MCAS
United_States | Virginia | E3 | ROANOKE REGIONAL AP | ROANOKE REGIONAL AP, VA, USA | 37.32N | 79.97W | 358 | -5.00 (NAE) | 82-06 | 724110 | -14.3 | -14 | -24 | 40.4 | 33.5 | 35.7 | 35.3 | 35 | 34.8333 | 36 | 31.8 | 33.6 | 33.1 | 33 | 32.8333 | 33 | 958 | United_StatesVirginiaROANOKE REGIONAL AP
United_States | Virginia | E3 | SHANNON ARPT | SHANNON ARPT, VA, USA | 38.27N | 77.45W | 26 | -5.00 (NAE) | 94-06 | 724033 | -14.8 | -15 | -25.3 | 40.5 | 35.2 | 37.2 | 37.4 | 37 | 36.6 | 37 | 33.3 | 34.9 | 35.7 | 35 | 34.6333 | 35 | 959 | United_StatesVirginiaSHANNON ARPT
United_States | Virginia | E3 | STAUNTON/SHENANDOAH | STAUNTON/SHENANDOAH, VA, USA | 38.27N | 78.90W | 366 | -5.00 (NAE) | 94-06 | 724105 | -16.5 | -17 | -27.1 | 40.3 | 34.1 | 37.1 | 36.1 | 36 | 35.7667 | 37 | 32.7 | 34.1 | 34 | 34 | 33.6 | 34 | 960 | United_StatesVirginiaSTAUNTON/SHENANDOAH
United_States | Virginia | E3 | VIRGINIA TECH ARPT | VIRGINIA TECH ARPT, VA, USA | 37.22N | 80.42W | 650 | -5.00 (NAE) | 94-06 | 724113 | -15.3 | -15 | -21.1 | 35.6 | 31.3 | 32.7 | 32.8 | 32 | 32.2667 | 33 | 29.8 | 31.2 | 31.4 | 31 | 30.8 | 31 | 961 | United_StatesVirginiaVIRGINIA TECH ARPT
United_States | Virginia | E3 | WALLOPS ISLAND UAU | WALLOPS ISLAND UAU, VA, USA | 37.94N | 75.50W | 15 | -5.00 (NAE) | 96-06 | 724020 | -11 | -11 | -19.7 | 37.8 | 33.4 | 34.6 | 33.9 | 34 | 33.9667 | 35 | 31.4 | 32.6 | 32.1 | 32 | 32.0333 | 32 | 962 | United_StatesVirginiaWALLOPS ISLAND UAU
United_States | Virginia | E3 | WASHINGTON DC DULLES INT'L AR | WASHINGTON DC DULLES INT'L AR, VA, USA | 38.94N | 77.45W | 99 | -5.00 (NAE) | 82-06 | 724030 | -17.2 | -17 | -29 | 41.1 | 34.3 | 36.1 | 35.8 | 35 | 35.4 | 36 | 32.4 | 34.3 | 33.8 | 34 | 33.5 | 34 | 963 | United_StatesVirginiaWASHINGTON DC DULLES INT'L AR
United_States | Virginia | E3 | WASHINGTON DC REAGAN AP | WASHINGTON DC REAGAN AP, VA, USA | 38.87N | 77.03W | 20 | -5.00 (NAE) | 82-06 | 724050 | -12.3 | -12 | -22.2 | 40.9 | 35.4 | 36.8 | 36 | 36 | 36.0667 | 37 | 33 | 35 | 34 | 34 | 34 | 34 | 964 | United_StatesVirginiaWASHINGTON DC REAGAN AP
United_States | Virginia | E3 | WINCHESTER RGNL | WINCHESTER RGNL, VA, USA | 39.15N | 78.15W | 222 | -5.00 (NAE) | 95-06 | 724053 | -14.5 | -15 | -22.2 | 49.6 | 34.7 | 37.2 | 36.3 | 36 | 36.0667 | 37 | 32.5 | 34.7 | 33.6 | 34 | 33.6 | 34 | 965 | United_StatesVirginiaWINCHESTER RGNL
United_States | Virginia | E3 | WISE/LONESOME PINE | WISE/LONESOME PINE, VA, USA | 36.98N | 82.53W | 817 | -5.00 (NAE) | 94-06 | 724117 | -15 | N/A | N/A | N/A | 30 | 31.3 | 31.3 | 31 | 30.8667 | 31 | 28.1 | 29.8 | 29.8 | 29 | 29.2333 | 29 | 966 | United_StatesVirginiaWISE/LONESOME PINE
United_States | Washington | W3 | ARLINGTON MUNI | ARLINGTON MUNI, WA, USA | 48.17N | 122.17W | 42 | -8.00 (NAP) | 92-06 | 727945 | -8.8 | -9 | -17 | 37 | 28 | 32.3 | 29.2 | 30 | 29.8333 | 32 | 25.8 | 28.6 | 27.5 | 27 | 27.3 | 27 | 967 | United_StatesWashingtonARLINGTON MUNI
United_States | Washington | W3 | BELLINGHAM INTL AP | BELLINGHAM INTL AP, WA, USA | 48.79N | 122.54W | 46 | -8.00 (NAP) | 82-06 | 727976 | -10.1 | -10 | -20 | 34.8 | 27.6 | 28.9 | 28 | 28 | 28.1667 | 29 | 24.6 | 26.3 | 26 | 26 | 25.6333 | 26 | 968 | United_StatesWashingtonBELLINGHAM INTL AP
United_States | Washington | W3 | BREMERTON NATIONAL | BREMERTON NATIONAL, WA, USA | 47.48N | 122.75W | 137 | -8.00 (NAP) | 89-06 | 727928 | -7.5 | -8 | -16.2 | 39.1 | 31.7 | 34 | 31.5 | 32 | 32.4 | 34 | 27.6 | 30.1 | 28.9 | 29 | 28.8667 | 29 | 969 | United_StatesWashingtonBREMERTON NATIONAL
United_States | Washington | W3 | DESTRUCTION ISLAND | DESTRUCTION ISLAND, WA, USA | 47.67N | 124.48W | 39 | -8.00 (NAP) | 85-06 | 994070 | -1.5 | -2 | -8.6 | 26.6 | 20.1 | 19.1 | 19.5 | 20 | 19.5667 | 19 | 17.1 | 17.3 | 17.8 | 17 | 17.4 | 17 | 970 | United_StatesWashingtonDESTRUCTION ISLAND
United_States | Washington | W3 | FAIRCHILD AFB | FAIRCHILD AFB, WA, USA | 47.62N | 117.65W | 743 | -8.00 (NAP) | 82-06 | 727855 | -18.7 | -19 | -30.8 | 40.9 | 32.6 | 36.4 | 35.1 | 35 | 34.7 | 36 | 29.4 | 33.8 | 32.8 | 32 | 32 | 32 | 971 | United_StatesWashingtonFAIRCHILD AFB
United_States | Washington | W3 | FELTS FLD | FELTS FLD, WA, USA | 47.68N | 117.32W | 610 | -8.00 (NAP) | 82-06 | 727856 | -17 | -17 | -28.8 | 41.5 | 34.3 | 37.5 | 36.8 | 36 | 36.2 | 38 | 31.4 | 35.1 | 34.5 | 34 | 33.6667 | 34 | 972 | United_StatesWashingtonFELTS FLD
United_States | Washington | W3 | FRIDAY HARBOR | FRIDAY HARBOR, WA, USA | 48.52N | 123.02W | 33 | -8.00 (NAP) | 99-06 | 727985 | -5.4 | -5 | -13.1 | 36.5 | 28 | 29.1 | 27.3 | 28 | 28.1333 | 29 | 24.1 | 26.3 | 24.8 | 25 | 25.0667 | 25 | 973 | United_StatesWashingtonFRIDAY HARBOR
United_States | Washington | W3 | GRAY AAF | GRAY AAF, WA, USA | 47.08N | 122.58W | 92 | -8.00 (NAP) | 82-06 | 742071 | -10 | -10 | -19.7 | 39.2 | 31.6 | 34.1 | 32.2 | 33 | 32.6333 | 34 | 27.1 | 30.4 | 29.7 | 29 | 29.0667 | 29 | 974 | United_StatesWashingtonGRAY AAF
United_States | Washington | W3 | HANFORD | HANFORD, WA, USA | 46.57N | 119.60W | 223 | -8.00 (NAP) | 82-95 | 727840 | -16 | -16 | -29.3 | 45.5 | 39.6 | 40.7 | 39.4 | 40 | 39.9 | 41 | 36 | 38 | 37.6 | 37 | 37.2 | 37 | 975 | United_StatesWashingtonHANFORD
United_States | Washington | W3 | HOQUIAM AP | HOQUIAM AP, WA, USA | 46.97N | 123.94W | 5 | -8.00 (NAP) | 82-06 | 727923 | -4.3 | -4 | -10.6 | 35 | 28 | 28 | 27.4 | 28 | 27.8 | 28 | 21.7 | 24 | 23 | 23 | 22.9 | 23 | 976 | United_StatesWashingtonHOQUIAM AP
United_States | Washington | W3 | KELSO WB AP | KELSO WB AP, WA, USA | 46.12N | 122.89W | 6 | -8.00 (NAP) | 90-06 | 727924 | -7.7 | -8 | -15.8 | 41.4 | 32 | 35.1 | 32.9 | 33 | 33.3333 | 35 | 27 | 31.2 | 30.2 | 29 | 29.4667 | 29 | 977 | United_StatesWashingtonKELSO WB AP
United_States | Washington | W3 | MC CHORD AFB/TACOMA | MC CHORD AFB/TACOMA, WA, USA | 47.13N | 122.48W | 88 | -8.00 (NAP) | 82-06 | 742060 | -10.3 | -10 | -19.3 | 38.5 | 31.5 | 33.7 | 31.9 | 32 | 32.3667 | 34 | 27.7 | 30.2 | 29.3 | 29 | 29.0667 | 29 | 978 | United_StatesWashingtonMC CHORD AFB/TACOMA
United_States | Washington | W3 | OLYMPIA AIRPORT | OLYMPIA AIRPORT, WA, USA | 46.97N | 122.90W | 61 | -8.00 (NAP) | 82-06 | 727920 | -10.8 | -11 | -21.4 | 40 | 32.3 | 34.6 | 32.6 | 33 | 33.1667 | 35 | 28.3 | 30.8 | 30 | 30 | 29.7 | 30 | 979 | United_StatesWashingtonOLYMPIA AIRPORT
United_States | Washington | W3 | OMAK | OMAK, WA, USA | 48.42N | 119.53W | 382 | -8.00 (NAP) | 98-06 | 727890 | -16 | -16 | -26 | 42.6 | 35.2 | 39.1 | 37.8 | 37 | 37.3667 | 39 | 32.5 | 37.3 | 36.3 | 35 | 35.3667 | 35 | 980 | United_StatesWashingtonOMAK
United_States | Washington | W3 | PASCO | PASCO, WA, USA | 46.27N | 119.12W | 123 | -8.00 (NAP) | 83-06 | 727845 | -16.9 | -17 | -34.1 | 47.6 | 37.6 | 41.3 | 38.9 | 39 | 39.2667 | 41 | 34 | 38.1 | 37 | 36 | 36.3667 | 36 | 981 | United_StatesWashingtonPASCO
United_States | Washington | W3 | PEARSON FLD | PEARSON FLD, WA, USA | 45.62N | 122.65W | 8 | -8.00 (NAP) | 98-06 | 727918 | -7 | -7 | -14.7 | 42.2 | 34.8 | 37 | 34.1 | 35 | 35.3 | 37 | 31 | 32.5 | 32.2 | 32 | 31.9 | 32 | 982 | United_StatesWashingtonPEARSON FLD
United_States | Washington | W3 | PULLMAN/MOSCOW RGNL | PULLMAN/MOSCOW RGNL, WA, USA | 46.75N | 117.12W | 778 | -8.00 (NAP) | 87-06 | 727857 | -18.1 | -18 | -34.4 | 40.7 | 32.7 | 36.2 | 36.2 | 35 | 35.0333 | 36 | 29.3 | 33.7 | 33.7 | 32 | 32.2333 | 32 | 983 | United_StatesWashingtonPULLMAN/MOSCOW RGNL
United_States | Washington | W3 | QUILLAYUTE STATE AIRPORT | QUILLAYUTE STATE AIRPORT, WA, USA | 47.93N | 124.56W | 63 | -8.00 (NAP) | 82-06 | 727970 | -7.4 | -7 | -14.2 | 38 | 29.8 | 29.1 | 29.1 | 29 | 29.3333 | 29 | 23.9 | 25.4 | 25.1 | 25 | 24.8 | 25 | 984 | United_StatesWashingtonQUILLAYUTE STATE AIRPORT
United_States | Washington | W3 | SEATTLE BOEING FIELD | SEATTLE BOEING FIELD, WA, USA | 47.53N | 122.30W | 9 | -8.00 (NAP) | 82-06 | 727935 | -7.3 | -7 | -16.6 | 38.4 | 31.3 | 33.2 | 31.9 | 32 | 32.1333 | 33 | 27.7 | 30.4 | 29.1 | 29 | 29.0667 | 29 | 985 | United_StatesWashingtonSEATTLE BOEING FIELD
United_States | Washington | W3 | SEATTLE SEATTLE-TACOMA INTL A | SEATTLE SEATTLE-TACOMA INTL A, WA, USA | 47.46N | 122.31W | 132 | -8.00 (NAP) | 82-06 | 727930 | -6.3 | -6 | -15.2 | 38.8 | 31.3 | 33.1 | 31.1 | 32 | 31.8333 | 33 | 27.4 | 29.6 | 28.5 | 29 | 28.5 | 29 | 986 | United_StatesWashingtonSEATTLE SEATTLE-TACOMA INTL A
United_States | Washington | W3 | SHELTON/SANDERSON | SHELTON/SANDERSON, WA, USA | 47.24N | 123.15W | 82 | -8.00 (NAP) | 98-06 | 727925 | -7.1 | -7 | -14.5 | 41.2 | 32.4 | 35.3 | 32.4 | 33 | 33.3667 | 35 | 28.7 | 30.5 | 29.9 | 30 | 29.7 | 30 | 987 | United_StatesWashingtonSHELTON/SANDERSON
United_States | Washington | W3 | SMITH ISLAND | SMITH ISLAND, WA, USA | 48.32N | 122.83W | 18 | -8.00 (NAP) | 85-06 | 994180 | -2.9 | -3 | -12.1 | 26.7 | 20.3 | 21.7 | 20.8 | 21 | 20.9333 | 22 | 17.5 | 19 | 18.7 | 18 | 18.4 | 18 | 988 | United_StatesWashingtonSMITH ISLAND
United_States | Washington | W3 | SNOHOMISH CO | SNOHOMISH CO, WA, USA | 47.90N | 122.28W | 189 | -8.00 (NAP) | 98-06 | 727937 | -4.9 | -5 | -11.9 | 34.6 | 27.4 | 30.2 | 27.5 | 28 | 28.3667 | 30 | 24.9 | 27 | 25.2 | 26 | 25.7 | 26 | 989 | United_StatesWashingtonSNOHOMISH CO
United_States | Washington | W3 | SPOKANE INTERNATIONAL AP | SPOKANE INTERNATIONAL AP, WA, USA | 47.62N | 117.53W | 721 | -8.00 (NAP) | 82-06 | 727850 | -20.1 | -20 | -33.1 | 40.3 | 33 | 36.5 | 35.5 | 35 | 35 | 37 | 30 | 34.1 | 33.6 | 33 | 32.5667 | 33 | 990 | United_StatesWashingtonSPOKANE INTERNATIONAL AP
United_States | Washington | W3 | STAMPEDE PASS | STAMPEDE PASS, WA, USA | 47.29N | 121.34W | 1209 | -8.00 (NAP) | 82-06 | 727815 | -15.1 | -15 | -25.5 | 36.4 | 26.6 | 29 | 28.3 | 28 | 27.9667 | 29 | 23 | 26 | 25.8 | 25 | 24.9333 | 25 | 991 | United_StatesWashingtonSTAMPEDE PASS
United_States | Washington | W3 | TACOMA NARROWS | TACOMA NARROWS, WA, USA | 47.27N | 122.57W | 91 | -8.00 (NAP) | 93-06 | 727938 | -3.5 | -4 | -9.2 | 40.6 | 31.3 | 32.9 | 29.1 | 31 | 31.1 | 33 | 27.7 | 29 | 27.4 | 28 | 28.0333 | 28 | 992 | United_StatesWashingtonTACOMA NARROWS
United_States | Washington | W3 | TATOOSH ISLAND | TATOOSH ISLAND, WA, USA | 48.38N | 124.73W | 48 | -8.00 (NAP) | 85-06 | 994300 | -1.6 | -2 | -7.6 | 26.4 | 19.6 | 19 | 18.9 | 19 | 19.1667 | 19 | 16 | 16.8 | 17 | 17 | 16.6 | 17 | 993 | United_StatesWashingtonTATOOSH ISLAND
United_States | Washington | W3 | WALLA WALLA CITY COUNTY AP | WALLA WALLA CITY COUNTY AP, WA, USA | 46.10N | 118.29W | 367 | -8.00 (NAP) | 82-06 | 727846 | -14.3 | -14 | -32.3 | 45.3 | 36.7 | 40.6 | 38.8 | 39 | 38.7 | 41 | 33.1 | 37.7 | 36.5 | 36 | 35.7667 | 36 | 994 | United_StatesWashingtonWALLA WALLA CITY COUNTY AP
United_States | Washington | W3 | WENATCHEE/PANGBORN | WENATCHEE/PANGBORN, WA, USA | 47.40N | 120.21W | 375 | -8.00 (NAP) | 82-06 | 727825 | -16.2 | -16 | -28.7 | 41.9 | 35.8 | 37.8 | 36.5 | 37 | 36.7 | 38 | 32.2 | 35.8 | 34.6 | 34 | 34.2 | 34 | 995 | United_StatesWashingtonWENATCHEE/PANGBORN
United_States | Washington | W3 | WEST POINT (LS) | WEST POINT (LS), WA, USA | 47.67N | 122.43W | 9 | -8.00 (NAP) | 85-06 | 994350 | -2.8 | -3 | -11.5 | 27.7 | 22.1 | 23.7 | 22.9 | 23 | 22.9 | 24 | 19.9 | 21.5 | 21 | 21 | 20.8 | 21 | 996 | United_StatesWashingtonWEST POINT (LS)
United_States | Washington | W3 | WHIDBEY ISLAND NAS | WHIDBEY ISLAND NAS, WA, USA | 48.35N | 122.65W | 14 | -8.00 (NAP) | 82-06 | 690230 | -8.5 | -9 | -17.1 | 31 | 23.6 | 24.6 | 24 | 24 | 24.0667 | 25 | 20.6 | 22.2 | 22.1 | 22 | 21.6333 | 22 | 997 | United_StatesWashingtonWHIDBEY ISLAND NAS
United_States | Washington | W3 | WILLIAM R FAIRCHILD | WILLIAM R FAIRCHILD, WA, USA | 48.12N | 123.50W | 91 | -8.00 (NAP) | 85-06 | 727885 | -5.9 | -6 | -12.4 | 37.9 | 28.2 | 29.9 | 28.9 | 29 | 29 | 30 | 23.7 | 26.3 | 25.6 | 25 | 25.2 | 25 | 998 | United_StatesWashingtonWILLIAM R FAIRCHILD
United_States | Washington | W3 | YAKIMA AIR TERMINAL | YAKIMA AIR TERMINAL, WA, USA | 46.56N | 120.53W | 325 | -8.00 (NAP) | 82-06 | 727810 | -18 | -18 | -31.6 | 42.3 | 35.8 | 38 | 36.6 | 37 | 36.8 | 38 | 32.6 | 35.9 | 34.7 | 34 | 34.4 | 34 | 999 | United_StatesWashingtonYAKIMA AIR TERMINAL
United_States | West_Virginia | E3 | BECKLEY RALEIGH CO MEM AP | BECKLEY RALEIGH CO MEM AP, WV, USA | 37.80N | 81.13W | 766 | -5.00 (NAE) | 82-06 | 724120 | -19.7 | -20 | -31.3 | 35.4 | 29.4 | 31.2 | 30.9 | 31 | 30.5 | 31 | 27.9 | 29.3 | 29 | 29 | 28.7333 | 29 | 1000 | United_StatesWest_VirginiaBECKLEY RALEIGH CO MEM AP
United_States | West_Virginia | E3 | BLUEFIELD/MERCER CO | BLUEFIELD/MERCER CO, WV, USA | 37.30N | 81.21W | 874 | -5.00 (NAE) | 82-06 | 724125 | -19.4 | -19 | -31.7 | 35.9 | 29.2 | 31.1 | 31.4 | 31 | 30.5667 | 31 | 27.6 | 29.1 | 29.1 | 29 | 28.6 | 29 | 1001 | United_StatesWest_VirginiaBLUEFIELD/MERCER CO
United_States | West_Virginia | E3 | CHARLESTON YEAGER ARPT | CHARLESTON YEAGER ARPT, WV, USA | 38.38N | 81.59W | 299 | -5.00 (NAE) | 82-06 | 724140 | -18 | -18 | -29.9 | 39.4 | 33 | 35 | 34.6 | 34 | 34.2 | 35 | 31.6 | 33 | 32.8 | 32 | 32.4667 | 32 | 1002 | United_StatesWest_VirginiaCHARLESTON YEAGER ARPT
United_States | West_Virginia | E3 | ELKINS ELKINS-RANDOLPH CO ARP | ELKINS ELKINS-RANDOLPH CO ARP, WV, USA | 38.89N | 79.85W | 603 | -5.00 (NAE) | 82-06 | 724170 | -24.2 | -24 | -34 | 37.3 | 30.5 | 32.3 | 32 | 32 | 31.6 | 32 | 29 | 30.4 | 30.3 | 30 | 29.9 | 30 | 1003 | United_StatesWest_VirginiaELKINS ELKINS-RANDOLPH CO ARP
United_States | West_Virginia | E3 | HARRISON MARION RGN | HARRISON MARION RGN, WV, USA | 39.28N | 80.22W | 380 | -5.00 (NAE) | 98-06 | 724175 | -17.2 | -17 | -23.7 | 38 | 32.6 | 32.8 | 32.9 | 33 | 32.7667 | 33 | 31.1 | 31.4 | 32 | 32 | 31.5 | 32 | 1004 | United_StatesWest_VirginiaHARRISON MARION RGN
United_States | West_Virginia | E3 | HUNTINGTON TRI-STATE ARPT | HUNTINGTON TRI-STATE ARPT, WV, USA | 38.38N | 82.56W | 255 | -5.00 (NAE) | 82-06 | 724250 | -18 | -18 | -31 | 40.1 | 33.7 | 35.4 | 35.1 | 35 | 34.7333 | 35 | 31.8 | 33.3 | 33.1 | 33 | 32.7333 | 33 | 1005 | United_StatesWest_VirginiaHUNTINGTON TRI-STATE ARPT
United_States | West_Virginia | E3 | MARTINSBURG EASTERN WV REG AP | MARTINSBURG EASTERN WV REG AP, WV, USA | 39.40N | 77.98W | 163 | -5.00 (NAE) | 82-06 | 724177 | -17.9 | -18 | -29.2 | 41.8 | 34.9 | 37 | 35.5 | 36 | 35.8 | 37 | 32.6 | 34.6 | 33 | 33 | 33.4 | 33 | 1006 | United_StatesWest_VirginiaMARTINSBURG EASTERN WV REG AP
United_States | West_Virginia | E3 | MORGANTOWN HART FIELD | MORGANTOWN HART FIELD, WV, USA | 39.64N | 79.92W | 382 | -5.00 (NAE) | 82-06 | 724176 | -18.5 | -19 | -29.7 | 38.2 | 32.2 | 33.8 | 33.7 | 33 | 33.2333 | 34 | 30.4 | 32.1 | 31.7 | 31 | 31.4 | 31 | 1007 | United_StatesWest_VirginiaMORGANTOWN HART FIELD
United_States | West_Virginia | E3 | PARKERSBURG WOOD COUNTY AP | PARKERSBURG WOOD COUNTY AP, WV, USA | 39.35N | 81.44W | 263 | -5.00 (NAE) | 82-06 | 724273 | -19.3 | -19 | -31.6 | 39.3 | 33.2 | 34.7 | 34.1 | 34 | 34 | 35 | 31.2 | 32.7 | 32.5 | 32 | 32.1333 | 32 | 1008 | United_StatesWest_VirginiaPARKERSBURG WOOD COUNTY AP
United_States | Wisconsin | M4 | ANTIGO\LANG(AWOS) | ANTIGO\LANG(AWOS), WI, USA | 45.15N | 87.15W | 464 | -6.00 (NAC) | 97-06 | 726626 | -26 | N/A | N/A | N/A | 29.1 | 32.6 | 31.2 | 31 | 30.9667 | 33 | 27.7 | 30.8 | 28 | 29 | 28.8333 | 29 | 1009 | United_StatesWisconsinANTIGO\LANG(AWOS)
United_States | Wisconsin | M4 | APPLETON/OUTAGAMIE | APPLETON/OUTAGAMIE, WI, USA | 44.25N | 88.52W | 280 | -6.00 (NAC) | 92-06 | 726457 | -23.9 | -24 | -31.4 | 41.1 | 32.6 | 34.8 | 32.4 | 33 | 33.2667 | 35 | 30.2 | 32.3 | 29.9 | 31 | 30.8 | 31 | 1010 | United_StatesWisconsinAPPLETON/OUTAGAMIE
United_States | Wisconsin | M4 | DEVILS ISLAND | DEVILS ISLAND, WI, USA | 47.08N | 90.73W | 211 | -6.00 (NAC) | 85-06 | 994190 | -23.7 | -24 | -34.3 | 36 | 26.2 | 29.9 | 28.7 | 28 | 28.2667 | 30 | 23.1 | 26.3 | 25.7 | 25 | 25.0333 | 25 | 1011 | United_StatesWisconsinDEVILS ISLAND
United_States | Wisconsin | M4 | EAGLE RIVER UNION | EAGLE RIVER UNION, WI, USA | 45.93N | 89.27W | 500 | -6.00 (NAC) | 97-06 | 726504 | -31.4 | -31 | -36 | 37.1 | 31.1 | 32.2 | 30.3 | 31 | 31.2 | 32 | 27.9 | 29.1 | 27.7 | 28 | 28.2333 | 28 | 1012 | United_StatesWisconsinEAGLE RIVER UNION
United_States | Wisconsin | M4 | EAU CLAIRE COUNTY AP | EAU CLAIRE COUNTY AP, WI, USA | 44.87N | 91.49W | 273 | -6.00 (NAC) | 82-06 | 726435 | -29.5 | -30 | -40.4 | 40.8 | 34.2 | 36 | 33.9 | 35 | 34.7 | 36 | 31.4 | 33 | 31.1 | 32 | 31.8333 | 32 | 1013 | United_StatesWisconsinEAU CLAIRE COUNTY AP
United_States | Wisconsin | M4 | FOND DU LAC CO. | FOND DU LAC CO., WI, USA | 43.77N | 88.49W | 246 | -6.00 (NAC) | 97-06 | 726506 | -23.9 | -24 | -31.9 | 37.5 | 32.4 | 33.8 | 32.5 | 33 | 32.9 | 34 | 30.1 | 32.2 | 30 | 31 | 30.7667 | 31 | 1014 | United_StatesWisconsinFOND DU LAC CO.
United_States | Wisconsin | M4 | GREEN BAY AUSTIN STRAUBEL INT | GREEN BAY AUSTIN STRAUBEL INT, WI, USA | 44.51N | 88.12W | 214 | -6.00 (NAC) | 82-06 | 726450 | -27 | -27 | -36.5 | 39.3 | 33.4 | 34.2 | 32.7 | 33 | 33.4333 | 34 | 30.7 | 31.5 | 29.9 | 31 | 30.7 | 31 | 1015 | United_StatesWisconsinGREEN BAY AUSTIN STRAUBEL INT
United_States | Wisconsin | M4 | HAYWARD MUNI ARPT | HAYWARD MUNI ARPT, WI, USA | 46.03N | 91.45W | 370 | -6.00 (NAC) | 97-06 | 726508 | -32.1 | -32 | -38 | 42.5 | 32.1 | 36.2 | 32.4 | 34 | 33.5667 | 36 | 28.9 | 32.5 | 29.2 | 30 | 30.2 | 30 | 1016 | United_StatesWisconsinHAYWARD MUNI ARPT
United_States | Wisconsin | M4 | JUNEAU\DODGE CO | JUNEAU\DODGE CO, WI, USA | 43.43N | 88.70W | 285 | -6.00 (NAC) | 97-06 | 726509 | -23 | -23 | -27.8 | 37.5 | 32.4 | 32.9 | 32.3 | 33 | 32.5333 | 33 | 30.1 | 31.3 | 29.1 | 30 | 30.1667 | 30 | 1017 | United_StatesWisconsinJUNEAU\DODGE CO
United_States | Wisconsin | M4 | KENOSHA RGNL | KENOSHA RGNL, WI, USA | 42.58N | 87.92W | 232 | -6.00 (NAC) | 97-06 | 726505 | -23 | -23 | -30.3 | 41.8 | 32.9 | 35.9 | 33.9 | 34 | 34.2333 | 36 | 31.2 | 32.6 | 31.4 | 32 | 31.7333 | 32 | 1018 | United_StatesWisconsinKENOSHA RGNL
United_States | Wisconsin | M4 | LA CROSSE MUNICIPAL ARPT | LA CROSSE MUNICIPAL ARPT, WI, USA | 43.75N | 91.26W | 200 | -6.00 (NAC) | 82-06 | 726430 | -27.1 | -27 | -38.7 | 42.5 | 35 | 36.3 | 35.2 | 36 | 35.5 | 36 | 32.4 | 33.6 | 32.3 | 33 | 32.7667 | 33 | 1019 | United_StatesWisconsinLA CROSSE MUNICIPAL ARPT
United_States | Wisconsin | M4 | MADISON DANE CO REGIONAL ARPT | MADISON DANE CO REGIONAL ARPT, WI, USA | 43.14N | 89.35W | 264 | -6.00 (NAC) | 82-06 | 726410 | -26.3 | -26 | -36.7 | 39.2 | 33.5 | 34.3 | 33.9 | 34 | 33.9 | 34 | 31.3 | 32.2 | 31.2 | 32 | 31.5667 | 32 | 1020 | United_StatesWisconsinMADISON DANE CO REGIONAL ARPT
United_States | Wisconsin | M4 | MANITOWAC MUNI AWOS | MANITOWAC MUNI AWOS, WI, USA | 44.13N | 87.68W | 198 | -6.00 (NAC) | 92-06 | 726455 | -23.4 | -23 | -33.4 | 40.8 | 31.3 | 32.8 | 31.3 | 32 | 31.8 | 33 | 28 | 30 | 27.9 | 29 | 28.6333 | 29 | 1021 | United_StatesWisconsinMANITOWAC MUNI AWOS
United_States | Wisconsin | M4 | MARSHFIELD MUNI | MARSHFIELD MUNI, WI, USA | 44.63N | 90.18W | 389 | -6.00 (NAC) | 92-06 | 726574 | -27.4 | -27 | -36.4 | 41.1 | 33.4 | 34.8 | 32.2 | 33 | 33.4667 | 35 | 29.8 | 31.3 | 30.1 | 30 | 30.4 | 30 | 1022 | United_StatesWisconsinMARSHFIELD MUNI
United_States | Wisconsin | M4 | MILWAUKEE MITCHELL INTL AP | MILWAUKEE MITCHELL INTL AP, WI, USA | 42.95N | 87.90W | 211 | -6.00 (NAC) | 82-06 | 726400 | -23.5 | -24 | -34.9 | 40.6 | 34.1 | 34.9 | 34.3 | 34 | 34.4333 | 35 | 31.4 | 32.5 | 31.3 | 32 | 31.7333 | 32 | 1023 | United_StatesWisconsinMILWAUKEE MITCHELL INTL AP
United_States | Wisconsin | M4 | MOSINEE/CENTRAL WI | MOSINEE/CENTRAL WI, WI, USA | 44.78N | 89.67W | 389 | -6.00 (NAC) | 82-06 | 726465 | -28.3 | -28 | -37.3 | 39.1 | 31.4 | 33.8 | 31.3 | 32 | 32.1667 | 34 | 29.3 | 31.3 | 28.9 | 30 | 29.8333 | 30 | 1024 | United_StatesWisconsinMOSINEE/CENTRAL WI
United_States | Wisconsin | M4 | PARK FALLS MUNI | PARK FALLS MUNI, WI, USA | 45.93N | 90.45W | 469 | -6.00 (NAC) | 82-96 | 727410 | -32 | N/A | N/A | N/A | 30.8 | 31 | 30.4 | 31 | 30.7333 | 31 | 28.7 | 28.7 | 28.4 | 29 | 28.6 | 29 | 1025 | United_StatesWisconsinPARK FALLS MUNI
United_States | Wisconsin | M4 | PHILLIPS/PRICE CO. | PHILLIPS/PRICE CO., WI, USA | 45.70N | 90.40W | 449 | -6.00 (NAC) | 92-06 | 726468 | -31.8 | -32 | -40.1 | 37.3 | 31.3 | 32.8 | 31.2 | 32 | 31.7667 | 33 | 28.6 | 30.1 | 28.2 | 29 | 28.9667 | 29 | 1026 | United_StatesWisconsinPHILLIPS/PRICE CO.
United_States | Wisconsin | M4 | RHINELANDER ONEIDA | RHINELANDER ONEIDA, WI, USA | 45.63N | 89.47W | 507 | -6.00 (NAC) | 89-06 | 727415 | -30.3 | -30 | -34.8 | 38.5 | 31 | 33.2 | 32 | 32 | 32.0667 | 33 | 28 | 31.2 | 28.1 | 29 | 29.1 | 29 | 1027 | United_StatesWisconsinRHINELANDER ONEIDA
United_States | Wisconsin | M4 | RICE LAKE MUNICIPAL | RICE LAKE MUNICIPAL, WI, USA | 45.48N | 91.72W | 347 | -6.00 (NAC) | 97-06 | 726467 | -29.1 | -29 | -37.7 | 39.4 | 32.1 | 33.8 | 33 | 33 | 32.9667 | 34 | 28.9 | 32.2 | 29.8 | 30 | 30.3 | 30 | 1028 | United_StatesWisconsinRICE LAKE MUNICIPAL
United_States | Wisconsin | M4 | SHEBOYGAN | SHEBOYGAN, WI, USA | 43.75N | 87.68W | 189 | -6.00 (NAC) | 85-06 | 994330 | -22 | -22 | -30.1 | 37.1 | 29.8 | 31.7 | 30.8 | 31 | 30.7667 | 32 | 26.3 | 28.5 | 27.8 | 28 | 27.5333 | 28 | 1029 | United_StatesWisconsinSHEBOYGAN
United_States | Wisconsin | M4 | SHEBOYGAN | SHEBOYGAN, WI, USA | 43.78N | 87.85W | 228 | -6.00 (NAC) | 82-06 | 726425 | -22 | N/A | N/A | N/A | 32.2 | 33.6 | 32.9 | 33 | 32.9 | 34 | 29 | 32 | 29.6 | 30 | 30.2 | 30 | 1030 | United_StatesWisconsinSHEBOYGAN
United_States | Wisconsin | M4 | STURGEON BAY | STURGEON BAY, WI, USA | 44.85N | 87.42W | 221 | -6.00 (NAC) | 92-06 | 726458 | -23.8 | -24 | -34.5 | 38.7 | 30.7 | 32.4 | 31 | 31 | 31.3667 | 32 | 27.8 | 29.9 | 27.7 | 28 | 28.4667 | 28 | 1031 | United_StatesWisconsinSTURGEON BAY
United_States | Wisconsin | M4 | WATERTOWN | WATERTOWN, WI, USA | 43.17N | 88.72W | 254 | -6.00 (NAC) | 95-06 | 726464 | -24.6 | -25 | -32.7 | 38.2 | 32.7 | 33.7 | 32.8 | 33 | 33.0667 | 34 | 31.1 | 32.2 | 31 | 31 | 31.4333 | 31 | 1032 | United_StatesWisconsinWATERTOWN
United_States | Wisconsin | M4 | WAUSAU MUNICIPAL ARPT | WAUSAU MUNICIPAL ARPT, WI, USA | 44.93N | 89.63W | 365 | -6.00 (NAC) | 82-06 | 726463 | -29.3 | -29 | -37.9 | 39.1 | 32.8 | 34.1 | 32.5 | 33 | 33.1333 | 34 | 30.2 | 31.5 | 29.9 | 31 | 30.5333 | 31 | 1033 | United_StatesWisconsinWAUSAU MUNICIPAL ARPT
United_States | Wisconsin | M4 | WISCONSIN RAPIDS | WISCONSIN RAPIDS, WI, USA | 44.35N | 89.83W | 308 | -6.00 (NAC) | 97-06 | 726452 | -27.2 | -27 | -34.5 | 39.9 | 32.2 | 34 | 32.9 | 33 | 33.0333 | 34 | 29.8 | 32.3 | 30.7 | 31 | 30.9333 | 31 | 1034 | United_StatesWisconsinWISCONSIN RAPIDS
United_States | Wisconsin | M4 | WITTMAN RGNL | WITTMAN RGNL, WI, USA | 43.98N | 88.55W | 253 | -6.00 (NAC) | 96-06 | 726456 | -24.2 | -24 | -31.4 | 38.7 | 32.2 | 33.9 | 32.5 | 33 | 32.8667 | 34 | 30 | 32.2 | 29.8 | 31 | 30.6667 | 31 | 1035 | United_StatesWisconsinWITTMAN RGNL
United_States | Wyoming | M4 | BIG PINEY (AMOS) | BIG PINEY (AMOS), WY, USA | 42.58N | 110.11W | 2126 | -7.00 (NAM) | 82-06 | 726710 | -33.4 | -33 | -48.4 | 35.9 | 29.6 | 32.4 | 31.1 | 31 | 31.0333 | 32 | 27.4 | 30.5 | 28.4 | 29 | 28.7667 | 29 | 1036 | United_StatesWyoming BIG PINEY (AMOS)
United_States | Wyoming | M4 | CASPER NATRONA CO INTL AP | CASPER NATRONA CO INTL AP, WY, USA | 42.90N | 106.47W | 1612 | -7.00 (NAM) | 82-06 | 725690 | -28.8 | -29 | -41.5 | 39.8 | 35.1 | 37.1 | 35.3 | 36 | 35.8333 | 37 | 32.7 | 35 | 33.4 | 34 | 33.7 | 34 | 1037 | United_StatesWyoming CASPER NATRONA CO INTL AP
United_States | Wyoming | M4 | CHEYENNE MUNICIPAL ARPT | CHEYENNE MUNICIPAL ARPT, WY, USA | 41.16N | 104.81W | 1872 | -7.00 (NAM) | 82-06 | 725640 | -26 | -26 | -38.3 | 37.8 | 32.6 | 34.4 | 32.5 | 33 | 33.1667 | 34 | 29.8 | 32.5 | 30.7 | 31 | 31 | 31 | 1038 | United_StatesWyoming CHEYENNE MUNICIPAL ARPT
United_States | Wyoming | M4 | CODY MUNI (AWOS) | CODY MUNI (AWOS), WY, USA | 44.52N | 109.02W | 1553 | -7.00 (NAM) | 82-06 | 726700 | -27.9 | -28 | -38.5 | 39.6 | 33.7 | 35.6 | 33.7 | 34 | 34.3333 | 36 | 30.6 | 33 | 32 | 32 | 31.8667 | 32 | 1039 | United_StatesWyoming CODY MUNI (AWOS)
United_States | Wyoming | M4 | GILLETTE/GILLETTE-C | GILLETTE/GILLETTE-C, WY, USA | 44.35N | 105.53W | 1230 | -7.00 (NAM) | 82-06 | 726650 | -27.5 | -28 | -39.2 | 42.6 | 36.1 | 38.2 | 36.6 | 37 | 36.9667 | 38 | 32.9 | 36 | 34.1 | 34 | 34.3333 | 34 | 1040 | United_StatesWyoming GILLETTE/GILLETTE-C
United_States | Wyoming | M4 | JACKSON HOLE | JACKSON HOLE, WY, USA | 43.60N | 110.73W | 2016 | -7.00 (NAM) | 92-06 | 725776 | -30.9 | -31 | -37.8 | 36.2 | 27.5 | 32.3 | 30.9 | 30 | 30.2333 | 32 | 25.5 | 30.2 | 28.4 | 28 | 28.0333 | 28 | 1041 | United_StatesWyoming JACKSON HOLE
United_States | Wyoming | M4 | LANDER HUNT FIELD | LANDER HUNT FIELD, WY, USA | 42.82N | 108.73W | 1694 | -7.00 (NAM) | 82-06 | 725760 | -27.2 | -27 | -39.1 | 39.3 | 34 | 36 | 34.1 | 35 | 34.7 | 36 | 31.3 | 34 | 32.4 | 33 | 32.5667 | 33 | 1042 | United_StatesWyoming LANDER HUNT FIELD
United_States | Wyoming | M4 | LARAMIE GENERAL BREES FIELD | LARAMIE GENERAL BREES FIELD, WY, USA | 41.31N | 105.67W | 2217 | -7.00 (NAM) | 82-06 | 725645 | -30.5 | -31 | -38.7 | 35.6 | 30.6 | 32 | 29.8 | 31 | 30.8 | 32 | 28 | 30.2 | 28 | 29 | 28.7333 | 29 | 1043 | United_StatesWyoming LARAMIE GENERAL BREES FIELD
United_States | Wyoming | M4 | ROCK SPRINGS ARPT | ROCK SPRINGS ARPT, WY, USA | 41.59N | 109.07W | 2056 | -7.00 (NAM) | 82-06 | 725744 | -25.5 | -26 | -35.8 | 37.5 | 31.8 | 33.7 | 31.8 | 32 | 32.4333 | 34 | 29 | 32 | 29.9 | 30 | 30.3 | 30 | 1044 | United_StatesWyoming ROCK SPRINGS ARPT
United_States | Wyoming | M4 | SHERIDAN COUNTY ARPT | SHERIDAN COUNTY ARPT, WY, USA | 44.77N | 106.98W | 1209 | -7.00 (NAM) | 82-06 | 726660 | -29 | -29 | -39.9 | 42.9 | 35.8 | 38 | 37 | 37 | 36.9333 | 38 | 32.1 | 35.8 | 35 | 34 | 34.3 | 34 | 1045 | United_StatesWyoming SHERIDAN COUNTY ARPT
United_States | Wyoming | M4 | WORLAND MUNICIPAL | WORLAND MUNICIPAL, WY, USA | 43.97N | 107.95W | 1283 | -7.00 (NAM) | 82-06 | 726665 | -33.9 | -34 | -49.3 | 43.3 | 37.4 | 38.6 | 36.7 | 38 | 37.5667 | 39 | 34.5 | 36.2 | 34.6 | 35 | 35.1 | 35 | 1046 | United_StatesWyoming WORLAND MUNICIPAL
United_States | Wyoming | M4 | YELLOWSTONE LAKE (RAMOS) | YELLOWSTONE LAKE (RAMOS), WY, USA | 44.54N | 110.42W | 2388 | -7.00 (NAM) | 83-06 | 726664 | -33.3 | -33 | -40.9 | 32.9 | 24.8 | 27.4 | 25.8 | 26 | 26 | 27 | 22.3 | 25.4 | 23.6 | 24 | 23.7667 | 24 | 1047 | United_StatesWyoming YELLOWSTONE LAKE (RAMOS)
Latin_America | Colombia |  | BARRANQUILLA/ERNEST | BARRANQUILLA/ERNEST, Colombia | 10.88N | 74.78W | 30 | -5.00 (SAP) | 82-06 | 800280 | 20.4 |  | 16.8 | 39.6 | 34.9 | 34.2 | 34.6 | 35 | 34.5667 |  | 33.2 | 33 | 33.2 | 33 | 33.1333 |  |  | Latin_AmericaColombiaBARRANQUILLA/ERNEST
Latin_America | Colombia |  | BOGOTA/ELDORADO | BOGOTA/ELDORADO, Colombia | 4.70N | 74.13W | 2546 | -5.00 (SAP) | 82-06 | 802220 | -0.5 |  | -5.6 | 30.5 | 20.4 | 20 | 20.2 | 20 | 20.2 |  | 19.2 | 18.9 | 19.1 | 19 | 19.0667 |  |  | Latin_AmericaColombiaBOGOTA/ELDORADO
Latin_America | Colombia |  | CALI/ALFONSO BONILL | CALI/ALFONSO BONILL, Colombia | 3.55N | 76.38W | 969 | -5.00 (SAP) | 82-06 | 802590 | 13.4 |  | 6.4 | 38.4 | 31.8 | 32 | 33.1 | 32 | 32.3 |  | 30.2 | 30.8 | 31.8 | 31 | 30.9333 |  |  | Latin_AmericaColombiaCALI/ALFONSO BONILL
Latin_America | Colombia |  | CARTAGENA/RAFAEL NU | CARTAGENA/RAFAEL NU, Colombia | 10.45N | 75.52W | 12 | -5.00 (SAP) | 82-06 | 800220 | 19.2 |  | 11.6 | 40 | 33 | 33 | 33 | 33 | 33 |  | 32.1 | 32.1 | 32.1 | 32 | 32.1 |  |  | Latin_AmericaColombiaCARTAGENA/RAFAEL NU
Latin_America | Colombia |  | RIONEGRO/J.M.CORDOV | RIONEGRO/J.M.CORDOV, Colombia | 6.13N | 75.43W | 2142 | -5.00 (SAP) | 87-06 | 801120 | 6.8 |  | -2 | 32.2 | 23.9 | 23.5 | 23.8 | 24 | 23.7333 |  | 23.1 | 23 | 23.1 | 23 | 23.0667 |  |  | Latin_AmericaColombiaRIONEGRO/J.M.CORDOV
Latin_America | Dominican_Republic |  | LAS AMERICAS | LAS AMERICAS, Dominican Republic | 18.43N | 69.67W | 18 | -4.00 (SAZ) | 82-06 | 784850 | 16.8 |  | 14.5 | 37.8 | 32.7 | 33.1 | 33.2 | 33 | 33 |  | 32 | 32.2 | 32.2 | 32 | 32.1333 |  |  | Latin_AmericaDominican_RepublicLAS AMERICAS
Latin_America | Dominican_Republic |  | SANTO DOMINGO | SANTO DOMINGO, Dominican Republic | 18.43N | 69.88W | 14 | -4.00 (SAZ) | 83-06 | 784860 | 18.4 |  | 15.3 | 40.8 | 32.5 | 32.9 | 33.1 | 33 | 32.8333 |  | 31.8 | 32.1 | 32.2 | 32 | 32.0333 |  |  | Latin_AmericaDominican_RepublicSANTO DOMINGO
Latin_America | Guatemala |  | GUATEMALA (AEROPUERTO) | GUATEMALA (AEROPUERTO), Guatemala | 14.58N | 90.52W | 1489 | -6.00 (CAM) | 82-06 | 786410 | 7.6 |  | 2.9 | 33.1 | 26.9 | 26.1 | 26.2 | 26 | 26.4 |  | 25.8 | 25.1 | 25.8 | 26 | 25.5667 |  |  | Latin_AmericaGuatemalaGUATEMALA (AEROPUERTO)
Latin_America | Honduras |  | LA MESA (SAN PEDRO SULA) | LA MESA (SAN PEDRO SULA), Honduras | 15.45N | 87.93W | 31 | -6.00 (CAM) | 82-06 | 787080 | N/A |  | N/A | N/A | 37.1 | 35.5 | 36 | 36 | 36.2 |  | 35.9 | 34.1 | 34.8 | 35 | 34.9333 |  |  | Latin_AmericaHondurasLA MESA (SAN PEDRO SULA)
Latin_America | Honduras |  | TEGUCIGALPA | TEGUCIGALPA, Honduras | 14.05N | 87.22W | 1007 | -6.00 (CAM) | 82-06 | 787200 | 7.5 |  | 3.1 | 37.3 | 31.1 | 29.9 | 30.8 | 31 | 30.6 |  | 29.9 | 28.8 | 29.8 | 30 | 29.5 |  |  | Latin_AmericaHondurasTEGUCIGALPA
Latin_America | Panama |  | MARCOS A GELABERT I | MARCOS A GELABERT I, Panama | 8.97N | 79.55W | 10 | -5.00 (SAP) | 82-99 | 783842 | 20.9 |  | 18.4 | 38.7 | 33.2 | 33.8 | 33.1 | 33 | 33.3667 |  | 32.2 | 32.2 | 32.1 | 32 | 32.1667 |  |  | Latin_AmericaPanamaMARCOS A GELABERT I
Latin_America | Panama |  | TOCUMEN | TOCUMEN, Panama | 9.05N | 79.37W | 45 | -5.00 (SAP) | 82-06 | 787920 | 18.6 |  | 10.1 | 39.1 | 33.2 | 34 | 34 | 34 | 33.7333 |  | 32.2 | 32.8 | 32.8 | 33 | 32.6 |  |  | Latin_AmericaPanamaTOCUMEN
Latin_America | Peru |  | AREQUIPA | AREQUIPA, Peru | 16.33S | 71.57W | 2520 | -5.00 (SAP) | 82-06 | 847520 | 2.2 |  | -3.2 | 29.1 | 24 | 23.8 | 24.1 | 24 | 23.9667 |  | 22.9 | 22.6 | 23.1 | 23 | 22.8667 |  |  | Latin_AmericaPeruAREQUIPA
Latin_America | Peru |  | CHICLAYO | CHICLAYO, Peru | 6.78S | 79.82W | 30 | -5.00 (SAP) | 82-06 | 844520 | 14.7 |  | 11.4 | 38.8 | 30.1 | 28.9 | 28 | 29 | 29 |  | 28.3 | 26.4 | 26 | 27 | 26.9 |  |  | Latin_AmericaPeruCHICLAYO
Latin_America | Peru |  | CUZCO | CUZCO, Peru | 13.53S | 71.93W | 3249 | -5.00 (SAP) | 82-06 | 846860 | -2.1 |  | -5.8 | 28.3 | 21.9 | 21.8 | 22.8 | 22 | 22.1667 |  | 20.2 | 20.5 | 21.2 | 21 | 20.6333 |  |  | Latin_AmericaPeruCUZCO
Latin_America | Peru |  | IQUITOS | IQUITOS, Peru | 3.78S | 73.30W | 126 | -5.00 (SAP) | 82-06 | 843770 | 16.2 |  | 10.2 | 39.4 | 33 | 33.1 | 33.9 | 33 | 33.3333 |  | 32 | 32.1 | 32.9 | 32 | 32.3333 |  |  | Latin_AmericaPeruIQUITOS
Latin_America | Peru |  | LIMA-CALLAO/AEROP. | LIMA-CALLAO/AEROP., Peru | 12.00S | 77.12W | 13 | -5.00 (SAP) | 82-06 | 846280 | 12.1 |  | 7.1 | 33.7 | 26.9 | 25 | 23.9 | 25 | 25.2667 |  | 24.8 | 22.8 | 21.7 | 23 | 23.1 |  |  | Latin_AmericaPeruLIMA-CALLAO/AEROP.
Latin_America | Peru |  | PISCO | PISCO, Peru | 13.73S | 76.22W | 7 | -5.00 (SAP) | 82-06 | 846910 | 10 |  | 8.1 | 35.2 | 26.8 | 24.9 | 23.8 | 25 | 25.1667 |  | 24.2 | 22.8 | 21.9 | 23 | 22.9667 |  |  | Latin_AmericaPeruPISCO
Latin_America | Peru |  | PIURA | PIURA, Peru | 5.20S | 80.60W | 55 | -5.00 (SAP) | 82-06 | 844010 | 14.9 |  | 10.5 | 37.1 | 31.1 | 30.2 | 30.2 | 31 | 30.5 |  | 29.8 | 28.8 | 28.7 | 29 | 29.1 |  |  | Latin_AmericaPeruPIURA
Latin_America | Peru |  | PUCALLPA | PUCALLPA, Peru | 8.37S | 74.57W | 149 | -5.00 (SAP) | 82-06 | 845150 | 15 |  | 10.4 | 40.9 | 33.2 | 34 | 35.1 | 34 | 34.1 |  | 32.4 | 33 | 34 | 33 | 33.1333 |  |  | Latin_AmericaPeruPUCALLPA
Latin_America | Peru |  | SAN JUAN | SAN JUAN, Peru | 15.38S | 75.17W | 60 | -5.00 (SAP) | 82-97 | 847210 | N/A |  | N/A | N/A | 24.2 | 22.8 | 21.1 | 23 | 22.7 |  | 23 | 20.9 | 20 | 21 | 21.3 |  |  | Latin_AmericaPeruSAN JUAN
Latin_America | Peru |  | TACNA | TACNA, Peru | 18.05S | 70.27W | 458 | -5.00 (SAP) | 82-00 | 847820 | 8.3 |  | 5.1 | 31.8 | 23.1 | 21.6 | 23.1 | 23 | 22.6 |  | 21.6 | 20 | 20.9 | 21 | 20.8333 |  |  | Latin_AmericaPeruTACNA
Latin_America | Peru |  | TALARA | TALARA, Peru | 4.57S | 81.23W | 85 | -5.00 (SAP) | 82-00 | 843900 | 14.5 |  | 9.3 | 36.7 | 30 | 29.1 | 28.1 | 29 | 29.0667 |  | 28.8 | 27.8 | 26.5 | 28 | 27.7 |  |  | Latin_AmericaPeruTALARA
Latin_America | Peru |  | TRUJILLO | TRUJILLO, Peru | 8.08S | 79.10W | 30 | -5.00 (SAP) | 82-00 | 845010 | N/A |  | N/A | N/A | 28.1 | 25.6 | 24.9 | 26 | 26.2 |  | 26.9 | 24.6 | 23.9 | 25 | 25.1333 |  |  | Latin_AmericaPeruTRUJILLO
Latin_America | Peru |  | TUMBES | TUMBES, Peru | 3.55S | 80.40W | 27 | -5.00 (SAP) | 82-00 | 843700 | N/A |  | N/A | N/A | 31.8 | 31.6 | 31.5 | 32 | 31.6333 |  | 30.6 | 30.3 | 30.1 | 30 | 30.3333 |  |  | Latin_AmericaPeruTUMBES
Latin_America | Puerto_Rico |  | AQUADILLA/BORINQUEN | AQUADILLA/BORINQUEN, Puerto Rico | 18.50N | 67.13W | 72 | -4.00 (SAW) | 83-06 | 785140 | N/A |  | N/A | N/A | 31.3 | 31.3 | 31.8 | 31 | 31.4667 |  | 30.8 | 30.9 | 31.1 | 31 | 30.9333 |  |  | Latin_AmericaPuerto_RicoAQUADILLA/BORINQUEN
Latin_America | Puerto_Rico |  | ROOSEVELT ROADS | ROOSEVELT ROADS, Puerto Rico | 18.25N | 65.63W | 12 | -4.00 (SAW) | 82-06 | 785350 | 18.3 |  | 15.8 | 34.5 | 32.1 | 32.9 | 33.1 | 33 | 32.7 |  | 31.2 | 31.9 | 32.1 | 32 | 31.7333 |  |  | Latin_AmericaPuerto_RicoROOSEVELT ROADS
Latin_America | Puerto_Rico |  | SAN JUAN INTL ARPT | SAN JUAN INTL ARPT, Puerto Rico | 18.42N | 66.00W | 19 | -4.00 (SAW) | 82-06 | 785260 | 19.3 |  | 16.7 | 37.1 | 33.7 | 33 | 33.1 | 33 | 33.2667 |  | 32.1 | 31.7 | 31.9 | 32 | 31.9 |  |  | Latin_AmericaPuerto_RicoSAN JUAN INTL ARPT
Latin_America | Puerto_Rico |  | SAN JUAN L M MARIN INTL AP | SAN JUAN L M MARIN INTL AP, Puerto Rico | 18.43N | 66.00W | 3 | -4.00 (SAW) | 96-06 | 785263 | 18.9 |  | 14.6 | 35.3 | 33.1 | 32.8 | 33 | 33 | 32.9667 |  | 31.8 | 31.6 | 31.7 | 32 | 31.7 |  |  | Latin_AmericaPuerto_RicoSAN JUAN L M MARIN INTL AP
GUA-Guanajuato
JAL-Jalisco
MEX-México
NLE-Nuevo León
ROO-Quintana Roo
SIN-Sinaloa
SLP-San Luis Potosí
TAM-Tamaulipas
VER-Veracruz
YUC-Yucatán
ZAC-Zacatecas

## ASHRAE ALL (hidden)
|  |  |  | Latitude | Longitude | Elevation | Time Zone | Period | WMO# | Extreme Annual Dry Bulb Mean |  | 50yr Min | 50yr Max | 0.4% Dry Bulb | [5 empty] | 2% Dry Bulb
Country | State or Providence | Station Name 1 | ASHRAE Name 2 | 3 | 4 | 5 | 6 | 7 | 8 | Min 9 | Min. from Solar ABC's 10 | 11 | 12 | Jun 13 | Jul 14 | Aug 15 | Rounded Avg. 16 | Avg. 17 | .4% From Solar ABC's 18 | Jun 19 | Jul 20 | Aug 21 | Rounded Avg. 22 | Avg. 23 | 2% From Solar ABC's 24 |  | Lookup Index
Albania |  | TIRANA | TIRANA, Albania | 41.33N | 19.78E | 90 | 1.00 (EUW) | 82-06 | 136150 | N/A |  | N/A | N/A | 35 | 37.3 | 35.3 | 36 | 35.8667 |  | 31.9 | 34.4 | 33.7 | 33 | 33.3333
Algeria |  | ADRAR | ADRAR, Algeria | 27.88N | 0.18W | 283 | 1.00 (AFW) | 85-06 | 606200 | 0.2 |  | -4 | 50.2 | 46.5 | 48.1 | 47.1 | 47 | 47.2333 |  | 45.4 | 47.1 | 46.1 | 46 | 46.2
Algeria |  | ANNABA | ANNABA, Algeria | 36.83N | 7.82E | 4 | 1.00 (AFW) | 82-06 | 603600 | 1.4 |  | -2 | 47.7 | 36.5 | 39.6 | 38.9 | 38 | 38.3333 |  | 31.8 | 34.7 | 34.2 | 34 | 33.5667
Algeria |  | BATNA | BATNA, Algeria | 35.75N | 6.32E | 826 | 1.00 (AFW) | 82-06 | 604680 | -5.7 |  | -9.3 | 45.6 | 38.4 | 40.2 | 39.8 | 39 | 39.4667 |  | 36.4 | 38.5 | 37.8 | 38 | 37.5667
Algeria |  | BECHAR | BECHAR, Algeria | 31.50N | 2.25W | 816 | 1.00 (AFW) | 82-06 | 605710 | -1.5 |  | -5.8 | 46 | 41.2 | 42.8 | 42 | 42 | 42 |  | 39.9 | 41.8 | 40.9 | 41 | 40.8667
Algeria |  | BEJAIA-AEROPORT | BEJAIA-AEROPORT, Algeria | 36.72N | 5.07E | 3 | 1.00 (AFW) | 82-06 | 604020 | 2 |  | -3.1 | 46.8 | 32.2 | 36.1 | 36.1 | 35 | 34.8 |  | 29.1 | 32.2 | 32.2 | 31 | 31.1667
Algeria |  | BISKRA | BISKRA, Algeria | 34.80N | 5.73E | 89 | 1.00 (AFW) | 82-06 | 605250 | 1.7 |  | -1.1 | 49.5 | 44.1 | 45.4 | 44.8 | 45 | 44.7667 |  | 42.1 | 43.6 | 42.9 | 43 | 42.8667
Algeria |  | BORDJ-BOU-ARRERIDJ | BORDJ-BOU-ARRERIDJ, Algeria | 36.07N | 4.77E | 930 | 1.00 (AFW) | 88-06 | 604440 | -2.4 |  | -7.1 | 42.1 | 36.9 | 38.5 | 37.4 | 38 | 37.6 |  | 35.2 | 36.9 | 36.1 | 36 | 36.0667
Algeria |  | CONSTANTINE | CONSTANTINE, Algeria | 36.28N | 6.62E | 694 | 1.00 (AFW) | 82-06 | 604190 | -2.9 |  | -7.9 | 45.3 | 39.3 | 40.3 | 40.2 | 40 | 39.9333 |  | 36.8 | 38.3 | 38.1 | 38 | 37.7333
Algeria |  | DAR-EL-BEIDA | DAR-EL-BEIDA, Algeria | 36.68N | 3.22E | 29 | 1.00 (AFW) | 82-06 | 603900 | -0.2 |  | -3.2 | 47.5 | 35.6 | 38.1 | 38.8 | 38 | 37.5 |  | 32.2 | 34.9 | 35.2 | 34 | 34.1
Algeria |  | DJANET | DJANET, Algeria | 24.27N | 9.47E | 970 | 1.00 (AFW) | 88-06 | 606700 | -1.9 |  | -8.4 | 42.6 | 40.5 | 40.2 | 39.9 | 40 | 40.2 |  | 39.1 | 39.3 | 38.9 | 39 | 39.1
Algeria |  | EL-BAYADH | EL-BAYADH, Algeria | 33.67N | 1.00E | 1347 | 1.00 (AFW) | 82-06 | 605500 | -6.1 |  | -10.5 | 41.6 | 35.4 | 36.8 | 36.1 | 36 | 36.1 |  | 33.9 | 35.7 | 34.9 | 35 | 34.8333
Algeria |  | EL-GOLEA | EL-GOLEA, Algeria | 30.57N | 2.87E | 403 | 1.00 (AFW) | 82-06 | 605900 | -2.3 |  | -5.9 | 49.2 | 44.2 | 46 | 45.1 | 45 | 45.1 |  | 42.9 | 44.5 | 43.6 | 44 | 43.6667
Algeria |  | EL-OUED | EL-OUED, Algeria | 33.50N | 6.78E | 69 | 1.00 (AFW) | 82-06 | 605590 | 0.5 |  | -1.9 | 50.3 | 45.1 | 46.6 | 46 | 46 | 45.9 |  | 43.1 | 44.8 | 44.1 | 44 | 44
Algeria |  | GHARDAIA | GHARDAIA, Algeria | 32.40N | 3.80E | 469 | 1.00 (AFW) | 82-06 | 605660 | 1.3 |  | -1.2 | 48.4 | 43.2 | 45.1 | 44.1 | 44 | 44.1333 |  | 41.7 | 43.3 | 42.7 | 43 | 42.5667
Algeria |  | HASSI-MESSAOUD | HASSI-MESSAOUD, Algeria | 31.67N | 6.15E | 144 | 1.00 (AFW) | 82-06 | 605810 | -0.1 |  | -1.9 | 53 | 46.6 | 48.2 | 47.1 | 47 | 47.3 |  | 44.9 | 46.2 | 45.2 | 45 | 45.4333
Algeria |  | ILLIZI | ILLIZI, Algeria | 26.50N | 8.42E | 544 | 1.00 (AFW) | 92-06 | 606400 | 0 |  | -4.2 | 48 | 44.1 | 45.1 | 44.1 | 44 | 44.4333 |  | 42.8 | 43.9 | 43 | 43 | 43.2333
Algeria |  | IN-AMENAS | IN-AMENAS, Algeria | 28.05N | 9.63E | 562 | 1.00 (AFW) | 82-06 | 606110 | -2.1 |  | -6.1 | 46.5 | 44.1 | 44.1 | 43.1 | 44 | 43.7667 |  | 42.4 | 42.7 | 41.6 | 42 | 42.2333
Algeria |  | IN-SALAH | IN-SALAH, Algeria | 27.23N | 2.50E | 269 | 1.00 (AFW) | 82-06 | 606300 | 0.7 |  | -2.2 | 50.1 | 46.7 | 47.8 | 46.9 | 47 | 47.1333 |  | 45.7 | 46.8 | 45.8 | 46 | 46.1
Algeria |  | JIJEL-ACHOUAT | JIJEL-ACHOUAT, Algeria | 36.80N | 5.88E | 10 | 1.00 (AFW) | 84-06 | 603510 | 3.4 |  | 0.9 | 47.8 | 35.4 | 37 | 37.6 | 37 | 36.6667 |  | 31.8 | 33.1 | 34.1 | 33 | 33
Algeria |  | MASCARA-MATEMORE | MASCARA-MATEMORE, Algeria | 35.60N | 0.30E | 476 | 1.00 (AFW) | 88-02 | 605060 | -3.2 |  | -6.2 | 45.7 | 38.7 | 41.2 | 40.4 | 40 | 40.1 |  | 36.1 | 39 | 38.6 | 38 | 37.9
Algeria |  | MECHERIA | MECHERIA, Algeria | 33.58N | 0.28W | 1150 | 1.00 (AFW) | 82-06 | 605490 | -4.7 |  | -14.5 | 41.4 | 37.1 | 38.4 | 37.6 | 38 | 37.7 |  | 35.6 | 37.4 | 36.4 | 36 | 36.4667
Algeria |  | ORAN-SENIA | ORAN-SENIA, Algeria | 35.63N | 0.60W | 91 | 1.00 (AFW) | 83-06 | 604900 | -0.1 |  | -3.4 | 43.5 | 33.2 | 36.3 | 37.2 | 36 | 35.5667 |  | 30.6 | 33.1 | 34.1 | 33 | 32.6
Algeria |  | OUARGLA | OUARGLA, Algeria | 31.93N | 5.40E | 148 | 1.00 (AFW) | 82-06 | 605800 | N/A |  | N/A | N/A | 46.2 | 48.2 | 47.6 | 47 | 47.3333 |  | 44.7 | 46.8 | 45.8 | 46 | 45.7667
Algeria |  | SETIF | SETIF, Algeria | 36.18N | 5.25E | 1040 | 1.00 (AFW) | 82-06 | 604450 | -3.9 |  | -9 | 43 | 36.1 | 37.9 | 37.1 | 37 | 37.0333 |  | 34.3 | 36.2 | 35.6 | 35 | 35.3667
Algeria |  | SKIKDA | SKIKDA, Algeria | 36.88N | 6.90E | 3 | 1.00 (AFW) | 83-06 | 603550 | 4.5 |  | 0.7 | 49.1 | 32.8 | 35.2 | 35.3 | 34 | 34.4333 |  | 29.2 | 31.2 | 32.4 | 31 | 30.9333
Algeria |  | TAMANRASSET | TAMANRASSET, Algeria | 22.80N | 5.45E | 1412 | 1.00 (AFW) | 86-06 | 606805 | -0.1 |  | -4.5 | 40.5 | 37.4 | 37.3 | 37 | 37 | 37.2333 |  | 36.2 | 36.8 | 36 | 36 | 36.3333
Algeria |  | TEBESSA | TEBESSA, Algeria | 35.42N | 8.12E | 823 | 1.00 (AFW) | 82-06 | 604750 | -3.4 |  | -6.8 | 43.5 | 38.5 | 40 | 39.1 | 39 | 39.2 |  | 36.6 | 38.2 | 37.7 | 38 | 37.5
Algeria |  | TIARET | TIARET, Algeria | 35.35N | 1.47E | 978 | 1.00 (AFW) | 85-06 | 605110 | -5.1 |  | -9.7 | 44.4 | 37.6 | 39 | 38.2 | 38 | 38.2667 |  | 35.5 | 37.2 | 36.9 | 37 | 36.5333
Algeria |  | TINDOUF | TINDOUF, Algeria | 27.70N | 8.17W | 439 | 1.00 (AFW) | 82-06 | 606560 | 1.2 |  | -3.8 | 50.9 | 44.9 | 46.2 | 45.4 | 46 | 45.5 |  | 43.2 | 45.5 | 44.5 | 44 | 44.4
Algeria |  | TLEMCEN-ZENATA | TLEMCEN-ZENATA, Algeria | 35.02N | 1.47W | 247 | 1.00 (AFW) | 82-06 | 605310 | -0.1 |  | -3.4 | 47.7 | 35.1 | 39.6 | 39.8 | 38 | 38.1667 |  | 32.4 | 36.2 | 36.2 | 35 | 34.9333
Algeria |  | TOUGGOURT | TOUGGOURT, Algeria | 33.12N | 6.13E | 92 | 1.00 (AFW) | 85-06 | 605550 | -0.1 |  | -2.3 | 51 | 45.3 | 46.9 | 46.1 | 46 | 46.1 |  | 43.1 | 45 | 44.2 | 44 | 44.1
Antarctica |  | BASE ARTURO PRAT | BASE ARTURO PRAT, Antarctica | 62.50S | 59.68W | 5 | -4.00 (XXX) | 85-03 | 890570 | -19 |  | -30.1 | 14.1 | 1.7 | 1.4 | 1.2 | 1 | 1.4333 |  | 1 | 0.7 | 0.6 | 1 | 0.76667
Antarctica |  | BASE ESPERANZA | BASE ESPERANZA, Antarctica | 63.40S | 56.98W | 24 | -4.00 (XXX) | 82-06 | 889630 | -27.2 |  | -34.7 | 15.8 | 5.6 | 5.2 | 4.8 | 5 | 5.2 |  | 3.1 | 2.8 | 2.6 | 3 | 2.8333
Antarctica |  | BASE JUBANY | BASE JUBANY, Antarctica | 62.23S | 58.63W | 4 | -4.00 (XXX) | 88-06 | 890530 | -20.9 |  | -31.6 | 17.4 | 4 | 2.7 | 2.5 | 3 | 3.0667 |  | 2.8 | 1.8 | 1.6 | 2 | 2.0667
Antarctica |  | BASE MARAMBIO | BASE MARAMBIO, Antarctica | 64.23S | 56.72W | 198 | -4.00 (XXX) | 82-06 | 890550 | -31.1 |  | -37.1 | 15.4 | 4.2 | 3.2 | 3.4 | 4 | 3.6 |  | 1.6 | 1.2 | 1.1 | 1 | 1.3
Antarctica |  | BASE ORCADAS | BASE ORCADAS, Antarctica | 60.73S | 44.73W | 8 | -3.00 (XXX) | 82-06 | 889680 | -28.9 |  | -36.4 | 15.6 | 2.5 | 3.2 | 3.1 | 3 | 2.9333 |  | 1 | 1.4 | 1.3 | 1 | 1.2333
Antarctica |  | BASE SAN MARTIN | BASE SAN MARTIN, Antarctica | 68.12S | 67.13W | 4 | -4.00 (XXX) | 83-06 | 890660 | -33.3 |  | -44.7 | 13.6 | 4.6 | 4.1 | 3.4 | 4 | 4.0333 |  | 1.9 | 2.4 | 1.8 | 2 | 2.0333
Antarctica |  | BELLINGSHAUSEN AWS | BELLINGSHAUSEN AWS, Antarctica | 62.20S | 58.93W | 16 | -4.00 (XXX) | 82-06 | 890500 | -19.7 |  | -28.2 | 10 | 1.7 | 1 | 1 | 1 | 1.2333 |  | 1.1 | 0.3 | 0.4 | 1 | 0.6
Antarctica |  | BERNARDO O`HIGGINS | BERNARDO O`HIGGINS, Antarctica | 63.32S | 57.90W | 10 | -4.00 (XXX) | 85-06 | 890590 | -22.6 |  | -30.8 | 16.7 | 0.7 | 0.6 | 0.6 | 1 | 0.63333 |  | -0.1 | -0.1 | 0 | 0 | -0.066667
Antarctica |  | BUTLER ISLAND | BUTLER ISLAND, Antarctica | 72.21S | 60.17W | 205 | -4.00 (XXX) | 90-06 | 892660 | N/A |  | N/A | N/A | 2.1 | 0.8 | -0.9 | 1 | 0.66667 |  | -3 | -4.4 | -4.6 | -4 | -4
Antarctica |  | CASEY | CASEY, Antarctica | 66.28S | 110.52E | 41 | 7.00 (XXX) | 83-06 | 896110 | -31.8 |  | -37 | 9.1 | -0.5 | -1.8 | -1.7 | -1 | -1.3333 |  | -3.5 | -3.8 | -3.3 | -4 | -3.5333
Antarctica |  | DAVIS | DAVIS, Antarctica | 68.58S | 77.95E | 13 | 5.00 (XXX) | 83-06 | 895710 | -32.4 |  | -41.2 | 11.7 | -1.3 | -2.8 | -2.8 | -2 | -2.3 |  | -3.7 | -4.4 | -5.1 | -4 | -4.4
Antarctica |  | DINAMET-URUGUAY | DINAMET-URUGUAY, Antarctica | 62.18S | 58.83W | 10 | -4.00 (XXX) | 86-06 | 890540 | -20 |  | -34.7 | 13.3 | 2 | 1.2 | 1.5 | 2 | 1.5667 |  | 1.2 | 0.8 | 0.6 | 1 | 0.86667
Antarctica |  | DUMONT DURVILLE | DUMONT DURVILLE, Antarctica | 66.67S | 140.02E | 43 | 9.00 (XXX) | 94-06 | 896420 | -29.9 |  | -32.1 | 9.8 | -4.5 | -4.3 | -2.4 | -4 | -3.7333 |  | -6.1 | -6.5 | -5.9 | -6 | -6.1667
Antarctica |  | FREI CHI-BASE | FREI CHI-BASE, Antarctica | 62.18S | 58.98W | 10 | -4.00 (XXX) | 85-06 | 890560 | -20 |  | -30.8 | 13.4 | 1.4 | 1.2 | 1.3 | 1 | 1.3 |  | 0.7 | 0.6 | 0.5 | 1 | 0.6
Antarctica |  | GREAT WALL | GREAT WALL, Antarctica | 62.22S | 58.97W | 10 | -4.00 (XXX) | 87-06 | 890580 | N/A |  | N/A | N/A | 1.7 | 1.2 | 1.2 | 1 | 1.3667 |  | 1.1 | 0.6 | 0.6 | 1 | 0.76667
Antarctica |  | HALLEY | HALLEY, Antarctica | 75.50S | 26.65W | 30 | -2.00 (XXX) | 83-06 | 890220 | N/A |  | N/A | N/A | -7.9 | -8.4 | -7.4 | -8 | -7.9 |  | -11.1 | -11.8 | -10.7 | -11 | -11.2
Antarctica |  | MANUELA | MANUELA, Antarctica | 74.95S | 163.69E | 78 | 11.00 (XXX) | 91-06 | 898640 | -40.2 |  | -46.6 | 9.2 | -10.3 | -9.7 | -8 | -9 | -9.3333 |  | -12.9 | -15.7 | -14 | -14 | -14.2
Antarctica |  | MARBLE POINT | MARBLE POINT, Antarctica | 77.43S | 163.75E | 108 | 11.00 (XXX) | 90-06 | 898660 | N/A |  | N/A | N/A | -6 | -8.8 | -5.8 | -7 | -6.8667 |  | -9.5 | -11.7 | -11.1 | -11 | -10.7667
Antarctica |  | MAWSON | MAWSON, Antarctica | 67.60S | 62.87E | 16 | 4.00 (XXX) | 91-06 | 895640 | -29.7 |  | -34.4 | 8.3 | -3.2 | -4.3 | -4.3 | -4 | -3.9333 |  | -5.2 | -5.8 | -7.8 | -6 | -6.2667
Antarctica |  | MIRNYJ | MIRNYJ, Antarctica | 66.55S | 93.02E | 30 | 6.00 (XXX) | 82-06 | 895920 | -32.8 |  | -40.3 | 8 | -3.8 | -3.4 | -3.8 | -4 | -3.6667 |  | -4.9 | -5.3 | -6 | -5 | -5.4
Antarctica |  | MOLODEZNAJA | MOLODEZNAJA, Antarctica | 67.67S | 45.85E | 40 | 3.00 (XXX) | 82-99 | 895420 | N/A |  | N/A | N/A | -4.4 | -3.9 | -5.2 | -5 | -4.5 |  | -5.5 | -5.5 | -6.8 | -6 | -5.9333
Antarctica |  | MOUNT SIPLE | MOUNT SIPLE, Antarctica | 73.20S | 127.05W | 230 | -8.00 (XXX) | 94-06 | 893270 | -35.8 |  | -48.8 | 13.5 | -1.3 | -2.5 | -2 | -2 | -1.9333 |  | -2.5 | -4.2 | -4.3 | -4 | -3.6667
Antarctica |  | NEUMAYER | NEUMAYER, Antarctica | 70.67S | 8.25W | 50 | -1.00 (XXX) | 92-06 | 890020 | -43.4 |  | -48.2 | 3.5 | -6.7 | -7.5 | -7.4 | -7 | -7.2 |  | -8.5 | -10.7 | -10.6 | -10 | -9.9333
Antarctica |  | NOVOLAZAREVSKAJA | NOVOLAZAREVSKAJA, Antarctica | 70.77S | 11.83E | 102 | 1.00 (XXX) | 82-06 | 895120 | -32.7 |  | -39.4 | 11.2 | -4 | -4.7 | -5.3 | -5 | -4.6667 |  | -5.4 | -6.6 | -8.1 | -7 | -6.7
Antarctica |  | POSSESSION ISLAND | POSSESSION ISLAND, Antarctica | 71.89S | 171.21E | 30 | 11.00 (XXX) | 94-06 | 898790 | -31.8 |  | -38.2 | 12.6 | -6.1 | -6.1 | -5.6 | -6 | -5.9333 |  | -8.3 | -10 | -9.4 | -9 | -9.2333
Antarctica |  | SIPLE DOME | SIPLE DOME, Antarctica | 81.65S | 148.77W | 620 | -10.00 (XXX) | 97-06 | 893450 | -51.1 |  | -60 | 14.8 | -9.1 | -12.2 | -14.1 | -12 | -11.8 |  | -12.3 | -14.9 | -17 | -15 | -14.7333
Antarctica |  | SYOWA | SYOWA, Antarctica | 69.00S | 39.58E | 21 | 3.00 (XXX) | 83-06 | 895320 | -36 |  | -44 | 8.6 | -3.4 | -4 | -5.1 | -4 | -4.1667 |  | -5 | -5.4 | -6.8 | -6 | -5.7333
Antigua and Barbuda |  | VC BIRD INTL AIRPOR | VC BIRD INTL AIRPOR, Antigua and Barbuda | 17.12N | 61.78W | 10 | -4.00 (SAZ) | 82-06 | 788620 | 19.6 |  | 17.1 | 34.8 | 31.3 | 32.1 | 32.1 | 32 | 31.8333 |  | 31 | 31.2 | 31.4 | 31 | 31.2
Argentina |  | AEROPARQUE BS. AS. | AEROPARQUE BS. AS., Argentina | 34.57S | 58.42W | 6 | -3.00 (SAE) | 82-06 | 875820 | 1.8 |  | -1.7 | 39.7 | 21.2 | 20.9 | 24.1 | 22 | 22.0667 |  | 19 | 18.2 | 21 | 19 | 19.4
Argentina |  | BAHIA BLANCA AERO | BAHIA BLANCA AERO, Argentina | 38.73S | 62.17W | 83 | -3.00 (SAE) | 82-06 | 877500 | -4.9 |  | -10.4 | 42.3 | 20.5 | 21.2 | 24.7 | 22 | 22.1333 |  | 17.8 | 18.2 | 21.8 | 19 | 19.2667
Argentina |  | BARILOCHE AERO | BARILOCHE AERO, Argentina | 41.15S | 71.17W | 840 | -3.00 (SAE) | 82-06 | 877650 | -10.6 |  | -18.1 | 35.6 | 12.5 | 12.4 | 14.9 | 13 | 13.2667 |  | 10.2 | 10.1 | 12 | 11 | 10.7667
Argentina |  | CATAMARCA AERO. | CATAMARCA AERO., Argentina | 28.60S | 65.77W | 454 | -3.00 (SAE) | 82-06 | 872220 | -1.6 |  | -7.1 | 44.6 | 25.2 | 29.1 | 35.6 | 30 | 29.9667 |  | 22.7 | 24.9 | 30.6 | 26 | 26.0667
Argentina |  | CERES AERO | CERES AERO, Argentina | 29.88S | 61.95W | 88 | -3.00 (SAE) | 82-06 | 872570 | -2.9 |  | -7.4 | 41.9 | 27 | 28.6 | 33.2 | 30 | 29.6 |  | 23.7 | 25.1 | 29.6 | 26 | 26.1333
Argentina |  | COMODORO RIVADAVIA | COMODORO RIVADAVIA, Argentina | 45.78S | 67.50W | 46 | -3.00 (SAE) | 82-06 | 878600 | -3.7 |  | -7.7 | 39.1 | 17.9 | 18.2 | 19.4 | 19 | 18.5 |  | 15.1 | 15.9 | 17.2 | 16 | 16.0667
Argentina |  | CONCORDIA AERO | CONCORDIA AERO, Argentina | 31.30S | 58.02W | 38 | -3.00 (SAE) | 82-06 | 873950 | -1.8 |  | -5.5 | 40.7 | 25.8 | 27.3 | 30.8 | 28 | 27.9667 |  | 23.1 | 24.1 | 27.1 | 25 | 24.7667
Argentina |  | CORDOBA AERO | CORDOBA AERO, Argentina | 31.32S | 64.22W | 474 | -3.00 (SAE) | 82-06 | 873440 | -3.9 |  | -8.2 | 42.7 | 25.9 | 27.8 | 32 | 29 | 28.5667 |  | 22.9 | 23.6 | 27.3 | 25 | 24.6
Argentina |  | CORRIENTES AERO. | CORRIENTES AERO., Argentina | 27.45S | 58.77W | 62 | -3.00 (SAE) | 82-06 | 871660 | 1.8 |  | -2.1 | 42.1 | 29.2 | 30.1 | 33.2 | 31 | 30.8333 |  | 27.2 | 28.1 | 30.8 | 29 | 28.7
Argentina |  | ESQUEL AERO | ESQUEL AERO, Argentina | 42.93S | 71.15W | 797 | -3.00 (SAE) | 82-06 | 878030 | -11.5 |  | -20.1 | 34.9 | 12.3 | 13.3 | 15.5 | 14 | 13.7 |  | 10.5 | 10.6 | 12.6 | 11 | 11.2333
Argentina |  | EZEIZA AERO | EZEIZA AERO, Argentina | 34.82S | 58.53W | 20 | -3.00 (SAE) | 82-06 | 875760 | -2.6 |  | -5.7 | 41.1 | 23.1 | 23.2 | 26.9 | 24 | 24.4 |  | 20.2 | 20.1 | 23.2 | 21 | 21.1667
Argentina |  | FORMOSA AERO | FORMOSA AERO, Argentina | 26.20S | 58.23W | 60 | -3.00 (SAE) | 82-06 | 871620 | 1 |  | -3.2 | 42.1 | 30.2 | 31.8 | 35.1 | 32 | 32.3667 |  | 28.8 | 29.5 | 32.9 | 30 | 30.4
Argentina |  | GUALEGUAYCHU AERO | GUALEGUAYCHU AERO, Argentina | 33.00S | 58.62W | 21 | -3.00 (SAE) | 82-06 | 874970 | -2.7 |  | -7.9 | 41.8 | 24.8 | 25.8 | 29.7 | 27 | 26.7667 |  | 21.9 | 22.3 | 25.5 | 23 | 23.2333
Argentina |  | IGUAZU AERO | IGUAZU AERO, Argentina | 25.73S | 54.47W | 270 | -3.00 (SAE) | 89-06 | 870970 | 0.3 |  | -2.9 | 39.7 | 28.1 | 29.1 | 32.9 | 30 | 30.0333 |  | 26.9 | 27.5 | 30.9 | 28 | 28.4333
Argentina |  | JUJUY AERO | JUJUY AERO, Argentina | 24.38S | 65.08W | 905 | -3.00 (SAE) | 82-06 | 870460 | -1.2 |  | -5.8 | 41.5 | 28 | 30.1 | 33.2 | 30 | 30.4333 |  | 24.9 | 26.1 | 30.2 | 27 | 27.0667
Argentina |  | JUNIN AERO | JUNIN AERO, Argentina | 34.55S | 60.92W | 81 | -3.00 (SAE) | 82-06 | 875480 | -4 |  | -6.5 | 43.5 | 21.9 | 22.7 | 26.7 | 24 | 23.7667 |  | 19.3 | 19.6 | 22.9 | 21 | 20.6
Argentina |  | LA RIOJA AERO. | LA RIOJA AERO., Argentina | 29.38S | 66.82W | 429 | -3.00 (SAE) | 82-06 | 872170 | -1.5 |  | -5.5 | 45.4 | 24.7 | 26.8 | 33.3 | 28 | 28.2667 |  | 22.2 | 23.4 | 28.3 | 25 | 24.6333
Argentina |  | LAGO ARGENTINO ARPT | LAGO ARGENTINO ARPT, Argentina | 50.33S | 72.30W | 220 | -3.00 (SAE) | 91-00 | 879030 | N/A |  | N/A | N/A | 10.2 | 11.6 | 12.7 | 12 | 11.5 |  | 8.2 | 9.7 | 10.9 | 10 | 9.6
Argentina |  | MALARGUE AERO | MALARGUE AERO, Argentina | 35.50S | 69.58W | 1425 | -3.00 (SAE) | 82-06 | 875060 | -9.8 |  | -16.8 | 35.9 | 20 | 20.4 | 24 | 21 | 21.4667 |  | 16.6 | 17.5 | 20.4 | 18 | 18.1667
Argentina |  | MAR DEL PLATA AERO | MAR DEL PLATA AERO, Argentina | 37.93S | 57.58W | 21 | -3.00 (SAE) | 82-06 | 876920 | -3.7 |  | -8 | 40.1 | 18.7 | 19 | 22.2 | 20 | 19.9667 |  | 16.7 | 16 | 18.9 | 17 | 17.2
Argentina |  | MARCOS JUAREZ AERO | MARCOS JUAREZ AERO, Argentina | 32.70S | 62.15W | 114 | -3.00 (SAE) | 82-06 | 874670 | -4.5 |  | -8.8 | 42.1 | 24.1 | 25.3 | 29.9 | 26 | 26.4333 |  | 20.6 | 21.6 | 25.6 | 23 | 22.6
Argentina |  | MENDOZA AERO | MENDOZA AERO, Argentina | 32.83S | 68.78W | 704 | -3.00 (SAE) | 82-06 | 874180 | -3.3 |  | -6.5 | 43.5 | 23 | 22.4 | 27.2 | 24 | 24.2 |  | 18.9 | 19.1 | 23.3 | 20 | 20.4333
Argentina |  | MONTE CASEROS AERO | MONTE CASEROS AERO, Argentina | 30.27S | 57.65W | 54 | -3.00 (SAE) | 82-06 | 873930 | 0.2 |  | -3.3 | 39.9 | 27 | 27.6 | 31.1 | 29 | 28.5667 |  | 24.6 | 25.1 | 28.1 | 26 | 25.9333
Argentina |  | NEUQUEN AERO | NEUQUEN AERO, Argentina | 38.95S | 68.13W | 271 | -3.00 (SAE) | 82-06 | 877150 | -6.1 |  | -9.4 | 41.2 | 20.4 | 20.2 | 24.2 | 22 | 21.6 |  | 17.2 | 17 | 20.7 | 18 | 18.3
Argentina |  | PARANA AERO | PARANA AERO, Argentina | 31.78S | 60.48W | 78 | -3.00 (SAE) | 82-06 | 873740 | 0.2 |  | -3.3 | 39.9 | 24.7 | 25.3 | 29.2 | 26 | 26.4 |  | 22.1 | 22.2 | 25.7 | 23 | 23.3333
Argentina |  | PASO DE LOS LIBRES | PASO DE LOS LIBRES, Argentina | 29.68S | 57.15W | 70 | -3.00 (SAE) | 82-06 | 872890 | 0.1 |  | -4.1 | 41.7 | 27.5 | 28.1 | 31.3 | 29 | 28.9667 |  | 25.2 | 25.9 | 28.7 | 27 | 26.6
Argentina |  | POSADAS AERO. | POSADAS AERO., Argentina | 27.37S | 55.97W | 125 | -3.00 (SAE) | 82-06 | 871780 | 1.7 |  | -2.1 | 40.7 | 29.1 | 30.1 | 32.9 | 31 | 30.7 |  | 27.6 | 28.1 | 30.9 | 29 | 28.8667
Argentina |  | PRESIDENCIA ROQUE S | PRESIDENCIA ROQUE S, Argentina | 26.82S | 60.45W | 92 | -3.00 (SAE) | 82-98 | 871490 | -1.4 |  | -4.6 | 44 | 29.8 | 32.1 | 36.2 | 33 | 32.7 |  | 27.7 | 29.7 | 33.4 | 30 | 30.2667
Argentina |  | RECONQUISTA AERO | RECONQUISTA AERO, Argentina | 29.18S | 59.70W | 53 | -3.00 (SAE) | 82-06 | 872700 | 0.1 |  | -4 | 41.5 | 27.8 | 29.4 | 32.8 | 30 | 30 |  | 25.5 | 26.8 | 29.6 | 27 | 27.3
Argentina |  | RESISTENCIA AERO | RESISTENCIA AERO, Argentina | 27.45S | 59.05W | 52 | -3.00 (SAE) | 82-06 | 871550 | -1.1 |  | -5.3 | 42.7 | 29.8 | 30.9 | 34.4 | 32 | 31.7 |  | 27.8 | 28.8 | 31.9 | 30 | 29.5
Argentina |  | RIO CUARTO AERO | RIO CUARTO AERO, Argentina | 33.12S | 64.23W | 421 | -3.00 (SAE) | 82-06 | 874530 | -2 |  | -6.4 | 40.7 | 22.2 | 23.9 | 28.7 | 25 | 24.9333 |  | 19.2 | 20.6 | 24.2 | 21 | 21.3333
Argentina |  | RIO GALLEGOS AERO | RIO GALLEGOS AERO, Argentina | 51.62S | 69.28W | 19 | -3.00 (SAE) | 82-06 | 879250 | -11.5 |  | -20.6 | 33.4 | 10.1 | 10.9 | 13 | 11 | 11.3333 |  | 8 | 8.3 | 10.8 | 9 | 9.0333
Argentina |  | RIO GRANDE B.A. | RIO GRANDE B.A., Argentina | 53.80S | 67.75W | 22 | -3.00 (SAE) | 82-06 | 879340 | N/A |  | N/A | N/A | 8.2 | 8.1 | 9.8 | 9 | 8.7 |  | 6.8 | 5.9 | 7.5 | 7 | 6.7333
Argentina |  | ROSARIO AERO | ROSARIO AERO, Argentina | 32.92S | 60.78W | 25 | -3.00 (SAE) | 82-06 | 874800 | -3.5 |  | -7.1 | 40.9 | 24.1 | 24.9 | 28.8 | 26 | 25.9333 |  | 21 | 21.7 | 25.1 | 23 | 22.6
Argentina |  | SALTA AERO | SALTA AERO, Argentina | 24.85S | 65.48W | 1221 | -3.00 (SAE) | 82-06 | 870470 | -3.5 |  | -7.4 | 39.6 | 28 | 30.3 | 32.2 | 30 | 30.1667 |  | 24.2 | 26.2 | 28.9 | 26 | 26.4333
Argentina |  | SAN ANTONIO OESTE A | SAN ANTONIO OESTE A, Argentina | 40.78S | 65.10W | 20 | -3.00 (SAE) | 95-06 | 877840 | N/A |  | N/A | N/A | 19 | 20.2 | 23.1 | 21 | 20.7667 |  | 16.3 | 17.4 | 19.6 | 18 | 17.7667
Argentina |  | SAN JUAN AERO | SAN JUAN AERO, Argentina | 31.40S | 68.42W | 598 | -3.00 (SAE) | 82-06 | 873110 | -4.8 |  | -8.9 | 46.2 | 25.1 | 26.9 | 29.1 | 27 | 27.0333 |  | 20 | 21.3 | 25 | 22 | 22.1
Argentina |  | SAN JULIAN AERO | SAN JULIAN AERO, Argentina | 49.32S | 67.75W | 62 | -3.00 (SAE) | 91-06 | 879090 | -7.4 |  | -12.6 | 37.9 | 13.9 | 15.2 | 16.6 | 15 | 15.2333 |  | 11 | 12.1 | 14.2 | 12 | 12.4333
Argentina |  | SAN LUIS AERO | SAN LUIS AERO, Argentina | 33.27S | 66.35W | 713 | -3.00 (SAE) | 82-06 | 874360 | -3.9 |  | -8.8 | 40.6 | 23.2 | 25 | 29.5 | 26 | 25.9 |  | 20.9 | 21.6 | 26.1 | 23 | 22.8667
Argentina |  | SAN MARTIN | SAN MARTIN, Argentina | 33.08S | 68.42W | 653 | -3.00 (SAE) | 82-06 | 874160 | N/A |  | N/A | N/A | 20 | 22.2 | 27.5 | 23 | 23.2333 |  | 18 | 19 | 23.5 | 20 | 20.1667
Argentina |  | SAN RAFAEL AERO | SAN RAFAEL AERO, Argentina | 34.58S | 68.40W | 748 | -3.00 (SAE) | 82-06 | 875090 | -4.9 |  | -8.8 | 42.1 | 23.1 | 23.7 | 27 | 25 | 24.6 |  | 19.9 | 20.2 | 23.4 | 21 | 21.1667
Argentina |  | SANTA ROSA AERO | SANTA ROSA AERO, Argentina | 36.57S | 64.27W | 191 | -3.00 (SAE) | 82-06 | 876230 | -6 |  | -10.2 | 42.3 | 20 | 21.6 | 25.2 | 22 | 22.2667 |  | 17.7 | 18.1 | 21.9 | 19 | 19.2333
Argentina |  | SANTIAGO DEL ESTERO | SANTIAGO DEL ESTERO, Argentina | 27.77S | 64.30W | 199 | -3.00 (SAE) | 82-06 | 871290 | -4.3 |  | -8.8 | 46 | 26.9 | 29.7 | 35 | 31 | 30.5333 |  | 23.7 | 26.2 | 31 | 27 | 26.9667
Argentina |  | SAUCE VIEJO AERO | SAUCE VIEJO AERO, Argentina | 31.70S | 60.82W | 18 | -3.00 (SAE) | 82-06 | 873710 | -2.8 |  | -7.9 | 42.6 | 26.2 | 27.4 | 31.3 | 28 | 28.3 |  | 23 | 23.2 | 27.1 | 24 | 24.4333
Argentina |  | TANDIL AERO | TANDIL AERO, Argentina | 37.23S | 59.25W | 175 | -3.00 (SAE) | 82-06 | 876450 | -6.4 |  | -11.7 | 37.4 | 18.2 | 18.9 | 21.3 | 19 | 19.4667 |  | 16.1 | 15.9 | 18.8 | 17 | 16.9333
Argentina |  | TARTAGAL AERO | TARTAGAL AERO, Argentina | 22.65S | 63.82W | 450 | -3.00 (SAE) | 94-06 | 870220 | 1.4 |  | -2.7 | 43.7 | 29.1 | 31 | 36.1 | 32 | 32.0667 |  | 26.5 | 28.4 | 33 | 29 | 29.3
Argentina |  | TRELEW AERO | TRELEW AERO, Argentina | 43.20S | 65.27W | 43 | -3.00 (SAE) | 82-06 | 878280 | -7.5 |  | -12.5 | 41.3 | 18.4 | 19.9 | 21.7 | 20 | 20 |  | 16 | 16.9 | 19.1 | 17 | 17.3333
Argentina |  | TUCUMAN AERO | TUCUMAN AERO, Argentina | 26.85S | 65.10W | 450 | -3.00 (SAE) | 82-06 | 871210 | 0.6 |  | -3 | 44.1 | 24.1 | 27.5 | 33.3 | 28 | 28.3 |  | 22.2 | 24.2 | 29 | 25 | 25.1333
Argentina |  | USHUAIA AERO | USHUAIA AERO, Argentina | 54.80S | 68.32W | 57 | -3.00 (SAE) | 93-06 | 879380 | -5.7 |  | -10.3 | 28.2 | 10.2 | 10 | 11.2 | 10 | 10.4667 |  | 8.3 | 8.2 | 9.1 | 9 | 8.5333
Argentina |  | VIEDMA AERO | VIEDMA AERO, Argentina | 40.85S | 63.02W | 7 | -3.00 (SAE) | 91-06 | 877910 | -5.2 |  | -8 | 41.7 | 18.2 | 19.5 | 22.2 | 20 | 19.9667 |  | 16 | 16.9 | 19.3 | 17 | 17.4
Argentina |  | VILLA REYNOLDS AERO | VILLA REYNOLDS AERO, Argentina | 33.73S | 65.38W | 486 | -3.00 (SAE) | 82-06 | 874480 | -9.4 |  | -16.2 | 44.3 | 24.9 | 25.9 | 30.7 | 27 | 27.1667 |  | 21.8 | 22.8 | 26.7 | 24 | 23.7667
Armenia |  | AMASIA | AMASIA, Armenia | 40.78N | 43.83E | 1866 | 4.00 (CAU) | 82-06 | 376820 | -24.8 |  | -30.7 | 34.7 | 27.2 | 30.9 | 30.7 | 30 | 29.6 |  | 25.1 | 29.2 | 28.8 | 28 | 27.7
Armenia |  | SEVAN | SEVAN, Armenia | 40.55N | 44.93E | 1937 | 4.00 (CAU) | 82-91 | 377090 | -19.9 |  | -29.3 | 31.8 | 23.1 | 25.7 | 26 | 25 | 24.9333 |  | 21.2 | 24 | 23.8 | 23 | 23
Armenia |  | YEREVAN/YEREVAN-ARA | YEREVAN/YEREVAN-ARA, Armenia | 40.13N | 44.47E | 1140 | 4.00 (CAU) | 82-03 | 377890 | -15 |  | -27.7 | 45.5 | 35.5 | 38.3 | 38.2 | 37 | 37.3333 |  | 33.4 | 36.4 | 36 | 35 | 35.2667
Aruba |  | QUEEN BEATRIX AIRPO | QUEEN BEATRIX AIRPO, Aruba | 12.50N | 70.02W | 5 | -4.00 (SAZ) | 82-06 | 789820 | 22.3 |  | 21.1 | 37.4 | 33.2 | 33.2 | 34 | 33 | 33.4667 |  | 32.6 | 32.3 | 33.2 | 33 | 32.7
Australia |  | ADELAIDE AIRPORT | ADELAIDE AIRPORT, Australia | 34.95S | 138.53E | 8 | 9.50 (AUA) | 82-06 | 946720 | 1.8 |  | -0.9 | 44.4 | 20.7 | 18.8 | 22.9 | 21 | 20.8 |  | 18.1 | 16.9 | 19.9 | 18 | 18.3
Australia |  | ADELAIDE REGIONAL O | ADELAIDE REGIONAL O, Australia | 34.92S | 138.62E | 51 | 9.50 (AUA) | 91-06 | 946750 | 2.7 |  | 2 | 44.6 | 21.5 | 19.5 | 23.6 | 22 | 21.5333 |  | 18.3 | 17.5 | 20.9 | 19 | 18.9
Australia |  | ADELE ISLAND | ADELE ISLAND, Australia | 15.52S | 123.15E | 5 | 8.00 (AUW) | 90-06 | 942100 | N/A |  | N/A | N/A | 31.1 | 30.4 | 30.7 | 31 | 30.7333 |  | 30.5 | 29.5 | 29.9 | 30 | 29.9667
Australia |  | AIREYS INLET | AIREYS INLET, Australia | 38.45S | 144.10E | 95 | 10.00 (AUE) | 91-06 | 948460 | 3.2 |  | -0.7 | 43.9 | 17.7 | 16.4 | 19.5 | 18 | 17.8667 |  | 15.6 | 14.6 | 16.7 | 16 | 15.6333
Australia |  | ALBANY AIRPORT | ALBANY AIRPORT, Australia | 34.93S | 117.80E | 69 | 8.00 (AUW) | 82-06 | 948020 | 2.4 |  | -0.2 | 44.9 | 20 | 18.9 | 20.6 | 20 | 19.8333 |  | 18.5 | 17.3 | 18.2 | 18 | 18
Australia |  | ALBURY AEROPORT | ALBURY AEROPORT, Australia | 36.07S | 146.95E | 165 | 10.00 (AUE) | 94-06 | 958960 | -1.9 |  | -4.2 | 43.9 | 18.1 | 15.8 | 20.2 | 18 | 18.0333 |  | 16.1 | 14.5 | 17.7 | 16 | 16.1
Australia |  | ALICE SPRINGS AIRPO | ALICE SPRINGS AIRPO, Australia | 23.80S | 133.88E | 547 | 9.50 (AUC) | 82-06 | 943260 | -2 |  | -5.8 | 45.3 | 28.1 | 27.5 | 30.9 | 29 | 28.8333 |  | 25.2 | 25.1 | 28.5 | 26 | 26.2667
Australia |  | AMBERLEY AMO | AMBERLEY AMO, Australia | 27.63S | 152.72E | 31 | 10.00 (AUB) | 92-06 | 945680 | -2 |  | -5.2 | 44.9 | 25.1 | 25.1 | 27.7 | 26 | 25.9667 |  | 23.3 | 23.1 | 25 | 24 | 23.8
Australia |  | APPLETHORPE GBHRS A | APPLETHORPE GBHRS A, Australia | 28.62S | 151.95E | 873 | 10.00 (AUB) | 98-06 | 945530 | -5.4 |  | -8.5 | 38 | 18.8 | 18.1 | 21 | 19 | 19.3 |  | 17.2 | 16.3 | 18.4 | 17 | 17.3
Australia |  | ARARAT PRISON | ARARAT PRISON, Australia | 37.28S | 142.98E | 296 | 10.00 (AUE) | 90-05 | 948340 | -3.4 |  | -6.3 | 43.1 | 16.2 | 14.8 | 18.4 | 16 | 16.4667 |  | 14.4 | 13.3 | 15.8 | 15 | 14.5
Australia |  | ARCHERFIELD AIRPORT | ARCHERFIELD AIRPORT, Australia | 27.57S | 153.00E | 13 | 10.00 (AUB) | 92-06 | 945750 | 2 |  | -0.6 | 44.9 | 24.5 | 24.5 | 25.9 | 25 | 24.9667 |  | 22.7 | 22.5 | 24 | 23 | 23.0667
Australia |  | ARGYLE AERODROME | ARGYLE AERODROME, Australia | 16.63S | 128.45E | 165 | 8.00 (AUW) | 94-06 | 942170 | 10.1 |  | 6.9 | 45 | 33.6 | 33.6 | 35.5 | 34 | 34.2333 |  | 32.2 | 32.2 | 34 | 33 | 32.8
Australia |  | AVALON AIRPORT | AVALON AIRPORT, Australia | 38.03S | 144.47E | 8 | 10.00 (AUE) | 97-06 | 948540 | -0.8 |  | -4 | 46.4 | 18.7 | 17.5 | 20.6 | 19 | 18.9333 |  | 16.5 | 15.6 | 17.9 | 17 | 16.6667
Australia |  | BALLARAT AERODROME | BALLARAT AERODROME, Australia | 37.52S | 143.78E | 436 | 10.00 (AUE) | 90-06 | 948520 | -2.9 |  | -5.7 | 42.7 | 14.4 | 13.4 | 16.7 | 15 | 14.8333 |  | 12.9 | 11.8 | 14.5 | 13 | 13.0667
Australia |  | BANKSTOWN AIRPORT A | BANKSTOWN AIRPORT A, Australia | 33.92S | 150.98E | 8 | 10.00 (AUE) | 92-06 | 947650 | 0.6 |  | -1.8 | 47.1 | 21.5 | 20.2 | 25.7 | 22 | 22.4667 |  | 19.5 | 18.3 | 21.9 | 20 | 19.9
Australia |  | BATCHELOR AERO | BATCHELOR AERO, Australia | 13.05S | 131.02E | 105 | 9.50 (AUC) | 94-06 | 941250 | 10.9 |  | 6.3 | 41.5 | 33.6 | 33.5 | 34.1 | 34 | 33.7333 |  | 32.4 | 32.5 | 33.2 | 33 | 32.7
Australia |  | BATHURST AIRPORT AW | BATHURST AIRPORT AW, Australia | 33.42S | 149.65E | 745 | 10.00 (AUE) | 90-06 | 947290 | -4.7 |  | -7.9 | 41.2 | 16.7 | 15.5 | 19.5 | 17 | 17.2333 |  | 14.5 | 13.6 | 16.5 | 15 | 14.8667
Australia |  | BEGA AWS | BEGA AWS, Australia | 36.67S | 149.82E | 42 | 10.00 (AUE) | 92-06 | 959310 | -2.7 |  | -5 | 45.4 | 20.6 | 19.1 | 22.3 | 21 | 20.6667 |  | 18.2 | 17.2 | 19.4 | 18 | 18.2667
Australia |  | BENDIGO AIRPORT AWS | BENDIGO AIRPORT AWS, Australia | 36.73S | 144.32E | 209 | 10.00 (AUE) | 90-06 | 948550 | -3.2 |  | -6.2 | 44.3 | 16.9 | 15.4 | 18.8 | 17 | 17.0333 |  | 15 | 13.9 | 16.6 | 15 | 15.1667
Australia |  | BILOELA THANGOOL AI | BILOELA THANGOOL AI, Australia | 24.48S | 150.57E | 199 | 10.00 (AUB) | 92-05 | 943760 | N/A |  | N/A | N/A | 26.6 | 25.4 | 27.4 | 26 | 26.4667 |  | 25.2 | 24 | 25.7 | 25 | 24.9667
Australia |  | BIRDSVILLE POLICE S | BIRDSVILLE POLICE S, Australia | 25.90S | 139.35E | 48 | 10.00 (AUB) | 88-01 | 944820 | N/A |  | N/A | N/A | 29.5 | 28.9 | 32.2 | 30 | 30.2 |  | 27.5 | 26.1 | 29.5 | 28 | 27.7
Australia |  | BOMBALA AWS | BOMBALA AWS, Australia | 37.00S | 149.23E | 762 | 10.00 (AUE) | 90-06 | 949290 | -6 |  | -8.3 | 40.1 | 15.6 | 14.5 | 18.6 | 16 | 16.2333 |  | 13.6 | 12.6 | 15.3 | 14 | 13.8333
Australia |  | BORROLOOLA | BORROLOOLA, Australia | 16.08S | 136.30E | 17 | 9.50 (AUC) | 94-06 | 941520 | 5.5 |  | 2.4 | 44.8 | 33.3 | 32.4 | 33.7 | 33 | 33.1333 |  | 31.8 | 31.1 | 32.2 | 32 | 31.7
Australia |  | BOULIA AIRPORT | BOULIA AIRPORT, Australia | 22.92S | 139.90E | 158 | 10.00 (AUB) | 82-05 | 943330 | 4.1 |  | 1.4 | 45.6 | 29.5 | 29.8 | 32.5 | 31 | 30.6 |  | 27.7 | 27.1 | 30.2 | 28 | 28.3333
Australia |  | BOURKE AIRPORT AWS | BOURKE AIRPORT AWS, Australia | 30.03S | 145.95E | 108 | 10.00 (AUE) | 90-06 | 947030 | N/A |  | N/A | N/A | 24.8 | 23.8 | 27.2 | 25 | 25.2667 |  | 21.9 | 21.6 | 25 | 23 | 22.8333
Australia |  | BOWEN AIRPORT | BOWEN AIRPORT, Australia | 20.02S | 148.20E | 6 | 10.00 (AUB) | 85-05 | 943660 | 5.8 |  | 3.4 | 39.3 | 26.7 | 26.5 | 27.3 | 27 | 26.8333 |  | 25.9 | 25.2 | 26.1 | 26 | 25.7333
Australia |  | BRAIDWOOD RACECOURS | BRAIDWOOD RACECOURS, Australia | 35.43S | 149.78E | 666 | 10.00 (AUE) | 90-06 | 949270 | -7.2 |  | -10.3 | 41.3 | 16.6 | 15.2 | 19.1 | 17 | 16.9667 |  | 14.5 | 13.4 | 16 | 15 | 14.6333
Australia |  | BRISBANE AERO | BRISBANE AERO, Australia | 27.38S | 153.13E | 10 | 10.00 (AUB) | 82-06 | 945780 | 3.1 |  | -0.3 | 40.3 | 24.1 | 23.9 | 24.8 | 24 | 24.2667 |  | 22.7 | 22 | 23 | 23 | 22.5667
Australia |  | BROKEN HILL AIRPORT | BROKEN HILL AIRPORT, Australia | 32.00S | 141.47E | 282 | 10.00 (AUE) | 90-06 | 946910 | 0 |  | -2.4 | 47 | 23.1 | 20.7 | 25.7 | 23 | 23.1667 |  | 20.5 | 18.5 | 22.6 | 21 | 20.5333
Australia |  | BROOME AIRPORT | BROOME AIRPORT, Australia | 17.95S | 122.23E | 9 | 8.00 (AUW) | 82-06 | 942030 | 7.8 |  | 4.3 | 44.7 | 32.8 | 32.5 | 34 | 33 | 33.1 |  | 31 | 30.8 | 32 | 31 | 31.2667
Australia |  | BUNDABERG AERO | BUNDABERG AERO, Australia | 24.90S | 152.32E | 27 | 10.00 (AUB) | 90-06 | 943870 | 5.3 |  | 3.9 | 38.3 | 25.7 | 24.7 | 25.4 | 25 | 25.2667 |  | 24.1 | 23.3 | 24.1 | 24 | 23.8333
Australia |  | BURKETOWN POST OFFI | BURKETOWN POST OFFI, Australia | 17.75S | 139.55E | 8 | 10.00 (AUB) | 90-05 | 942590 | N/A |  | N/A | N/A | 31.8 | 30.4 | 31.3 | 31 | 31.1667 |  | 30.5 | 29.2 | 30.1 | 30 | 29.9333
Australia |  | BUSSELTON AERO | BUSSELTON AERO, Australia | 33.68S | 115.40E | 17 | 8.00 (AUW) | 97-06 | 956110 | 1.1 |  | -1.2 | 38 | 19.7 | 18.7 | 19.1 | 19 | 19.1667 |  | 18.8 | 17.6 | 17.9 | 18 | 18.1
Australia |  | CAIRNS AERO | CAIRNS AERO, Australia | 16.88S | 145.75E | 8 | 10.00 (AUB) | 82-06 | 942870 | 11 |  | 7.1 | 40 | 28 | 27.3 | 28.2 | 28 | 27.8333 |  | 27 | 26.4 | 27.1 | 27 | 26.8333
Australia |  | CAMDEN AIRPORT | CAMDEN AIRPORT, Australia | 34.03S | 150.68E | 75 | 10.00 (AUE) | 97-06 | 947550 | -2.1 |  | -5.3 | 44.9 | 21.6 | 20.2 | 22.9 | 22 | 21.5667 |  | 19.5 | 18.4 | 20.8 | 20 | 19.5667
Australia |  | CANBERRA AIRPORT | CANBERRA AIRPORT, Australia | 35.30S | 149.20E | 580 | 10.00 (AUE) | 82-06 | 949260 | -5.3 |  | -8.8 | 42 | 16.8 | 14.9 | 18.9 | 17 | 16.8667 |  | 14.5 | 13.2 | 16 | 15 | 14.5667
Australia |  | CANTERBURY RACECOUR | CANTERBURY RACECOUR, Australia | 33.90S | 151.12E | 3 | 10.00 (AUE) | 96-06 | 947660 | 1.3 |  | -1.7 | 46.9 | 21.7 | 20.7 | 23.3 | 22 | 21.9 |  | 19.9 | 18.6 | 20.8 | 20 | 19.7667
Australia |  | CAPE BORDA | CAPE BORDA, Australia | 35.75S | 136.58E | 144 | 9.50 (AUA) | 90-04 | 948050 | N/A |  | N/A | N/A | 16.7 | 16.2 | 17.6 | 17 | 16.8333 |  | 16 | 15.3 | 16.2 | 16 | 15.8333
Australia |  | CAPE BRUNY LIGHTHOU | CAPE BRUNY LIGHTHOU, Australia | 43.50S | 147.15E | 53 | 10.00 (AUE) | 82-05 | 949670 | 2.8 |  | 0.6 | 37.4 | 15.2 | 14.7 | 17.1 | 16 | 15.6667 |  | 13.8 | 13.3 | 14.6 | 14 | 13.9
Australia |  | CAPE DON AWS | CAPE DON AWS, Australia | 11.32S | 131.77E | 20 | 9.50 (AUC) | 90-03 | 941290 | N/A |  | N/A | N/A | 30.5 | 29.5 | 30.1 | 30 | 30.0333 |  | 29.8 | 28.7 | 29.1 | 29 | 29.2
Australia |  | CAPE FOURCROY | CAPE FOURCROY, Australia | 11.78S | 130.02E | 7 | 9.50 (AUC) | 83-06 | 941220 | 14.4 |  | 10.5 | 35.9 | 31.3 | 31.9 | 32.1 | 32 | 31.7667 |  | 30.6 | 30.6 | 31.1 | 31 | 30.7667
Australia |  | CAPE GRIM B.A.P.S. | CAPE GRIM B.A.P.S., Australia | 40.67S | 144.68E | 92 | 10.00 (AUE) | 88-06 | 949540 | 3.7 |  | 1.7 | 29.7 | 15.1 | 14.2 | 14.7 | 15 | 14.6667 |  | 14.2 | 13.5 | 13.7 | 14 | 13.8
Australia |  | CAPE JAFFA AWS | CAPE JAFFA AWS, Australia | 36.97S | 139.72E | 18 | 9.50 (AUA) | 91-06 | 948130 | N/A |  | N/A | N/A | 17.2 | 15.9 | 18.1 | 17 | 17.0667 |  | 15.7 | 14.8 | 16 | 16 | 15.5
Australia |  | CAPE LEEUWIN | CAPE LEEUWIN, Australia | 34.37S | 115.13E | 14 | 8.00 (AUW) | 82-06 | 946010 | 7.7 |  | 5 | 39.1 | 20.5 | 19.2 | 19.9 | 20 | 19.8667 |  | 19.5 | 18.1 | 18.3 | 19 | 18.6333
Australia |  | CAPE MORETON LIGHTH | CAPE MORETON LIGHTH, Australia | 27.03S | 153.47E | 101 | 10.00 (AUB) | 90-06 | 945940 | 9.5 |  | 7.3 | 35 | 22.4 | 21.3 | 21.9 | 22 | 21.8667 |  | 21.7 | 20.6 | 21 | 21 | 21.1
Australia |  | CAPE NATURALISTE | CAPE NATURALISTE, Australia | 33.53S | 115.02E | 110 | 8.00 (AUW) | 96-06 | 946000 | 5.8 |  | 3.2 | 37.4 | 20.6 | 20.4 | 19.8 | 20 | 20.2667 |  | 19.6 | 18.3 | 18.4 | 19 | 18.7667
Australia |  | CAPE NELSON LIGHTHO | CAPE NELSON LIGHTHO, Australia | 38.43S | 141.55E | 47 | 10.00 (AUE) | 96-06 | 948260 | 3.6 |  | 1.7 | 42.6 | 18.2 | 16.4 | 19.2 | 18 | 17.9333 |  | 15.8 | 14.7 | 17.1 | 16 | 15.8667
Australia |  | CAPE OTWAY LIGHTHOU | CAPE OTWAY LIGHTHOU, Australia | 38.85S | 143.52E | 83 | 10.00 (AUE) | 82-06 | 948420 | 4.5 |  | 2.6 | 43 | 17.8 | 15.8 | 19.1 | 18 | 17.5667 |  | 16 | 14.5 | 16.8 | 16 | 15.7667
Australia |  | CAPE SORELL | CAPE SORELL, Australia | 42.20S | 145.17E | 20 | 10.00 (AUE) | 94-06 | 949740 | 3.2 |  | 1.6 | 28.9 | 15.7 | 14.4 | 15.9 | 15 | 15.3333 |  | 14.6 | 13.6 | 14.5 | 14 | 14.2333
Australia |  | CAPE WESSEL AWS | CAPE WESSEL AWS, Australia | 11.02S | 136.75E | 19 | 9.50 (AUC) | 82-06 | 941470 | N/A |  | N/A | N/A | 31 | 29.7 | 30.3 | 30 | 30.3333 |  | 30 | 29.1 | 29.6 | 30 | 29.5667
Australia |  | CARNARVON AIRPORT | CARNARVON AIRPORT, Australia | 24.88S | 113.67E | 8 | 8.00 (AUW) | 82-06 | 943000 | 5.7 |  | 2.5 | 46.7 | 27.2 | 26.6 | 27.4 | 27 | 27.0667 |  | 25.5 | 24.1 | 25 | 25 | 24.8667
Australia |  | CATO ISLAND | CATO ISLAND, Australia | 23.25S | 155.53E | 7 | 10.00 (AUB) | 82-06 | 943940 | 15.1 |  | 8.8 | 37.2 | 27.6 | 24.8 | 24.4 | 26 | 25.6 |  | 24.7 | 23.5 | 23.6 | 24 | 23.9333
Australia |  | CEDUNA AMO | CEDUNA AMO, Australia | 32.13S | 133.70E | 16 | 9.50 (AUA) | 82-06 | 946530 | 0.1 |  | -3.1 | 48.9 | 23.9 | 23 | 27.2 | 25 | 24.7 |  | 20.8 | 20.4 | 23.7 | 22 | 21.6333
Australia |  | CENTRE ISLAND | CENTRE ISLAND, Australia | 15.75S | 136.80E | 13 | 9.50 (AUC) | 82-06 | 942480 | 15.2 |  | 10.1 | 39.7 | 29.4 | 28.2 | 29.3 | 29 | 28.9667 |  | 28.4 | 27 | 28.3 | 28 | 27.9
Australia |  | CERBERUS AWS | CERBERUS AWS, Australia | 38.35S | 145.17E | 14 | 10.00 (AUE) | 90-06 | 948980 | -0.3 |  | -3.5 | 44.2 | 17.9 | 16.6 | 19.9 | 18 | 18.1333 |  | 16.1 | 15 | 17.3 | 16 | 16.1333
Australia |  | CESSNOCK AIRPORT | CESSNOCK AIRPORT, Australia | 32.78S | 151.33E | 62 | 10.00 (AUE) | 97-06 | 957710 | -2.8 |  | -6.4 | 46 | 21.4 | 20.4 | 23.9 | 22 | 21.9 |  | 19.1 | 18.5 | 21.5 | 20 | 19.7
Australia |  | CHARLEVILLE AERO | CHARLEVILLE AERO, Australia | 26.42S | 146.27E | 303 | 10.00 (AUB) | 82-06 | 945100 | -1.8 |  | -5.2 | 44.7 | 25.3 | 25.2 | 28.4 | 26 | 26.3 |  | 23.6 | 23 | 25.7 | 24 | 24.1
Australia |  | COBAR AIRPORT AWS | COBAR AIRPORT AWS, Australia | 31.53S | 145.80E | 218 | 10.00 (AUE) | 94-06 | 947100 | -3.6 |  | -6.9 | 48.5 | 23.1 | 21 | 27.4 | 24 | 23.8333 |  | 20.8 | 19 | 23.4 | 21 | 21.0667
Australia |  | COBAR MO | COBAR MO, Australia | 31.48S | 145.83E | 264 | 10.00 (AUE) | 82-06 | 947110 | 0.3 |  | -2.8 | 47.5 | 22.9 | 21.2 | 26.5 | 24 | 23.5333 |  | 20.4 | 19.2 | 22.7 | 21 | 20.7667
Australia |  | COCONUT ISLAND | COCONUT ISLAND, Australia | 10.05S | 143.07E | 4 | 10.00 (AUB) | 92-06 | 941820 | N/A |  | N/A | N/A | 30.7 | 29.5 | 30 | 30 | 30.0667 |  | 29.7 | 28.6 | 29.1 | 29 | 29.1333
Australia |  | COFFS HARBOUR MO | COFFS HARBOUR MO, Australia | 30.32S | 153.12E | 6 | 10.00 (AUE) | 82-06 | 947910 | 1.6 |  | -1.1 | 43.7 | 23.2 | 22.5 | 24.2 | 23 | 23.3 |  | 21.4 | 20.5 | 21.9 | 21 | 21.2667
Australia |  | COMBIENBAR | COMBIENBAR, Australia | 37.33S | 149.02E | 641 | 10.00 (AUE) | 94-06 | 949140 | 0.6 |  | -1.2 | 42.5 | 17.1 | 15.5 | 19.4 | 17 | 17.3333 |  | 15.2 | 13.4 | 17 | 15 | 15.2
Australia |  | CONDOBOLIN AIRPORT | CONDOBOLIN AIRPORT, Australia | 33.07S | 147.22E | 194 | 10.00 (AUE) | 94-06 | 957080 | -3.5 |  | -7.6 | 47 | 21.3 | 19.4 | 24.8 | 22 | 21.8333 |  | 18.7 | 17 | 21 | 19 | 18.9
Australia |  | COOBER PEDY AIRPORT | COOBER PEDY AIRPORT, Australia | 29.03S | 134.72E | 226 | 9.50 (AUA) | 97-06 | 954580 | 1.8 |  | 0.3 | 46.2 | 24.6 | 24.8 | 28.9 | 26 | 26.1 |  | 21.9 | 22.2 | 25.4 | 23 | 23.1667
Australia |  | COOKTOWN MISSION | COOKTOWN MISSION, Australia | 15.43S | 145.18E | 9 | 10.00 (AUB) | 82-04 | 942830 | 10.8 |  | 6.2 | 41.8 | 28.1 | 27.2 | 28.6 | 28 | 27.9667 |  | 27 | 26.4 | 27.2 | 27 | 26.8667
Australia |  | COOLANGATTA AIRPORT | COOLANGATTA AIRPORT, Australia | 28.17S | 153.50E | 6 | 10.00 (AUB) | 90-06 | 945920 | 3.4 |  | 0.2 | 41 | 23.6 | 23 | 24.4 | 24 | 23.6667 |  | 22.3 | 21.8 | 22.4 | 22 | 22.1667
Australia |  | COOMA AIRPORT AWS | COOMA AIRPORT AWS, Australia | 36.30S | 148.97E | 931 | 10.00 (AUE) | 91-06 | 949210 | -8.5 |  | -11 | 39.9 | 15.4 | 13.6 | 17.8 | 16 | 15.6 |  | 13.4 | 11.7 | 14.7 | 13 | 13.2667
Australia |  | COONABARABRAN NAMOI | COONABARABRAN NAMOI, Australia | 31.27S | 149.27E | 510 | 10.00 (AUE) | 90-05 | 947280 | -5.3 |  | -9.2 | 41.9 | 20.2 | 19.7 | 23.2 | 21 | 21.0333 |  | 18.2 | 17.3 | 20.2 | 19 | 18.5667
Australia |  | CREAL REEF | CREAL REEF, Australia | 20.53S | 150.38E | 5 | 10.00 (AUB) | 91-06 | 943710 | 16.4 |  | 15.2 | 32.9 | 25 | 23.6 | 23.3 | 24 | 23.9667 |  | 24.6 | 23.1 | 23 | 24 | 23.5667
Australia |  | CUNDERDIN AIRFIELD | CUNDERDIN AIRFIELD, Australia | 31.62S | 117.22E | 217 | 8.00 (AUW) | 98-06 | 956250 | -1.3 |  | -3.8 | 45.4 | 22.6 | 20.7 | 23 | 22 | 22.1 |  | 20.4 | 18.5 | 19.5 | 19 | 19.4667
Australia |  | CUNNAMULLA POST OFF | CUNNAMULLA POST OFF, Australia | 28.07S | 145.68E | 191 | 10.00 (AUB) | 82-05 | 945000 | 1.3 |  | -1.4 | 46.4 | 25.6 | 24.7 | 29.2 | 27 | 26.5 |  | 23.5 | 22.5 | 26.2 | 24 | 24.0667
Australia |  | CURTIN AERO | CURTIN AERO, Australia | 17.58S | 123.82E | 78 | 8.00 (AUW) | 90-06 | 942040 | 10 |  | 6.8 | 45.5 | 34.1 | 33.8 | 35.7 | 35 | 34.5333 |  | 32.7 | 32.6 | 34.3 | 33 | 33.2
Australia |  | DARWIN AIRPORT | DARWIN AIRPORT, Australia | 12.42S | 130.88E | 30 | 9.50 (AUC) | 82-06 | 941200 | 14.8 |  | 11.2 | 38.4 | 32.5 | 32.2 | 33 | 33 | 32.5667 |  | 31.5 | 31.1 | 31.6 | 31 | 31.4
Australia |  | DERBY AERO | DERBY AERO, Australia | 17.37S | 123.67E | 7 | 8.00 (AUW) | 97-06 | 952050 | N/A |  | N/A | N/A | 32.9 | 33.2 | 34.1 | 33 | 33.4 |  | 31.7 | 31.9 | 32.9 | 32 | 32.1667
Australia |  | DEVONPORT AIRPORT | DEVONPORT AIRPORT, Australia | 41.17S | 146.42E | 10 | 10.00 (AUE) | 92-06 | 959600 | -0.3 |  | -2.1 | 28.7 | 15.7 | 14.7 | 14.9 | 15 | 15.1 |  | 14.6 | 13.6 | 13.7 | 14 | 13.9667
Australia |  | DOUBLE ISLAND POINT | DOUBLE ISLAND POINT, Australia | 25.93S | 153.18E | 95 | 10.00 (AUB) | 90-06 | 945840 | N/A |  | N/A | N/A | 25 | 23.3 | 24.6 | 24 | 24.3 |  | 23.4 | 22 | 23.3 | 23 | 22.9
Australia |  | DUBBO AIRPORT AWS | DUBBO AIRPORT AWS, Australia | 32.22S | 148.57E | 285 | 10.00 (AUE) | 97-06 | 957190 | -2.9 |  | -5.2 | 46.3 | 21 | 19.5 | 21.9 | 21 | 20.8 |  | 19 | 17.5 | 19.9 | 19 | 18.8
Australia |  | DUNNS HILL | DUNNS HILL, Australia | 37.88S | 145.33E | 561 | 10.00 (AUE) | 94-06 | 948720 | 0.4 |  | -2.8 | 39.9 | 14.7 | 12.1 | 16.4 | 14 | 14.4 |  | 13.3 | 10.9 | 14.2 | 13 | 12.8
Australia |  | EAST SALE AIRPORT | EAST SALE AIRPORT, Australia | 38.10S | 147.13E | 8 | 10.00 (AUE) | 82-06 | 949070 | -2.1 |  | -5.2 | 43.6 | 18.4 | 17.6 | 20.5 | 19 | 18.8333 |  | 16.2 | 15.6 | 17.7 | 17 | 16.5
Australia |  | EDDYSTONE POINT | EDDYSTONE POINT, Australia | 41.00S | 148.35E | 21 | 10.00 (AUE) | 82-06 | 949830 | 2.5 |  | -0.6 | 37 | 16.3 | 15.3 | 15.8 | 16 | 15.8 |  | 15.2 | 14.3 | 14.6 | 15 | 14.7
Australia |  | EDITHBURGH AWS | EDITHBURGH AWS, Australia | 35.12S | 137.73E | 7 | 9.50 (AUA) | 90-06 | 948090 | N/A |  | N/A | N/A | 19.3 | 18.2 | 20.6 | 19 | 19.3667 |  | 17.2 | 16.4 | 17.3 | 17 | 16.9667
Australia |  | EILDON FIRE TOWER | EILDON FIRE TOWER, Australia | 37.22S | 145.83E | 638 | 10.00 (AUE) | 96-06 | 948810 | 0.1 |  | -1.8 | 38.2 | 14.5 | 12.3 | 15.2 | 14 | 14 |  | 12.8 | 10.9 | 13.2 | 12 | 12.3
Australia |  | EMERALD AIRPORT | EMERALD AIRPORT, Australia | 23.57S | 148.18E | 190 | 10.00 (AUB) | 83-06 | 943630 | 3 |  | -0.4 | 44.3 | 27.1 | 26.4 | 29.6 | 28 | 27.7 |  | 25.5 | 24.8 | 27.4 | 26 | 25.9
Australia |  | ESPERANCE | ESPERANCE, Australia | 33.83S | 121.88E | 27 | 8.00 (AUW) | 82-06 | 946380 | 4 |  | 1.1 | 46.4 | 22.7 | 21.6 | 25 | 23 | 23.1 |  | 20.3 | 19.1 | 21.2 | 20 | 20.2
Australia |  | ESPERANCE AERO | ESPERANCE AERO, Australia | 33.68S | 121.83E | 144 | 8.00 (AUW) | 92-06 | 956380 | 3.7 |  | 1.8 | 47.8 | 21.3 | 20.8 | 24.1 | 22 | 22.0667 |  | 19.3 | 18.2 | 20.3 | 19 | 19.2667
Australia |  | FALLS CREEK AWS | FALLS CREEK AWS, Australia | 36.87S | 147.27E | 1767 | 10.00 (AUE) | 90-06 | 949030 | -7.7 |  | -9.1 | 28 | 8.7 | 6.5 | 8.4 | 8 | 7.8667 |  | 6.6 | 4.1 | 6.5 | 6 | 5.7333
Australia |  | FLINDERS ISLAND AIR | FLINDERS ISLAND AIR, Australia | 40.10S | 148.00E | 10 | 10.00 (AUE) | 93-06 | 949800 | -1.1 |  | -3 | 41 | 17.8 | 15.9 | 18.1 | 17 | 17.2667 |  | 16.2 | 15 | 16.2 | 16 | 15.8
Australia |  | FLINDERS REEF | FLINDERS REEF, Australia | 17.72S | 148.45E | 7 | 10.00 (AUB) | 82-06 | 942900 | 18.8 |  | 14.3 | 34.1 | 26.2 | 25.4 | 25.2 | 26 | 25.6 |  | 25.6 | 24.7 | 24.4 | 25 | 24.9
Australia |  | FORBES AIRPORT | FORBES AIRPORT, Australia | 33.37S | 147.92E | 231 | 10.00 (AUE) | 96-06 | 947150 | -3.6 |  | -7.7 | 46.3 | 20.5 | 18.4 | 21.6 | 20 | 20.1667 |  | 18.2 | 16.6 | 18.9 | 18 | 17.9
Australia |  | FORREST | FORREST, Australia | 30.83S | 128.12E | 160 | 8.00 (AUW) | 93-06 | 956460 | -0.5 |  | -3.4 | 47.5 | 24.3 | 25 | 30.4 | 27 | 26.5667 |  | 22.1 | 22.4 | 26.4 | 24 | 23.6333
Australia |  | FRANKSTON AWS | FRANKSTON AWS, Australia | 38.15S | 145.12E | 6 | 10.00 (AUE) | 94-06 | 948710 | 3.5 |  | 1.2 | 40.4 | 18.2 | 15.5 | 18.7 | 17 | 17.4667 |  | 16.6 | 14.3 | 16.8 | 16 | 15.9
Australia |  | GABO ISLAND | GABO ISLAND, Australia | 37.57S | 149.90E | 15 | 10.00 (AUE) | 82-06 | 949330 | 6 |  | 4.5 | 36.5 | 17.9 | 17.3 | 18.3 | 18 | 17.8333 |  | 16.8 | 15.6 | 16.3 | 16 | 16.2333
Australia |  | GANNET CAY | GANNET CAY, Australia | 21.97S | 152.47E | 8 | 10.00 (AUB) | 91-06 | 943790 | N/A |  | N/A | N/A | 24.6 | 23.4 | 23 | 24 | 23.6667 |  | 24.2 | 23 | 22.6 | 23 | 23.2667
Australia |  | GAYNDAH POST OFFICE | GAYNDAH POST OFFICE, Australia | 25.63S | 151.62E | 108 | 10.00 (AUB) | 90-02 | 945430 | 0.5 |  | -2.4 | 42.7 | 25.9 | 25.6 | 27.6 | 26 | 26.3667 |  | 24.4 | 24 | 25.8 | 25 | 24.7333
Australia |  | GEELONG AIRPORT | GEELONG AIRPORT, Australia | 38.23S | 144.33E | 35 | 10.00 (AUE) | 90-06 | 948570 | -0.3 |  | -4.2 | 45.4 | 18.2 | 17.3 | 20.2 | 19 | 18.5667 |  | 16.1 | 15.3 | 17.5 | 16 | 16.3
Australia |  | GELANTIPY | GELANTIPY, Australia | 37.22S | 148.27E | 760 | 10.00 (AUE) | 93-06 | 949130 | -1.9 |  | -4.4 | 37.5 | 15.4 | 13.5 | 17.4 | 15 | 15.4333 |  | 13.5 | 11.7 | 14.7 | 13 | 13.3
Australia |  | GEORGETOWN POST OFF | GEORGETOWN POST OFF, Australia | 18.30S | 143.55E | 295 | 10.00 (AUB) | 82-05 | 942750 | 4.7 |  | -1.2 | 43.6 | 30.9 | 30.6 | 33.1 | 32 | 31.5333 |  | 29.5 | 29.2 | 31.3 | 30 | 30
Australia |  | GERALDTON AIRPORT | GERALDTON AIRPORT, Australia | 28.80S | 114.70E | 35 | 8.00 (AUW) | 82-06 | 944030 | 3.3 |  | 0.6 | 46.7 | 25.1 | 23.4 | 24.2 | 24 | 24.2333 |  | 23 | 21.4 | 21.9 | 22 | 22.1
Australia |  | GILES METEOROLOGICA | GILES METEOROLOGICA, Australia | 25.03S | 128.30E | 599 | 8.00 (AUW) | 82-06 | 944610 | 1.8 |  | -1.5 | 44 | 26.7 | 25.8 | 29 | 27 | 27.1667 |  | 24 | 23.7 | 26.8 | 25 | 24.8333
Australia |  | GLADSTONE AIRPORT | GLADSTONE AIRPORT, Australia | 23.87S | 151.22E | 17 | 10.00 (AUB) | 94-06 | 943810 | 6.1 |  | 3.9 | 38.5 | 26.1 | 25.1 | 25.8 | 26 | 25.6667 |  | 24.7 | 23.7 | 24.3 | 24 | 24.2333
Australia |  | GLADSTONE RADAR | GLADSTONE RADAR, Australia | 23.85S | 151.27E | 75 | 10.00 (AUB) | 82-06 | 943800 | 9 |  | 6 | 39.2 | 25.9 | 25 | 26.3 | 26 | 25.7333 |  | 24.4 | 23.7 | 24.7 | 24 | 24.2667
Australia |  | GLEN INNES AIRPORT | GLEN INNES AIRPORT, Australia | 29.68S | 151.70E | 1045 | 10.00 (AUE) | 98-06 | 945880 | -9.5 |  | -13.3 | 36 | 17.4 | 16.1 | 19.2 | 18 | 17.5667 |  | 15.7 | 14.8 | 16.6 | 16 | 15.7
Australia |  | GOLD COAST SEAWAY | GOLD COAST SEAWAY, Australia | 27.93S | 153.43E | 3 | 10.00 (AUB) | 93-06 | 945800 | 7.5 |  | 2.7 | 39 | 24.2 | 23.6 | 24.9 | 24 | 24.2333 |  | 22.7 | 22 | 23.1 | 23 | 22.6
Australia |  | GOLDSTREAM | GOLDSTREAM, Australia | 37.73S | 145.40E | 84 | 10.00 (AUE) | 95-06 | 948640 | -3.3 |  | -6 | 43.7 | 18.1 | 16 | 20 | 18 | 18.0333 |  | 16.7 | 14.7 | 17.4 | 16 | 16.2667
Australia |  | GOONDIWINDI AIRPORT | GOONDIWINDI AIRPORT, Australia | 28.52S | 150.32E | 219 | 10.00 (AUB) | 90-05 | 945300 | N/A |  | N/A | N/A | 23.5 | 23.3 | 27.3 | 25 | 24.7 |  | 22.1 | 21.2 | 24.2 | 23 | 22.5
Australia |  | GOULBURN AIRPORT AW | GOULBURN AIRPORT AW, Australia | 34.82S | 149.73E | 641 | 10.00 (AUE) | 90-06 | 957160 | -7.7 |  | -11.4 | 43.1 | 17 | 15.2 | 19.4 | 17 | 17.2 |  | 14.9 | 13.2 | 16.5 | 15 | 14.8667
Australia |  | GOVE AIRPORT | GOVE AIRPORT, Australia | 12.28S | 136.82E | 53 | 9.50 (AUC) | 86-06 | 941500 | 14.1 |  | 10.7 | 39.4 | 29.6 | 28.9 | 29.9 | 29 | 29.4667 |  | 28.9 | 28.1 | 28.7 | 29 | 28.5667
Australia |  | GREEN ISLAND | GREEN ISLAND, Australia | 16.77S | 145.97E | 3 | 10.00 (AUB) | 93-06 | 952890 | 16.5 |  | 12.2 | 38.2 | 26 | 25.1 | 26.3 | 26 | 25.8 |  | 25.2 | 24.4 | 25.3 | 25 | 24.9667
Australia |  | GRIFFITH AWS | GRIFFITH AWS, Australia | 34.32S | 146.07E | 125 | 10.00 (AUE) | 90-03 | 947050 | N/A |  | N/A | N/A | 21.3 | 19.1 | 23.5 | 21 | 21.3 |  | 19 | 17.1 | 19.6 | 19 | 18.5667
Australia |  | HALLS CREEK AIRPORT | HALLS CREEK AIRPORT, Australia | 18.23S | 127.67E | 424 | 8.00 (AUW) | 97-06 | 942120 | 7.6 |  | 4.6 | 44.9 | 31.5 | 31.1 | 33.3 | 32 | 31.9667 |  | 30 | 29.7 | 31.9 | 31 | 30.5333
Australia |  | HAMILTON AIRPORT | HAMILTON AIRPORT, Australia | 37.65S | 142.07E | 242 | 10.00 (AUE) | 90-06 | 948290 | -0.4 |  | -2.8 | 43 | 16.4 | 14.7 | 18.2 | 16 | 16.4333 |  | 14.5 | 13.2 | 15.9 | 15 | 14.5333
Australia |  | HAY AWS | HAY AWS, Australia | 34.53S | 144.87E | 90 | 10.00 (AUE) | 91-06 | 947010 | N/A |  | N/A | N/A | 21.3 | 19.3 | 23.9 | 22 | 21.5 |  | 19 | 17 | 20.4 | 19 | 18.8
Australia |  | HERON ISLAND RES ST | HERON ISLAND RES ST, Australia | 23.45S | 151.92E | 5 | 10.00 (AUB) | 90-06 | 943860 | 13 |  | 11.2 | 35 | 25.5 | 24.1 | 25.3 | 25 | 24.9667 |  | 24.4 | 23.1 | 24.2 | 24 | 23.9
Australia |  | HOBART AIRPORT | HOBART AIRPORT, Australia | 42.83S | 147.50E | 27 | 10.00 (AUE) | 82-06 | 949750 | 0.2 |  | -2.4 | 42.3 | 16.8 | 16.1 | 18.4 | 17 | 17.1 |  | 15.2 | 14.5 | 16.2 | 15 | 15.3
Australia |  | HOBART ELLERSLIE RO | HOBART ELLERSLIE RO, Australia | 42.88S | 147.33E | 51 | 10.00 (AUE) | 90-06 | 949700 | 0.7 |  | -1.6 | 41.6 | 16.4 | 15.8 | 18.6 | 17 | 16.9333 |  | 14.9 | 14.2 | 16.3 | 15 | 15.1333
Australia |  | HOLMES REEF | HOLMES REEF, Australia | 16.47S | 147.87E | 8 | 10.00 (AUB) | 91-06 | 942890 | N/A |  | N/A | N/A | 26.6 | 26 | 25.1 | 26 | 25.9 |  | 26.1 | 25.1 | 24.5 | 25 | 25.2333
Australia |  | HOMEBUSH (OLYMPIC SITE) | HOMEBUSH (OLYMPIC SITE), Australia | 33.85S | 151.07E | 28 | 10.00 (AUE) | 96-06 | 957650 | 2.7 |  | -8.9 | 46 | 21.9 | 20.9 | 23.7 | 22 | 22.1667 |  | 20.2 | 19 | 21.5 | 20 | 20.2333
Australia |  | HUNTERS HILL | HUNTERS HILL, Australia | 36.22S | 147.53E | 981 | 10.00 (AUE) | 97-06 | 948780 | -1.8 |  | -3.5 | 36.8 | 13.3 | 10.7 | 15.1 | 13 | 13.0333 |  | 11.5 | 9.4 | 12.8 | 11 | 11.2333
Australia |  | JABIRU AIRPORT | JABIRU AIRPORT, Australia | 12.67S | 132.90E | 28 | 9.50 (AUC) | 91-06 | 941370 | 13.4 |  | 9.8 | 41.8 | 33.7 | 33.7 | 35.1 | 34 | 34.1667 |  | 32.7 | 32.7 | 34 | 33 | 33.1333
Australia |  | JACUP | JACUP, Australia | 33.88S | 119.10E | 306 | 8.00 (AUW) | 94-06 | 956360 | 0.7 |  | -1.7 | 45.1 | 21.1 | 19.5 | 21.7 | 21 | 20.7667 |  | 18.7 | 17.1 | 18.6 | 18 | 18.1333
Australia |  | JANDAKOT AERO | JANDAKOT AERO, Australia | 32.10S | 115.88E | 31 | 8.00 (AUW) | 93-06 | 946090 | -0.8 |  | -3.9 | 43.3 | 22.1 | 21.6 | 21.7 | 22 | 21.8 |  | 20.3 | 19.4 | 19.8 | 20 | 19.8333
Australia |  | KALGOORLIE-BOULDER | KALGOORLIE-BOULDER, Australia | 30.78S | 121.45E | 370 | 8.00 (AUW) | 82-06 | 946370 | -0.3 |  | -2.4 | 47 | 22.9 | 23 | 27.2 | 24 | 24.3667 |  | 20.6 | 20.3 | 24 | 22 | 21.6333
Australia |  | KARRATHA AERO | KARRATHA AERO, Australia | 20.72S | 116.77E | 6 | 8.00 (AUW) | 94-06 | 953070 | 9.6 |  | 6.2 | 46.6 | 30.7 | 29.2 | 30.6 | 30 | 30.1667 |  | 28.7 | 27.7 | 29.2 | 29 | 28.5333
Australia |  | KARRATHA LEGENDRE I | KARRATHA LEGENDRE I, Australia | 20.37S | 116.85E | 29 | 8.00 (AUW) | 93-06 | 943070 | 15.3 |  | 13.2 | 40.6 | 27.3 | 26 | 27 | 27 | 26.7667 |  | 26 | 25 | 25.9 | 26 | 25.6333
Australia |  | KATANNING | KATANNING, Australia | 33.68S | 117.55E | 311 | 8.00 (AUW) | 90-99 | 946290 | N/A |  | N/A | N/A | 19.2 | 18.6 | 20.6 | 19 | 19.4667 |  | 17.3 | 16.6 | 17.5 | 17 | 17.1333
Australia |  | KATOOMBA | KATOOMBA, Australia | 33.72S | 150.28E | 1030 | 10.00 (AUE) | 90-05 | 947440 | -1.5 |  | -3.3 | 38 | 14.9 | 13.7 | 18 | 16 | 15.5333 |  | 13.2 | 11.9 | 15 | 13 | 13.3667
Australia |  | KHANCOBAN | KHANCOBAN, Australia | 36.23S | 148.13E | 340 | 10.00 (AUE) | 98-06 | 949190 | -2.5 |  | -3.9 | 42 | 16.3 | 15.8 | 18.7 | 17 | 16.9333 |  | 14.1 | 13.5 | 16.2 | 15 | 14.6
Australia |  | KILMORE GAP | KILMORE GAP, Australia | 37.38S | 144.97E | 528 | 10.00 (AUE) | 94-06 | 948600 | 0.7 |  | -1.4 | 40.1 | 13.7 | 11.6 | 15.3 | 14 | 13.5333 |  | 12.5 | 10.3 | 13.2 | 12 | 12
Australia |  | KING ISLAND AIRPORT | KING ISLAND AIRPORT, Australia | 39.88S | 143.88E | 38 | 10.00 (AUE) | 96-06 | 948500 | 1.1 |  | -0.1 | 39.5 | 16.6 | 14.7 | 16.9 | 16 | 16.0667 |  | 15 | 14 | 15.2 | 15 | 14.7333
Australia |  | KING ISLAND CURRIE | KING ISLAND CURRIE, Australia | 39.93S | 143.85E | 24 | 10.00 (AUE) | 82-95 | 948510 | N/A |  | N/A | N/A | 15.8 | 15.2 | 16.4 | 16 | 15.8 |  | 14.7 | 14.5 | 15.1 | 15 | 14.7667
Australia |  | KUNUNURRA AERO | KUNUNURRA AERO, Australia | 15.78S | 128.72E | 44 | 8.00 (AUW) | 92-06 | 942160 | 9.1 |  | 6.9 | 45.1 | 33.9 | 34 | 35.6 | 35 | 34.5 |  | 32.8 | 32.6 | 34.1 | 33 | 33.1667
Australia |  | KYANCUTTA | KYANCUTTA, Australia | 33.13S | 135.55E | 58 | 9.50 (AUA) | 90-03 | 946570 | -1.6 |  | -7.9 | 46.5 | 22.5 | 21.6 | 25.4 | 23 | 23.1667 |  | 19.7 | 19.6 | 22.1 | 20 | 20.4667
Australia |  | LADY ELLIOT ISLAND | LADY ELLIOT ISLAND, Australia | 24.12S | 152.72E | 4 | 10.00 (AUB) | 82-06 | 943880 | N/A |  | N/A | N/A | 25.2 | 23.5 | 24 | 24 | 24.2333 |  | 24.1 | 22.7 | 23.1 | 23 | 23.3
Australia |  | LAKE GRACE | LAKE GRACE, Australia | 33.12S | 118.47E | 287 | 8.00 (AUW) | 83-04 | 946350 | 0.7 |  | -1 | 44.3 | 21.1 | 19.3 | 20.6 | 20 | 20.3333 |  | 18.9 | 17.1 | 18.3 | 18 | 18.1
Australia |  | LANCELIN | LANCELIN, Australia | 31.02S | 115.32E | 5 | 8.00 (AUW) | 90-06 | 956060 | 4.4 |  | 1.8 | 44.7 | 23.2 | 22.2 | 22.1 | 23 | 22.5 |  | 21.6 | 20.2 | 20.5 | 21 | 20.7667
Australia |  | LATROBE VALLEY AIRP | LATROBE VALLEY AIRP, Australia | 38.22S | 146.47E | 56 | 10.00 (AUE) | 90-06 | 948910 | -1.7 |  | -3.6 | 43 | 17.7 | 17.5 | 19.8 | 18 | 18.3333 |  | 15.6 | 15.3 | 17.4 | 16 | 16.1
Australia |  | LAUNCESTON AIRPORT | LAUNCESTON AIRPORT, Australia | 41.53S | 147.20E | 178 | 10.00 (AUE) | 88-06 | 949680 | -3.1 |  | -5.3 | 36.3 | 14.8 | 13.7 | 15.2 | 15 | 14.5667 |  | 13.6 | 12.7 | 13.6 | 13 | 13.3
Australia |  | LAVERTON AERO | LAVERTON AERO, Australia | 28.62S | 122.42E | 465 | 8.00 (AUW) | 92-06 | 944490 | -0.4 |  | -3 | 45.9 | 24.2 | 24.2 | 28.7 | 26 | 25.7 |  | 21.6 | 22.5 | 25.7 | 23 | 23.2667
Australia |  | LAVERTON AERODROME | LAVERTON AERODROME, Australia | 37.87S | 144.75E | 20 | 10.00 (AUE) | 82-06 | 948650 | -0.5 |  | -3.5 | 45 | 18.2 | 17.2 | 20.3 | 19 | 18.5667 |  | 16.4 | 15.2 | 17.5 | 16 | 16.3667
Australia |  | LEARMONTH AIRPORT | LEARMONTH AIRPORT, Australia | 22.23S | 114.08E | 5 | 8.00 (AUW) | 82-06 | 943020 | 6.5 |  | 2.9 | 47.5 | 27.8 | 27.2 | 29.6 | 28 | 28.2 |  | 26.2 | 25.5 | 27.8 | 27 | 26.5
Australia |  | LEINSTER AERO | LEINSTER AERO, Australia | 27.85S | 120.70E | 498 | 8.00 (AUW) | 94-06 | 954480 | N/A |  | N/A | N/A | 25.1 | 24.5 | 29.2 | 26 | 26.2667 |  | 22.7 | 22.6 | 26.5 | 24 | 23.9333
Australia |  | LEONORA POST OFFICE | LEONORA POST OFFICE, Australia | 28.88S | 121.33E | 380 | 8.00 (AUW) | 82-05 | 944480 | 1.1 |  | -0.7 | 47.4 | 23.8 | 24.1 | 28.3 | 25 | 25.4 |  | 21.8 | 21.7 | 24.8 | 23 | 22.7667
Australia |  | LIHOU REEF | LIHOU REEF, Australia | 17.12S | 152.00E | 9 | 10.00 (AUB) | 82-06 | 942960 | 16.6 |  | -2.8 | 49.1 | 34.8 | 29.4 | 25.2 | 30 | 29.8 |  | 27.9 | 25.2 | 24.7 | 26 | 25.9333
Australia |  | LONGERENONG | LONGERENONG, Australia | 36.67S | 142.30E | 91 | 10.00 (AUE) | 98-06 | 958350 | -2.4 |  | -5.7 | 45.7 | 18.8 | 16.5 | 20.7 | 19 | 18.6667 |  | 16 | 14.7 | 17.9 | 16 | 16.2
Australia |  | LONGREACH AERO | LONGREACH AERO, Australia | 23.43S | 144.28E | 192 | 10.00 (AUB) | 82-06 | 943460 | 1 |  | -1.5 | 46.9 | 29.2 | 29.1 | 31.5 | 30 | 29.9333 |  | 27.3 | 26.8 | 29.1 | 28 | 27.7333
Australia |  | LOOKOUT HILL | LOOKOUT HILL, Australia | 37.28S | 143.25E | 965 | 10.00 (AUE) | 92-06 | 948350 | -1.5 |  | -4.6 | 36.3 | 11.6 | 11.9 | 14.8 | 13 | 12.7667 |  | 9.9 | 9.4 | 12.1 | 10 | 10.4667
Australia |  | LORD HOWE ISLAND AE | LORD HOWE ISLAND AE, Australia | 31.53S | 159.07E | 7 | 10.50 (AUH) | 83-06 | 949950 | 8.3 |  | 6.2 | 31.6 | 21.7 | 20.7 | 20.7 | 21 | 21.0333 |  | 21 | 20.1 | 20 | 20 | 20.3667
Australia |  | LOW ROCKY POINT (AWS) | LOW ROCKY POINT (AWS), Australia | 42.98S | 145.50E | 35 | 10.00 (AUE) | 92-06 | 959610 | 1.3 |  | -0.7 | 35.1 | 16.1 | 14.6 | 16.7 | 16 | 15.8 |  | 14.4 | 13.5 | 14.8 | 14 | 14.2333
Australia |  | LUCINDA POINT AWS | LUCINDA POINT AWS, Australia | 18.52S | 146.40E | 10 | 10.00 (AUB) | 90-06 | 942950 | N/A |  | N/A | N/A | 25.8 | 25.1 | 25.7 | 26 | 25.5333 |  | 25 | 23.9 | 24.6 | 25 | 24.5
Australia |  | MAATSUYKER ISLAND L | MAATSUYKER ISLAND L, Australia | 43.65S | 146.27E | 148 | 10.00 (AUE) | 90-06 | 949620 | 3.1 |  | 0.6 | 31.6 | 16 | 14.3 | 15.7 | 15 | 15.3333 |  | 14 | 13 | 13.9 | 14 | 13.6333
Australia |  | MACKAY MO | MACKAY MO, Australia | 21.12S | 149.22E | 33 | 10.00 (AUB) | 82-06 | 943670 | 7.4 |  | 4.7 | 36.7 | 25.5 | 24.5 | 25.7 | 25 | 25.2333 |  | 23.6 | 22.9 | 24.4 | 24 | 23.6333
Australia |  | MACQUARIE ISLAND | MACQUARIE ISLAND, Australia | 54.50S | 158.95E | 8 | 11.00 (PCC) | 82-06 | 949980 | -4.7 |  | -9.6 | 14.3 | 7.2 | 7.1 | 7.1 | 7 | 7.1333 |  | 6.7 | 6.6 | 6.6 | 7 | 6.6333
Australia |  | MALLACOOTA | MALLACOOTA, Australia | 37.60S | 149.73E | 22 | 10.00 (AUE) | 94-06 | 949350 | 1.8 |  | 0.1 | 42 | 19.4 | 18.3 | 20.8 | 20 | 19.5 |  | 17.2 | 16.3 | 18.1 | 17 | 17.2
Australia |  | MANDURAH | MANDURAH, Australia | 32.52S | 115.72E | 4 | 8.00 (AUW) | 90-06 | 946050 | 3.8 |  | -1.5 | 43 | 21.5 | 20.4 | 20.5 | 21 | 20.8 |  | 19.8 | 18.7 | 19.1 | 19 | 19.2
Australia |  | MANGALORE AWS COMPO | MANGALORE AWS COMPO, Australia | 36.88S | 145.18E | 141 | 10.00 (AUE) | 91-06 | 948740 | -2.5 |  | -4.3 | 43.2 | 17.7 | 15.2 | 18.6 | 17 | 17.1667 |  | 15.5 | 13.7 | 16.3 | 15 | 15.1667
Australia |  | MANGROVE MOUNTAIN A | MANGROVE MOUNTAIN A, Australia | 33.28S | 151.22E | 305 | 10.00 (AUE) | 97-06 | 957740 | 1.5 |  | -0.5 | 44.2 | 20.1 | 18.6 | 22 | 20 | 20.2333 |  | 17.9 | 16.7 | 19.7 | 18 | 18.1
Australia |  | MARION REEF | MARION REEF, Australia | 19.08S | 152.38E | 8 | 10.00 (AUB) | 82-06 | 942980 | 18.4 |  | 15.6 | 38.4 | 26.6 | 25.2 | 24.4 | 25 | 25.4 |  | 25.8 | 24.4 | 24 | 25 | 24.7333
Australia |  | MARLA POLICE STATIO | MARLA POLICE STATIO, Australia | 27.30S | 133.62E | 324 | 9.50 (AUA) | 85-04 | 944770 | N/A |  | N/A | N/A | 27.8 | 26.2 | 29.8 | 28 | 27.9333 |  | 24.2 | 23.8 | 26.6 | 25 | 24.8667
Australia |  | MAROOCHYDORE AERO | MAROOCHYDORE AERO, Australia | 26.60S | 153.10E | 4 | 10.00 (AUB) | 94-06 | 945690 | 3 |  | 1.1 | 38.9 | 24.4 | 23.7 | 24.9 | 24 | 24.3333 |  | 22.7 | 22.1 | 22.7 | 23 | 22.5
Australia |  | MARYBOROUGH COMPOSI | MARYBOROUGH COMPOSI, Australia | 25.52S | 152.72E | 11 | 10.00 (AUB) | 90-05 | 945670 | 2 |  | -0.2 | 38.3 | 25.5 | 24.9 | 25.7 | 25 | 25.3667 |  | 23.9 | 23.2 | 24.3 | 24 | 23.8
Australia |  | MEEKATHARRA AIRPORT | MEEKATHARRA AIRPORT, Australia | 26.62S | 118.55E | 519 | 8.00 (AUW) | 82-06 | 944300 | 2.5 |  | -0.2 | 45.7 | 25 | 24.5 | 29.2 | 26 | 26.2333 |  | 23.1 | 22.7 | 26.6 | 24 | 24.1333
Australia |  | MELBOURNE | MELBOURNE, Australia | 37.82S | 144.97E | 32 | 10.00 (AUE) | 91-06 | 948680 | 2.4 |  | -0.5 | 44.6 | 18.9 | 17.4 | 21 | 19 | 19.1 |  | 17.3 | 15.8 | 18.7 | 17 | 17.2667
Australia |  | MELBOURNE AIRPORT | MELBOURNE AIRPORT, Australia | 37.67S | 144.85E | 119 | 10.00 (AUE) | 85-06 | 948660 | 0.6 |  | -2.3 | 44.6 | 17.9 | 16.3 | 19.9 | 18 | 18.0333 |  | 16.1 | 14.8 | 17.2 | 16 | 16.0333
Australia |  | MILDURA AIRPORT | MILDURA AIRPORT, Australia | 34.23S | 142.08E | 53 | 10.00 (AUE) | 82-06 | 946930 | -1 |  | -4.4 | 47.1 | 21.4 | 19.8 | 24.8 | 22 | 22 |  | 18.7 | 17.6 | 21.4 | 19 | 19.2333
Australia |  | MILINGIMBI | MILINGIMBI, Australia | 12.12S | 134.90E | 5 | 9.50 (AUC) | 88-06 | 941400 | N/A |  | N/A | N/A | 31 | 30.5 | 30.7 | 31 | 30.7333 |  | 30.2 | 29.6 | 29.7 | 30 | 29.8333
Australia |  | MOOMBA AIRPORT | MOOMBA AIRPORT, Australia | 28.10S | 140.20E | 38 | 9.50 (AUA) | 96-06 | 954810 | 2.2 |  | -0.9 | 47.4 | 27.1 | 25.7 | 29.4 | 27 | 27.4 |  | 24.7 | 23.1 | 26.9 | 25 | 24.9
Australia |  | MOORABBIN AIRPORT | MOORABBIN AIRPORT, Australia | 37.98S | 145.10E | 13 | 10.00 (AUE) | 92-06 | 948700 | 0.2 |  | -2.6 | 44.4 | 18.6 | 17.1 | 20.7 | 19 | 18.8 |  | 16.9 | 15.3 | 18.3 | 17 | 16.8333
Australia |  | MOREE | MOREE, Australia | 29.47S | 149.85E | 212 | 10.00 (AUE) | 82-95 | 945270 | -0.9 |  | -3.2 | 44.2 | 22.3 | 22.2 | 23.3 | 23 | 22.6 |  | 20.6 | 20.1 | 21.2 | 21 | 20.6333
Australia |  | MOREE AERO | MOREE AERO, Australia | 29.48S | 149.83E | 218 | 10.00 (AUE) | 95-06 | 955270 | -1.5 |  | -4.6 | 43.4 | 23.4 | 21.6 | 26.4 | 24 | 23.8 |  | 21.9 | 20.3 | 23.5 | 22 | 21.9
Australia |  | MORTLAKE AWS | MORTLAKE AWS, Australia | 38.07S | 142.77E | 131 | 10.00 (AUE) | 90-06 | 948400 | -1.8 |  | -5.2 | 44 | 17.3 | 15.6 | 18.7 | 17 | 17.2 |  | 15.1 | 14 | 16.1 | 15 | 15.0667
Australia |  | MORUYA HEADS PILOT | MORUYA HEADS PILOT, Australia | 35.92S | 150.15E | 17 | 10.00 (AUE) | 90-05 | 949370 | 2.7 |  | -0.2 | 42.7 | 20.6 | 19.7 | 22.8 | 21 | 21.0333 |  | 19.1 | 17.8 | 19.4 | 19 | 18.7667
Australia |  | MOUNT BOYCE | MOUNT BOYCE, Australia | 33.62S | 150.27E | 1080 | 10.00 (AUE) | 90-06 | 947430 | -2.1 |  | -4 | 37.9 | 18.7 | 13.4 | 17 | 16 | 16.3667 |  | 15 | 11.6 | 14.5 | 14 | 13.7
Australia |  | MOUNT BULLER AWS | MOUNT BULLER AWS, Australia | 37.15S | 146.43E | 1707 | 10.00 (AUE) | 93-06 | 948940 | N/A |  | N/A | N/A | 8.5 | 6.5 | 7.8 | 8 | 7.6 |  | 7 | 4.4 | 6.5 | 6 | 5.9667
Australia |  | MOUNT GAMBIER AERO | MOUNT GAMBIER AERO, Australia | 37.73S | 140.78E | 69 | 9.50 (AUA) | 82-06 | 948210 | -0.4 |  | -3.1 | 43.3 | 17.7 | 16.2 | 19.3 | 18 | 17.7333 |  | 15.5 | 14.5 | 16.9 | 16 | 15.6333
Australia |  | MOUNT ISA AERO | MOUNT ISA AERO, Australia | 20.68S | 139.48E | 341 | 10.00 (AUB) | 82-06 | 943320 | 2 |  | -2 | 45.2 | 30.3 | 29.7 | 32.4 | 31 | 30.8 |  | 28.3 | 27.9 | 30.6 | 29 | 28.9333
Australia |  | MOUNT LAWLEY PERTH | MOUNT LAWLEY PERTH, Australia | 31.92S | 115.87E | 25 | 8.00 (AUW) | 90-06 | 946080 | 1.4 |  | -1.3 | 44.7 | 22.4 | 22 | 22.6 | 22 | 22.3333 |  | 20.7 | 19.7 | 20.4 | 20 | 20.2667
Australia |  | MT HOTHAM AWS | MT HOTHAM AWS, Australia | 36.97S | 147.12E | 1849 | 10.00 (AUE) | 90-06 | 949060 | -8.5 |  | -10 | 25.5 | 6.9 | 4.4 | 7 | 6 | 6.1 |  | 5.5 | 2.5 | 5.1 | 4 | 4.3667
Australia |  | MT LOFTY AWS | MT LOFTY AWS, Australia | 34.97S | 138.70E | 730 | 9.50 (AUA) | 90-06 | 956780 | N/A |  | N/A | N/A | 15.9 | 13 | 16.7 | 15 | 15.2 |  | 13.3 | 11.6 | 15.2 | 13 | 13.3667
Australia |  | MT MOORNAPA | MT MOORNAPA, Australia | 37.75S | 147.13E | 486 | 10.00 (AUE) | 94-06 | 959130 | 1.6 |  | -0.2 | 45.1 | 17.4 | 15.7 | 19.9 | 18 | 17.6667 |  | 15.6 | 13.8 | 17 | 15 | 15.4667
Australia |  | MT WELLINGTON | MT WELLINGTON, Australia | 42.88S | 147.23E | 1261 | 10.00 (AUE) | 90-06 | 959790 | -5.8 |  | -8.2 | 31.9 | 8.5 | 6.4 | 10 | 8 | 8.3 |  | 6.8 | 5 | 7.2 | 6 | 6.3333
Australia |  | MUDGEE AIRPORT AWS | MUDGEE AIRPORT AWS, Australia | 32.57S | 149.62E | 472 | 10.00 (AUE) | 90-06 | 947270 | -4.8 |  | -8 | 43.1 | 19 | 17.8 | 21.5 | 19 | 19.4333 |  | 16.6 | 15.9 | 18.8 | 17 | 17.1
Australia |  | NAMBOUR DPI | NAMBOUR DPI, Australia | 26.65S | 152.93E | 33 | 10.00 (AUB) | 96-06 | 955720 | N/A |  | N/A | N/A | 25.3 | 24.8 | 26.6 | 26 | 25.5667 |  | 23.4 | 22.9 | 24.4 | 24 | 23.5667
Australia |  | NEPTUNE ISLAND | NEPTUNE ISLAND, Australia | 35.33S | 136.12E | 32 | 9.50 (AUA) | 82-06 | 948040 | 8.5 |  | 5.9 | 35 | 18 | 17.4 | 18.6 | 18 | 18 |  | 17.2 | 16.5 | 16.9 | 17 | 16.8667
Australia |  | NEWCASTLE NOBBYS SI | NEWCASTLE NOBBYS SI, Australia | 32.92S | 151.78E | 33 | 10.00 (AUE) | 90-06 | 947740 | 5.3 |  | 1.8 | 42.9 | 21.9 | 21.2 | 25.4 | 23 | 22.8333 |  | 20 | 19 | 21.3 | 20 | 20.1
Australia |  | NORAH HEAD LIGHTHOU | NORAH HEAD LIGHTHOU, Australia | 33.27S | 151.57E | 20 | 10.00 (AUE) | 95-06 | 957700 | 6.1 |  | 4.3 | 43.4 | 21.8 | 20.5 | 24.8 | 22 | 22.3667 |  | 19.8 | 18.7 | 21.1 | 20 | 19.8667
Australia |  | NORMANTON | NORMANTON, Australia | 17.67S | 141.08E | 10 | 10.00 (AUB) | 84-00 | 942670 | N/A |  | N/A | N/A | 32.2 | 32 | 34 | 33 | 32.7333 |  | 31 | 30.7 | 32.1 | 31 | 31.2667
Australia |  | NORSEMAN | NORSEMAN, Australia | 32.20S | 121.78E | 278 | 8.00 (AUW) | 90-04 | 946390 | N/A |  | N/A | N/A | 21.6 | 21.8 | 25.3 | 23 | 22.9 |  | 19.8 | 19.6 | 21.9 | 20 | 20.4333
Australia |  | NORTH EAST ISLAND | NORTH EAST ISLAND, Australia | 13.65S | 136.93E | 18 | 9.50 (AUC) | 83-06 | 941510 | 19.8 |  | 14.8 | 35.9 | 29.8 | 28.2 | 28.3 | 29 | 28.7667 |  | 29 | 27.6 | 27.7 | 28 | 28.1
Australia |  | NOWRA RAN AIR STATI | NOWRA RAN AIR STATI, Australia | 34.95S | 150.53E | 105 | 10.00 (AUE) | 89-06 | 947500 | 1.9 |  | -0.7 | 46.7 | 21.1 | 19.9 | 23.7 | 22 | 21.5667 |  | 19 | 17.8 | 20.6 | 19 | 19.1333
Australia |  | NULLARBOR ROADHOUSE | NULLARBOR ROADHOUSE, Australia | 31.45S | 130.90E | 65 | 9.50 (AUA) | 91-06 | 946510 | 0.8 |  | -1.5 | 47.7 | 24.3 | 24.1 | 28.6 | 26 | 25.6667 |  | 21.2 | 21.4 | 24.8 | 22 | 22.4667
Australia |  | NULLO MOUNTAIN AWS | NULLO MOUNTAIN AWS, Australia | 32.73S | 150.23E | 1130 | 10.00 (AUE) | 90-06 | 947540 | -2 |  | -4 | 37 | 14.2 | 12.6 | 17.2 | 15 | 14.6667 |  | 12.7 | 11 | 14.3 | 13 | 12.6667
Australia |  | OAKEY AERO | OAKEY AERO, Australia | 27.42S | 151.73E | 407 | 10.00 (AUB) | 97-06 | 945520 | -5 |  | -7.8 | 42.1 | 23.3 | 23 | 25.7 | 24 | 24 |  | 21.6 | 20.9 | 23.2 | 22 | 21.9
Australia |  | ONSLOW | ONSLOW, Australia | 21.63S | 115.12E | 5 | 8.00 (AUW) | 90-04 | 943050 | 9 |  | 6.7 | 49 | 28.2 | 28.4 | 29.4 | 29 | 28.6667 |  | 26.7 | 26.3 | 27.6 | 27 | 26.8667
Australia |  | OUSE FIRE STATION | OUSE FIRE STATION, Australia | 42.48S | 146.72E | 91 | 10.00 (AUE) | 98-06 | 949570 | -5 |  | -6.8 | 40.9 | 16.1 | 15.2 | 18.4 | 17 | 16.5667 |  | 14.2 | 13.5 | 15.7 | 14 | 14.4667
Australia |  | PARABURDOO AERO | PARABURDOO AERO, Australia | 23.17S | 117.75E | 424 | 8.00 (AUW) | 96-06 | 943160 | 4 |  | 0.8 | 47 | 29.1 | 28.8 | 31.3 | 30 | 29.7333 |  | 27.3 | 27 | 29.4 | 28 | 27.9
Australia |  | PARKES (MACARTHUR ST) | PARKES (MACARTHUR ST), Australia | 33.13S | 148.17E | 324 | 10.00 (AUE) | 90-05 | 947170 | N/A |  | N/A | N/A | 20.5 | 19 | 24.3 | 21 | 21.2667 |  | 18.5 | 17.1 | 20.4 | 19 | 18.6667
Australia |  | PAYNES FIND | PAYNES FIND, Australia | 29.27S | 117.68E | 340 | 8.00 (AUW) | 91-05 | 944040 | -0.3 |  | -2.7 | 46.1 | 24.3 | 22.9 | 25.9 | 24 | 24.3667 |  | 21.8 | 20.4 | 22.8 | 22 | 21.6667
Australia |  | PEARCE RAAF | PEARCE RAAF, Australia | 31.67S | 116.02E | 54 | 8.00 (AUW) | 95-06 | 946120 | 1 |  | -3.4 | 45.3 | 22.9 | 21.9 | 22.5 | 22 | 22.4333 |  | 21.3 | 19.6 | 20.2 | 20 | 20.3667
Australia |  | PENRITH | PENRITH, Australia | 33.72S | 150.68E | 25 | 10.00 (AUE) | 96-06 | 947630 | 0.6 |  | -1.6 | 46.7 | 21.5 | 20.7 | 23.4 | 22 | 21.8667 |  | 19.4 | 18.9 | 21.2 | 20 | 19.8333
Australia |  | PERTH AIRPORT | PERTH AIRPORT, Australia | 31.93S | 115.97E | 20 | 8.00 (AUW) | 82-06 | 946100 | 1.9 |  | -1.3 | 45.4 | 22.9 | 21.9 | 22.6 | 22 | 22.4667 |  | 21 | 19.8 | 20.4 | 20 | 20.4
Australia |  | POINT WILSON | POINT WILSON, Australia | 38.10S | 144.53E | 18 | 10.00 (AUE) | 94-06 | 948470 | 4.4 |  | 2.4 | 39.5 | 17.8 | 16.2 | 18.6 | 18 | 17.5333 |  | 16.2 | 14.6 | 16.6 | 16 | 15.8
Australia |  | PORT ARTHUR (PALM.) | PORT ARTHUR (PALM.), Australia | 43.17S | 147.83E | 193 | 10.00 (AUE) | 90-02 | 949780 | N/A |  | N/A | N/A | 14.9 | 14.1 | 16.1 | 15 | 15.0333 |  | 13.6 | 12.8 | 14.2 | 14 | 13.5333
Australia |  | PORT FAIRY AWS | PORT FAIRY AWS, Australia | 38.40S | 142.23E | 10 | 10.00 (AUE) | 91-06 | 948300 | 1 |  | -1.8 | 44.7 | 18.4 | 16.6 | 19.7 | 18 | 18.2333 |  | 16 | 15.1 | 17.2 | 16 | 16.1
Australia |  | PORT HEDLAND AIRPOR | PORT HEDLAND AIRPOR, Australia | 20.37S | 118.63E | 9 | 8.00 (AUW) | 82-06 | 943120 | 7.4 |  | 4.1 | 47.4 | 31.6 | 30.7 | 32.4 | 32 | 31.5667 |  | 29.5 | 28.9 | 30.6 | 30 | 29.6667
Australia |  | PORT KEATS AWS AUT | PORT KEATS AWS AUT, Australia | 14.23S | 129.45E | 18 | 9.50 (AUC) | 83-99 | 941110 | N/A |  | N/A | N/A | 32.9 | 31.8 | 31.8 | 32 | 32.1667 |  | 31.1 | 30.5 | 30.4 | 31 | 30.6667
Australia |  | PORT MACQUARIE AIRP | PORT MACQUARIE AIRP, Australia | 31.43S | 152.85E | 5 | 10.00 (AUE) | 96-06 | 947860 | -0.1 |  | -2.5 | 47.9 | 22.6 | 21.1 | 23.5 | 22 | 22.4 |  | 21.1 | 19.5 | 21.3 | 21 | 20.6333
Australia |  | PORTLAND CASHMORE A | PORTLAND CASHMORE A, Australia | 38.32S | 141.47E | 82 | 10.00 (AUE) | 95-06 | 948280 | 1 |  | -0.9 | 41.9 | 17.2 | 15.4 | 18.3 | 17 | 16.9667 |  | 15.1 | 14.1 | 16.5 | 15 | 15.2333
Australia |  | PROSERPINE AIRPORT | PROSERPINE AIRPORT, Australia | 20.50S | 148.53E | 20 | 10.00 (AUB) | 96-06 | 943650 | 2.6 |  | -2.6 | 40.6 | 27.3 | 27.1 | 28.2 | 28 | 27.5333 |  | 25.6 | 25.2 | 26.9 | 26 | 25.9
Australia |  | QUILPIE AIRPORT | QUILPIE AIRPORT, Australia | 26.62S | 144.25E | 198 | 10.00 (AUB) | 90-05 | 944940 | 1.9 |  | -0.1 | 46.6 | 26.6 | 26.2 | 29.9 | 28 | 27.5667 |  | 24.8 | 23.9 | 27.2 | 25 | 25.3
Australia |  | RAVENSTHORPE HOPETO | RAVENSTHORPE HOPETO, Australia | 33.93S | 120.13E | 27 | 8.00 (AUW) | 98-06 | 956350 | 2 |  | -1 | 45.7 | 23.3 | 22.4 | 25 | 24 | 23.5667 |  | 21.2 | 19.7 | 21.9 | 21 | 20.9333
Australia |  | REDESDALE | REDESDALE, Australia | 37.02S | 144.53E | 290 | 10.00 (AUE) | 94-06 | 948590 | -2.2 |  | -4.8 | 43.4 | 16.2 | 14.6 | 17.9 | 16 | 16.2333 |  | 14.2 | 13.1 | 15.7 | 14 | 14.3333
Australia |  | RENMARK | RENMARK, Australia | 34.17S | 140.75E | 21 | 9.50 (AUA) | 90-01 | 946870 | 0.3 |  | -4.8 | 47.2 | 22.2 | 21.2 | 24.8 | 23 | 22.7333 |  | 19.1 | 18.6 | 21.7 | 20 | 19.8
Australia |  | RHYLL (AWS) | RHYLL (AWS), Australia | 38.45S | 145.30E | 14 | 10.00 (AUE) | 91-06 | 948920 | 3.8 |  | -2 | 38.3 | 16.9 | 15.5 | 18.3 | 17 | 16.9 |  | 15.6 | 14.3 | 16.4 | 15 | 15.4333
Australia |  | RICHMOND POST OFFIC | RICHMOND POST OFFIC, Australia | 20.73S | 143.13E | 214 | 10.00 (AUB) | 84-98 | 943400 | 2.8 |  | -1.7 | 46 | 30.5 | 31 | 33.1 | 32 | 31.5333 |  | 29.1 | 29.2 | 31.1 | 30 | 29.8
Australia |  | RICHMOND RAAF | RICHMOND RAAF, Australia | 33.60S | 150.78E | 20 | 10.00 (AUE) | 97-06 | 957530 | -2.7 |  | -5.5 | 47.2 | 21.6 | 20.9 | 24 | 22 | 22.1667 |  | 19.7 | 18.8 | 21.6 | 20 | 20.0333
Australia |  | ROCKHAMPTON AERO | ROCKHAMPTON AERO, Australia | 23.38S | 150.48E | 14 | 10.00 (AUB) | 82-06 | 943740 | 3.7 |  | 1.3 | 41.9 | 27.4 | 26.6 | 29.1 | 28 | 27.7 |  | 25.5 | 24.8 | 26.8 | 26 | 25.7
Australia |  | ROEBOURNE POST OFFI | ROEBOURNE POST OFFI, Australia | 20.78S | 117.15E | 13 | 8.00 (AUW) | 90-05 | 943090 | 9.8 |  | 8.2 | 48.9 | 32.2 | 30.9 | 33.3 | 32 | 32.1333 |  | 29.9 | 29.1 | 31.5 | 30 | 30.1667
Australia |  | ROMA AIRPORT | ROMA AIRPORT, Australia | 26.55S | 148.78E | 304 | 10.00 (AUB) | 82-06 | 945150 | -3 |  | -6.3 | 44.4 | 24.8 | 24.8 | 28.1 | 26 | 25.9 |  | 23.1 | 22.7 | 25.1 | 24 | 23.6333
Australia |  | ROTTNEST ISLAND | ROTTNEST ISLAND, Australia | 32.02S | 115.50E | 43 | 8.00 (AUW) | 90-06 | 946020 | 8.3 |  | 6 | 41.9 | 21.3 | 20.7 | 20.5 | 21 | 20.8333 |  | 20.2 | 19.2 | 19.2 | 20 | 19.5333
Australia |  | RUNDLE ISLAND | RUNDLE ISLAND, Australia | 23.53S | 151.28E | 20 | 10.00 (AUB) | 97-06 | 943780 | 12 |  | 9.3 | 34.8 | 23.6 | 22.4 | 22.7 | 23 | 22.9 |  | 22.7 | 21.2 | 21.6 | 22 | 21.8333
Australia |  | SCONE AIRPORT | SCONE AIRPORT, Australia | 32.03S | 150.83E | 223 | 10.00 (AUE) | 90-06 | 957580 | -2.9 |  | -4.4 | 44.1 | 21.6 | 21.2 | 25 | 23 | 22.6 |  | 19.1 | 18.6 | 21.9 | 20 | 19.8667
Australia |  | SCORESBY RESEARCH | SCORESBY RESEARCH, Australia | 37.87S | 145.25E | 90 | 10.00 (AUE) | 98-06 | 958670 | -0.1 |  | -2.4 | 44.7 | 18.6 | 16.2 | 20.1 | 18 | 18.3 |  | 17.1 | 15 | 17.7 | 17 | 16.6
Australia |  | SHARK BAY (DENHAM) | SHARK BAY (DENHAM), Australia | 25.92S | 113.52E | 10 | 8.00 (AUW) | 82-03 | 944020 | 7.9 |  | 5 | 48.3 | 26.2 | 24.9 | 26.1 | 26 | 25.7333 |  | 24.1 | 22.8 | 23.7 | 24 | 23.5333
Australia |  | SHEOAKS AWS | SHEOAKS AWS, Australia | 37.90S | 144.12E | 237 | 10.00 (AUE) | 91-06 | 948630 | -1 |  | -3.6 | 43.9 | 17.6 | 15.6 | 19 | 17 | 17.4 |  | 15.4 | 14.1 | 16.7 | 15 | 15.4
Australia |  | SHEPPARTON AIRPORT | SHEPPARTON AIRPORT, Australia | 36.43S | 145.40E | 114 | 10.00 (AUE) | 98-06 | 948750 | -3 |  | -5.8 | 42.9 | 18.5 | 16.5 | 19.8 | 18 | 18.2667 |  | 16.4 | 14.7 | 17.5 | 16 | 16.2
Australia |  | SMITHTON AERODROME | SMITHTON AERODROME, Australia | 40.83S | 145.08E | 9 | 10.00 (AUE) | 96-06 | 949530 | -1.3 |  | -2.9 | 31.4 | 15.6 | 14.6 | 15.7 | 15 | 15.3 |  | 14.6 | 13.7 | 14.4 | 14 | 14.2333
Australia |  | SOUTHERN CROSS | SOUTHERN CROSS, Australia | 31.23S | 119.33E | 356 | 8.00 (AUW) | 83-02 | 946340 | -0.4 |  | -2.3 | 45 | 22.1 | 21.9 | 24.8 | 23 | 22.9333 |  | 20.2 | 19.1 | 21.8 | 20 | 20.3667
Australia |  | SOUTHERN CROSS AIRF | SOUTHERN CROSS AIRF, Australia | 31.23S | 119.35E | 348 | 8.00 (AUW) | 98-06 | 956340 | N/A |  | N/A | N/A | 22.6 | 21.2 | 25.7 | 23 | 23.1667 |  | 20.6 | 19 | 22.3 | 21 | 20.6333
Australia |  | ST LAWRENCE POST OF | ST LAWRENCE POST OF, Australia | 22.35S | 149.53E | 18 | 10.00 (AUB) | 92-05 | 943690 | 5.8 |  | 3.2 | 42.7 | 27.2 | 26.8 | 27.3 | 27 | 27.1 |  | 26 | 24.9 | 25.8 | 26 | 25.5667
Australia |  | STRAHAN AERODROME | STRAHAN AERODROME, Australia | 42.15S | 145.28E | 22 | 10.00 (AUE) | 82-06 | 949560 | -0.7 |  | -3.3 | 36.4 | 16.4 | 14.9 | 17.4 | 16 | 16.2333 |  | 14.3 | 13.6 | 15 | 14 | 14.3
Australia |  | SWAN HILL AERODROME | SWAN HILL AERODROME, Australia | 35.38S | 143.53E | 71 | 10.00 (AUE) | 90-06 | 948430 | -1.9 |  | -5.5 | 47.7 | 20.5 | 18.8 | 22.5 | 21 | 20.6 |  | 17.8 | 16.6 | 19.7 | 18 | 18.0333
Australia |  | SWANBOURNE | SWANBOURNE, Australia | 31.95S | 115.77E | 20 | 8.00 (AUW) | 94-06 | 946140 | 4.1 |  | 1.6 | 43.8 | 22.2 | 21.5 | 21 | 22 | 21.5667 |  | 20.5 | 19.6 | 19.6 | 20 | 19.9
Australia |  | SYDNEY AIRPORT AMO | SYDNEY AIRPORT AMO, Australia | 33.93S | 151.18E | 5 | 10.00 (AUE) | 82-06 | 947670 | 4 |  | 0.2 | 46.5 | 22.1 | 21.8 | 25.1 | 23 | 23 |  | 20 | 19.2 | 21.8 | 20 | 20.3333
Australia |  | SYDNEY REGIONAL OFF | SYDNEY REGIONAL OFF, Australia | 33.85S | 151.20E | 40 | 10.00 (AUE) | 91-06 | 947680 | 5.7 |  | 4.1 | 44.1 | 21.7 | 21.1 | 24.6 | 22 | 22.4667 |  | 19.8 | 18.8 | 21.5 | 20 | 20.0333
Australia |  | TAMWORTH AIRPORT AW | TAMWORTH AIRPORT AW, Australia | 31.07S | 150.83E | 396 | 10.00 (AUE) | 92-06 | 957620 | -3.5 |  | -7.4 | 42.8 | 21.8 | 19.6 | 24 | 22 | 21.8 |  | 19.7 | 18 | 21.4 | 20 | 19.7
Australia |  | TELFER AERO | TELFER AERO, Australia | 21.72S | 122.22E | 292 | 8.00 (AUW) | 96-06 | 943190 | 5.1 |  | 2 | 46 | 31.7 | 30.1 | 32.7 | 32 | 31.5 |  | 29.1 | 28.2 | 31.2 | 30 | 29.5
Australia |  | TENNANT CREEK MET O | TENNANT CREEK MET O, Australia | 19.63S | 134.18E | 377 | 9.50 (AUC) | 82-06 | 942380 | 7.6 |  | 4.8 | 43.6 | 30.5 | 30.7 | 32.9 | 31 | 31.3667 |  | 28.7 | 28.3 | 31.1 | 29 | 29.3667
Australia |  | TEWANTIN RSL PARK | TEWANTIN RSL PARK, Australia | 26.38S | 153.03E | 7 | 10.00 (AUB) | 98-06 | 945700 | 5.5 |  | 3.4 | 43.9 | 24.7 | 23.7 | 24.9 | 24 | 24.4333 |  | 23.2 | 22.2 | 23.2 | 23 | 22.8667
Australia |  | THREDBO (CRACKENBACK) | THREDBO (CRACKENBACK), Australia | 36.50S | 148.28E | 1957 | 10.00 (AUE) | 97-06 | 959090 | N/A |  | N/A | N/A | 7.8 | 3.3 | 6.6 | 6 | 5.9 |  | 5.5 | 2.3 | 4.6 | 4 | 4.1333
Australia |  | TINDAL RAAF | TINDAL RAAF, Australia | 14.52S | 132.37E | 135 | 9.50 (AUC) | 90-00 | 941310 | 7.6 |  | 1.7 | 45 | 32.8 | 32.9 | 34.8 | 34 | 33.5 |  | 31.7 | 31.6 | 33.5 | 32 | 32.2667
Australia |  | TOOWOOMBA AIRPORT | TOOWOOMBA AIRPORT, Australia | 27.55S | 151.92E | 642 | 10.00 (AUB) | 98-06 | 955510 | 0 |  | -3.8 | 39.8 | 20.7 | 20.5 | 23.4 | 22 | 21.5333 |  | 19.1 | 18.6 | 20.8 | 20 | 19.5
Australia |  | TOWN OF 1770 | TOWN OF 1770, Australia | 24.15S | 151.88E | 47 | 10.00 (AUB) | 90-06 | 943840 | N/A |  | N/A | N/A | 24.1 | 23.1 | 23.1 | 23 | 23.4333 |  | 23.2 | 21.9 | 22.2 | 22 | 22.4333
Australia |  | TOWNSVILLE AERO | TOWNSVILLE AERO, Australia | 19.25S | 146.77E | 9 | 10.00 (AUB) | 82-06 | 942940 | 6.5 |  | 2.8 | 44.5 | 28 | 27.2 | 28.1 | 28 | 27.7667 |  | 27 | 26.1 | 26.9 | 27 | 26.6667
Australia |  | TROUGHTON ISLAND | TROUGHTON ISLAND, Australia | 13.75S | 126.15E | 8 | 8.00 (AUW) | 92-06 | 941020 | N/A |  | N/A | N/A | 30.2 | 29.6 | 29.7 | 30 | 29.8333 |  | 29.7 | 28.9 | 29.1 | 29 | 29.2333
Australia |  | TUGGERANONG ISABELL | TUGGERANONG ISABELL, Australia | 35.42S | 149.10E | 588 | 10.00 (AUE) | 98-06 | 949250 | -6.5 |  | -7.9 | 41.3 | 16.9 | 14.9 | 18.6 | 17 | 16.8 |  | 14.7 | 13.3 | 16.2 | 15 | 14.7333
Australia |  | TUNNAK FIRE STATION | TUNNAK FIRE STATION, Australia | 42.45S | 147.47E | 462 | 10.00 (AUE) | 90-06 | 949600 | -3 |  | -6.3 | 38.5 | 15 | 13.7 | 14.3 | 14 | 14.3333 |  | 13.8 | 12.5 | 12.7 | 13 | 13
Australia |  | ULLADULLA AWS | ULLADULLA AWS, Australia | 35.35S | 150.48E | 37 | 10.00 (AUE) | 91-06 | 949380 | 5.1 |  | 2.7 | 45.6 | 20.5 | 19.6 | 22.6 | 21 | 20.9 |  | 18.9 | 17.9 | 19.5 | 19 | 18.7667
Australia |  | URANDANGIE | URANDANGIE, Australia | 21.60S | 138.30E | 175 | 10.00 (AUB) | 90-05 | 943290 | 1.9 |  | -0.9 | 46.1 | 31.1 | 31 | 33.5 | 32 | 31.8667 |  | 29 | 28.7 | 31.6 | 30 | 29.7667
Australia |  | VICTORIA RIVER DOWN | VICTORIA RIVER DOWN, Australia | 16.40S | 131.02E | 90 | 9.50 (AUC) | 92-06 | 942320 | 4.2 |  | 1.5 | 43.8 | 32.2 | 32.1 | 33.8 | 33 | 32.7 |  | 30.9 | 30.8 | 32.5 | 31 | 31.4
Australia |  | WAGGA WAGGA AMO | WAGGA WAGGA AMO, Australia | 35.17S | 147.45E | 213 | 10.00 (AUE) | 82-06 | 949100 | -2.4 |  | -4.8 | 46 | 19.2 | 16.6 | 20.7 | 19 | 18.8333 |  | 16.7 | 14.9 | 17.8 | 16 | 16.4667
Australia |  | WALGETT AIRPORT | WALGETT AIRPORT, Australia | 30.03S | 148.12E | 134 | 10.00 (AUE) | 97-06 | 957150 | -3.5 |  | -6.6 | 46.6 | 24 | 22.6 | 26.6 | 24 | 24.4 |  | 21.9 | 20.7 | 23.8 | 22 | 22.1333
Australia |  | WANGARATTA AERO | WANGARATTA AERO, Australia | 36.42S | 146.30E | 153 | 10.00 (AUE) | 95-06 | 948890 | -3.7 |  | -7.5 | 45 | 17.9 | 15.8 | 19.2 | 18 | 17.6333 |  | 16 | 14.3 | 16.8 | 16 | 15.7
Australia |  | WARBURTO POINT | WARBURTO POINT, Australia | 34.00S | 137.53E | 1 | 9.50 (AUA) | 82-94 | 946660 | 3.9 |  | 1.6 | 47.2 | 22 | 21.3 | 25.7 | 23 | 23 |  | 19.6 | 19 | 22.5 | 20 | 20.3667
Australia |  | WARRNAMBOOL AIRPORT | WARRNAMBOOL AIRPORT, Australia | 38.28S | 142.43E | 68 | 10.00 (AUE) | 90-00 | 948320 | N/A |  | N/A | N/A | 17 | 16.2 | 19.2 | 17 | 17.4667 |  | 15.2 | 14.3 | 16.6 | 15 | 15.3667
Australia |  | WARWICK | WARWICK, Australia | 28.20S | 152.10E | 476 | 10.00 (AUB) | 94-06 | 945550 | -4.3 |  | -8.3 | 41 | 21.9 | 21.7 | 26.2 | 23 | 23.2667 |  | 20.4 | 19.7 | 22.5 | 21 | 20.8667
Australia |  | WEIPA AERO | WEIPA AERO, Australia | 12.68S | 141.92E | 19 | 10.00 (AUB) | 93-06 | 941700 | 14.2 |  | 10.9 | 39.9 | 32.1 | 31.7 | 32.8 | 32 | 32.2 |  | 31.1 | 30.8 | 31.7 | 31 | 31.2
Australia |  | WILLIAMTOWN RAAF | WILLIAMTOWN RAAF, Australia | 32.80S | 151.83E | 8 | 10.00 (AUE) | 82-06 | 947760 | 1.4 |  | -2.2 | 44.8 | 21.6 | 21.3 | 25.1 | 23 | 22.6667 |  | 19.5 | 19 | 21.7 | 20 | 20.0667
Australia |  | WILLIS ISLAND | WILLIS ISLAND, Australia | 16.30S | 149.97E | 9 | 10.00 (AUB) | 82-06 | 942990 | 20 |  | 17.2 | 35.2 | 27.9 | 27.2 | 27.2 | 27 | 27.4333 |  | 27 | 26.5 | 26.4 | 27 | 26.6333
Australia |  | WILSONS PROMONTORY | WILSONS PROMONTORY, Australia | 39.12S | 146.42E | 97 | 10.00 (AUE) | 82-06 | 948930 | 5.4 |  | 2 | 40 | 17.7 | 16.1 | 19.2 | 18 | 17.6667 |  | 15.9 | 14.5 | 16.6 | 16 | 15.6667
Australia |  | WINDORAH | WINDORAH, Australia | 25.42S | 142.65E | 129 | 10.00 (AUB) | 83-05 | 944880 | 2.3 |  | 0.1 | 47.7 | 28 | 27.6 | 31.2 | 29 | 28.9333 |  | 26.1 | 25.3 | 28.6 | 27 | 26.6667
Australia |  | WINTON (POST OFFICE) | WINTON (POST OFFICE), Australia | 22.38S | 143.03E | 184 | 10.00 (AUB) | 90-06 | 943390 | 3 |  | 0 | 46.3 | 30 | 30.1 | 31.9 | 31 | 30.6667 |  | 28.1 | 27.6 | 29.7 | 28 | 28.4667
Australia |  | WONTHAGGI COMPOSITE | WONTHAGGI COMPOSITE, Australia | 38.60S | 145.58E | 42 | 10.00 (AUE) | 90-04 | 958810 | 1.3 |  | -1.7 | 46.4 | 18.1 | 16.4 | 19.5 | 18 | 18 |  | 16 | 14.9 | 16.9 | 16 | 15.9333
Australia |  | WOOMERA AERODROME | WOOMERA AERODROME, Australia | 31.15S | 136.82E | 167 | 9.50 (AUA) | 82-06 | 946590 | 2.4 |  | 0 | 46.1 | 23.5 | 22.1 | 26.6 | 24 | 24.0667 |  | 20.1 | 19.9 | 23.8 | 21 | 21.2667
Australia |  | WYNDHAM | WYNDHAM, Australia | 15.48S | 128.12E | 16 | 8.00 (AUW) | 82-99 | 942140 | N/A |  | N/A | N/A | 34.5 | 35 | 36 | 35 | 35.1667 |  | 33.4 | 33.2 | 34.8 | 34 | 33.8
Australia |  | WYNYARD AIRPORT | WYNYARD AIRPORT, Australia | 41.00S | 145.73E | 12 | 10.00 (AUE) | 92-06 | 959570 | -2.1 |  | -3.4 | 34.3 | 15.3 | 14.7 | 15.5 | 15 | 15.1667 |  | 14.3 | 13.7 | 14.2 | 14 | 14.0667
Australia |  | YEPPOON AWS | YEPPOON AWS, Australia | 23.13S | 150.75E | 6 | 10.00 (AUB) | 94-06 | 943730 | 4.8 |  | 3.2 | 39.8 | 24.4 | 24.4 | 25.2 | 25 | 24.6667 |  | 23.3 | 22.2 | 23.1 | 23 | 22.8667
Australia |  | YOUNG AIRPORT | YOUNG AIRPORT, Australia | 34.25S | 148.25E | 381 | 10.00 (AUE) | 90-06 | 947120 | -4.8 |  | -7.5 | 44.7 | 19.7 | 16.7 | 20.3 | 19 | 18.9 |  | 16.7 | 14.8 | 17.4 | 16 | 16.3
Australia |  | YULARA AERO | YULARA AERO, Australia | 25.20S | 130.98E | 492 | 9.50 (AUC) | 92-06 | 944620 | -0.1 |  | -3.7 | 45.9 | 28.5 | 26.4 | 30.8 | 29 | 28.5667 |  | 25.5 | 24.2 | 28.1 | 26 | 25.9333
Austria |  | AIGEN IM ENNSTAL | AIGEN IM ENNSTAL, Austria | 47.53N | 14.13E | 649 | 1.00 (EUW) | 82-06 | 111570 | -20.8 |  | -29.9 | 35.5 | 29.9 | 30.6 | 29.8 | 30 | 30.1 |  | 27.4 | 28.3 | 27.6 | 28 | 27.7667
Austria |  | ALLENTSTEIG | ALLENTSTEIG, Austria | 48.68N | 15.37E | 607 | 1.00 (EUW) | 94-06 | 110190 | -17.3 |  | -23.7 | 37.6 | 29.7 | 30.2 | 30.5 | 30 | 30.1333 |  | 26.9 | 27.6 | 27.5 | 27 | 27.3333
Austria |  | ALPINZENTRUM RUDOLF | ALPINZENTRUM RUDOLF, Austria | 47.13N | 12.63E | 2310 | 1.00 (EUW) | 93-06 | 111380 | -21.1 |  | -28.1 | 31.4 | 16.1 | 17.6 | 17.7 | 17 | 17.1333 |  | 14.6 | 15.8 | 15.9 | 15 | 15.4333
Austria |  | AMSTETTEN | AMSTETTEN, Austria | 48.10N | 14.90E | 271 | 1.00 (EUW) | 96-06 | 110180 | N/A |  | N/A | N/A | 31.8 | 32.6 | 31.8 | 32 | 32.0667 |  | 29.5 | 29.8 | 29.3 | 30 | 29.5333
Austria |  | ARRIACH | ARRIACH, Austria | 46.73N | 13.85E | 896 | 1.00 (EUW) | 93-06 | 112750 | N/A |  | N/A | N/A | 27.7 | 28.2 | 28.4 | 28 | 28.1 |  | 25.7 | 25.6 | 25.9 | 26 | 25.7333
Austria |  | BAD RADKERSBURG | BAD RADKERSBURG, Austria | 46.68N | 15.98E | 214 | 1.00 (EUW) | 94-06 | 112480 | N/A |  | N/A | N/A | 31.8 | 31.7 | 33.1 | 32 | 32.2 |  | 29.4 | 29.7 | 30.9 | 30 | 30
Austria |  | BISCHOFSHOFEN | BISCHOFSHOFEN, Austria | 47.40N | 13.22E | 548 | 1.00 (EUW) | 90-06 | 111410 | -16.5 |  | -21.8 | 36 | 30.7 | 31.6 | 30.3 | 31 | 30.8667 |  | 28.6 | 28.9 | 28 | 29 | 28.5
Austria |  | BREGENZ | BREGENZ, Austria | 47.50N | 9.75E | 439 | 1.00 (EUW) | 91-06 | 111010 | -11.5 |  | -20.2 | 39 | 30.2 | 30.5 | 30.9 | 31 | 30.5333 |  | 27.5 | 28.3 | 28.1 | 28 | 27.9667
Austria |  | BRENNER | BRENNER, Austria | 47.00N | 11.52E | 1447 | 1.00 (EUW) | 94-06 | 111280 | -17 |  | -25.3 | 30.4 | 25.5 | 26 | 26.2 | 26 | 25.9 |  | 23.6 | 23.8 | 23.6 | 24 | 23.6667
Austria |  | DELLACH IM DRAUTAL | DELLACH IM DRAUTAL, Austria | 46.73N | 13.08E | 625 | 1.00 (EUW) | 93-06 | 112700 | -16.9 |  | -22.7 | 37.9 | 31.1 | 31 | 32.1 | 31 | 31.4 |  | 29.2 | 28.8 | 29.1 | 29 | 29.0333
Austria |  | DORNBIRN | DORNBIRN, Austria | 47.43N | 9.73E | 411 | 1.00 (EUW) | 95-06 | 113020 | -13.4 |  | -21 | 37.9 | 31.3 | 31.3 | 32.1 | 32 | 31.5667 |  | 29.1 | 28.9 | 28.5 | 29 | 28.8333
Austria |  | EISENSTADT | EISENSTADT, Austria | 47.85N | 16.53E | 192 | 1.00 (EUW) | 82-06 | 111900 | -13.5 |  | -22.1 | 38.4 | 31.5 | 33.3 | 32.8 | 33 | 32.5333 |  | 29 | 30.7 | 30.2 | 30 | 29.9667
Austria |  | FELDKIRCH | FELDKIRCH, Austria | 47.27N | 9.62E | 439 | 1.00 (EUW) | 95-06 | 111050 | -13 |  | -19.1 | 37.6 | 31.5 | 31.1 | 32 | 32 | 31.5333 |  | 28.9 | 28.6 | 28.1 | 29 | 28.5333
Austria |  | FEUERKOGEL | FEUERKOGEL, Austria | 47.82N | 13.72E | 1621 | 1.00 (EUW) | 93-06 | 111550 | -16.7 |  | -23.4 | 30.3 | 22.3 | 24 | 22.6 | 23 | 22.9667 |  | 20.4 | 21.4 | 20.7 | 21 | 20.8333
Austria |  | FREISTADT | FREISTADT, Austria | 48.50N | 14.50E | 548 | 1.00 (EUW) | 94-06 | 110150 | -19.8 |  | -25.3 | 36.5 | 30.6 | 31.6 | 31.2 | 31 | 31.1333 |  | 28.8 | 29 | 28.5 | 29 | 28.7667
Austria |  | GMUNDEN | GMUNDEN, Austria | 47.90N | 13.80E | 428 | 1.00 (EUW) | 90-06 | 111540 | -14.2 |  | -18.4 | 37.7 | 31.6 | 32.8 | 32.1 | 32 | 32.1667 |  | 29.3 | 29.8 | 29.3 | 29 | 29.4667
Austria |  | GRAZ-THALERHOF-FLUG | GRAZ-THALERHOF-FLUG, Austria | 47.00N | 15.43E | 347 | 1.00 (EUW) | 82-06 | 112400 | -16.6 |  | -26.1 | 38.5 | 32 | 32.2 | 32.9 | 32 | 32.3667 |  | 29.2 | 30.1 | 30.2 | 30 | 29.8333
Austria |  | GUMPOLDSKIRCHEN | GUMPOLDSKIRCHEN, Austria | 48.03N | 16.28E | 233 | 1.00 (EUW) | 93-06 | 110820 | -13.5 |  | -20.3 | 39.6 | 32.1 | 33.1 | 33.2 | 33 | 32.8 |  | 29.7 | 30.7 | 30.9 | 30 | 30.4333
Austria |  | HAHNENKAMM/EHRENBAC | HAHNENKAMM/EHRENBAC, Austria | 47.42N | 12.37E | 1763 | 1.00 (EUW) | 93-06 | 111350 | -17.3 |  | -25.2 | 28.1 | 20.9 | 22.7 | 21 | 22 | 21.5333 |  | 19.3 | 20.5 | 19.3 | 20 | 19.7
Austria |  | HOHE WAND/HOCHKOGEL | HOHE WAND/HOCHKOGEL, Austria | 47.82N | 16.03E | 939 | 1.00 (EUW) | 94-06 | 113850 | N/A |  | N/A | N/A | 28 | 28.9 | 29.5 | 29 | 28.8 |  | 25.4 | 26 | 26.4 | 26 | 25.9333
Austria |  | INNSBRUCK-FLUGHAFEN | INNSBRUCK-FLUGHAFEN, Austria | 47.27N | 11.35E | 584 | 1.00 (EUW) | 82-06 | 111200 | -14.8 |  | -22.8 | 36.8 | 31.2 | 32.2 | 32 | 32 | 31.8 |  | 29 | 29.9 | 29.2 | 29 | 29.3667
Austria |  | ISCHGL/IDALPE | ISCHGL/IDALPE, Austria | 46.98N | 10.32E | 2319 | 1.00 (EUW) | 93-06 | 113100 | N/A |  | N/A | N/A | 18.3 | 18.7 | 18.9 | 19 | 18.6333 |  | 16.3 | 16.9 | 16.7 | 17 | 16.6333
Austria |  | JAUERLING | JAUERLING, Austria | 48.33N | 15.33E | 959 | 1.00 (EUW) | 95-06 | 110240 | N/A |  | N/A | N/A | 26.6 | 26.9 | 27.8 | 27 | 27.1 |  | 24 | 24.7 | 25.1 | 25 | 24.6
Austria |  | KLAGENFURT-FLUGHAFE | KLAGENFURT-FLUGHAFE, Austria | 46.65N | 14.33E | 476 | 1.00 (EUW) | 82-06 | 112310 | -17.7 |  | -25.8 | 37.8 | 31.3 | 32.4 | 32.6 | 32 | 32.1 |  | 29 | 30 | 30 | 30 | 29.6667
Austria |  | KLEINZICKEN | KLEINZICKEN, Austria | 47.20N | 16.33E | 267 | 1.00 (EUW) | 94-06 | 111920 | -18.5 |  | -28.2 | 39.7 | 32.1 | 32.4 | 33 | 33 | 32.5 |  | 29.8 | 30.2 | 31 | 30 | 30.3333
Austria |  | KOETSCHACH-MAUTHEN | KOETSCHACH-MAUTHEN, Austria | 46.68N | 13.00E | 711 | 1.00 (EUW) | 92-06 | 112550 | -14.9 |  | -20.4 | 35.6 | 29.7 | 30.3 | 29.8 | 30 | 29.9333 |  | 27.7 | 27.9 | 27.1 | 28 | 27.5667
Austria |  | KREMSMUENSTER | KREMSMUENSTER, Austria | 48.05N | 14.13E | 389 | 1.00 (EUW) | 90-06 | 110120 | -15.4 |  | -19.1 | 36.9 | 30.8 | 32.1 | 31.6 | 32 | 31.5 |  | 28.8 | 29.2 | 28.8 | 29 | 28.9333
Austria |  | KUFSTEIN | KUFSTEIN, Austria | 47.58N | 12.17E | 493 | 1.00 (EUW) | 94-06 | 111300 | -15.3 |  | -20.8 | 37.8 | 31.1 | 32.5 | 32.3 | 32 | 31.9667 |  | 29.3 | 29.7 | 29 | 29 | 29.3333
Austria |  | LANDECK | LANDECK, Austria | 47.13N | 10.57E | 806 | 1.00 (EUW) | 95-06 | 111120 | -13.1 |  | -19.2 | 37.1 | 31.2 | 31 | 32.2 | 31 | 31.4667 |  | 28.9 | 28.5 | 28.9 | 29 | 28.7667
Austria |  | LANGENLOIS | LANGENLOIS, Austria | 48.47N | 15.70E | 204 | 1.00 (EUW) | 93-06 | 110750 | -15.7 |  | -24.6 | 39 | 32.2 | 33.2 | 33.1 | 33 | 32.8333 |  | 29.7 | 30.7 | 30.9 | 30 | 30.4333
Austria |  | LASSNITZHOEHE | LASSNITZHOEHE, Austria | 47.07N | 15.58E | 533 | 1.00 (EUW) | 93-06 | 112920 | -13 |  | -16.7 | 36.3 | 30.2 | 30.1 | 30.7 | 30 | 30.3333 |  | 28.1 | 28.3 | 28.6 | 28 | 28.3333
Austria |  | LIENZ | LIENZ, Austria | 46.83N | 12.82E | 666 | 1.00 (EUW) | 90-06 | 112040 | -18.2 |  | -24.1 | 37.2 | 30.8 | 30.4 | 32 | 31 | 31.0667 |  | 28.8 | 28.5 | 29 | 29 | 28.7667
Austria |  | LILIENFELD/TARSCHBE | LILIENFELD/TARSCHBE, Austria | 48.03N | 15.58E | 696 | 1.00 (EUW) | 94-06 | 110780 | -14.5 |  | -21 | 34.9 | 29.2 | 29.7 | 29.9 | 30 | 29.6 |  | 26.7 | 27.5 | 27.2 | 27 | 27.1333
Austria |  | LINZ/HOERSCHING-FLU | LINZ/HOERSCHING-FLU, Austria | 48.23N | 14.18E | 313 | 1.00 (EUW) | 82-06 | 110100 | -16.5 |  | -27.8 | 38.4 | 31.4 | 33.1 | 32.8 | 32 | 32.4333 |  | 28.9 | 30.5 | 30 | 30 | 29.8
Austria |  | LINZ/STADT | LINZ/STADT, Austria | 48.30N | 14.28E | 263 | 1.00 (EUW) | 94-06 | 110600 | -13.1 |  | -18.7 | 37.3 | 32 | 32.7 | 32.5 | 32 | 32.4 |  | 29.9 | 30.1 | 29.7 | 30 | 29.9
Austria |  | LITSCHAU | LITSCHAU, Austria | 48.95N | 15.03E | 555 | 1.00 (EUW) | 83-06 | 110210 | -20.2 |  | -29.1 | 37.2 | 29.7 | 30.5 | 30.9 | 30 | 30.3667 |  | 27.2 | 27.5 | 28.1 | 28 | 27.6
Austria |  | LUNZ | LUNZ, Austria | 47.85N | 15.07E | 615 | 1.00 (EUW) | 95-06 | 111700 | -22.7 |  | -29.9 | 36.2 | 30.3 | 30.7 | 29.7 | 30 | 30.2333 |  | 27.9 | 28.1 | 26.9 | 28 | 27.6333
Austria |  | MARIAPFARR | MARIAPFARR, Austria | 47.15N | 13.75E | 1151 | 1.00 (EUW) | 93-06 | 113480 | -20.9 |  | -27.9 | 31.2 | 27 | 27.5 | 27.6 | 27 | 27.3667 |  | 25 | 25.2 | 25.2 | 25 | 25.1333
Austria |  | MARIAZELL | MARIAZELL, Austria | 47.77N | 15.32E | 875 | 1.00 (EUW) | 83-02 | 111720 | -20.1 |  | -32 | 34 | 28 | 29.2 | 29.3 | 29 | 28.8333 |  | 25.2 | 26.7 | 26.9 | 26 | 26.2667
Austria |  | MATTSEE | MATTSEE, Austria | 47.98N | 13.10E | 503 | 1.00 (EUW) | 90-06 | 111520 | -15.9 |  | -25.6 | 36.8 | 30.6 | 31.5 | 31.6 | 31 | 31.2333 |  | 28 | 28.5 | 28.6 | 28 | 28.3667
Austria |  | MOENICHKIRCHEN | MOENICHKIRCHEN, Austria | 47.52N | 16.03E | 994 | 1.00 (EUW) | 90-06 | 111850 | -14.1 |  | -20.6 | 32.6 | 25.5 | 25.9 | 27 | 26 | 26.1333 |  | 23.5 | 24 | 24.6 | 24 | 24.0333
Austria |  | MURAU | MURAU, Austria | 47.12N | 14.18E | 813 | 1.00 (EUW) | 93-06 | 112800 | -18.4 |  | -25.3 | 35.9 | 29.7 | 30.2 | 30.4 | 30 | 30.1 |  | 27.9 | 27.8 | 27.9 | 28 | 27.8667
Austria |  | NEUSIEDL | NEUSIEDL, Austria | 47.95N | 16.85E | 132 | 1.00 (EUW) | 90-06 | 111940 | -13.5 |  | -21.1 | 39.9 | 32.6 | 33.9 | 33.4 | 33 | 33.3 |  | 30.4 | 31.5 | 31.1 | 31 | 31
Austria |  | OBERTAUERN | OBERTAUERN, Austria | 47.25N | 13.57E | 1743 | 1.00 (EUW) | 90-06 | 111490 | N/A |  | N/A | N/A | 22.7 | 23 | 22.4 | 23 | 22.7 |  | 20.7 | 20.6 | 20 | 20 | 20.4333
Austria |  | POYSDORF | POYSDORF, Austria | 48.67N | 16.63E | 207 | 1.00 (EUW) | 93-06 | 110320 | -15.6 |  | -25 | 39.4 | 32.2 | 33.3 | 33.5 | 33 | 33 |  | 29.7 | 31.2 | 31.1 | 31 | 30.6667
Austria |  | PUCHBERG | PUCHBERG, Austria | 47.78N | 15.90E | 582 | 1.00 (EUW) | 93-06 | 113820 | -19.3 |  | -26 | 36.9 | 30.2 | 30.7 | 31 | 31 | 30.6333 |  | 28 | 28.4 | 28.4 | 28 | 28.2667
Austria |  | RAMSAU/DACHSTEIN | RAMSAU/DACHSTEIN, Austria | 47.43N | 13.63E | 1209 | 1.00 (EUW) | 94-06 | 113510 | -17.3 |  | -26.4 | 32.1 | 27 | 27.1 | 26.5 | 27 | 26.8667 |  | 24.8 | 24.7 | 24.6 | 25 | 24.7
Austria |  | RAX/SEILBAHN-BERGST | RAX/SEILBAHN-BERGST, Austria | 47.72N | 15.78E | 1554 | 1.00 (EUW) | 95-06 | 111800 | N/A |  | N/A | N/A | 21.9 | 22.7 | 22.7 | 22 | 22.4333 |  | 19.9 | 20.6 | 20.7 | 20 | 20.4
Austria |  | REICHENAU/RAX | REICHENAU/RAX, Austria | 47.70N | 15.83E | 486 | 1.00 (EUW) | 93-06 | 113800 | -16.8 |  | -22.6 | 36.3 | 30.5 | 31.4 | 31.4 | 31 | 31.1 |  | 28.2 | 28.7 | 28.8 | 29 | 28.5667
Austria |  | RETZ | RETZ, Austria | 48.77N | 15.95E | 323 | 1.00 (EUW) | 95-06 | 110220 | -14.2 |  | -20.7 | 37.9 | 31.1 | 32.7 | 31.9 | 32 | 31.9 |  | 28.5 | 30.4 | 29.4 | 29 | 29.4333
Austria |  | SALZBURG-FLUGHAFEN | SALZBURG-FLUGHAFEN, Austria | 47.80N | 13.00E | 450 | 1.00 (EUW) | 82-06 | 111500 | -16.7 |  | -26.3 | 38.1 | 31 | 33 | 32.6 | 32 | 32.2 |  | 28.9 | 30.5 | 29.8 | 30 | 29.7333
Austria |  | SCHMITTENHOEHE | SCHMITTENHOEHE, Austria | 47.33N | 12.73E | 1953 | 1.00 (EUW) | 90-06 | 113400 | N/A |  | N/A | N/A | 20.3 | 21 | 21.7 | 21 | 21 |  | 18.7 | 18.9 | 19.6 | 19 | 19.0667
Austria |  | SCHOECKL | SCHOECKL, Austria | 47.20N | 15.47E | 1442 | 1.00 (EUW) | 93-06 | 112410 | N/A |  | N/A | N/A | 22.4 | 22.7 | 23.6 | 23 | 22.9 |  | 20.7 | 21.1 | 21.2 | 21 | 21
Austria |  | ST. MICHAEL/LEOBEN | ST. MICHAEL/LEOBEN, Austria | 47.33N | 15.00E | 572 | 1.00 (EUW) | 90-06 | 111740 | -17.5 |  | -25.3 | 37.8 | 31.1 | 31.3 | 32 | 31 | 31.4667 |  | 28.8 | 28.9 | 29.1 | 29 | 28.9333
Austria |  | ST. POELTEN | ST. POELTEN, Austria | 48.18N | 15.62E | 284 | 1.00 (EUW) | 94-05 | 110280 | -15.6 |  | -23.6 | 38.4 | 32.2 | 32.8 | 32.4 | 32 | 32.4667 |  | 29.6 | 29.9 | 30.3 | 30 | 29.9333
Austria |  | ST. WOLFGANG | ST. WOLFGANG, Austria | 47.73N | 13.45E | 537 | 1.00 (EUW) | 91-06 | 113570 | -13.7 |  | -20.8 | 34.9 | 29.6 | 30.7 | 30.2 | 30 | 30.1667 |  | 27.8 | 28.2 | 27.7 | 28 | 27.9
Austria |  | STIFT ZWETTL | STIFT ZWETTL, Austria | 48.62N | 15.20E | 506 | 1.00 (EUW) | 94-06 | 110200 | N/A |  | N/A | N/A | 30.1 | 30.8 | 30.7 | 31 | 30.5333 |  | 27.4 | 27.8 | 27.9 | 28 | 27.7
Austria |  | TULLN | TULLN, Austria | 48.32N | 16.12E | 176 | 1.00 (EUW) | 82-06 | 110300 | -16.2 |  | -27.3 | 38.9 | 31.8 | 33.7 | 33.2 | 33 | 32.9 |  | 29.2 | 31 | 30.6 | 30 | 30.2667
Austria |  | VILLACH | VILLACH, Austria | 46.62N | 13.88E | 494 | 1.00 (EUW) | 94-06 | 112130 | -15.3 |  | -24.1 | 39.3 | 32.1 | 32.6 | 32.5 | 32 | 32.4 |  | 29.8 | 29.8 | 29.3 | 30 | 29.6333
Austria |  | VIRGEN | VIRGEN, Austria | 47.00N | 12.45E | 1190 | 1.00 (EUW) | 94-06 | 112520 | -14.5 |  | -22.7 | 33.3 | 27.3 | 27.2 | 28.6 | 28 | 27.7 |  | 25.5 | 25.2 | 25.6 | 25 | 25.4333
Austria |  | WARTH | WARTH, Austria | 47.25N | 10.18E | 1471 | 1.00 (EUW) | 92-06 | 113080 | N/A |  | N/A | N/A | 25.6 | 25.1 | 25.3 | 25 | 25.3333 |  | 23.1 | 23 | 22.7 | 23 | 22.9333
Austria |  | WIEN/CITY | WIEN/CITY, Austria | 48.20N | 16.37E | 171 | 1.00 (EUW) | 92-06 | 110340 | -11 |  | -17.5 | 39.2 | 32.2 | 34.1 | 33.5 | 33 | 33.2667 |  | 30 | 31.7 | 31.3 | 31 | 31
Austria |  | WIEN/HOHE WARTE | WIEN/HOHE WARTE, Austria | 48.25N | 16.37E | 200 | 1.00 (EUW) | 82-06 | 110350 | -12.5 |  | -20.9 | 38.3 | 31.1 | 33.1 | 33.4 | 33 | 32.5333 |  | 28.7 | 30.6 | 30.7 | 30 | 30
Austria |  | WIEN/SCHWECHAT-FLUG | WIEN/SCHWECHAT-FLUG, Austria | 48.12N | 16.57E | 190 | 1.00 (EUW) | 82-06 | 110360 | -14.8 |  | -23.2 | 38.8 | 31.2 | 33.1 | 33.5 | 33 | 32.6 |  | 28.8 | 30.9 | 30.9 | 30 | 30.2
Austria |  | WIENER NEUSTADT | WIENER NEUSTADT, Austria | 47.83N | 16.22E | 285 | 1.00 (EUW) | 94-06 | 111820 | -17.8 |  | -26.5 | 40.3 | 32 | 33.2 | 33.4 | 33 | 32.8667 |  | 29.8 | 30.8 | 30.8 | 30 | 30.4667
Austria |  | WINDISCHGARSTEN | WINDISCHGARSTEN, Austria | 47.73N | 14.33E | 614 | 1.00 (EUW) | 90-06 | 113550 | -18.6 |  | -27.5 | 37.1 | 31.2 | 32.2 | 31.6 | 32 | 31.6667 |  | 28.8 | 29.4 | 28.7 | 29 | 28.9667
Austria |  | ZELL AM SEE | ZELL AM SEE, Austria | 47.33N | 12.80E | 767 | 1.00 (EUW) | 90-06 | 111440 | -17.4 |  | -29.4 | 36.3 | 30.3 | 30.7 | 29.9 | 30 | 30.3 |  | 28 | 28.1 | 27.1 | 28 | 27.7333
Austria |  | ZELTWEG | ZELTWEG, Austria | 47.20N | 14.75E | 682 | 1.00 (EUW) | 82-06 | 111650 | -20.4 |  | -29.6 | 36 | 29.9 | 30.7 | 30.8 | 30 | 30.4667 |  | 27.1 | 28.2 | 28.2 | 28 | 27.8333
Azerbaijan |  | LANKARAN | LANKARAN, Azerbaijan | 38.73N | 48.83E | -12 | 4.00 (CAU) | 82-06 | 379850 | -5.4 |  | -11.6 | 38.2 | 32.4 | 34.4 | 33.1 | 33 | 33.3 |  | 29.7 | 32.3 | 31.4 | 31 | 31.1333
Azerbaijan |  | ZAKATALA | ZAKATALA, Azerbaijan | 41.67N | 46.65E | 490 | 4.00 (CAU) | 82-05 | 375750 | N/A |  | N/A | N/A | 33.2 | 35.6 | 34.3 | 34 | 34.3667 |  | 30.6 | 33.7 | 32.1 | 32 | 32.1333
Bahamas |  | NASSAU AIRPORT NEW | NASSAU AIRPORT NEW, Bahamas | 25.05N | 77.47W | 7 | -5.00 (NAE) | 82-06 | 780730 | 10.9 |  | 5.8 | 35.4 | 33.1 | 33.2 | 34 | 33 | 33.4333 |  | 32.1 | 32.8 | 33 | 33 | 32.6333
Bahamas |  | SETTLEMENT POINT | SETTLEMENT POINT, Bahamas | 26.68N | 79.00W | 3 | -5.00 (NAE) | 85-06 | 994390 | 12.4 |  | 6.4 | 34.2 | 30.5 | 31.7 | 32.2 | 31 | 31.4667 |  | 29.7 | 30.7 | 31.1 | 31 | 30.5
Bahrain |  | BAHRAIN (INT. AIRPORT) | BAHRAIN (INT. AIRPORT), Bahrain | 26.27N | 50.65E | 2 | 3.00 (AFE) | 83-06 | 411500 | 9.1 |  | 3.2 | 47.3 | 41.1 | 42.2 | 41.9 | 42 | 41.7333 |  | 39.1 | 40.1 | 40 | 40 | 39.7333
Barbados |  | GRANTLEY ADAMS | GRANTLEY ADAMS, Barbados | 13.07N | 59.48W | 56 | -4.00 (SAZ) | 82-06 | 789540 | 20.4 |  | 17.8 | 33.2 | 31.2 | 31.2 | 31.6 | 31 | 31.3333 |  | 30.9 | 30.8 | 31.1 | 31 | 30.9333
Belarus |  | BARANOVICHI | BARANOVICHI, Belarus | 53.12N | 26.00E | 193 | 2.00 (EUE) | 82-06 | 269410 | -22.6 |  | -33.7 | 34.8 | 28.7 | 30.7 | 30 | 30 | 29.8 |  | 26.3 | 28.5 | 27.5 | 27 | 27.4333
Belarus |  | BOBRUISK | BOBRUISK, Belarus | 53.22N | 29.18E | 156 | 2.00 (EUE) | 82-06 | 269610 | -25.2 |  | -35.8 | 35.9 | 29.6 | 31.3 | 30.2 | 30 | 30.3667 |  | 27.1 | 28.9 | 27.6 | 28 | 27.8667
Belarus |  | BREST | BREST, Belarus | 52.12N | 23.68E | 146 | 2.00 (EUE) | 82-06 | 330080 | -19.7 |  | -31.6 | 35.9 | 30.2 | 32.2 | 31.6 | 31 | 31.3333 |  | 27.9 | 30 | 28.8 | 29 | 28.9
Belarus |  | GOMEL | GOMEL, Belarus | 52.40N | 30.95E | 126 | 2.00 (EUE) | 82-06 | 330410 | -23.7 |  | -34.2 | 36.7 | 30.1 | 32 | 31.1 | 31 | 31.0667 |  | 27.9 | 29.6 | 28.5 | 29 | 28.6667
Belarus |  | GRODNO | GRODNO, Belarus | 53.60N | 24.05E | 134 | 2.00 (EUE) | 82-06 | 268250 | -21.7 |  | -33.1 | 36.2 | 28.3 | 31.6 | 30.7 | 30 | 30.2 |  | 26.1 | 28.9 | 27.8 | 28 | 27.6
Belarus |  | KOSTUCKOVICHI | KOSTUCKOVICHI, Belarus | 53.35N | 32.07E | 167 | 2.00 (EUE) | 82-06 | 268870 | -25.5 |  | -35.8 | 36 | 29 | 30.9 | 29.6 | 30 | 29.8333 |  | 26.9 | 28.4 | 27.2 | 28 | 27.5
Belarus |  | LEPEL | LEPEL, Belarus | 54.88N | 28.70E | 174 | 2.00 (EUE) | 82-06 | 266590 | -24.1 |  | -32.8 | 35.1 | 28.5 | 30.9 | 29.4 | 30 | 29.6 |  | 26.3 | 28.2 | 26.7 | 27 | 27.0667
Belarus |  | LIDA | LIDA, Belarus | 53.85N | 25.32E | 157 | 2.00 (EUE) | 82-06 | 268320 | -21.9 |  | -32.1 | 35.4 | 28.7 | 31.4 | 30.2 | 30 | 30.1 |  | 26.3 | 28.7 | 27.3 | 27 | 27.4333
Belarus |  | LYNTUPY | LYNTUPY, Belarus | 55.05N | 26.32E | 212 | 2.00 (EUE) | 82-06 | 266450 | -24.7 |  | -35.1 | 35 | 28 | 31 | 28 | 29 | 29 |  | 25.7 | 27.8 | 26 | 27 | 26.5
Belarus |  | MINSK | MINSK, Belarus | 53.93N | 27.63E | 231 | 2.00 (EUE) | 82-06 | 268500 | -23.2 |  | -34.5 | 35.9 | 29.1 | 31.1 | 30.7 | 30 | 30.3 |  | 26.9 | 28.9 | 27.8 | 28 | 27.8667
Belarus |  | MOGILEV | MOGILEV, Belarus | 53.95N | 30.07E | 192 | 2.00 (EUE) | 82-06 | 268630 | -25 |  | -34.2 | 35.2 | 28.5 | 30.7 | 29.5 | 30 | 29.5667 |  | 26.3 | 28.1 | 26.8 | 27 | 27.0667
Belarus |  | MOZYR | MOZYR, Belarus | 51.95N | 29.17E | 190 | 2.00 (EUE) | 82-06 | 330360 | -23.3 |  | -35.9 | 36.7 | 30.5 | 32.1 | 30.9 | 31 | 31.1667 |  | 27.8 | 29.9 | 28.5 | 29 | 28.7333
Belarus |  | ORSHA | ORSHA, Belarus | 54.50N | 30.42E | 185 | 2.00 (EUE) | 82-06 | 267630 | -25.9 |  | -35.2 | 35.4 | 28.2 | 30.5 | 29 | 29 | 29.2333 |  | 26 | 27.8 | 26.5 | 27 | 26.7667
Belarus |  | PINSK | PINSK, Belarus | 52.12N | 26.12E | 142 | 2.00 (EUE) | 82-06 | 330190 | -21 |  | -31.4 | 35.7 | 30 | 31.6 | 31.1 | 31 | 30.9 |  | 27.5 | 29.5 | 28.5 | 29 | 28.5
Belarus |  | SLUTSK | SLUTSK, Belarus | 53.03N | 27.55E | 162 | 2.00 (EUE) | 82-06 | 269510 | -23.6 |  | -34.8 | 35.5 | 29.3 | 31.2 | 30.4 | 30 | 30.3 |  | 26.8 | 28.8 | 27.7 | 28 | 27.7667
Belarus |  | VERHNEDVINSK | VERHNEDVINSK, Belarus | 55.82N | 27.95E | 132 | 2.00 (EUE) | 82-06 | 265540 | -25.3 |  | -34.9 | 34.7 | 28.1 | 30.6 | 28.5 | 29 | 29.0667 |  | 26 | 27.5 | 26.3 | 27 | 26.6
Belarus |  | VITEBSK | VITEBSK, Belarus | 55.17N | 30.22E | 176 | 2.00 (EUE) | 82-06 | 266660 | -25 |  | -34.6 | 35.1 | 28.4 | 30.6 | 28.7 | 29 | 29.2333 |  | 26.2 | 28 | 26.3 | 27 | 26.8333
Belarus |  | ZHITCKOVICHI | ZHITCKOVICHI, Belarus | 52.22N | 27.87E | 137 | 2.00 (EUE) | 82-06 | 330270 | -23.2 |  | -34.3 | 36.3 | 30.1 | 32 | 30.5 | 31 | 30.8667 |  | 27.8 | 29.6 | 28.3 | 29 | 28.5667
Belgium |  | ANTWERPEN/DEURNE | ANTWERPEN/DEURNE, Belgium | 51.20N | 4.47E | 14 | 1.00 (EUW) | 82-06 | 64500 | -9.3 |  | -17.5 | 37.7 | 30.4 | 31.9 | 31.8 | 31 | 31.3667 |  | 27.1 | 29.1 | 29 | 28 | 28.4
Belgium |  | BEAUVECHAIN | BEAUVECHAIN, Belgium | 50.75N | 4.77E | 127 | 1.00 (EUW) | 82-06 | 64580 | -9.7 |  | -19.5 | 37.4 | 29.9 | 31.3 | 31.7 | 31 | 30.9667 |  | 26.8 | 28.7 | 28.8 | 28 | 28.1
Belgium |  | BIERSET | BIERSET, Belgium | 50.65N | 5.45E | 178 | 1.00 (EUW) | 82-06 | 64780 | -10.6 |  | -21.3 | 37.9 | 30.2 | 31.8 | 32.2 | 31 | 31.4 |  | 27 | 29.2 | 29 | 28 | 28.4
Belgium |  | BRUXELLES NATIONAL | BRUXELLES NATIONAL, Belgium | 50.90N | 4.53E | 58 | 1.00 (EUW) | 82-06 | 64510 | -9 |  | -18.7 | 37.5 | 29.8 | 31.4 | 31.7 | 31 | 30.9667 |  | 26.9 | 28.9 | 28.9 | 28 | 28.2333
Belgium |  | CHARLEROI/GOSSELIES | CHARLEROI/GOSSELIES, Belgium | 50.47N | 4.45E | 192 | 1.00 (EUW) | 82-06 | 64490 | -9.7 |  | -18.8 | 38.3 | 30.3 | 31.9 | 32.5 | 32 | 31.5667 |  | 27 | 29.3 | 29 | 28 | 28.4333
Belgium |  | CHIEVRES | CHIEVRES, Belgium | 50.57N | 3.83E | 63 | 1.00 (EUW) | 82-06 | 64320 | -10.4 |  | -23 | 37.5 | 29.9 | 32 | 31.6 | 31 | 31.1667 |  | 27.3 | 29.3 | 28.9 | 29 | 28.5
Belgium |  | ELSENBORN | ELSENBORN, Belgium | 50.47N | 6.18E | 570 | 1.00 (EUW) | 86-06 | 64960 | -16.5 |  | -25 | 35.8 | 28.2 | 29.4 | 30.5 | 29 | 29.3667 |  | 25.1 | 26.7 | 27 | 26 | 26.2667
Belgium |  | FLORENNES | FLORENNES, Belgium | 50.23N | 4.65E | 299 | 1.00 (EUW) | 82-06 | 64560 | -10.8 |  | -19.8 | 36.6 | 29.2 | 30.5 | 31.5 | 30 | 30.4 |  | 26 | 28.1 | 28.1 | 27 | 27.4
Belgium |  | GENT/INDUSTRIE-ZONE | GENT/INDUSTRIE-ZONE, Belgium | 51.18N | 3.82E | 13 | 1.00 (EUW) | 83-06 | 64310 | -9.3 |  | -20.7 | 37.6 | 30.2 | 31.6 | 31 | 31 | 30.9333 |  | 27.2 | 28.7 | 28.5 | 28 | 28.1333
Belgium |  | KLEINE BROGEL | KLEINE BROGEL, Belgium | 51.17N | 5.47E | 64 | 1.00 (EUW) | 82-06 | 64790 | -11.8 |  | -21.7 | 39.6 | 31.2 | 33 | 32.8 | 32 | 32.3333 |  | 28.1 | 30.1 | 29.9 | 29 | 29.3667
Belgium |  | KOKSIJDE | KOKSIJDE, Belgium | 51.08N | 2.65E | 9 | 1.00 (EUW) | 82-06 | 64000 | -8.6 |  | -18.1 | 36.9 | 28.5 | 29.5 | 30.3 | 29 | 29.4333 |  | 24.8 | 26.5 | 26.6 | 26 | 25.9667
Belgium |  | LIEGE | LIEGE, Belgium | 50.63N | 5.45E | 201 | 1.00 (EUW) | 82-06 | 64324 | -12.2 |  | -25.9 | 36.4 | 30.2 | 31.9 | 31 | 31 | 31.0333 |  | 26.9 | 29.1 | 27.1 | 28 | 27.7
Belgium |  | OOSTENDE (AIRPORT) | OOSTENDE (AIRPORT), Belgium | 51.20N | 2.87E | 5 | 1.00 (EUW) | 82-06 | 64070 | -8.6 |  | -16.6 | 36.2 | 27.9 | 29 | 29.6 | 29 | 28.8333 |  | 23.7 | 25.3 | 25.2 | 25 | 24.7333
Belgium |  | OOSTENDE (PIER) | OOSTENDE (PIER), Belgium | 51.23N | 2.92E | 15 | 1.00 (EUW) | 82-05 | 64080 | -6.2 |  | -14.9 | 35.8 | 26.2 | 27.8 | 29.2 | 28 | 27.7333 |  | 22.7 | 24.9 | 25.2 | 24 | 24.2667
Belgium |  | SEMMERZAKE | SEMMERZAKE, Belgium | 50.93N | 3.67E | 37 | 1.00 (EUW) | 90-06 | 64280 | -8.1 |  | -16.8 | 37.6 | 30.2 | 31.9 | 31.8 | 31 | 31.3 |  | 26.8 | 28.9 | 29.1 | 28 | 28.2667
Belgium |  | ST. TRUIDEN (BAFB) | ST. TRUIDEN (BAFB), Belgium | 50.80N | 5.20E | 75 | 1.00 (EUW) | 82-92 | 64700 | -12.4 |  | -29 | 38.1 | 28.3 | 31.3 | 31.2 | 30 | 30.2667 |  | 26.4 | 28.8 | 28 | 28 | 27.7333
Belgium |  | ST-HUBERT | ST-HUBERT, Belgium | 50.03N | 5.40E | 557 | 1.00 (EUW) | 82-92 | 64760 | -12.1 |  | -24.2 | 32.2 | 25.5 | 27.4 | 28.3 | 27 | 27.0667 |  | 23.4 | 25.7 | 24.8 | 25 | 24.6333
Belgium |  | UCCLE | UCCLE, Belgium | 50.80N | 4.35E | 104 | 1.00 (EUW) | 82-06 | 64470 | -8.7 |  | -18.3 | 36.9 | 29.6 | 31.3 | 31.5 | 31 | 30.8 |  | 26.8 | 28.8 | 28.6 | 28 | 28.0667
Belize |  | BELIZE/PHILLIP GOLD | BELIZE/PHILLIP GOLD, Belize | 17.53N | 88.30W | 5 | -6.00 (CAM) | 82-06 | 785830 | 14.3 |  | 12.1 | 38.5 | 33.2 | 32.2 | 32.9 | 33 | 32.7667 |  | 32.2 | 31.9 | 32.2 | 32 | 32.1
Benin |  | BOHICON | BOHICON, Benin | 7.17N | 2.07E | 167 | 1.00 (AFW) | 82-06 | 653380 | N/A |  | N/A | N/A | 32.7 | 31.1 | 30.9 | 32 | 31.5667 |  | 31.7 | 30.1 | 29.9 | 31 | 30.5667
Benin |  | COTONOU | COTONOU, Benin | 6.35N | 2.38E | 9 | 1.00 (AFW) | 82-06 | 653440 | 19.6 |  | 14.6 | 41.2 | 31.2 | 29.2 | 29 | 30 | 29.8 |  | 30.4 | 28.7 | 28.2 | 29 | 29.1
Benin |  | KANDI | KANDI, Benin | 11.13N | 2.93E | 292 | 1.00 (AFW) | 82-06 | 653060 | N/A |  | N/A | N/A | 37 | 33.3 | 32.5 | 34 | 34.2667 |  | 35.2 | 32.3 | 31.3 | 33 | 32.9333
Benin |  | NATITINGOU | NATITINGOU, Benin | 10.32N | 1.38E | 461 | 1.00 (AFW) | 82-06 | 653190 | N/A |  | N/A | N/A | 33.9 | 31.6 | 31.1 | 32 | 32.2 |  | 32.5 | 30.5 | 29.9 | 31 | 30.9667
Benin |  | PARAKOU | PARAKOU, Benin | 9.35N | 2.62E | 393 | 1.00 (AFW) | 82-06 | 653300 | 15.7 |  | 13.9 | 40.5 | 33.1 | 31.4 | 30.6 | 32 | 31.7 |  | 32 | 30.2 | 29.6 | 31 | 30.6
Benin |  | SAVE | SAVE, Benin | 8.03N | 2.47E | 200 | 1.00 (AFW) | 82-06 | 653350 | N/A |  | N/A | N/A | 32.9 | 31 | 30.7 | 32 | 31.5333 |  | 31.8 | 30.1 | 29.7 | 31 | 30.5333
Bermuda |  | BERMUDA INTL | BERMUDA INTL, Bermuda | 32.37N | 64.68W | 6 | -4.00 (NAA) | 82-06 | 780160 | 10.3 |  | 7 | 33.9 | 30.2 | 31.8 | 32.1 | 31 | 31.3667 |  | 29.2 | 30.9 | 31.2 | 30 | 30.4333
Bolivia |  | COCHABAMBA | COCHABAMBA, Bolivia | 17.42S | 66.18W | 2548 | -4.00 (SAW) | 82-06 | 852230 | -1.2 |  | -4.1 | 34.4 | 27 | 27.1 | 28.8 | 28 | 27.6333 |  | 25.3 | 25.7 | 27.1 | 26 | 26.0333
Bolivia |  | LA PAZ/ALTO | LA PAZ/ALTO, Bolivia | 16.52S | 68.18W | 4038 | -4.00 (SAW) | 82-06 | 852010 | -6.9 |  | -10.6 | 25.8 | 15.1 | 15.2 | 16.4 | 16 | 15.5667 |  | 14 | 14.1 | 15.2 | 14 | 14.4333
Bolivia |  | VIRU-VIRU | VIRU-VIRU, Bolivia | 17.63S | 63.13W | 373 | -4.00 (SAW) | 86-06 | 852440 | 6.5 |  | 2.4 | 40 | 30.1 | 30.9 | 33.8 | 32 | 31.6 |  | 29 | 29.8 | 32.2 | 30 | 30.3333
Bosnia and Herzegovina |  | BANJA LUKA | BANJA LUKA, Bosnia and Herzegovina | 44.78N | 17.22E | 156 | 1.00 (EUW) | 82-06 | 132420 | -14.9 |  | -26.3 | 41 | 33.3 | 35.7 | 35.2 | 35 | 34.7333 |  | 30.8 | 33.1 | 32.3 | 32 | 32.0667
Bosnia and Herzegovina |  | BIHAC | BIHAC, Bosnia and Herzegovina | 44.82N | 15.88E | 250 | 1.00 (EUW) | 82-92 | 132280 | -14.7 |  | -25 | 39.5 | 31.1 | 34.8 | 33.8 | 33 | 33.2333 |  | 28.7 | 32.3 | 31.1 | 31 | 30.7
Bosnia and Herzegovina |  | BJELASNICA | BJELASNICA, Bosnia and Herzegovina | 43.72N | 18.27E | 2070 | 1.00 (EUW) | 82-06 | 146520 | -21.4 |  | -28.7 | 28.8 | 19.1 | 21.3 | 20.5 | 20 | 20.3 |  | 16.4 | 19.1 | 18.2 | 18 | 17.9
Bosnia and Herzegovina |  | MOSTAR | MOSTAR, Bosnia and Herzegovina | 43.33N | 17.78E | 108 | 1.00 (EUW) | 82-06 | 133480 | N/A |  | N/A | N/A | 36.4 | 38 | 37.7 | 37 | 37.3667 |  | 32.9 | 35.7 | 35.2 | 35 | 34.6
Bosnia and Herzegovina |  | SARAJEVO/BUTMIR | SARAJEVO/BUTMIR, Bosnia and Herzegovina | 43.82N | 18.33E | 511 | 1.00 (EUW) | 82-06 | 133530 | -18.7 |  | -28.6 | 40.4 | 32.3 | 34.9 | 34.7 | 34 | 33.9667 |  | 30.2 | 32.2 | 31.9 | 31 | 31.4333
Bosnia and Herzegovina |  | SARAJEVO-BJELAVE | SARAJEVO-BJELAVE, Bosnia and Herzegovina | 43.87N | 18.43E | 638 | 1.00 (EUW) | 82-06 | 146540 | -15.4 |  | -21.6 | 38.6 | 31.6 | 34.2 | 33.6 | 33 | 33.1333 |  | 29.4 | 31.8 | 30.9 | 31 | 30.7
Botswana |  | SERETSE KHAMA INTER | SERETSE KHAMA INTER, Botswana | 24.55S | 25.92E | 1005 | 2.00 (AFS) | 85-06 | 682400 | -1.1 |  | -6.1 | 42.7 | 27.1 | 27.2 | 31.1 | 28 | 28.4667 |  | 25.2 | 25.5 | 28.8 | 27 | 26.5
Brazil |  | ANAPOLIS (BRAZ-AFB) | ANAPOLIS (BRAZ-AFB), Brazil | 16.23S | 48.97W | 1137 | -3.00 (SAB) | 83-01 | 834190 | N/A |  | N/A | N/A | 28.8 | 29.1 | 31.9 | 30 | 29.9333 |  | 27.7 | 28.1 | 30.1 | 29 | 28.6333
Brazil |  | ARACAJU (AEROPORTO) | ARACAJU (AEROPORTO), Brazil | 10.98S | 37.07W | 9 | -3.00 (SAB) | 83-01 | 830950 | 18.2 |  | 14.8 | 41 | 30.1 | 29.2 | 29.1 | 29 | 29.4667 |  | 29.2 | 28.8 | 28.3 | 29 | 28.7667
Brazil |  | BELEM (AEROPORTO) | BELEM (AEROPORTO), Brazil | 1.38S | 48.48W | 16 | -3.00 (SAB) | 82-06 | 821930 | 21.1 |  | 17.9 | 39.3 | 33.1 | 33.1 | 33.2 | 33 | 33.1333 |  | 32.2 | 32.2 | 32.6 | 32 | 32.3333
Brazil |  | BELO HORIZONTE | BELO HORIZONTE, Brazil | 19.93S | 43.93W | 850 | -3.00 (SAB) | 90-06 | 835870 | 8.2 |  | 4.4 | 37.4 | 27.9 | 28.8 | 31.1 | 29 | 29.2667 |  | 26.8 | 27 | 29.1 | 28 | 27.6333
Brazil |  | BELO HORIZONTE (AERO) | BELO HORIZONTE (AERO), Brazil | 19.85S | 43.95W | 785 | -3.00 (SAB) | 82-01 | 835830 | N/A |  | N/A | N/A | 28.9 | 29 | 31.9 | 30 | 29.9333 |  | 27.7 | 27.8 | 30 | 29 | 28.5
Brazil |  | BOA VISTA (AEROPORTO) | BOA VISTA (AEROPORTO), Brazil | 2.83N | 60.70W | 140 | -4.00 (SAZ) | 82-06 | 820220 | 20.8 |  | 18.1 | 43 | 34.1 | 34 | 35.2 | 34 | 34.4333 |  | 33 | 32.9 | 34.1 | 33 | 33.3333
Brazil |  | BRASILIA (AEROPORTO) | BRASILIA (AEROPORTO), Brazil | 15.87S | 47.93W | 1061 | -3.00 (SAB) | 82-06 | 833780 | 7.2 |  | 0.8 | 37.5 | 28.9 | 29.2 | 31.9 | 30 | 30 |  | 27.9 | 28.1 | 30.2 | 29 | 28.7333
Brazil |  | CAMPINAS (AEROPORTO) | CAMPINAS (AEROPORTO), Brazil | 23.00S | 47.13W | 661 | -3.00 (SAB) | 82-06 | 837210 | 5.8 |  | -0.2 | 39.7 | 28.2 | 29.2 | 32.1 | 30 | 29.8333 |  | 27.1 | 28 | 30.2 | 28 | 28.4333
Brazil |  | CAMPO GRANDE (AERO) | CAMPO GRANDE (AERO), Brazil | 20.47S | 54.67W | 567 | -4.00 (SAZ) | 82-06 | 836120 | 4.9 |  | -0.1 | 43.5 | 33 | 34 | 36.3 | 34 | 34.4333 |  | 31.8 | 32.2 | 35 | 33 | 33
Brazil |  | CARAVELAS (AEROPORTO) | CARAVELAS (AEROPORTO), Brazil | 17.63S | 39.25W | 4 | -3.00 (SAB) | 83-94 | 834970 | 14.4 |  | 11.8 | 39.4 | 29.2 | 28.6 | 28.4 | 29 | 28.7333 |  | 28.4 | 27.9 | 27.5 | 28 | 27.9333
Brazil |  | CUIABA (AEROPORTO) | CUIABA (AEROPORTO), Brazil | 15.65S | 56.10W | 187 | -4.00 (SAZ) | 82-06 | 833620 | 10.4 |  | 5 | 42.3 | 35.2 | 36.1 | 38.8 | 37 | 36.7 |  | 34.1 | 34.9 | 37.2 | 35 | 35.4
Brazil |  | CURITIBA (AEROPORTO) | CURITIBA (AEROPORTO), Brazil | 25.52S | 49.17W | 908 | -3.00 (SAB) | 82-06 | 838400 | -1.1 |  | -6.1 | 35.5 | 26 | 26.9 | 29.5 | 27 | 27.4667 |  | 24.2 | 25.1 | 27.8 | 26 | 25.7
Brazil |  | EDUARDO GOMES INTL | EDUARDO GOMES INTL, Brazil | 3.03S | 60.05W | 2 | -4.00 (SAZ) | 82-06 | 821110 | 19.8 |  | 15.8 | 40 | 35 | 35.1 | 36.1 | 35 | 35.4 |  | 33.9 | 34.1 | 35.1 | 34 | 34.3667
Brazil |  | FERNANDO DE NORONHA | FERNANDO DE NORONHA, Brazil | 3.85S | 32.42W | 56 | -3.00 (SAB) | 82-03 | 824000 | 20 |  | 13.7 | 43 | 30.2 | 29.9 | 29.2 | 30 | 29.7667 |  | 29.8 | 29.1 | 29 | 29 | 29.3
Brazil |  | FLORIANOPOLIS (AERO) | FLORIANOPOLIS (AERO), Brazil | 27.67S | 48.55W | 5 | -3.00 (SAB) | 82-06 | 838990 | 3.9 |  | -1 | 39.5 | 27.3 | 28.1 | 29.7 | 28 | 28.3667 |  | 25.2 | 24.9 | 25.5 | 25 | 25.2
Brazil |  | FORTALEZA (AEROPORTO) | FORTALEZA (AEROPORTO), Brazil | 3.78S | 38.53W | 25 | -3.00 (SAB) | 82-06 | 823980 | 21 |  | 17.2 | 40.2 | 31.9 | 31.2 | 31.9 | 32 | 31.6667 |  | 31.1 | 31 | 31.1 | 31 | 31.0667
Brazil |  | FOZ DO IGUACU (AERO) | FOZ DO IGUACU (AERO), Brazil | 25.52S | 54.58W | 180 | -4.00 (SAZ) | 85-06 | 838270 | 0.2 |  | -4.1 | 40.9 | 29.8 | 30 | 33.2 | 31 | 31 |  | 28.1 | 28.2 | 31.6 | 29 | 29.3
Brazil |  | GALEAO | GALEAO, Brazil | 22.82S | 43.25W | 6 | -3.00 (SAB) | 82-06 | 837460 | 12.5 |  | 8.7 | 45.2 | 33.1 | 33.2 | 35.8 | 34 | 34.0333 |  | 31 | 31.1 | 32.2 | 31 | 31.4333
Brazil |  | GOIANIA (AEROPORTO) | GOIANIA (AEROPORTO), Brazil | 16.63S | 49.22W | 747 | -3.00 (SAB) | 82-06 | 834240 | 8.2 |  | 3.1 | 39.2 | 31.6 | 32.2 | 35 | 33 | 32.9333 |  | 30.8 | 31.2 | 33.8 | 32 | 31.9333
Brazil |  | GUARULHOS | GUARULHOS, Brazil | 23.43S | 46.47W | 768 | -3.00 (SAB) | 88-06 | 837753 | 3.8 |  | -2.7 | 36.9 | 27.2 | 28.2 | 31.1 | 29 | 28.8333 |  | 26.1 | 26.8 | 29 | 27 | 27.3
Brazil |  | LONDRINA (AEROPORTO) | LONDRINA (AEROPORTO), Brazil | 23.33S | 51.13W | 569 | -3.00 (SAB) | 84-06 | 837680 | 4.5 |  | -1.3 | 39.1 | 28.2 | 29.2 | 32.4 | 30 | 29.9333 |  | 27 | 27.5 | 30.7 | 28 | 28.4
Brazil |  | MACAPA | MACAPA, Brazil | 0.03N | 51.05W | 15 | -3.00 (SAB) | 86-06 | 820980 | 20.9 |  | 12.6 | 36.1 | 33.8 | 33.9 | 34.1 | 34 | 33.9333 |  | 32.3 | 32.9 | 33.2 | 33 | 32.8
Brazil |  | MACEIO (AEROPORTO) | MACEIO (AEROPORTO), Brazil | 9.52S | 35.78W | 117 | -3.00 (SAB) | 82-06 | 829930 | 17.4 |  | 13.1 | 40.5 | 30 | 29.3 | 29.9 | 30 | 29.7333 |  | 29.1 | 28.4 | 28.9 | 29 | 28.8
Brazil |  | MANAUS (AEROPORTO) | MANAUS (AEROPORTO), Brazil | 3.15S | 59.98W | 84 | -4.00 (SAZ) | 82-06 | 823320 | 20.3 |  | 17.3 | 40.8 | 33 | 34 | 34.8 | 34 | 33.9333 |  | 32.1 | 32.9 | 33.8 | 33 | 32.9333
Brazil |  | NATAL AEROPORTO | NATAL AEROPORTO, Brazil | 5.92S | 35.25W | 52 | -3.00 (SAB) | 83-06 | 825990 | 19.4 |  | 14.3 | 40.1 | 31.7 | 31.1 | 31.2 | 31 | 31.3333 |  | 30.9 | 30.2 | 30.2 | 30 | 30.4333
Brazil |  | PORTO ALEGRE (AERO) | PORTO ALEGRE (AERO), Brazil | 30.00S | 51.18W | 3 | -3.00 (SAB) | 82-06 | 839710 | 1.6 |  | -4.2 | 41.3 | 29.4 | 30.1 | 32 | 31 | 30.5 |  | 26.8 | 26.9 | 28.8 | 28 | 27.5
Brazil |  | PORTO VELHO (AERO) | PORTO VELHO (AERO), Brazil | 8.77S | 63.92W | 102 | -4.00 (SAZ) | 83-06 | 828240 | 15.5 |  | 9.4 | 39.8 | 34.2 | 35.2 | 36.2 | 35 | 35.2 |  | 33.2 | 34 | 35.1 | 34 | 34.1
Brazil |  | RECIFE (AEROPORTO) | RECIFE (AEROPORTO), Brazil | 8.07S | 34.85W | 19 | -3.00 (SAB) | 82-06 | 828990 | 20.1 |  | 16.8 | 39.9 | 31.7 | 31.1 | 31.1 | 31 | 31.3 |  | 31 | 30.2 | 30.2 | 30 | 30.4667
Brazil |  | RIO BRANCO | RIO BRANCO, Brazil | 10.00S | 67.80W | 143 | -5.00 (SAP) | 90-06 | 829170 | 12.1 |  | 6.3 | 40.3 | 33.2 | 35.1 | 36.2 | 35 | 34.8333 |  | 32.5 | 33.9 | 35.2 | 34 | 33.8667
Brazil |  | RIO DE JANEIRO (AERO) | RIO DE JANEIRO (AERO), Brazil | 22.90S | 43.17W | 3 | -3.00 (SAB) | 84-06 | 837550 | 14.8 |  | 11.1 | 39.9 | 30.2 | 30.2 | 32 | 31 | 30.8 |  | 28.2 | 28.4 | 29.1 | 29 | 28.5667
Brazil |  | SALVADOR (AEROPORTO) | SALVADOR (AEROPORTO), Brazil | 12.90S | 38.33W | 6 | -3.00 (SAB) | 82-06 | 832480 | 18.6 |  | 15.3 | 40.3 | 30.2 | 30.1 | 29.9 | 30 | 30.0667 |  | 29.9 | 29.1 | 29 | 29 | 29.3333
Brazil |  | SANTAREM-AEROPORTO | SANTAREM-AEROPORTO, Brazil | 2.43S | 54.72W | 72 | -4.00 (SAZ) | 82-06 | 822440 | 21 |  | 17.1 | 38.3 | 32.1 | 32.2 | 33.2 | 33 | 32.5 |  | 31.3 | 32 | 32.4 | 32 | 31.9
Brazil |  | SAO LUIZ (AEROPORTO) | SAO LUIZ (AEROPORTO), Brazil | 2.60S | 44.23W | 53 | -3.00 (SAB) | 84-06 | 822810 | 20.5 |  | 13.2 | 39.4 | 33.2 | 33.2 | 34 | 33 | 33.4667 |  | 32.5 | 32.4 | 33.1 | 33 | 32.6667
Brazil |  | SAO PAULO (AEROPORTO) | SAO PAULO (AEROPORTO), Brazil | 23.62S | 46.65W | 803 | -3.00 (SAB) | 82-06 | 837800 | 6.1 |  | 0.1 | 36.8 | 27.2 | 28.1 | 30.9 | 29 | 28.7333 |  | 26 | 26.8 | 28.8 | 27 | 27.2
Brazil |  | TERESINA (AEROPORTO) | TERESINA (AEROPORTO), Brazil | 5.05S | 42.82W | 69 | -3.00 (SAB) | 83-06 | 825790 | 19.6 |  | 15.4 | 42.8 | 35.6 | 36.3 | 37.2 | 36 | 36.3667 |  | 34.4 | 35.2 | 36.5 | 35 | 35.3667
Brazil |  | UBERABA | UBERABA, Brazil | 19.78S | 47.97W | 807 | -3.00 (SAB) | 83-01 | 835760 | 6.7 |  | -1.1 | 39.1 | 29.8 | 30.2 | 33.2 | 31 | 31.0667 |  | 28.3 | 29.2 | 31.9 | 30 | 29.8
Brazil |  | VITORIA (AEROPORTO) | VITORIA (AEROPORTO), Brazil | 20.27S | 40.28W | 4 | -3.00 (SAB) | 82-06 | 836490 | 14 |  | 8.8 | 39.4 | 31.1 | 30.9 | 30.9 | 31 | 30.9667 |  | 29.7 | 29.2 | 29.4 | 29 | 29.4333
British Indian Ocean Territory |  | DIEGO GARCIA NAF | DIEGO GARCIA NAF, British Indian Ocean Territory | 7.30S | 72.40E | 3 | 5.50 (IND) | 82-06 | 619670 | 21.8 |  | 18.8 | 40.2 | 31.2 | 30.2 | 30.2 | 31 | 30.5333 |  | 30.2 | 29.7 | 29.6 | 30 | 29.8333
Brunei Darussalam |  | BRUNEI AIRPORT | BRUNEI AIRPORT, Brunei Darussalam | 4.93N | 114.93E | 15 | 8.00 (CHN) | 82-06 | 963150 | 20.4 |  | 14.9 | 39.5 | 33.8 | 34 | 34 | 34 | 33.9333 |  | 33 | 33 | 33.1 | 33 | 33.0333
Bulgaria |  | BOTEV VRAH (TOP/SOMMET) | BOTEV VRAH (TOP/SOMMET), Bulgaria | 42.67N | 24.83E | 2389 | 2.00 (EUE) | 82-06 | 156270 | -22.4 |  | -30.7 | 23.1 | 14.8 | 18.8 | 17.7 | 17 | 17.1 |  | 13.2 | 16.2 | 15.5 | 15 | 14.9667
Bulgaria |  | BURGAS | BURGAS, Bulgaria | 42.48N | 27.48E | 28 | 2.00 (EUE) | 82-06 | 156550 | -10.7 |  | -16.8 | 41.8 | 31.2 | 34 | 33.2 | 33 | 32.8 |  | 29.2 | 31.1 | 30.9 | 30 | 30.4
Bulgaria |  | CHERNI VRAH (TOP/SOMMET) | CHERNI VRAH (TOP/SOMMET), Bulgaria | 42.58N | 23.27E | 2292 | 2.00 (EUE) | 82-06 | 156130 | -22.4 |  | -28.3 | 23.4 | 16.9 | 19.7 | 18.6 | 18 | 18.4 |  | 14.8 | 17.1 | 16.7 | 16 | 16.2
Bulgaria |  | CHIRPAN | CHIRPAN, Bulgaria | 42.20N | 25.33E | 178 | 2.00 (EUE) | 90-06 | 156350 | -16.4 |  | -26.5 | 44 | 34.1 | 37.5 | 36.7 | 36 | 36.1 |  | 31.8 | 33.9 | 34.1 | 33 | 33.2667
Bulgaria |  | ELHOVO | ELHOVO, Bulgaria | 42.18N | 26.57E | 139 | 2.00 (EUE) | 93-06 | 156420 | -13.3 |  | -20.7 | 44.1 | 33.2 | 37.2 | 36.4 | 36 | 35.6 |  | 31.5 | 33.8 | 33.8 | 33 | 33.0333
Bulgaria |  | IVAILO | IVAILO, Bulgaria | 42.22N | 24.33E | 214 | 2.00 (EUE) | 82-06 | 156280 | -15 |  | -24.5 | 43.9 | 34.7 | 37.1 | 36.7 | 36 | 36.1667 |  | 32.2 | 34.2 | 33.9 | 33 | 33.4333
Bulgaria |  | KALIAKPA | KALIAKPA, Bulgaria | 43.37N | 28.47E | 64 | 2.00 (EUE) | 82-06 | 155620 | -12.1 |  | -17.7 | 33.8 | 27.2 | 29.9 | 30.1 | 29 | 29.0667 |  | 26 | 28.6 | 28.5 | 28 | 27.7
Bulgaria |  | KURDJALI | KURDJALI, Bulgaria | 41.65N | 25.37E | 331 | 2.00 (EUE) | 82-06 | 157300 | -13 |  | -19.2 | 42.4 | 32.7 | 36.3 | 35.7 | 35 | 34.9 |  | 30.4 | 33 | 32.9 | 32 | 32.1
Bulgaria |  | KUSTENDIL | KUSTENDIL, Bulgaria | 42.27N | 22.77E | 527 | 2.00 (EUE) | 82-06 | 156010 | -15.9 |  | -25.2 | 40.6 | 32.8 | 35 | 35.3 | 34 | 34.3667 |  | 30.5 | 32.4 | 32.9 | 32 | 31.9333
Bulgaria |  | LOM | LOM, Bulgaria | 43.82N | 23.25E | 33 | 2.00 (EUE) | 82-06 | 155110 | -13.2 |  | -23 | 39.6 | 33.1 | 34.9 | 34.6 | 34 | 34.2 |  | 30.9 | 32.7 | 32.4 | 32 | 32
Bulgaria |  | LOVETCH | LOVETCH, Bulgaria | 43.13N | 24.72E | 221 | 2.00 (EUE) | 90-06 | 155250 | -15 |  | -22.5 | 44 | 34.2 | 37.8 | 36.5 | 36 | 36.1667 |  | 31.5 | 33.6 | 34.1 | 33 | 33.0667
Bulgaria |  | MOURGASH | MOURGASH, Bulgaria | 42.83N | 23.67E | 1692 | 2.00 (EUE) | 90-06 | 156000 | -20.2 |  | -26.9 | 32.5 | 21.3 | 25.2 | 24.3 | 24 | 23.6 |  | 19.3 | 21.6 | 22 | 21 | 20.9667
Bulgaria |  | MUSSALA (TOP/SOMMET) | MUSSALA (TOP/SOMMET), Bulgaria | 42.18N | 23.58E | 2927 | 2.00 (EUE) | 82-06 | 156150 | -25.3 |  | -32.7 | 21.4 | 13.5 | 16.3 | 15.5 | 15 | 15.1 |  | 11.3 | 13.7 | 13.2 | 13 | 12.7333
Bulgaria |  | PLEVEN | PLEVEN, Bulgaria | 43.42N | 24.60E | 71 | 2.00 (EUE) | 82-99 | 155260 | -17.7 |  | -30.2 | 44.5 | 35 | 38 | 37 | 37 | 36.6667 |  | 32.1 | 35 | 34.6 | 34 | 33.9
Bulgaria |  | PLOVDIV | PLOVDIV, Bulgaria | 42.13N | 24.75E | 185 | 2.00 (EUE) | 82-06 | 156250 | -14.1 |  | -23 | 44.5 | 34.8 | 38.2 | 36.8 | 37 | 36.6 |  | 32.1 | 34.6 | 34 | 34 | 33.5667
Bulgaria |  | RAZGRAD | RAZGRAD, Bulgaria | 43.52N | 26.53E | 347 | 2.00 (EUE) | 90-06 | 155490 | -15.1 |  | -21.5 | 41.2 | 32 | 35.4 | 34.6 | 34 | 34 |  | 29.7 | 31.9 | 32.5 | 31 | 31.3667
Bulgaria |  | ROUSSE | ROUSSE, Bulgaria | 43.85N | 25.95E | 45 | 2.00 (EUE) | 82-06 | 155350 | -14.2 |  | -22 | 45.3 | 35.1 | 38.5 | 37.1 | 37 | 36.9 |  | 32.4 | 35 | 34.3 | 34 | 33.9
Bulgaria |  | SANDANSKI | SANDANSKI, Bulgaria | 41.52N | 23.27E | 207 | 2.00 (EUE) | 82-06 | 157120 | -9.6 |  | -17.3 | 43.4 | 35.8 | 39 | 37.8 | 38 | 37.5333 |  | 33.3 | 35.8 | 35.4 | 35 | 34.8333
Bulgaria |  | SHABLA | SHABLA, Bulgaria | 43.53N | 28.53E | 28 | 2.00 (EUE) | 93-06 | 155610 | -11.7 |  | -18 | 34.3 | 28.2 | 30.1 | 30.2 | 30 | 29.5 |  | 26.2 | 28.7 | 28.7 | 28 | 27.8667
Bulgaria |  | SHUMEN | SHUMEN, Bulgaria | 43.27N | 26.93E | 220 | 2.00 (EUE) | 82-90 | 155440 | -14.9 |  | -23.3 | 40.9 | 31.7 | 35.8 | 32.7 | 33 | 33.4 |  | 28.5 | 32.3 | 30.8 | 31 | 30.5333
Bulgaria |  | SLIVEN | SLIVEN, Bulgaria | 42.67N | 26.32E | 257 | 2.00 (EUE) | 82-06 | 156400 | -10.1 |  | -15.3 | 42.2 | 32.4 | 35.6 | 35.3 | 34 | 34.4333 |  | 30.2 | 32.4 | 32.4 | 32 | 31.6667
Bulgaria |  | SOFIA (OBSERV.) | SOFIA (OBSERV.), Bulgaria | 42.65N | 23.38E | 591 | 2.00 (EUE) | 82-06 | 156140 | -17.3 |  | -28.1 | 42.1 | 32.1 | 35.8 | 34.6 | 34 | 34.1667 |  | 29.3 | 32.1 | 32 | 31 | 31.1333
Bulgaria |  | SVICHTOV | SVICHTOV, Bulgaria | 43.62N | 25.35E | 26 | 2.00 (EUE) | 90-06 | 155330 | -13.7 |  | -22.7 | 44.4 | 34.4 | 36.9 | 35.9 | 36 | 35.7333 |  | 32.1 | 33.9 | 33.7 | 33 | 33.2333
Bulgaria |  | SVILENGRAD | SVILENGRAD, Bulgaria | 41.77N | 26.20E | 55 | 2.00 (EUE) | 82-03 | 157410 | -13.5 |  | -23.7 | 44.7 | 35.1 | 38.7 | 37.6 | 37 | 37.1333 |  | 32.9 | 35.6 | 35 | 35 | 34.5
Bulgaria |  | VARNA | VARNA, Bulgaria | 43.20N | 27.92E | 43 | 2.00 (EUE) | 82-06 | 155520 | -12 |  | -19.1 | 41.8 | 31.1 | 33.2 | 33.2 | 33 | 32.5 |  | 28.8 | 30.9 | 31 | 30 | 30.2333
Bulgaria |  | VELIKO TARNOVO | VELIKO TARNOVO, Bulgaria | 43.08N | 25.65E | 218 | 2.00 (EUE) | 82-06 | 155300 | -15.6 |  | -24.2 | 44.8 | 34 | 36.8 | 37.1 | 36 | 35.9667 |  | 31.5 | 33.9 | 34.5 | 33 | 33.3
Bulgaria |  | VIDIN | VIDIN, Bulgaria | 43.82N | 22.88E | 33 | 2.00 (EUE) | 93-06 | 155020 | -16.5 |  | -26.2 | 42.3 | 35.3 | 36.4 | 36.5 | 36 | 36.0667 |  | 32.6 | 33.9 | 34.2 | 34 | 33.5667
Bulgaria |  | VRATZA | VRATZA, Bulgaria | 43.20N | 23.53E | 310 | 2.00 (EUE) | 90-06 | 155050 | -14.5 |  | -22.2 | 43.9 | 33.5 | 37.5 | 35.6 | 36 | 35.5333 |  | 30.8 | 33.1 | 33.2 | 32 | 32.3667
Burkina Faso |  | BOBO-DIOULASSO | BOBO-DIOULASSO, Burkina Faso | 11.17N | 4.32W | 460 | 0.00 (GRW) | 82-06 | 655100 | N/A |  | N/A | N/A | 34.7 | 33 | 31.4 | 33 | 33.0333 |  | 33.4 | 31.6 | 30.4 | 32 | 31.8
Burkina Faso |  | BOROMO | BOROMO, Burkina Faso | 11.75N | 2.93W | 271 | 0.00 (GRW) | 82-06 | 655160 | N/A |  | N/A | N/A | 37.4 | 34.9 | 33.9 | 35 | 35.4 |  | 35.9 | 33.7 | 32.4 | 34 | 34
Burkina Faso |  | DORI | DORI, Burkina Faso | 14.03N | 0.03W | 277 | 0.00 (GRW) | 82-06 | 655010 | N/A |  | N/A | N/A | 41.4 | 39.6 | 38.3 | 40 | 39.7667 |  | 40 | 38.1 | 36.2 | 38 | 38.1
Burkina Faso |  | OUAGADOUGOU | OUAGADOUGOU, Burkina Faso | 12.35N | 1.52W | 306 | 0.00 (GRW) | 82-06 | 655030 | 13.1 |  | 8.4 | 44.4 | 38.2 | 35.2 | 34 | 36 | 35.8 |  | 36.8 | 34 | 32.5 | 34 | 34.4333
Burkina Faso |  | OUAHIGOUYA | OUAHIGOUYA, Burkina Faso | 13.57N | 2.42W | 336 | 0.00 (GRW) | 82-06 | 655020 | N/A |  | N/A | N/A | 39.9 | 37.6 | 35.9 | 38 | 37.8 |  | 38.4 | 36 | 34.3 | 36 | 36.2333
Canada | Alberta | BANFF CS | BANFF CS, AB, Canada | 51.19N | 115.55W | 1397 | -7.00 (NAM) | 94-06 | 711220 | -36.7 |  | -50 | 35.4 | 26.6 | 30.4 | 29.7 | 29 | 28.9 |  | 23 | 28.2 | 27.4 | 26 | 26.2 |  |  | CanadaAlbertaBANFF CS
Canada | Alberta | BOW ISLAND | BOW ISLAND, AB, Canada | 49.73N | 111.45W | 817 | -7.00 (NAM) | 94-06 | 712310 | -33.4 |  | -41.6 | 37.1 | 30.9 | 33.1 | 33.6 | 33 | 32.5333 |  | 27.4 | 31.2 | 31.4 | 30 | 30 |  |  | CanadaAlbertaBOW ISLAND
Canada | Alberta | BOW VALLEY | BOW VALLEY, AB, Canada | 51.08N | 115.07W | 1298 | -7.00 (NAM) | 94-06 | 712320 | -37.1 |  | -47.7 | 37.3 | 27.4 | 32.3 | 31 | 30 | 30.2333 |  | 24 | 29.3 | 28.6 | 27 | 27.3 |  |  | CanadaAlbertaBOW VALLEY
Canada | Alberta | BRETON PLOTS | BRETON PLOTS, AB, Canada | 53.09N | 114.44W | 852 | -7.00 (NAM) | 95-06 | 712330 | N/A |  | N/A | N/A | 30.3 | 32.7 | 31.4 | 31 | 31.4667 |  | 26.7 | 29.6 | 28.4 | 28 | 28.2333 |  |  | CanadaAlbertaBRETON PLOTS
Canada | Alberta | BROOKS | BROOKS, AB, Canada | 50.55N | 111.85W | 747 | -7.00 (NAM) | 94-06 | 714570 | -33.8 |  | -43.8 | 38.7 | 30.7 | 34.2 | 34 | 33 | 32.9667 |  | 27.7 | 32 | 31.7 | 30 | 30.4667 |  |  | CanadaAlbertaBROOKS
Canada | Alberta | CALGARY INT'L A | CALGARY INT'L A, AB, Canada | 51.11N | 114.02W | 1084 | -7.00 (NAM) | 82-06 | 718770 | -32.4 |  | -42.1 | 36 | 28.3 | 31.1 | 31.1 | 30 | 30.1667 |  | 25.5 | 28.6 | 28.6 | 28 | 27.5667 |  |  | CanadaAlbertaCALGARY INT'L A
Canada | Alberta | CAMROSE | CAMROSE, AB, Canada | 53.03N | 112.81W | 739 | -7.00 (NAM) | 94-06 | 712540 | -37.2 |  | -50.3 | 37.1 | 28.7 | 31.6 | 30.6 | 30 | 30.3 |  | 25.9 | 28.2 | 27.9 | 27 | 27.3333 |  |  | CanadaAlbertaCAMROSE
Canada | Alberta | CARDSTON | CARDSTON, AB, Canada | 49.20N | 113.29W | 1136 | -7.00 (NAM) | 94-06 | 711530 | -32.4 |  | -42.1 | 38.3 | 28.6 | 33.5 | 33.2 | 32 | 31.7667 |  | 25.9 | 31.2 | 31 | 29 | 29.3667 |  |  | CanadaAlbertaCARDSTON
Canada | Alberta | CLARESHOLM | CLARESHOLM, AB, Canada | 50.00N | 113.64W | 1009 | -7.00 (NAM) | 94-06 | 712340 | -34.6 |  | -44 | 37.9 | 28.9 | 33.3 | 33.2 | 32 | 31.8 |  | 26.1 | 31.1 | 31 | 29 | 29.4 |  |  | CanadaAlbertaCLARESHOLM
Canada | Alberta | COLD LAKE A | COLD LAKE A, AB, Canada | 54.42N | 110.28W | 541 | -7.00 (NAM) | 82-06 | 711200 | -38.5 |  | -50 | 36.8 | 28.2 | 29.7 | 30.9 | 30 | 29.6 |  | 25.9 | 27.7 | 27.9 | 27 | 27.1667 |  |  | CanadaAlbertaCOLD LAKE A
Canada | Alberta | COP UPPER | COP UPPER, AB, Canada | 51.08N | 114.22W | 1235 | -7.00 (NAM) | 94-06 | 712350 | -30.3 |  | -40.3 | 37.2 | 27.1 | 30.9 | 30.7 | 30 | 29.5667 |  | 23.6 | 28.2 | 28.1 | 27 | 26.6333 |  |  | CanadaAlbertaCOP UPPER
Canada | Alberta | CORONATION (AUT) | CORONATION (AUT), AB, Canada | 52.08N | 111.45W | 791 | -7.00 (NAM) | 82-03 | 718730 | -37.1 |  | -45 | 38.4 | 29.6 | 32.5 | 32.5 | 32 | 31.5333 |  | 26.4 | 29.5 | 29.9 | 29 | 28.6 |  |  | CanadaAlbertaCORONATION (AUT)
Canada | Alberta | CROWSNEST | CROWSNEST, AB, Canada | 49.63N | 114.48W | 1303 | -7.00 (NAM) | 94-06 | 712360 | -34.6 |  | -45.8 | 36 | 27.2 | 31.6 | 30.8 | 30 | 29.8667 |  | 24.2 | 29 | 28.5 | 27 | 27.2333 |  |  | CanadaAlbertaCROWSNEST
Canada | Alberta | DRUMHELLER EAST | DRUMHELLER EAST, AB, Canada | 51.43N | 112.67W | 678 | -7.00 (NAM) | 94-06 | 712370 | -36.3 |  | -48 | 39.3 | 30.7 | 33.8 | 34.4 | 33 | 32.9667 |  | 27.9 | 31.4 | 32 | 30 | 30.4333 |  |  | CanadaAlbertaDRUMHELLER EAST
Canada | Alberta | EDMONTON CITY CENTRE A | EDMONTON CITY CENTRE A, AB, Canada | 53.57N | 113.52W | 671 | -7.00 (NAM) | 82-04 | 718790 | -31.7 |  | -43.6 | 35.5 | 28.7 | 30.3 | 30.5 | 30 | 29.8333 |  | 25.9 | 27.8 | 27.8 | 27 | 27.1667 |  |  | CanadaAlbertaEDMONTON CITY CENTRE A
Canada | Alberta | EDMONTON INT'L A | EDMONTON INT'L A, AB, Canada | 53.32N | 113.58W | 723 | -7.00 (NAM) | 82-06 | 711230 | -36.7 |  | -47.9 | 35.4 | 28.1 | 29.7 | 29.8 | 29 | 29.2 |  | 25.3 | 27 | 27.1 | 26 | 26.4667 |  |  | CanadaAlbertaEDMONTON INT'L A
Canada | Alberta | EDMONTON NAMAO A | EDMONTON NAMAO A, AB, Canada | 53.67N | 113.47W | 688 | -7.00 (NAM) | 82-01 | 711210 | -33.2 |  | -44.9 | 34.7 | 27.4 | 28.9 | 29.4 | 29 | 28.5667 |  | 25.1 | 26.8 | 27.1 | 26 | 26.3333 |  |  | CanadaAlbertaEDMONTON NAMAO A
Canada | Alberta | EDSON A | EDSON A, AB, Canada | 53.60N | 116.48W | 925 | -7.00 (NAM) | 82-06 | 718810 | -38.2 |  | -51.3 | 33.8 | 27 | 29 | 28.7 | 28 | 28.2333 |  | 24.2 | 26.6 | 26.5 | 26 | 25.7667 |  |  | CanadaAlbertaEDSON A
Canada | Alberta | ELK ISLAND NAT PARK | ELK ISLAND NAT PARK, AB, Canada | 53.68N | 112.87W | 716 | -7.00 (NAM) | 94-06 | 712380 | -37.7 |  | -47.8 | 37.4 | 28.5 | 31.7 | 30.4 | 30 | 30.2 |  | 26.1 | 28.2 | 27.9 | 27 | 27.4 |  |  | CanadaAlbertaELK ISLAND NAT PARK
Canada | Alberta | ESTHER 1 | ESTHER 1, AB, Canada | 51.67N | 110.21W | 707 | -7.00 (NAM) | 94-06 | 712400 | -35.6 |  | -45.9 | 39.8 | 30.2 | 34.4 | 34.5 | 33 | 33.0333 |  | 27.7 | 31.7 | 32.1 | 31 | 30.5 |  |  | CanadaAlbertaESTHER 1
Canada | Alberta | FORT CHIPEWYAN A | FORT CHIPEWYAN A, AB, Canada | 58.77N | 111.12W | 232 | -7.00 (NAM) | 93-06 | 719330 | -43.9 |  | -48.8 | 36.1 | 28.9 | 30.1 | 28.9 | 29 | 29.3 |  | 26.1 | 27.9 | 26.1 | 27 | 26.7 |  |  | CanadaAlbertaFORT CHIPEWYAN A
Canada | Alberta | FORT MCMURRAY A | FORT MCMURRAY A, AB, Canada | 56.65N | 111.22W | 369 | -7.00 (NAM) | 82-06 | 719320 | -39.9 |  | -47.2 | 37.7 | 29.4 | 31.2 | 31.9 | 31 | 30.8333 |  | 27 | 28.8 | 28.7 | 28 | 28.1667 |  |  | CanadaAlbertaFORT MCMURRAY A
Canada | Alberta | GARDEN RIVER | GARDEN RIVER, AB, Canada | 58.71N | 113.87W | 241 | -7.00 (NAM) | 94-06 | 712530 | -43 |  | -46.5 | 35.4 | 30.5 | 30.6 | 30.2 | 30 | 30.4333 |  | 27.7 | 28.6 | 26.9 | 28 | 27.7333 |  |  | CanadaAlbertaGARDEN RIVER
Canada | Alberta | GRANDE PRAIRIE A | GRANDE PRAIRIE A, AB, Canada | 55.18N | 118.88W | 669 | -7.00 (NAM) | 82-06 | 719400 | -40.2 |  | -52.2 | 34.5 | 28.1 | 29.9 | 29.9 | 29 | 29.3 |  | 25.1 | 27.3 | 27.2 | 27 | 26.5333 |  |  | CanadaAlbertaGRANDE PRAIRIE A
Canada | Alberta | HIGH LEVEL A | HIGH LEVEL A, AB, Canada | 58.62N | 117.16W | 338 | -7.00 (NAM) | 82-06 | 710660 | -43.1 |  | -51.4 | 33.9 | 28.4 | 30.1 | 29.6 | 29 | 29.3667 |  | 26.3 | 27.8 | 26.9 | 27 | 27 |  |  | CanadaAlbertaHIGH LEVEL A
Canada | Alberta | HIGHVALE | HIGHVALE, AB, Canada | 53.45N | 114.47W | 747 | -7.00 (NAM) | 94-06 | 712410 | -33.5 |  | -43.1 | 36 | 28.4 | 30.8 | 30.1 | 30 | 29.7667 |  | 25.3 | 27.8 | 27.1 | 27 | 26.7333 |  |  | CanadaAlbertaHIGHVALE
Canada | Alberta | JASPER | JASPER, AB, Canada | 52.88N | 118.07W | 1062 | -7.00 (NAM) | 82-92 | 718880 | -35.1 |  | -47.4 | 32.9 | 27.5 | 29.8 | 28.8 | 29 | 28.7 |  | 24.9 | 27.8 | 26.8 | 27 | 26.5 |  |  | CanadaAlbertaJASPER
Canada | Alberta | JASPER WARDEN | JASPER WARDEN, AB, Canada | 52.93N | 118.03W | 1020 | -7.00 (NAM) | 94-06 | 714860 | -36.2 |  | -48.9 | 37.5 | 28.5 | 32.7 | 31.6 | 31 | 30.9333 |  | 25.6 | 29.8 | 29 | 28 | 28.1333 |  |  | CanadaAlbertaJASPER WARDEN
Canada | Alberta | LAC LA BICHE (AUT) | LAC LA BICHE (AUT), AB, Canada | 54.77N | 112.02W | 567 | -7.00 (NAM) | 94-04 | 729310 | -38.4 |  | -48.3 | 35.2 | 28.7 | 29.7 | 30.1 | 30 | 29.5 |  | 25.9 | 27.2 | 27.3 | 27 | 26.8 |  |  | CanadaAlbertaLAC LA BICHE (AUT)
Canada | Alberta | LACOMBE CDA 2 | LACOMBE CDA 2, AB, Canada | 52.45N | 113.76W | 860 | -7.00 (NAM) | 94-06 | 712420 | -36.6 |  | -49 | 36.6 | 28.2 | 31.1 | 31.1 | 30 | 30.1333 |  | 25.4 | 28.3 | 27.9 | 27 | 27.2 |  |  | CanadaAlbertaLACOMBE CDA 2
Canada | Alberta | LETHBRIDGE A | LETHBRIDGE A, AB, Canada | 49.63N | 112.80W | 929 | -7.00 (NAM) | 82-06 | 718740 | -34.3 |  | -44.6 | 39.7 | 30.9 | 33.7 | 34.4 | 33 | 33 |  | 27.9 | 31.3 | 31.5 | 30 | 30.2333 |  |  | CanadaAlbertaLETHBRIDGE A
Canada | Alberta | LETHBRIDGE CDA | LETHBRIDGE CDA, AB, Canada | 49.70N | 112.78W | 921 | -7.00 (NAM) | 94-06 | 712430 | -31.9 |  | -43.7 | 39.6 | 30.6 | 34.2 | 34.3 | 33 | 33.0333 |  | 27.2 | 31.8 | 32.1 | 30 | 30.3667 |  |  | CanadaAlbertaLETHBRIDGE CDA
Canada | Alberta | LLOYDMINSTER A | LLOYDMINSTER A, AB, Canada | 53.31N | 110.07W | 668 | -7.00 (NAM) | 82-06 | 718710 | -36.2 |  | -46.1 | 38.5 | 29.3 | 30.7 | 31.7 | 31 | 30.5667 |  | 26.3 | 27.7 | 28.6 | 28 | 27.5333 |  |  | CanadaAlbertaLLOYDMINSTER A
Canada | Alberta | MEDICINE HAT A | MEDICINE HAT A, AB, Canada | 50.02N | 110.72W | 717 | -7.00 (NAM) | 82-06 | 718720 | -34.3 |  | -44 | 40.2 | 32.6 | 34.5 | 35.6 | 34 | 34.2333 |  | 29.6 | 32.4 | 32.6 | 32 | 31.5333 |  |  | CanadaAlbertaMEDICINE HAT A
Canada | Alberta | MILDRED LAKE | MILDRED LAKE, AB, Canada | 57.04N | 111.56W | 310 | -7.00 (NAM) | 94-06 | 712550 | -37.5 |  | -45 | 37.7 | 30.6 | 31.5 | 31.9 | 31 | 31.3333 |  | 27.8 | 29.4 | 28.5 | 29 | 28.5667 |  |  | CanadaAlbertaMILDRED LAKE
Canada | Alberta | MILK RIVER | MILK RIVER, AB, Canada | 49.13N | 112.05W | 1050 | -7.00 (NAM) | 94-06 | 712440 | -34.8 |  | -44.1 | 39.2 | 29.9 | 34.2 | 34 | 33 | 32.7 |  | 26.8 | 32 | 31.9 | 30 | 30.2333 |  |  | CanadaAlbertaMILK RIVER
Canada | Alberta | NAKISKA RIDGETOP | NAKISKA RIDGETOP, AB, Canada | 50.94N | 115.19W | 2543 | -7.00 (NAM) | 94-06 | 712450 | -32.8 |  | -40.7 | 25.8 | 17.2 | 21.7 | 19.7 | 20 | 19.5333 |  | 14 | 19.2 | 17.5 | 17 | 16.9 |  |  | CanadaAlbertaNAKISKA RIDGETOP
Canada | Alberta | ONEFOUR CDA | ONEFOUR CDA, AB, Canada | 49.12N | 110.47W | 935 | -7.00 (NAM) | 94-06 | 711160 | -32.2 |  | -41.8 | 40.3 | 31.8 | 35.5 | 35.7 | 34 | 34.3333 |  | 28.3 | 33.7 | 33.1 | 32 | 31.7 |  |  | CanadaAlbertaONEFOUR CDA
Canada | Alberta | PEACE RIVER A | PEACE RIVER A, AB, Canada | 56.23N | 117.45W | 571 | -7.00 (NAM) | 82-06 | 710680 | -38.7 |  | -50.1 | 35.1 | 28.2 | 29.6 | 30.1 | 29 | 29.3 |  | 25.4 | 27.1 | 27.2 | 27 | 26.5667 |  |  | CanadaAlbertaPEACE RIVER A
Canada | Alberta | PINCHER CREEK (AUT) | PINCHER CREEK (AUT), AB, Canada | 49.52N | 113.98W | 1190 | -7.00 (NAM) | 94-06 | 718750 | -32.8 |  | -41.8 | 37.3 | 27.9 | 32.4 | 31.9 | 31 | 30.7333 |  | 24.7 | 30 | 29.7 | 28 | 28.1333 |  |  | CanadaAlbertaPINCHER CREEK (AUT)
Canada | Alberta | RED DEER A | RED DEER A, AB, Canada | 52.18N | 113.89W | 905 | -7.00 (NAM) | 82-06 | 718780 | -36.6 |  | -47.4 | 35.5 | 27.7 | 30.3 | 30.3 | 29 | 29.4333 |  | 25.3 | 27.6 | 27.8 | 27 | 26.9 |  |  | CanadaAlbertaRED DEER A
Canada | Alberta | RED EARTH | RED EARTH, AB, Canada | 56.55N | 115.28W | 546 | -7.00 (NAM) | 94-06 | 712460 | -39.7 |  | -48.9 | 35.3 | 28.7 | 30.2 | 30.6 | 30 | 29.8333 |  | 26.4 | 28.1 | 27.4 | 27 | 27.3 |  |  | CanadaAlbertaRED EARTH
Canada | Alberta | ROCKY MTN HOUSE (AUT) | ROCKY MTN HOUSE (AUT), AB, Canada | 52.42N | 114.91W | 988 | -7.00 (NAM) | 82-06 | 719280 | -38.5 |  | -48.9 | 33.8 | 26.5 | 29.2 | 28.7 | 28 | 28.1333 |  | 24 | 26.8 | 26.3 | 26 | 25.7 |  |  | CanadaAlbertaROCKY MTN HOUSE (AUT)
Canada | Alberta | SLAVE LAKE A | SLAVE LAKE A, AB, Canada | 55.28N | 114.78W | 583 | -7.00 (NAM) | 82-06 | 710690 | -37.3 |  | -48.4 | 35 | 26.8 | 28.8 | 29.7 | 28 | 28.4333 |  | 24 | 26.1 | 26.2 | 25 | 25.4333 |  |  | CanadaAlbertaSLAVE LAKE A
Canada | Alberta | SPRINGBANK A | SPRINGBANK A, AB, Canada | 51.10N | 114.37W | 1201 | -7.00 (NAM) | 88-02 | 718600 | -36.1 |  | -47.5 | 33.7 | 25.5 | 28.5 | 29.5 | 28 | 27.8333 |  | 23.2 | 26.3 | 27.4 | 26 | 25.6333 |  |  | CanadaAlbertaSPRINGBANK A
Canada | Alberta | STAVELY AAFC | STAVELY AAFC, AB, Canada | 50.18N | 113.88W | 1364 | -7.00 (NAM) | 96-06 | 715550 | -28.1 |  | -38.5 | 34.2 | 25.2 | 30 | 29.8 | 28 | 28.3333 |  | 22.4 | 27.6 | 27.7 | 26 | 25.9 |  |  | CanadaAlbertaSTAVELY AAFC
Canada | Alberta | SUNDRE A | SUNDRE A, AB, Canada | 51.78N | 114.68W | 1114 | -7.00 (NAM) | 94-06 | 712480 | -38.6 |  | -50.7 | 35.1 | 28.2 | 30.3 | 30.5 | 30 | 29.6667 |  | 24.2 | 27.8 | 27.9 | 27 | 26.6333 |  |  | CanadaAlbertaSUNDRE A
Canada | Alberta | THREE HILLS | THREE HILLS, AB, Canada | 51.83N | 113.21W | 907 | -7.00 (NAM) | 94-06 | 712490 | -32.9 |  | -42.9 | 38.2 | 28.7 | 32.3 | 32.5 | 31 | 31.1667 |  | 25.7 | 29.4 | 29.8 | 28 | 28.3 |  |  | CanadaAlbertaTHREE HILLS
Canada | Alberta | VAUXHALL CDA CS | VAUXHALL CDA CS, AB, Canada | 50.05N | 112.13W | 779 | -7.00 (NAM) | 94-06 | 712510 | -35 |  | -47.6 | 39.5 | 30.4 | 33.8 | 34.5 | 33 | 32.9 |  | 27.5 | 31.8 | 32.1 | 30 | 30.4667 |  |  | CanadaAlbertaVAUXHALL CDA CS
Canada | Alberta | VEGREVILLE | VEGREVILLE, AB, Canada | 53.51N | 112.10W | 639 | -7.00 (NAM) | 94-06 | 714580 | -38.6 |  | -51 | 36.7 | 29.5 | 31.7 | 30.5 | 31 | 30.5667 |  | 26 | 28 | 28.1 | 27 | 27.3667 |  |  | CanadaAlbertaVEGREVILLE
Canada | Alberta | WAINWRIGHT CFB AIRFIELD 21 | WAINWRIGHT CFB AIRFIELD 21, AB, Canada | 52.83N | 111.10W | 686 | -7.00 (NAM) | 95-06 | 711180 | -36 |  | -46 | 40.7 | 30.3 | 33.5 | 33.7 | 33 | 32.5 |  | 27.2 | 29.9 | 30 | 29 | 29.0333 |  |  | CanadaAlbertaWAINWRIGHT CFB AIRFIELD 21
Canada | Alberta | WATERTON PARK GATE | WATERTON PARK GATE, AB, Canada | 49.13N | 113.81W | 1289 | -7.00 (NAM) | 94-06 | 711540 | -36.6 |  | -48.8 | 36 | 28.1 | 32 | 31.2 | 30 | 30.4333 |  | 24.6 | 29.6 | 29.3 | 28 | 27.8333 |  |  | CanadaAlbertaWATERTON PARK GATE
Canada | Alberta | WHITECOURT A | WHITECOURT A, AB, Canada | 54.14N | 115.79W | 782 | -7.00 (NAM) | 82-98 | 719300 | -36 |  | -48.7 | 32.6 | 26.7 | 28.3 | 28.5 | 28 | 27.8333 |  | 24.1 | 26.2 | 26.1 | 25 | 25.4667 |  |  | CanadaAlbertaWHITECOURT A
Canada | British Columbia | ABBOTSFORD A | ABBOTSFORD A, BC, Canada | 49.03N | 122.36W | 59 | -8.00 (NAP) | 82-06 | 711080 | -10.7 |  | -20.4 | 38.3 | 30.7 | 32.6 | 31.2 | 32 | 31.5 |  | 27.5 | 29.6 | 29.2 | 29 | 28.7667 |  |  | CanadaBritish ColumbiaABBOTSFORD A
Canada | British Columbia | AGASSIZ CS | AGASSIZ CS, BC, Canada | 49.25N | 121.77W | 15 | -8.00 (NAP) | 94-06 | 711130 | -8.5 |  | -16.4 | 38.8 | 31.2 | 33.5 | 31.2 | 32 | 31.9667 |  | 27.9 | 30.6 | 29.3 | 29 | 29.2667 |  |  | CanadaBritish ColumbiaAGASSIZ CS
Canada | British Columbia | ALERT BAY | ALERT BAY, BC, Canada | 50.58N | 126.93W | 59 | -8.00 (NAP) | 82-94 | 711100 | -6.7 |  | -15.6 | 35 | 19.9 | 22.5 | 22.4 | 22 | 21.6 |  | 17.2 | 19.3 | 19.7 | 19 | 18.7333 |  |  | CanadaBritish ColumbiaALERT BAY
Canada | British Columbia | AMPHITRITE POINT | AMPHITRITE POINT, BC, Canada | 48.92N | 125.54W | 27 | -8.00 (NAP) | 82-99 | 711120 | -3.9 |  | -10.5 | 25.7 | 19.9 | 20.2 | 20.7 | 20 | 20.2667 |  | 16.6 | 17.9 | 18.6 | 18 | 17.7 |  |  | CanadaBritish ColumbiaAMPHITRITE POINT
Canada | British Columbia | BALLENAS ISLAND | BALLENAS ISLAND, BC, Canada | 49.35N | 124.16W | 13 | -8.00 (NAP) | 94-06 | 717690 | -1.9 |  | -6.9 | 32.6 | 25 | 26.1 | 25.4 | 26 | 25.5 |  | 22.8 | 24.2 | 23.7 | 24 | 23.5667 |  |  | CanadaBritish ColumbiaBALLENAS ISLAND
Canada | British Columbia | BLUE RIVER CS | BLUE RIVER CS, BC, Canada | 52.13N | 119.29W | 683 | -8.00 (NAP) | 93-06 | 718830 | -31.6 |  | -47.2 | 38.8 | 30.8 | 33.7 | 33.1 | 33 | 32.5333 |  | 27.6 | 31.2 | 30.4 | 30 | 29.7333 |  |  | CanadaBritish ColumbiaBLUE RIVER CS
Canada | British Columbia | BONILLA ISLAND (AUT) | BONILLA ISLAND (AUT), BC, Canada | 53.50N | 130.63W | 15 | -8.00 (NAP) | 94-06 | 714840 | -6.9 |  | -14.5 | 28.3 | 17.6 | 16.7 | 17.4 | 17 | 17.2333 |  | 14.3 | 15.6 | 16.4 | 15 | 15.4333 |  |  | CanadaBritish ColumbiaBONILLA ISLAND (AUT)
Canada | British Columbia | BURNS LAKE DECKER LAKE | BURNS LAKE DECKER LAKE, BC, Canada | 54.38N | 125.96W | 713 | -8.00 (NAP) | 94-06 | 719520 | -36.4 |  | -46.5 | 36.1 | 31.6 | 30.9 | 29.3 | 31 | 30.6 |  | 26.9 | 27.4 | 26.5 | 27 | 26.9333 |  |  | CanadaBritish ColumbiaBURNS LAKE DECKER LAKE
Canada | British Columbia | CAPE SCOTT | CAPE SCOTT, BC, Canada | 50.78N | 128.43W | 72 | -8.00 (NAP) | 82-01 | 711110 | -3.6 |  | -11.8 | 25.6 | 15.9 | 17.2 | 17.8 | 17 | 16.9667 |  | 14.8 | 16.4 | 16.8 | 16 | 16 |  |  | CanadaBritish ColumbiaCAPE SCOTT
Canada | British Columbia | CAPE ST JAMES CS | CAPE ST JAMES CS, BC, Canada | 51.94N | 131.02W | 92 | -8.00 (NAP) | 82-06 | 711070 | -5.7 |  | -14.4 | 27.1 | 20.4 | 20.1 | 21.1 | 21 | 20.5333 |  | 16.7 | 17.8 | 19.1 | 18 | 17.8667 |  |  | CanadaBritish ColumbiaCAPE ST JAMES CS
Canada | British Columbia | CATHEDRAL POINT (AUT) | CATHEDRAL POINT (AUT), BC, Canada | 52.19N | 127.47W | 31 | -8.00 (NAP) | 94-06 | 714820 | -8.2 |  | -16.9 | 32.7 | 25.7 | 25.3 | 24.5 | 25 | 25.1667 |  | 21.7 | 23.1 | 22.1 | 22 | 22.3 |  |  | CanadaBritish ColumbiaCATHEDRAL POINT (AUT)
Canada | British Columbia | CLINTON (AUT) | CLINTON (AUT), BC, Canada | 51.14N | 121.50W | 1057 | -8.00 (NAP) | 94-06 | 714740 | -30.6 |  | -42.2 | 36.9 | 28.6 | 32.6 | 31.4 | 31 | 30.8667 |  | 25.8 | 29.6 | 28.8 | 28 | 28.0667 |  |  | CanadaBritish ColumbiaCLINTON (AUT)
Canada | British Columbia | COMOX A | COMOX A, BC, Canada | 49.72N | 124.90W | 26 | -8.00 (NAP) | 82-06 | 718930 | -7.2 |  | -14.5 | 34.5 | 28.8 | 29.5 | 28.4 | 29 | 28.9 |  | 25.1 | 26.7 | 26.1 | 26 | 25.9667 |  |  | CanadaBritish ColumbiaCOMOX A
Canada | British Columbia | CRANBROOK A | CRANBROOK A, BC, Canada | 49.61N | 115.78W | 940 | -7.00 (NAM) | 82-06 | 718800 | -27.8 |  | -40 | 39 | 31.1 | 34.3 | 33 | 33 | 32.8 |  | 28.1 | 32 | 31.1 | 30 | 30.4 |  |  | CanadaBritish ColumbiaCRANBROOK A
Canada | British Columbia | CRESTON CAMPBELL SCIENTIFIC | CRESTON CAMPBELL SCIENTIFIC, BC, Canada | 49.08N | 116.50W | 646 | -8.00 (NAP) | 94-06 | 717700 | -16.3 |  | -26.7 | 39.2 | 30.8 | 35.2 | 34.8 | 34 | 33.6 |  | 28.1 | 33 | 32.4 | 31 | 31.1667 |  |  | CanadaBritish ColumbiaCRESTON CAMPBELL SCIENTIFIC
Canada | British Columbia | CUMSHEWA ISLAND | CUMSHEWA ISLAND, BC, Canada | 53.03N | 131.60W | 17 | -8.00 (NAP) | 94-06 | 717710 | -5.6 |  | -14.6 | 24.4 | 20.6 | 19.8 | 20.2 | 20 | 20.2 |  | 16.9 | 17.8 | 18.5 | 18 | 17.7333 |  |  | CanadaBritish ColumbiaCUMSHEWA ISLAND
Canada | British Columbia | DEASE LAKE | DEASE LAKE, BC, Canada | 58.43N | 130.01W | 807 | -8.00 (NAP) | 83-93 | 719580 | -41.3 |  | -48.6 | 35 | 25.5 | 26.3 | 27.1 | 26 | 26.3 |  | 23.1 | 24.3 | 23.2 | 24 | 23.5333 |  |  | CanadaBritish ColumbiaDEASE LAKE
Canada | British Columbia | DISCOVERY ISLAND | DISCOVERY ISLAND, BC, Canada | 48.42N | 123.23W | 15 | -8.00 (NAP) | 97-06 | 710310 | -1.8 |  | -10.6 | 33.3 | 25.8 | 26.2 | 25.3 | 26 | 25.7667 |  | 22.4 | 22.7 | 22.2 | 22 | 22.4333 |  |  | CanadaBritish ColumbiaDISCOVERY ISLAND
Canada | British Columbia | ENTRANCE ISLAND CS | ENTRANCE ISLAND CS, BC, Canada | 49.22N | 123.80W | 5 | -8.00 (NAP) | 94-06 | 717720 | -2.6 |  | -8.5 | 34.6 | 25.4 | 26.1 | 26.7 | 26 | 26.0667 |  | 22.2 | 23.7 | 23.7 | 23 | 23.2 |  |  | CanadaBritish ColumbiaENTRANCE ISLAND CS
Canada | British Columbia | ESQUIMALT HARBOUR | ESQUIMALT HARBOUR, BC, Canada | 48.43N | 123.44W | 3 | -8.00 (NAP) | 94-06 | 717980 | -3.6 |  | -8.8 | 31.6 | 24.6 | 24.1 | 24.4 | 24 | 24.3667 |  | 21 | 22.2 | 21.9 | 22 | 21.7 |  |  | CanadaBritish ColumbiaESQUIMALT HARBOUR
Canada | British Columbia | ESTEVAN POINT CS | ESTEVAN POINT CS, BC, Canada | 49.38N | 126.54W | 7 | -8.00 (NAP) | 94-06 | 718940 | -3.7 |  | -8.9 | 27.4 | 22.5 | 22 | 21.5 | 22 | 22 |  | 18.2 | 19.9 | 19.9 | 19 | 19.3333 |  |  | CanadaBritish ColumbiaESTEVAN POINT CS
Canada | British Columbia | FORT NELSON A | FORT NELSON A, BC, Canada | 58.84N | 122.60W | 382 | -8.00 (NAP) | 82-06 | 719450 | -39.5 |  | -48.6 | 35.4 | 28.8 | 30.6 | 30.1 | 30 | 29.8333 |  | 26.7 | 27.8 | 27.3 | 27 | 27.2667 |  |  | CanadaBritish ColumbiaFORT NELSON A
Canada | British Columbia | FORT ST JOHN A | FORT ST JOHN A, BC, Canada | 56.24N | 120.74W | 695 | -7.00 (NAD) | 82-06 | 719430 | -36.2 |  | -45.7 | 33.2 | 27 | 28.8 | 28.4 | 28 | 28.0667 |  | 24.2 | 26.1 | 25.9 | 25 | 25.4 |  |  | CanadaBritish ColumbiaFORT ST JOHN A
Canada | British Columbia | GREY ISLET (AUT) | GREY ISLET (AUT), BC, Canada | 54.58N | 130.70W | 8 | -8.00 (NAP) | 94-06 | 714760 | -7.3 |  | -13.3 | 26.8 | 21.2 | 20 | 21.1 | 21 | 20.7667 |  | 17.8 | 18.2 | 18.9 | 18 | 18.3 |  |  | CanadaBritish ColumbiaGREY ISLET (AUT)
Canada | British Columbia | HERBERT ISLAND (AUT) | HERBERT ISLAND (AUT), BC, Canada | 50.94N | 127.64W | 17 | -8.00 (NAP) | 94-06 | 714850 | -2.5 |  | -8 | 26.9 | 16.2 | 16.7 | 17.8 | 17 | 16.9 |  | 14.8 | 15.7 | 16.3 | 16 | 15.6 |  |  | CanadaBritish ColumbiaHERBERT ISLAND (AUT)
Canada | British Columbia | HOLLAND ROCK | HOLLAND ROCK, BC, Canada | 54.17N | 130.36W | 5 | -8.00 (NAP) | 94-06 | 712190 | -7.4 |  | -15.3 | 29.1 | 19 | 17.1 | 19.4 | 19 | 18.5 |  | 15.1 | 15.7 | 17 | 16 | 15.9333 |  |  | CanadaBritish ColumbiaHOLLAND ROCK
Canada | British Columbia | HOPE | HOPE, BC, Canada | 49.37N | 121.48W | 39 | -8.00 (NAP) | 82-05 | 711140 | -12.9 |  | -25.1 | 39.6 | 31.1 | 32.9 | 32.1 | 32 | 32.0333 |  | 28.1 | 30.3 | 29.6 | 29 | 29.3333 |  |  | CanadaBritish ColumbiaHOPE
Canada | British Columbia | HOWE SOUND - PAM ROCKS | HOWE SOUND - PAM ROCKS, BC, Canada | 49.49N | 123.30W | 5 | -8.00 (NAP) | 94-06 | 712110 | -3.8 |  | -10 | 34 | 25.5 | 27.7 | 28 | 27 | 27.0667 |  | 23 | 25.3 | 24.7 | 24 | 24.3333 |  |  | CanadaBritish ColumbiaHOWE SOUND - PAM ROCKS
Canada | British Columbia | KAMLOOPS A | KAMLOOPS A, BC, Canada | 50.70N | 120.44W | 345 | -8.00 (NAP) | 82-06 | 718870 | -22.5 |  | -36 | 40.8 | 34.4 | 36.7 | 35.2 | 35 | 35.4333 |  | 31.2 | 34.3 | 32.9 | 33 | 32.8 |  |  | CanadaBritish ColumbiaKAMLOOPS A
Canada | British Columbia | KELOWNA A | KELOWNA A, BC, Canada | 49.96N | 119.38W | 430 | -8.00 (NAP) | 82-04 | 712030 | -22.5 |  | -38 | 40.4 | 33.6 | 36 | 34.4 | 35 | 34.6667 |  | 30.1 | 33.3 | 32.2 | 32 | 31.8667 |  |  | CanadaBritish ColumbiaKELOWNA A
Canada | British Columbia | KINDAKUN ROCKS (AUT) | KINDAKUN ROCKS (AUT), BC, Canada | 53.32N | 132.77W | 14 | -8.00 (NAP) | 94-06 | 714720 | -5.2 |  | -10.1 | 31.7 | 17.9 | 16.7 | 18.4 | 18 | 17.6667 |  | 14.2 | 15.4 | 17 | 16 | 15.5333 |  |  | CanadaBritish ColumbiaKINDAKUN ROCKS (AUT)
Canada | British Columbia | LANGARA | LANGARA, BC, Canada | 54.26N | 133.06W | 41 | -8.00 (NAP) | 82-01 | 718990 | -5.6 |  | -14.7 | 25.1 | 15.2 | 16.1 | 17.7 | 16 | 16.3333 |  | 13.9 | 15.1 | 16.2 | 15 | 15.0667 |  |  | CanadaBritish ColumbiaLANGARA
Canada | British Columbia | LILLOOET | LILLOOET, BC, Canada | 50.68N | 121.93W | 235 | -8.00 (NAP) | 97-06 | 719990 | -17.8 |  | -32.4 | 43.7 | 35.1 | 38.6 | 36.7 | 37 | 36.8 |  | 32.2 | 35.7 | 34.4 | 34 | 34.1 |  |  | CanadaBritish ColumbiaLILLOOET
Canada | British Columbia | LUCY ISLAND LIGHTSTATION | LUCY ISLAND LIGHTSTATION, BC, Canada | 54.30N | 130.61W | 26 | -8.00 (NAP) | 94-06 | 712200 | -7.8 |  | -14.3 | 28.8 | 20.9 | 18.6 | 20.1 | 20 | 19.8667 |  | 16.6 | 17 | 17.9 | 17 | 17.1667 |  |  | CanadaBritish ColumbiaLUCY ISLAND LIGHTSTATION
Canada | British Columbia | LYTTON | LYTTON, BC, Canada | 50.22N | 121.58W | 225 | -8.00 (NAP) | 82-06 | 718910 | -19 |  | -31.9 | 42.9 | 35.5 | 38.5 | 36.8 | 37 | 36.9333 |  | 32 | 35.3 | 34.2 | 34 | 33.8333 |  |  | CanadaBritish ColumbiaLYTTON
Canada | British Columbia | MACKENZIE A | MACKENZIE A, BC, Canada | 55.31N | 123.14W | 690 | -7.00 (NAD) | 94-06 | 719440 | -35.9 |  | -53 | 33.8 | 28.5 | 30.8 | 28.8 | 29 | 29.3667 |  | 26 | 27.5 | 26.5 | 27 | 26.6667 |  |  | CanadaBritish ColumbiaMACKENZIE A
Canada | British Columbia | MALAHAT | MALAHAT, BC, Canada | 48.57N | 123.53W | 366 | -8.00 (NAP) | 94-06 | 717740 | -7.1 |  | -15.2 | 36.2 | 29.1 | 31.5 | 28.4 | 30 | 29.6667 |  | 25.4 | 28.4 | 26.6 | 27 | 26.8 |  |  | CanadaBritish ColumbiaMALAHAT
Canada | British Columbia | NAKUSP CS | NAKUSP CS, BC, Canada | 50.27N | 117.81W | 512 | -8.00 (NAP) | 94-06 | 712160 | -15.2 |  | -25.3 | 41.6 | 30.7 | 35 | 33.6 | 33 | 33.1 |  | 27.8 | 31.9 | 30.5 | 30 | 30.0667 |  |  | CanadaBritish ColumbiaNAKUSP CS
Canada | British Columbia | NELSON CS | NELSON CS, BC, Canada | 49.49N | 117.31W | 535 | -8.00 (NAP) | 94-06 | 717760 | -13.9 |  | -23.8 | 39.5 | 30.3 | 35.2 | 34 | 33 | 33.1667 |  | 27.3 | 32.2 | 31.6 | 30 | 30.3667 |  |  | CanadaBritish ColumbiaNELSON CS
Canada | British Columbia | OSOYOOS CS | OSOYOOS CS, BC, Canada | 49.03N | 119.44W | 283 | -8.00 (NAP) | 94-06 | 712150 | -15 |  | -24.7 | 43.1 | 36.4 | 38.5 | 37.4 | 37 | 37.4333 |  | 32.5 | 35.9 | 35 | 34 | 34.4667 |  |  | CanadaBritish ColumbiaOSOYOOS CS
Canada | British Columbia | PEMBERTON AIRPORT CS | PEMBERTON AIRPORT CS, BC, Canada | 50.30N | 122.74W | 204 | -8.00 (NAP) | 94-06 | 717770 | -16.6 |  | -25.3 | 42.4 | 34.4 | 37.1 | 34.4 | 35 | 35.3 |  | 30.8 | 34.3 | 32.6 | 33 | 32.5667 |  |  | CanadaBritish ColumbiaPEMBERTON AIRPORT CS
Canada | British Columbia | PENTICTON A | PENTICTON A, BC, Canada | 49.46N | 119.60W | 344 | -8.00 (NAP) | 82-06 | 718890 | -15.9 |  | -25.7 | 39.3 | 33.2 | 35.5 | 34.2 | 34 | 34.3 |  | 30 | 33.1 | 31.8 | 32 | 31.6333 |  |  | CanadaBritish ColumbiaPENTICTON A
Canada | British Columbia | PITT MEADOWS CS | PITT MEADOWS CS, BC, Canada | 49.21N | 122.69W | 5 | -8.00 (NAP) | 94-06 | 717750 | -10.2 |  | -18.7 | 40.1 | 31.2 | 34.2 | 31.7 | 32 | 32.3667 |  | 28 | 31.4 | 29.8 | 30 | 29.7333 |  |  | CanadaBritish ColumbiaPITT MEADOWS CS
Canada | British Columbia | POINT ATKINSON | POINT ATKINSON, BC, Canada | 49.33N | 123.26W | 35 | -8.00 (NAP) | 96-06 | 710370 | N/A |  | N/A | N/A | 26.1 | 27.7 | 26 | 27 | 26.6 |  | 23.3 | 25.4 | 24.5 | 24 | 24.4 |  |  | CanadaBritish ColumbiaPOINT ATKINSON
Canada | British Columbia | PORT ALBERNI (AUT) | PORT ALBERNI (AUT), BC, Canada | 49.32N | 124.93W | 76 | -8.00 (NAP) | 94-06 | 714750 | -8.8 |  | -16.8 | 40.3 | 32.7 | 35.1 | 33.1 | 34 | 33.6333 |  | 28.6 | 31.9 | 30.8 | 30 | 30.4333 |  |  | CanadaBritish ColumbiaPORT ALBERNI (AUT)
Canada | British Columbia | PORT HARDY A | PORT HARDY A, BC, Canada | 50.68N | 127.37W | 22 | -8.00 (NAP) | 82-06 | 711090 | -6.9 |  | -13.7 | 30.5 | 21.9 | 22.4 | 22.1 | 22 | 22.1333 |  | 18.2 | 19.6 | 19.8 | 19 | 19.2 |  |  | CanadaBritish ColumbiaPORT HARDY A
Canada | British Columbia | PRINCE GEORGE A | PRINCE GEORGE A, BC, Canada | 53.89N | 122.68W | 691 | -8.00 (NAP) | 82-06 | 718960 | -34.4 |  | -48.3 | 35 | 28.6 | 30.5 | 29.6 | 30 | 29.5667 |  | 25.9 | 27.7 | 27.2 | 27 | 26.9333 |  |  | CanadaBritish ColumbiaPRINCE GEORGE A
Canada | British Columbia | PRINCE RUPERT A | PRINCE RUPERT A, BC, Canada | 54.29N | 130.44W | 35 | -8.00 (NAP) | 82-04 | 718980 | -14.4 |  | -22.8 | 31.6 | 21.4 | 20.5 | 21.9 | 21 | 21.2667 |  | 17.1 | 18.1 | 18.9 | 18 | 18.0333 |  |  | CanadaBritish ColumbiaPRINCE RUPERT A
Canada | British Columbia | PRINCETON CS | PRINCETON CS, BC, Canada | 49.47N | 120.51W | 700 | -8.00 (NAP) | 94-06 | 710320 | -26.8 |  | -41.2 | 41.6 | 32.9 | 36.6 | 35.7 | 35 | 35.0667 |  | 29.5 | 33.7 | 32.9 | 32 | 32.0333 |  |  | CanadaBritish ColumbiaPRINCETON CS
Canada | British Columbia | PUNTZI MOUNTAIN (AUT) | PUNTZI MOUNTAIN (AUT), BC, Canada | 52.11N | 124.14W | 910 | -8.00 (NAP) | 94-06 | 710500 | -39.5 |  | -56.9 | 36.9 | 29.2 | 32.6 | 31.1 | 31 | 30.9667 |  | 25.9 | 29.4 | 28.6 | 28 | 27.9667 |  |  | CanadaBritish ColumbiaPUNTZI MOUNTAIN (AUT)
Canada | British Columbia | QUESNEL A | QUESNEL A, BC, Canada | 53.03N | 122.51W | 545 | -8.00 (NAP) | 82-06 | 711030 | -32 |  | -45.4 | 37.6 | 30.5 | 32.7 | 30.9 | 31 | 31.3667 |  | 27.5 | 29.5 | 28.4 | 28 | 28.4667 |  |  | CanadaBritish ColumbiaQUESNEL A
Canada | British Columbia | REVELSTOKE A | REVELSTOKE A, BC, Canada | 50.96N | 118.18W | 445 | -8.00 (NAP) | 82-06 | 718820 | -20.6 |  | -32.2 | 38.7 | 31.2 | 34 | 32.3 | 33 | 32.5 |  | 28.2 | 30.7 | 29.4 | 29 | 29.4333 |  |  | CanadaBritish ColumbiaREVELSTOKE A
Canada | British Columbia | ROSE SPIT (AUT) | ROSE SPIT (AUT), BC, Canada | 54.16N | 131.66W | 7 | -8.00 (NAP) | 94-06 | 714770 | -6.4 |  | -11.2 | 24 | 17.6 | 17.1 | 18.3 | 18 | 17.6667 |  | 14.8 | 16.2 | 17.1 | 16 | 16.0333 |  |  | CanadaBritish ColumbiaROSE SPIT (AUT)
Canada | British Columbia | SALMON ARM CS | SALMON ARM CS, BC, Canada | 50.70N | 119.29W | 351 | -8.00 (NAP) | 94-06 | 712180 | -19.9 |  | -34.2 | 41 | 32.1 | 35.5 | 34.3 | 34 | 33.9667 |  | 29.4 | 33.1 | 31.4 | 31 | 31.3 |  |  | CanadaBritish ColumbiaSALMON ARM CS
Canada | British Columbia | SANDHEADS CS | SANDHEADS CS, BC, Canada | 49.11N | 123.30W | 0 | -8.00 (NAP) | 94-06 | 712090 | -5.5 |  | -11.2 | 27.6 | 22.5 | 24.3 | 23.3 | 23 | 23.3667 |  | 21 | 22.6 | 22 | 22 | 21.8667 |  |  | CanadaBritish ColumbiaSANDHEADS CS
Canada | British Columbia | SANDSPIT A | SANDSPIT A, BC, Canada | 53.25N | 131.81W | 6 | -8.00 (NAP) | 82-03 | 711010 | -6.8 |  | -14.7 | 27.3 | 20.1 | 21.9 | 22 | 21 | 21.3333 |  | 17.5 | 19.2 | 20.2 | 19 | 18.9667 |  |  | CanadaBritish ColumbiaSANDSPIT A
Canada | British Columbia | SARTINE ISLAND (AUT) | SARTINE ISLAND (AUT), BC, Canada | 50.82N | 128.91W | 112 | -8.00 (NAP) | 94-06 | 714780 | -2.8 |  | -7.9 | 28.5 | 18.6 | 16.1 | 17.1 | 17 | 17.2667 |  | 14.1 | 15.2 | 16.2 | 15 | 15.1667 |  |  | CanadaBritish ColumbiaSARTINE ISLAND (AUT)
Canada | British Columbia | SHERINGHAM POINT | SHERINGHAM POINT, BC, Canada | 48.38N | 123.92W | 22 | -8.00 (NAP) | 94-06 | 717800 | -3.3 |  | -11.1 | 33.3 | 25.3 | 25.7 | 24.4 | 25 | 25.1333 |  | 20.2 | 21.8 | 20.5 | 21 | 20.8333 |  |  | CanadaBritish ColumbiaSHERINGHAM POINT
Canada | British Columbia | SISTERS ISLAND | SISTERS ISLAND, BC, Canada | 49.49N | 124.43W | 20 | -8.00 (NAP) | 96-06 | 717810 | -2 |  | -6.5 | 30.5 | 24.4 | 25.4 | 24.7 | 25 | 24.8333 |  | 21.9 | 23.5 | 23.1 | 23 | 22.8333 |  |  | CanadaBritish ColumbiaSISTERS ISLAND
Canada | British Columbia | SMITHERS A | SMITHERS A, BC, Canada | 54.82N | 127.18W | 522 | -8.00 (NAP) | 82-06 | 719500 | -30.9 |  | -40.8 | 36.5 | 29.3 | 30.4 | 29.4 | 30 | 29.7 |  | 26.2 | 27.1 | 26.2 | 27 | 26.5 |  |  | CanadaBritish ColumbiaSMITHERS A
Canada | British Columbia | SOLANDER ISLAND (AUT) | SOLANDER ISLAND (AUT), BC, Canada | 50.11N | 127.94W | 99 | -8.00 (NAP) | 94-06 | 714790 | -1.9 |  | -9.8 | 30.5 | 22.1 | 16.9 | 19.1 | 19 | 19.3667 |  | 14.7 | 15.5 | 16.7 | 16 | 15.6333 |  |  | CanadaBritish ColumbiaSOLANDER ISLAND (AUT)
Canada | British Columbia | SPARWOOD CS | SPARWOOD CS, BC, Canada | 49.75N | 114.89W | 1138 | -7.00 (NAM) | 94-06 | 717820 | -31.2 |  | -40.3 | 36.9 | 28.1 | 32.4 | 32 | 31 | 30.8333 |  | 25.3 | 30.1 | 29.6 | 28 | 28.3333 |  |  | CanadaBritish ColumbiaSPARWOOD CS
Canada | British Columbia | SQUAMISH | SQUAMISH, BC, Canada | 49.78N | 123.16W | 52 | -8.00 (NAP) | 94-06 | 712070 | -8.7 |  | -15.6 | 37.9 | 31 | 32.7 | 30.4 | 31 | 31.3667 |  | 27.3 | 29.6 | 28.2 | 28 | 28.3667 |  |  | CanadaBritish ColumbiaSQUAMISH
Canada | British Columbia | SUMMERLAND CS | SUMMERLAND CS, BC, Canada | 49.56N | 119.64W | 454 | -8.00 (NAP) | 94-06 | 717680 | -16 |  | -24.9 | 39.7 | 32.1 | 36.2 | 34.7 | 34 | 34.3333 |  | 29.5 | 33.8 | 32.4 | 32 | 31.9 |  |  | CanadaBritish ColumbiaSUMMERLAND CS
Canada | British Columbia | TERRACE A | TERRACE A, BC, Canada | 54.47N | 128.58W | 217 | -8.00 (NAP) | 82-06 | 719510 | -19.5 |  | -28.5 | 36.8 | 30.2 | 31.2 | 29.9 | 30 | 30.4333 |  | 26.6 | 27.8 | 26.8 | 27 | 27.0667 |  |  | CanadaBritish ColumbiaTERRACE A
Canada | British Columbia | VANCOUVER HARBOUR CS | VANCOUVER HARBOUR CS, BC, Canada | 49.30N | 123.12W | 3 | -8.00 (NAP) | 94-06 | 712010 | -4.2 |  | -11.5 | 32.1 | 26.9 | 28.3 | 26.8 | 27 | 27.3333 |  | 24.1 | 25.9 | 25.3 | 25 | 25.1 |  |  | CanadaBritish ColumbiaVANCOUVER HARBOUR CS
Canada | British Columbia | VANCOUVER INT'L A | VANCOUVER INT'L A, BC, Canada | 49.20N | 123.18W | 4 | -8.00 (NAP) | 82-06 | 718920 | -9.1 |  | -17.2 | 32.2 | 25.9 | 27.4 | 26.5 | 27 | 26.6 |  | 23.3 | 25.2 | 24.5 | 24 | 24.3333 |  |  | CanadaBritish ColumbiaVANCOUVER INT'L A
Canada | British Columbia | VERNON CS | VERNON CS, BC, Canada | 50.22N | 119.19W | 482 | -8.00 (NAP) | 94-06 | 711150 | -19 |  | -34.2 | 42.1 | 32.9 | 36.4 | 34.7 | 35 | 34.6667 |  | 29.7 | 33.9 | 32.5 | 32 | 32.0333 |  |  | CanadaBritish ColumbiaVERNON CS
Canada | British Columbia | VICTORIA GONZALES CS | VICTORIA GONZALES CS, BC, Canada | 48.41N | 123.33W | 70 | -8.00 (NAP) | 94-06 | 712000 | -3.9 |  | -10.9 | 36.7 | 28.4 | 27 | 26.3 | 27 | 27.2333 |  | 23.3 | 24.1 | 22.9 | 23 | 23.4333 |  |  | CanadaBritish ColumbiaVICTORIA GONZALES CS
Canada | British Columbia | VICTORIA HARTLAND CS | VICTORIA HARTLAND CS, BC, Canada | 48.53N | 123.46W | 154 | -8.00 (NAP) | 94-06 | 710380 | -4.4 |  | -10.6 | 35.9 | 30.1 | 31.7 | 29.7 | 31 | 30.5 |  | 27 | 29.1 | 27.5 | 28 | 27.8667 |  |  | CanadaBritish ColumbiaVICTORIA HARTLAND CS
Canada | British Columbia | VICTORIA INT'L A | VICTORIA INT'L A, BC, Canada | 48.65N | 123.43W | 19 | -8.00 (NAP) | 82-06 | 717990 | -6.6 |  | -14 | 34.6 | 28.7 | 29.5 | 28.4 | 29 | 28.8667 |  | 24.8 | 26.5 | 25.8 | 26 | 25.7 |  |  | CanadaBritish ColumbiaVICTORIA INT'L A
Canada | British Columbia | VICTORIA MARINE | VICTORIA MARINE, BC, Canada | 48.37N | 123.75W | 32 | -8.00 (NAP) | 82-92 | 712020 | -7.2 |  | -16.6 | 28.4 | 22.4 | 23.8 | 22.3 | 23 | 22.8333 |  | 18.8 | 20.2 | 20.6 | 20 | 19.8667 |  |  | CanadaBritish ColumbiaVICTORIA MARINE
Canada | British Columbia | VICTORIA UNIVERSITY CS | VICTORIA UNIVERSITY CS, BC, Canada | 48.46N | 123.30W | 60 | -8.00 (NAP) | 94-06 | 717830 | -4.2 |  | -9.4 | 35.3 | 28.5 | 30.1 | 28.5 | 29 | 29.0333 |  | 24.9 | 27.4 | 26.3 | 26 | 26.2 |  |  | CanadaBritish ColumbiaVICTORIA UNIVERSITY CS
Canada | British Columbia | WEST VANCOUVER AUT | WEST VANCOUVER AUT, BC, Canada | 49.35N | 123.19W | 168 | -8.00 (NAP) | 94-06 | 717840 | -6.5 |  | -15.9 | 36.3 | 29.6 | 30.2 | 27.9 | 29 | 29.2333 |  | 26 | 26.8 | 26.1 | 26 | 26.3 |  |  | CanadaBritish ColumbiaWEST VANCOUVER AUT
Canada | British Columbia | WHITE ROCK CAMPBELL SCIENTIFI | WHITE ROCK CAMPBELL SCIENTIFI, BC, Canada | 49.02N | 122.78W | 13 | -8.00 (NAP) | 94-06 | 717850 | -6.8 |  | -14.4 | 34.4 | 26.5 | 27.9 | 26.3 | 27 | 26.9 |  | 23.3 | 25 | 24.1 | 24 | 24.1333 |  |  | CanadaBritish ColumbiaWHITE ROCK CAMPBELL SCIENTIFI
Canada | British Columbia | WILLIAMS LAKE A | WILLIAMS LAKE A, BC, Canada | 52.18N | 122.05W | 940 | -8.00 (NAP) | 82-06 | 711040 | -32.8 |  | -45.6 | 35.6 | 28.7 | 30.7 | 29.9 | 30 | 29.7667 |  | 25.8 | 28.2 | 27.3 | 27 | 27.1 |  |  | CanadaBritish ColumbiaWILLIAMS LAKE A
Canada | British Columbia | YOHO PARK | YOHO PARK, BC, Canada | 51.44N | 116.34W | 1615 | -7.00 (NAM) | 94-06 | 717860 | -35.5 |  | -44.5 | 32.6 | 24.9 | 28.2 | 27.6 | 27 | 26.9 |  | 21.8 | 26.1 | 25.2 | 24 | 24.3667 |  |  | CanadaBritish ColumbiaYOHO PARK
Canada | Manitoba | BERENS RIVER CS | BERENS RIVER CS, MB, Canada | 52.36N | 97.02W | 222 | -6.00 (NAC) | 88-06 | 711580 | -38.9 |  | -44.4 | 36 | 30.9 | 29.2 | 29.7 | 30 | 29.9333 |  | 26.7 | 27 | 27.3 | 27 | 27 |  |  | CanadaManitobaBERENS RIVER CS
Canada | Manitoba | BRANDON A | BRANDON A, MB, Canada | 49.91N | 99.95W | 409 | -6.00 (NAC) | 82-06 | 711400 | -37.1 |  | -44 | 39.1 | 33.1 | 31.9 | 33.8 | 33 | 32.9333 |  | 28.9 | 29.5 | 30.8 | 30 | 29.7333 |  |  | CanadaManitobaBRANDON A
Canada | Manitoba | CARBERRY CS | CARBERRY CS, MB, Canada | 49.91N | 99.36W | 384 | -6.00 (NAC) | 94-06 | 711700 | -37.5 |  | -45.6 | 38.3 | 32.5 | 31.5 | 33.5 | 33 | 32.5 |  | 28.9 | 29.5 | 30.4 | 30 | 29.6 |  |  | CanadaManitobaCARBERRY CS
Canada | Manitoba | CARMAN U OF M CS | CARMAN U OF M CS, MB, Canada | 49.50N | 98.03W | 268 | -6.00 (NAC) | 95-06 | 711470 | -35.5 |  | -42.5 | 35.7 | 31.3 | 31.2 | 32.8 | 32 | 31.7667 |  | 29 | 29.6 | 30.4 | 30 | 29.6667 |  |  | CanadaManitobaCARMAN U OF M CS
Canada | Manitoba | CHURCHILL A | CHURCHILL A, MB, Canada | 58.74N | 94.06W | 29 | -6.00 (NAC) | 82-06 | 719130 | -39.6 |  | -45.9 | 35.8 | 26.6 | 29 | 28.6 | 28 | 28.0667 |  | 23.3 | 26.2 | 24.7 | 25 | 24.7333 |  |  | CanadaManitobaCHURCHILL A
Canada | Manitoba | DAUPHIN A | DAUPHIN A, MB, Canada | 51.10N | 100.05W | 305 | -6.00 (NAC) | 82-06 | 718550 | -36.6 |  | -42.9 | 39.2 | 32.6 | 32.1 | 33.5 | 33 | 32.7333 |  | 28.9 | 29.6 | 30.5 | 30 | 29.6667 |  |  | CanadaManitobaDAUPHIN A
Canada | Manitoba | DELTA MARSH CS | DELTA MARSH CS, MB, Canada | 50.18N | 98.38W | 248 | -6.00 (NAC) | 97-06 | 715630 | -35.1 |  | -43.1 | 37.2 | 31 | 31.4 | 31.5 | 31 | 31.3 |  | 28 | 29.3 | 28.8 | 29 | 28.7 |  |  | CanadaManitobaDELTA MARSH CS
Canada | Manitoba | EMERSON AUT | EMERSON AUT, MB, Canada | 49.00N | 97.24W | 242 | -6.00 (NAC) | 96-06 | 715600 | -33.6 |  | -43.3 | 35.3 | 30.8 | 32 | 32.7 | 32 | 31.8333 |  | 28.8 | 30.3 | 30.1 | 30 | 29.7333 |  |  | CanadaManitobaEMERSON AUT
Canada | Manitoba | FISHER BRANCH (AUT) | FISHER BRANCH (AUT), MB, Canada | 51.08N | 97.55W | 253 | -6.00 (NAC) | 94-06 | 714420 | -37.8 |  | -45.5 | 37.7 | 31.6 | 30.2 | 32.2 | 31 | 31.3333 |  | 27.9 | 28.9 | 29.1 | 29 | 28.6333 |  |  | CanadaManitobaFISHER BRANCH (AUT)
Canada | Manitoba | GEORGE ISLAND (AUT) | GEORGE ISLAND (AUT), MB, Canada | 52.82N | 97.62W | 223 | -6.00 (NAC) | 94-06 | 714450 | N/A |  | N/A | N/A | 23.4 | 25.7 | 25.2 | 25 | 24.7667 |  | 21.1 | 24.2 | 23.8 | 23 | 23.0333 |  |  | CanadaManitobaGEORGE ISLAND (AUT)
Canada | Manitoba | GILLAM A | GILLAM A, MB, Canada | 56.36N | 94.71W | 145 | -6.00 (NAC) | 82-06 | 719120 | -40.6 |  | -46.8 | 36.4 | 29.5 | 30.1 | 30.7 | 30 | 30.1 |  | 26.1 | 27.5 | 26.7 | 27 | 26.7667 |  |  | CanadaManitobaGILLAM A
Canada | Manitoba | GIMLI INDUSTRIAL PARK | GIMLI INDUSTRIAL PARK, MB, Canada | 50.63N | 97.05W | 230 | -6.00 (NAC) | 82-06 | 718560 | -37.2 |  | -44.6 | 38.5 | 31.6 | 30.4 | 31.6 | 31 | 31.2 |  | 27.6 | 28.5 | 28.8 | 28 | 28.3 |  |  | CanadaManitobaGIMLI INDUSTRIAL PARK
Canada | Manitoba | GRAND RAPIDS (AUT) | GRAND RAPIDS (AUT), MB, Canada | 53.19N | 99.27W | 223 | -6.00 (NAC) | 94-06 | 718580 | -40.3 |  | -45.3 | 37.3 | 35.1 | 30.8 | 31.6 | 33 | 32.5 |  | 28.8 | 28.4 | 28.3 | 29 | 28.5 |  |  | CanadaManitobaGRAND RAPIDS (AUT)
Canada | Manitoba | GRETNA (AUT) | GRETNA (AUT), MB, Canada | 49.03N | 97.56W | 253 | -6.00 (NAC) | 94-06 | 714410 | -35.1 |  | -45.5 | 36.7 | 33.3 | 31.5 | 32.5 | 32 | 32.4333 |  | 29.6 | 29.6 | 30.1 | 30 | 29.7667 |  |  | CanadaManitobaGRETNA (AUT)
Canada | Manitoba | HUNTERS POINT MARINE | HUNTERS POINT MARINE, MB, Canada | 53.03N | 100.93W | 256 | -6.00 (NAC) | 94-05 | 711420 | N/A |  | N/A | N/A | 30 | 29.3 | 30 | 30 | 29.7667 |  | 25.4 | 26.9 | 26.3 | 26 | 26.2 |  |  | CanadaManitobaHUNTERS POINT MARINE
Canada | Manitoba | ISLAND LAKE A | ISLAND LAKE A, MB, Canada | 53.85N | 94.65W | 236 | -6.00 (NAC) | 86-06 | 711450 | -40.1 |  | -45.5 | 37 | 30.1 | 30.1 | 30.3 | 30 | 30.1667 |  | 27 | 27.6 | 27.5 | 27 | 27.3667 |  |  | CanadaManitobaISLAND LAKE A
Canada | Manitoba | LYNN LAKE A | LYNN LAKE A, MB, Canada | 56.86N | 101.08W | 357 | -6.00 (NAC) | 82-05 | 710780 | -42.9 |  | -48.3 | 36.3 | 28.8 | 30.2 | 30.9 | 30 | 29.9667 |  | 26.3 | 27.7 | 27.2 | 27 | 27.0667 |  |  | CanadaManitobaLYNN LAKE A
Canada | Manitoba | MELITA | MELITA, MB, Canada | 49.28N | 100.99W | 446 | -6.00 (NAC) | 94-06 | 714470 | -36.6 |  | -44.3 | 38.5 | 31.7 | 31.7 | 33.2 | 32 | 32.2 |  | 28.4 | 29.9 | 30.7 | 30 | 29.6667 |  |  | CanadaManitobaMELITA
Canada | Manitoba | NORWAY HOUSE A | NORWAY HOUSE A, MB, Canada | 53.95N | 97.85W | 224 | -6.00 (NAC) | 82-05 | 711410 | -41.3 |  | -47 | 35.4 | 30.2 | 29.9 | 29.6 | 30 | 29.9 |  | 26.4 | 27.6 | 27.5 | 27 | 27.1667 |  |  | CanadaManitobaNORWAY HOUSE A
Canada | Manitoba | OAKPOINT MARINE | OAKPOINT MARINE, MB, Canada | 50.50N | 98.04W | 250 | -6.00 (NAC) | 94-06 | 711440 | -35.5 |  | -42.5 | 34 | 28.9 | 29.2 | 29.8 | 29 | 29.3 |  | 26 | 27.3 | 27.6 | 27 | 26.9667 |  |  | CanadaManitobaOAKPOINT MARINE
Canada | Manitoba | PILOT MOUND (AUT) | PILOT MOUND (AUT), MB, Canada | 49.19N | 98.90W | 470 | -6.00 (NAC) | 82-06 | 711480 | -35.2 |  | -40.6 | 37.7 | 30 | 30.2 | 32.7 | 31 | 30.9667 |  | 27.1 | 28.6 | 29.7 | 28 | 28.4667 |  |  | CanadaManitobaPILOT MOUND (AUT)
Canada | Manitoba | PINAWA | PINAWA, MB, Canada | 50.18N | 96.06W | 268 | -6.00 (NAC) | 94-06 | 714480 | -38.4 |  | -46.3 | 38.1 | 32.2 | 31.2 | 31.4 | 32 | 31.6 |  | 28.5 | 29 | 29 | 29 | 28.8333 |  |  | CanadaManitobaPINAWA
Canada | Manitoba | PORTAGE SOUTHPORT A | PORTAGE SOUTHPORT A, MB, Canada | 49.90N | 98.27W | 270 | -6.00 (NAC) | 82-92 | 718510 | -34.7 |  | -39.6 | 41.6 | 34.9 | 33 | 35.4 | 34 | 34.4333 |  | 30.3 | 31.1 | 31.8 | 31 | 31.0667 |  |  | CanadaManitobaPORTAGE SOUTHPORT A
Canada | Manitoba | ROBLIN | ROBLIN, MB, Canada | 51.18N | 101.36W | 540 | -6.00 (NAC) | 96-06 | 715530 | -37.6 |  | -44.5 | 37.3 | 28.9 | 30.9 | 32.5 | 31 | 30.7667 |  | 26.5 | 28.7 | 29.2 | 28 | 28.1333 |  |  | CanadaManitobaROBLIN
Canada | Manitoba | SHOAL LAKE CS | SHOAL LAKE CS, MB, Canada | 50.45N | 100.60W | 561 | -6.00 (NAC) | 94-06 | 711500 | -38.1 |  | -45.2 | 37.1 | 29.8 | 30.2 | 31.8 | 31 | 30.6 |  | 27.1 | 28.2 | 28.7 | 28 | 28 |  |  | CanadaManitobaSHOAL LAKE CS
Canada | Manitoba | SPRAGUE | SPRAGUE, MB, Canada | 49.02N | 95.60W | 329 | -6.00 (NAC) | 94-06 | 714490 | -37.4 |  | -49.8 | 36.6 | 31.2 | 31.4 | 31.2 | 31 | 31.2667 |  | 27.9 | 29.2 | 28.1 | 28 | 28.4 |  |  | CanadaManitobaSPRAGUE
Canada | Manitoba | SWAN RIVER RCS | SWAN RIVER RCS, MB, Canada | 52.12N | 101.23W | 335 | -6.00 (NAC) | 94-06 | 714430 | -36.9 |  | -43.3 | 37.1 | 31.9 | 31.7 | 32.3 | 32 | 31.9667 |  | 28.1 | 29.3 | 29.8 | 29 | 29.0667 |  |  | CanadaManitobaSWAN RIVER RCS
Canada | Manitoba | THE PAS A | THE PAS A, MB, Canada | 53.97N | 101.10W | 270 | -6.00 (NAC) | 82-06 | 718670 | -38.7 |  | -43.3 | 37.9 | 30.7 | 31.1 | 31.2 | 31 | 31 |  | 27.1 | 28.4 | 28.5 | 28 | 28 |  |  | CanadaManitobaTHE PAS A
Canada | Manitoba | THOMPSON A | THOMPSON A, MB, Canada | 55.80N | 97.86W | 223 | -6.00 (NAC) | 82-06 | 710790 | -43.6 |  | -50.3 | 37.5 | 29.8 | 31 | 30.8 | 31 | 30.5333 |  | 26.8 | 28.1 | 27.9 | 28 | 27.6 |  |  | CanadaManitobaTHOMPSON A
Canada | Manitoba | VICTORIA BEACH (AUT) | VICTORIA BEACH (AUT), MB, Canada | 50.70N | 96.57W | 220 | -6.00 (NAC) | 96-06 | 715520 | -33.7 |  | -38.8 | 33.5 | 28.3 | 29.6 | 29.8 | 29 | 29.2333 |  | 25.5 | 27.9 | 27.5 | 27 | 26.9667 |  |  | CanadaManitobaVICTORIA BEACH (AUT)
Canada | Manitoba | WASAGAMING | WASAGAMING, MB, Canada | 50.66N | 99.94W | 627 | -6.00 (NAC) | 94-06 | 714440 | -40 |  | -49.3 | 36.8 | 29.7 | 30.1 | 31.6 | 30 | 30.4667 |  | 26.6 | 28.2 | 28.5 | 28 | 27.7667 |  |  | CanadaManitobaWASAGAMING
Canada | Manitoba | WILSON CREEK WEIR CS | WILSON CREEK WEIR CS, MB, Canada | 50.71N | 99.53W | 351 | -6.00 (NAC) | 97-06 | 711490 | -33.6 |  | -39.7 | 39 | 30.1 | 31.9 | 33 | 32 | 31.6667 |  | 27.2 | 30 | 30 | 29 | 29.0667 |  |  | CanadaManitobaWILSON CREEK WEIR CS
Canada | Manitoba | WINNIPEG RICHARDSON INT'L A | WINNIPEG RICHARDSON INT'L A, MB, Canada | 49.92N | 97.23W | 239 | -6.00 (NAC) | 82-06 | 718520 | -35.4 |  | -41.7 | 40 | 33.3 | 31.9 | 33.6 | 33 | 32.9333 |  | 29.4 | 29.9 | 30.7 | 30 | 30 |  |  | CanadaManitobaWINNIPEG RICHARDSON INT'L A
Canada | New Brunswick | BAS CARAQUET | BAS CARAQUET, NB, Canada | 47.80N | 64.83W | 5 | -4.00 (NAA) | 94-06 | 715980 | -24.7 |  | -30.8 | 36.8 | 30.2 | 30.2 | 30.8 | 30 | 30.4 |  | 27 | 27.5 | 27.9 | 27 | 27.4667 |  |  | CanadaNew BrunswickBAS CARAQUET
Canada | New Brunswick | CHARLO A | CHARLO A, NB, Canada | 47.98N | 66.33W | 40 | -4.00 (NAA) | 82-03 | 717110 | -28.7 |  | -35.9 | 35.2 | 30.5 | 30.6 | 31 | 31 | 30.7 |  | 27.3 | 28.1 | 27.8 | 28 | 27.7333 |  |  | CanadaNew BrunswickCHARLO A
Canada | New Brunswick | FREDERICTON A | FREDERICTON A, NB, Canada | 45.87N | 66.53W | 21 | -4.00 (NAA) | 82-06 | 717000 | -28.1 |  | -36.5 | 36.4 | 32 | 31.5 | 32 | 32 | 31.8333 |  | 28.6 | 29.2 | 29.4 | 29 | 29.0667 |  |  | CanadaNew BrunswickFREDERICTON A
Canada | New Brunswick | MIRAMICHI A | MIRAMICHI A, NB, Canada | 47.01N | 65.47W | 33 | -4.00 (NAA) | 82-91 | 717170 | -27.9 |  | -34.2 | 36 | 31.5 | 32.7 | 31 | 32 | 31.7333 |  | 28.6 | 30.3 | 29.2 | 29 | 29.3667 |  |  | CanadaNew BrunswickMIRAMICHI A
Canada | New Brunswick | MIRAMICHI RCS | MIRAMICHI RCS, NB, Canada | 47.01N | 65.46W | 33 | -4.00 (NAA) | 98-06 | 717440 | -28.2 |  | -35 | 38.6 | 33 | 32 | 32.9 | 33 | 32.6333 |  | 30.1 | 29.9 | 30.1 | 30 | 30.0333 |  |  | CanadaNew BrunswickMIRAMICHI RCS
Canada | New Brunswick | MISCOU ISLAND (AUT) | MISCOU ISLAND (AUT), NB, Canada | 48.01N | 64.49W | 4 | -4.00 (NAA) | 87-06 | 717190 | -24 |  | -29.2 | 34.7 | 28 | 28.2 | 28.7 | 28 | 28.3 |  | 24.7 | 25.8 | 25.8 | 25 | 25.4333 |  |  | CanadaNew BrunswickMISCOU ISLAND (AUT)
Canada | New Brunswick | MONCTON A | MONCTON A, NB, Canada | 46.10N | 64.69W | 71 | -4.00 (NAA) | 82-06 | 717050 | -26.4 |  | -34.2 | 35.1 | 29.7 | 30.3 | 30.7 | 30 | 30.2333 |  | 27 | 28.2 | 28.1 | 28 | 27.7667 |  |  | CanadaNew BrunswickMONCTON A
Canada | New Brunswick | POINT ESCUMINAC (AUT) | POINT ESCUMINAC (AUT), NB, Canada | 47.07N | 64.80W | 4 | -4.00 (NAA) | 87-01 | 714140 | -24.7 |  | -31 | 36.3 | 30.3 | 29.9 | 30.4 | 30 | 30.2 |  | 26.8 | 26.9 | 26.7 | 27 | 26.8 |  |  | CanadaNew BrunswickPOINT ESCUMINAC (AUT)
Canada | New Brunswick | POINT LEPREAU CS | POINT LEPREAU CS, NB, Canada | 45.07N | 66.45W | 6 | -4.00 (NAA) | 94-06 | 716990 | -21.7 |  | -28 | 32.6 | 24.6 | 26.5 | 25.9 | 26 | 25.6667 |  | 21.5 | 23 | 23.4 | 23 | 22.6333 |  |  | CanadaNew BrunswickPOINT LEPREAU CS
Canada | New Brunswick | SAINT JOHN A | SAINT JOHN A, NB, Canada | 45.32N | 65.89W | 109 | -4.00 (NAA) | 82-06 | 716090 | -26.4 |  | -34.4 | 33.9 | 27.5 | 27.8 | 28.5 | 28 | 27.9333 |  | 24.7 | 25.8 | 25.8 | 25 | 25.4333 |  |  | CanadaNew BrunswickSAINT JOHN A
Canada | New Brunswick | ST LEONARD CS | ST LEONARD CS, NB, Canada | 47.16N | 67.83W | 245 | -4.00 (NAA) | 85-06 | 710190 | -30.4 |  | -35.3 | 35.1 | 30.4 | 30.3 | 30.2 | 30 | 30.3 |  | 27.6 | 28 | 27.4 | 28 | 27.6667 |  |  | CanadaNew BrunswickST LEONARD CS
Canada | New Brunswick | ST STEPHEN (AUT) | ST STEPHEN (AUT), NB, Canada | 45.22N | 67.25W | 26 | -4.00 (NAA) | 87-06 | 716070 | -29.4 |  | -37.5 | 37.5 | 31.6 | 31.6 | 31.8 | 32 | 31.6667 |  | 28.7 | 28.9 | 29.4 | 29 | 29 |  |  | CanadaNew BrunswickST STEPHEN (AUT)
Canada | Newfoundland and Labrador | ARGENTIA (AUT) | ARGENTIA (AUT), NF, Canada | 47.29N | 53.99W | 15 | -3.50 (NAF) | 87-06 | 718070 | -15.1 |  | -21.9 | 26.9 | 18.3 | 21.2 | 22.4 | 21 | 20.6333 |  | 15.9 | 19 | 20.4 | 18 | 18.4333 |  |  | CanadaNewfoundland and LabradorARGENTIA (AUT)
Canada | Newfoundland and Labrador | BADGER (AUT) | BADGER (AUT), NF, Canada | 48.97N | 56.07W | 103 | -3.50 (NAF) | 87-06 | 714000 | -32.7 |  | -41.6 | 36.7 | 29.2 | 30.9 | 30.5 | 30 | 30.2 |  | 26.6 | 28.5 | 27.7 | 28 | 27.6 |  |  | CanadaNewfoundland and LabradorBADGER (AUT)
Canada | Newfoundland and Labrador | BONAVISTA | BONAVISTA, NF, Canada | 48.67N | 53.11W | 26 | -3.50 (NAF) | 82-06 | 711960 | -18.2 |  | -26.5 | 29.6 | 22.8 | 25.6 | 25.5 | 25 | 24.6333 |  | 20.3 | 23.5 | 23.8 | 23 | 22.5333 |  |  | CanadaNewfoundland and LabradorBONAVISTA
Canada | Newfoundland and Labrador | BURGEO 2 | BURGEO 2, NF, Canada | 47.62N | 57.62W | 11 | -3.50 (NAF) | 82-06 | 711940 | -18.5 |  | -25.8 | 29.3 | 19.5 | 22.2 | 23 | 22 | 21.5667 |  | 16.9 | 20 | 21.4 | 19 | 19.4333 |  |  | CanadaNewfoundland and LabradorBURGEO 2
Canada | Newfoundland and Labrador | CAPE KAKKIVIAK | CAPE KAKKIVIAK, NF, Canada | 59.98N | 64.16W | 551 | -4.00 (NAA) | 94-06 | 711760 | N/A |  | N/A | N/A | 17.8 | 20.9 | 20.2 | 20 | 19.6333 |  | 13.6 | 18.5 | 17 | 16 | 16.3667 |  |  | CanadaNewfoundland and LabradorCAPE KAKKIVIAK
Canada | Newfoundland and Labrador | CAPE RACE (AUT) | CAPE RACE (AUT), NF, Canada | 46.66N | 53.08W | 27 | -3.50 (NAF) | 94-06 | 718000 | -16.1 |  | -22.8 | 30.8 | 17.7 | 20.5 | 22 | 20 | 20.0667 |  | 14.5 | 18 | 19.7 | 17 | 17.4 |  |  | CanadaNewfoundland and LabradorCAPE RACE (AUT)
Canada | Newfoundland and Labrador | CARTWRIGHT | CARTWRIGHT, NF, Canada | 53.71N | 57.04W | 14 | -4.00 (NAA) | 82-06 | 718180 | -30.4 |  | -35.1 | 34.7 | 26.2 | 27.1 | 27.7 | 27 | 27 |  | 22 | 23.9 | 23.9 | 23 | 23.2667 |  |  | CanadaNewfoundland and LabradorCARTWRIGHT
Canada | Newfoundland and Labrador | CHURCHILL FALLS | CHURCHILL FALLS, NF, Canada | 53.56N | 64.09W | 440 | -4.00 (NAA) | 82-06 | 711820 | -39.1 |  | -43.4 | 33 | 27.6 | 27 | 27 | 27 | 27.2 |  | 23.4 | 24.5 | 23.7 | 24 | 23.8667 |  |  | CanadaNewfoundland and LabradorCHURCHILL FALLS
Canada | Newfoundland and Labrador | COMFORT COVE | COMFORT COVE, NF, Canada | 49.27N | 54.88W | 99 | -3.50 (NAF) | 82-96 | 711930 | -24.5 |  | -31.3 | 32.8 | 26.9 | 28.6 | 27.2 | 28 | 27.5667 |  | 23.5 | 26.1 | 25.7 | 25 | 25.1 |  |  | CanadaNewfoundland and LabradorCOMFORT COVE
Canada | Newfoundland and Labrador | CORNER BROOK | CORNER BROOK, NF, Canada | 48.93N | 57.92W | 152 | -3.50 (NAF) | 94-06 | 719730 | -22.9 |  | -31.2 | 33.5 | 26.5 | 28 | 28.3 | 28 | 27.6 |  | 24.1 | 26.2 | 26 | 25 | 25.4333 |  |  | CanadaNewfoundland and LabradorCORNER BROOK
Canada | Newfoundland and Labrador | DANIELS HARBOUR | DANIELS HARBOUR, NF, Canada | 50.24N | 57.58W | 19 | -3.50 (NAF) | 82-06 | 711850 | -24 |  | -34.1 | 27.2 | 19.7 | 22.6 | 22.5 | 22 | 21.6 |  | 17.8 | 20.5 | 20.9 | 20 | 19.7333 |  |  | CanadaNewfoundland and LabradorDANIELS HARBOUR
Canada | Newfoundland and Labrador | DEER LAKE A | DEER LAKE A, NF, Canada | 49.22N | 57.40W | 22 | -3.50 (NAF) | 82-06 | 718090 | -29.9 |  | -39.2 | 34.2 | 27.4 | 29.1 | 29 | 29 | 28.5 |  | 24.8 | 27.1 | 26.6 | 26 | 26.1667 |  |  | CanadaNewfoundland and LabradorDEER LAKE A
Canada | Newfoundland and Labrador | ENGLEE (AUT) | ENGLEE (AUT), NF, Canada | 50.72N | 56.11W | 30 | -3.50 (NAF) | 94-06 | 714170 | -22.7 |  | -29.6 | 30.7 | 22.5 | 25 | 25.4 | 24 | 24.3 |  | 19.9 | 22.7 | 23 | 22 | 21.8667 |  |  | CanadaNewfoundland and LabradorENGLEE (AUT)
Canada | Newfoundland and Labrador | FEROLLE POINT (AUT) | FEROLLE POINT (AUT), NF, Canada | 51.02N | 57.10W | 6 | -3.50 (NAF) | 94-06 | 714060 | -25 |  | -33.4 | 25.8 | 16.4 | 19.5 | 20.6 | 19 | 18.8333 |  | 14.5 | 18 | 19.2 | 17 | 17.2333 |  |  | CanadaNewfoundland and LabradorFEROLLE POINT (AUT)
Canada | Newfoundland and Labrador | GANDER INT'L A | GANDER INT'L A, NF, Canada | 48.95N | 54.58W | 151 | -3.50 (NAF) | 82-06 | 718030 | -22.2 |  | -30 | 32.6 | 26.5 | 28.4 | 27.5 | 27 | 27.4667 |  | 23.9 | 26.2 | 25.7 | 25 | 25.2667 |  |  | CanadaNewfoundland and LabradorGANDER INT'L A
Canada | Newfoundland and Labrador | GOOSE A | GOOSE A, NF, Canada | 53.32N | 60.42W | 49 | -4.00 (NAA) | 82-06 | 718160 | -33.4 |  | -37.5 | 37.7 | 30.9 | 30.4 | 31 | 31 | 30.7667 |  | 26.1 | 27.2 | 27.2 | 27 | 26.8333 |  |  | CanadaNewfoundland and LabradorGOOSE A
Canada | Newfoundland and Labrador | GRATES COVE | GRATES COVE, NF, Canada | 48.17N | 52.94W | 46 | -3.50 (NAF) | 94-06 | 713360 | N/A |  | N/A | N/A | 22.1 | 24.2 | 24.7 | 24 | 23.6667 |  | 19.8 | 22.8 | 22.7 | 22 | 21.7667 |  |  | CanadaNewfoundland and LabradorGRATES COVE
Canada | Newfoundland and Labrador | HOPEDALE (AUT) | HOPEDALE (AUT), NF, Canada | 55.45N | 60.22W | 12 | -4.00 (NAA) | 82-06 | 719000 | -31.1 |  | -35.7 | 31.9 | 23.6 | 24.5 | 27 | 25 | 25.0333 |  | 19.6 | 21.7 | 22.3 | 21 | 21.2 |  |  | CanadaNewfoundland and LabradorHOPEDALE (AUT)
Canada | Newfoundland and Labrador | LA SCIE | LA SCIE, NF, Canada | 49.92N | 55.67W | 194 | -3.50 (NAF) | 92-06 | 713370 | -21.5 |  | -27.7 | 33 | 27.7 | 28.7 | 28.1 | 28 | 28.1667 |  | 24.1 | 25.9 | 25.7 | 25 | 25.2333 |  |  | CanadaNewfoundland and LabradorLA SCIE
Canada | Newfoundland and Labrador | MARTICOT ISLAND | MARTICOT ISLAND, NF, Canada | 47.33N | 54.59W | 22 | -3.50 (NAF) | 94-06 | 716920 | N/A |  | N/A | N/A | 17.9 | 20.2 | 21.4 | 20 | 19.8333 |  | 15.2 | 18.1 | 19.7 | 18 | 17.6667 |  |  | CanadaNewfoundland and LabradorMARTICOT ISLAND
Canada | Newfoundland and Labrador | POOLS ISLAND | POOLS ISLAND, NF, Canada | 49.11N | 53.58W | 19 | -3.50 (NAF) | 94-06 | 719310 | -19.5 |  | -28 | 32.6 | 25.8 | 26.1 | 27.1 | 26 | 26.3333 |  | 21.5 | 23.8 | 23.7 | 23 | 23 |  |  | CanadaNewfoundland and LabradorPOOLS ISLAND
Canada | Newfoundland and Labrador | PORT AUX BASQUES | PORT AUX BASQUES, NF, Canada | 47.57N | 59.15W | 40 | -3.50 (NAF) | 82-06 | 711970 | -17.5 |  | -24.6 | 25.8 | 18.8 | 21.1 | 22.3 | 21 | 20.7333 |  | 17 | 19.5 | 20.7 | 19 | 19.0667 |  |  | CanadaNewfoundland and LabradorPORT AUX BASQUES
Canada | Newfoundland and Labrador | SAGLEK | SAGLEK, NF, Canada | 58.33N | 62.59W | 501 | -4.00 (NAA) | 89-06 | 713350 | -33.8 |  | -38.8 | 27.7 | 22.3 | 21.9 | 21.6 | 22 | 21.9333 |  | 16.1 | 19.3 | 18.6 | 18 | 18 |  |  | CanadaNewfoundland and LabradorSAGLEK
Canada | Newfoundland and Labrador | SAGONA ISLAND | SAGONA ISLAND, NF, Canada | 47.37N | 55.79W | 60 | -3.50 (NAF) | 94-06 | 714080 | -14.7 |  | -22.6 | 26 | 16.7 | 20.1 | 20.7 | 19 | 19.1667 |  | 14.8 | 18.2 | 19.7 | 18 | 17.5667 |  |  | CanadaNewfoundland and LabradorSAGONA ISLAND
Canada | Newfoundland and Labrador | ST ANTHONY | ST ANTHONY, NF, Canada | 51.38N | 56.10W | 29 | -3.50 (NAF) | 82-06 | 715580 | -28 |  | -32.8 | 29.2 | 22.8 | 24.6 | 24.6 | 24 | 24 |  | 19.8 | 22.4 | 22.5 | 22 | 21.5667 |  |  | CanadaNewfoundland and LabradorST ANTHONY
Canada | Newfoundland and Labrador | ST JOHN'S A | ST JOHN'S A, NF, Canada | 47.62N | 52.74W | 141 | -3.50 (NAF) | 82-06 | 718010 | -18.4 |  | -25.8 | 31.8 | 24 | 26.6 | 26.7 | 26 | 25.7667 |  | 21.8 | 24.7 | 24.6 | 24 | 23.7 |  |  | CanadaNewfoundland and LabradorST JOHN'S A
Canada | Newfoundland and Labrador | ST LAWRENCE | ST LAWRENCE, NF, Canada | 46.92N | 55.38W | 49 | -3.50 (NAF) | 82-06 | 718020 | -17.3 |  | -23.7 | 31 | 22.3 | 24.4 | 24.9 | 24 | 23.8667 |  | 18.7 | 22.2 | 22.9 | 21 | 21.2667 |  |  | CanadaNewfoundland and LabradorST LAWRENCE
Canada | Newfoundland and Labrador | STEPHENVILLE A | STEPHENVILLE A, NF, Canada | 48.53N | 58.55W | 26 | -3.50 (NAF) | 82-06 | 718150 | -21.4 |  | -29.6 | 30.5 | 23.3 | 25 | 25 | 24 | 24.4333 |  | 20.4 | 23.2 | 23 | 22 | 22.2 |  |  | CanadaNewfoundland and LabradorSTEPHENVILLE A
Canada | Newfoundland and Labrador | TWILLINGATE (AUT) | TWILLINGATE (AUT), NF, Canada | 49.68N | 54.80W | 92 | -3.50 (NAF) | 94-06 | 714020 | -16.6 |  | -23.9 | 32.4 | 25.4 | 26.5 | 26.2 | 26 | 26.0333 |  | 22.4 | 24.4 | 23.8 | 24 | 23.5333 |  |  | CanadaNewfoundland and LabradorTWILLINGATE (AUT)
Canada | Newfoundland and Labrador | WABUSH LAKE A | WABUSH LAKE A, NF, Canada | 52.93N | 66.87W | 551 | -4.00 (NAA) | 82-06 | 718250 | -40.1 |  | -46.3 | 33.9 | 28.4 | 27.2 | 26.5 | 27 | 27.3667 |  | 23.9 | 24.4 | 23.6 | 24 | 23.9667 |  |  | CanadaNewfoundland and LabradorWABUSH LAKE A
Canada | Northwest Territories | AULAVIK NATIONAL PARK | AULAVIK NATIONAL PARK, NT, Canada | 74.14N | 119.99W | 32 | -7.00 (NAM) | 96-06 | 719740 | -44.4 |  | -47.2 | 25.7 | 15 | 19.9 | 17.9 | 18 | 17.6 |  | 12.2 | 16.8 | 13.8 | 14 | 14.2667 |  |  | CanadaNorthwest TerritoriesAULAVIK NATIONAL PARK
Canada | Northwest Territories | CAPE PARRY A | CAPE PARRY A, NT, Canada | 70.17N | 124.72W | 87 | -7.00 (NAM) | 82-06 | 719480 | -39.2 |  | -46.6 | 27.1 | 16.1 | 20 | 17.4 | 18 | 17.8333 |  | 12 | 17 | 14.1 | 14 | 14.3667 |  |  | CanadaNorthwest TerritoriesCAPE PARRY A
Canada | Northwest Territories | COLVILLE LAKE | COLVILLE LAKE, NT, Canada | 67.04N | 126.08W | 259 | -7.00 (NAM) | 94-06 | 710550 | -45.6 |  | -50.3 | 32.8 | 26.2 | 28.3 | 24.2 | 26 | 26.2333 |  | 22.8 | 25.4 | 21.9 | 23 | 23.3667 |  |  | CanadaNorthwest TerritoriesCOLVILLE LAKE
Canada | Northwest Territories | FORT GOOD HOPE CS | FORT GOOD HOPE CS, NT, Canada | 66.24N | 128.64W | 82 | -7.00 (NAM) | 98-06 | 714910 | N/A |  | N/A | N/A | 31.1 | 32.3 | 27.5 | 30 | 30.3 |  | 28.1 | 28.9 | 25.5 | 28 | 27.5 |  |  | CanadaNorthwest TerritoriesFORT GOOD HOPE CS
Canada | Northwest Territories | FORT LIARD | FORT LIARD, NT, Canada | 60.23N | 123.47W | 213 | -7.00 (NAM) | 94-06 | 714970 | -41.6 |  | -50.9 | 36 | 30.5 | 31.8 | 30.2 | 31 | 30.8333 |  | 28 | 28.7 | 27.1 | 28 | 27.9333 |  |  | CanadaNorthwest TerritoriesFORT LIARD
Canada | Northwest Territories | FORT PROVIDENCE | FORT PROVIDENCE, NT, Canada | 61.32N | 117.60W | 162 | -7.00 (NAM) | 94-06 | 710870 | -42.7 |  | -47.6 | 35.2 | 30.1 | 31.6 | 29.9 | 31 | 30.5333 |  | 27.6 | 28.6 | 27.2 | 28 | 27.8 |  |  | CanadaNorthwest TerritoriesFORT PROVIDENCE
Canada | Northwest Territories | FORT RELIANCE | FORT RELIANCE, NT, Canada | 62.72N | 109.17W | 166 | -6.00 (NAS) | 82-91 | 710730 | -45.7 |  | -51.2 | 35.3 | 23.8 | 27.7 | 25.9 | 26 | 25.8 |  | 20.1 | 24.1 | 22.9 | 22 | 22.3667 |  |  | CanadaNorthwest TerritoriesFORT RELIANCE
Canada | Northwest Territories | FORT SIMPSON A | FORT SIMPSON A, NT, Canada | 61.76N | 121.24W | 169 | -7.00 (NAM) | 82-06 | 719460 | -42.8 |  | -49.5 | 36 | 30.2 | 31 | 30.4 | 31 | 30.5333 |  | 27.5 | 28.3 | 27.5 | 28 | 27.7667 |  |  | CanadaNorthwest TerritoriesFORT SIMPSON A
Canada | Northwest Territories | FORT SMITH A | FORT SMITH A, NT, Canada | 60.02N | 111.96W | 205 | -7.00 (NAM) | 82-06 | 719340 | -41.9 |  | -48.6 | 35.2 | 29.2 | 31.2 | 30.9 | 30 | 30.4333 |  | 27 | 28.4 | 27.6 | 28 | 27.6667 |  |  | CanadaNorthwest TerritoriesFORT SMITH A
Canada | Northwest Territories | HANBURY RIVER | HANBURY RIVER, NT, Canada | 63.60N | 105.13W | 317 | -7.00 (NAM) | 94-06 | 719630 | -42.8 |  | -48.1 | 31.2 | 24.3 | 26.9 | 25 | 25 | 25.4 |  | 21.8 | 24.7 | 21.8 | 23 | 22.7667 |  |  | CanadaNorthwest TerritoriesHANBURY RIVER
Canada | Northwest Territories | HAY RIVER A | HAY RIVER A, NT, Canada | 60.84N | 115.78W | 165 | -7.00 (NAM) | 82-06 | 719350 | -40.3 |  | -45.6 | 35.2 | 28.7 | 30.6 | 29 | 29 | 29.4333 |  | 25.5 | 27.4 | 26.5 | 26 | 26.4667 |  |  | CanadaNorthwest TerritoriesHAY RIVER A
Canada | Northwest Territories | INNER WHALEBACKS | INNER WHALEBACKS, NT, Canada | 61.92N | 113.73W | 165 | -7.00 (NAM) | 94-06 | 711620 | N/A |  | N/A | N/A | 18.1 | 24 | 20.9 | 21 | 21 |  | 15.1 | 21.3 | 19.1 | 19 | 18.5 |  |  | CanadaNorthwest TerritoriesINNER WHALEBACKS
Canada | Northwest Territories | INUVIK A | INUVIK A, NT, Canada | 68.30N | 133.48W | 68 | -7.00 (NAM) | 82-06 | 719570 | -44.2 |  | -52.1 | 33.7 | 27.8 | 28.5 | 27.1 | 28 | 27.8 |  | 25 | 26.5 | 23.3 | 25 | 24.9333 |  |  | CanadaNorthwest TerritoriesINUVIK A
Canada | Northwest Territories | LAC LA MARTRE | LAC LA MARTRE, NT, Canada | 63.13N | 117.25W | 271 | -7.00 (NAM) | 95-06 | 711630 | N/A |  | N/A | N/A | 30.9 | 30.4 | 28.1 | 30 | 29.8 |  | 27 | 27.4 | 25.3 | 27 | 26.5667 |  |  | CanadaNorthwest TerritoriesLAC LA MARTRE
Canada | Northwest Territories | LINDBURG LANDING | LINDBURG LANDING, NT, Canada | 61.12N | 122.85W | 183 | -7.00 (NAM) | 98-06 | 716820 | -42.9 |  | -49.1 | 35.6 | 30.2 | 30.3 | 29.8 | 30 | 30.1 |  | 27.6 | 28.1 | 26.5 | 27 | 27.4 |  |  | CanadaNorthwest TerritoriesLINDBURG LANDING
Canada | Northwest Territories | LITTLE CHICAGO | LITTLE CHICAGO, NT, Canada | 67.18N | 130.23W | 63 | -7.00 (NAM) | 94-06 | 711640 | N/A |  | N/A | N/A | 29.6 | 30.1 | 27.1 | 29 | 28.9333 |  | 27.1 | 27.7 | 24.6 | 26 | 26.4667 |  |  | CanadaNorthwest TerritoriesLITTLE CHICAGO
Canada | Northwest Territories | LIVERPOOL BAY | LIVERPOOL BAY, NT, Canada | 69.60N | 130.91W | 102 | -7.00 (NAM) | 94-06 | 719600 | N/A |  | N/A | N/A | 22.9 | 24.8 | 21.4 | 23 | 23.0333 |  | 19.1 | 22 | 18.3 | 20 | 19.8 |  |  | CanadaNorthwest TerritoriesLIVERPOOL BAY
Canada | Northwest Territories | MOULD BAY A | MOULD BAY A, NT, Canada | 76.23N | 119.33W | 12 | -7.00 (NAM) | 82-93 | 710720 | -48 |  | -54.2 | 18 | 10 | 13.2 | 8.6 | 11 | 10.6 |  | 7.8 | 11 | 6.7 | 9 | 8.5 |  |  | CanadaNorthwest TerritoriesMOULD BAY A
Canada | Northwest Territories | NICHOLSON PENINSULA | NICHOLSON PENINSULA, NT, Canada | 69.93N | 128.97W | 89 | -7.00 (NAM) | 82-93 | 719560 | -41.9 |  | -49 | 29.9 | 21.5 | 24.1 | 20.5 | 22 | 22.0333 |  | 17.8 | 20.8 | 17.3 | 19 | 18.6333 |  |  | CanadaNorthwest TerritoriesNICHOLSON PENINSULA
Canada | Northwest Territories | NORMAN WELLS A | NORMAN WELLS A, NT, Canada | 65.28N | 126.80W | 73 | -7.00 (NAM) | 82-06 | 710430 | -44 |  | -48.6 | 35.4 | 29.9 | 30.9 | 28.3 | 30 | 29.7 |  | 27.2 | 27.9 | 25.7 | 27 | 26.9333 |  |  | CanadaNorthwest TerritoriesNORMAN WELLS A
Canada | Northwest Territories | PELLY ISLAND | PELLY ISLAND, NT, Canada | 69.63N | 135.44W | 17 | -7.00 (NAM) | 94-06 | 715020 | N/A |  | N/A | N/A | 19.3 | 24.3 | 20.1 | 21 | 21.2333 |  | 14.2 | 20.4 | 17.4 | 17 | 17.3333 |  |  | CanadaNorthwest TerritoriesPELLY ISLAND
Canada | Northwest Territories | RAE LAKES | RAE LAKES, NT, Canada | 64.11N | 117.33W | 223 | -7.00 (NAM) | 94-06 | 711650 | -45.1 |  | -51.1 | 34.1 | 28.7 | 28.7 | 26.8 | 28 | 28.0667 |  | 25.1 | 26.5 | 24.1 | 25 | 25.2333 |  |  | CanadaNorthwest TerritoriesRAE LAKES
Canada | Northwest Territories | SACHS HARBOUR CLIMATE | SACHS HARBOUR CLIMATE, NT, Canada | 71.99N | 125.25W | 88 | -7.00 (NAM) | 94-06 | 714670 | -41.7 |  | -46.7 | 24 | 15.3 | 18.7 | 15.5 | 17 | 16.5 |  | 12.4 | 16 | 13.3 | 14 | 13.9 |  |  | CanadaNorthwest TerritoriesSACHS HARBOUR CLIMATE
Canada | Northwest Territories | TROUT LAKE | TROUT LAKE, NT, Canada | 60.44N | 121.24W | 498 | -7.00 (NAM) | 94-06 | 711660 | N/A |  | N/A | N/A | 28.2 | 28.2 | 28.5 | 28 | 28.3 |  | 25.9 | 26 | 25.1 | 26 | 25.6667 |  |  | CanadaNorthwest TerritoriesTROUT LAKE
Canada | Northwest Territories | TUKTOYAKTUK | TUKTOYAKTUK, NT, Canada | 69.43N | 133.02W | 5 | -7.00 (NAM) | 94-06 | 719850 | -41.2 |  | -46 | 32.7 | 24 | 26.6 | 23.1 | 25 | 24.5667 |  | 21 | 24.1 | 19.9 | 22 | 21.6667 |  |  | CanadaNorthwest TerritoriesTUKTOYAKTUK
Canada | Northwest Territories | YELLOWKNIFE A | YELLOWKNIFE A, NT, Canada | 62.46N | 114.44W | 206 | -7.00 (NAM) | 82-06 | 719360 | -42.8 |  | -49.8 | 33 | 26.3 | 28.1 | 27.2 | 27 | 27.2 |  | 23.8 | 25.7 | 24.4 | 25 | 24.6333 |  |  | CanadaNorthwest TerritoriesYELLOWKNIFE A
Canada | Northwest Territories | YOHIN | YOHIN, NT, Canada | 61.24N | 123.74W | 204 | -7.00 (NAM) | 82-06 | 710200 | -42.6 |  | -47.1 | 34.7 | 27.6 | 30 | 27.6 | 28 | 28.4 |  | 23 | 26.2 | 23.5 | 24 | 24.2333 |  |  | CanadaNorthwest TerritoriesYOHIN
Canada | Nova Scotia | AMHERST (AUT) | AMHERST (AUT), NS, Canada | 45.85N | 64.27W | 23 | -4.00 (NAA) | 94-05 | 714100 | -24.2 |  | -32.1 | 32.2 | 26.4 | 27.3 | 27.1 | 27 | 26.9333 |  | 23.6 | 25.3 | 25.3 | 25 | 24.7333 |  |  | CanadaNova ScotiaAMHERST (AUT)
Canada | Nova Scotia | BACCARO POINT | BACCARO POINT, NS, Canada | 43.45N | 65.47W | 13 | -4.00 (NAA) | 94-06 | 716910 | -16.5 |  | -21.5 | 25.5 | 21 | 21.3 | 21.4 | 21 | 21.2333 |  | 16.6 | 18.5 | 19.2 | 18 | 18.1 |  |  | CanadaNova ScotiaBACCARO POINT
Canada | Nova Scotia | BEAVER ISLAND (AUT) | BEAVER ISLAND (AUT), NS, Canada | 44.82N | 62.33W | 16 | -4.00 (NAA) | 94-06 | 714030 | -17 |  | -23.1 | 25.5 | 18.2 | 20.8 | 21.7 | 20 | 20.2333 |  | 16 | 19.1 | 20.5 | 19 | 18.5333 |  |  | CanadaNova ScotiaBEAVER ISLAND (AUT)
Canada | Nova Scotia | BRIER ISLAND | BRIER ISLAND, NS, Canada | 44.29N | 66.35W | 16 | -4.00 (NAA) | 94-06 | 719880 | -15.2 |  | -21.5 | 26.5 | 20.5 | 22.6 | 22.4 | 22 | 21.8333 |  | 18.1 | 20.5 | 20.6 | 20 | 19.7333 |  |  | CanadaNova ScotiaBRIER ISLAND
Canada | Nova Scotia | CARIBOU POINT (AUT) | CARIBOU POINT (AUT), NS, Canada | 45.77N | 62.68W | 2 | -4.00 (NAA) | 94-06 | 714150 | -21.8 |  | -29.2 | 35 | 28.2 | 29.5 | 30.1 | 29 | 29.2667 |  | 25.1 | 27.1 | 27.2 | 26 | 26.4667 |  |  | CanadaNova ScotiaCARIBOU POINT (AUT)
Canada | Nova Scotia | GRAND ETANG | GRAND ETANG, NS, Canada | 46.55N | 61.05W | 13 | -4.00 (NAA) | 94-06 | 715970 | -18.2 |  | -26.6 | 32.9 | 26.1 | 28.5 | 28.4 | 28 | 27.6667 |  | 24.2 | 26.7 | 26.5 | 26 | 25.8 |  |  | CanadaNova ScotiaGRAND ETANG
Canada | Nova Scotia | GREENWOOD A | GREENWOOD A, NS, Canada | 44.98N | 64.92W | 28 | -4.00 (NAA) | 82-06 | 713970 | -23.1 |  | -32.6 | 35.4 | 30.1 | 30.9 | 31 | 31 | 30.6667 |  | 27.3 | 28.8 | 28.7 | 28 | 28.2667 |  |  | CanadaNova ScotiaGREENWOOD A
Canada | Nova Scotia | HALIFAX STANFIELD INT'L A | HALIFAX STANFIELD INT'L A, NS, Canada | 44.88N | 63.52W | 145 | -4.00 (NAA) | 82-06 | 713950 | -21.9 |  | -29.2 | 35.3 | 29.4 | 29.3 | 29.7 | 29 | 29.4667 |  | 26 | 27.3 | 27.4 | 27 | 26.9 |  |  | CanadaNova ScotiaHALIFAX STANFIELD INT'L A
Canada | Nova Scotia | HART ISLAND (AUT) | HART ISLAND (AUT), NS, Canada | 45.35N | 60.98W | 8 | -4.00 (NAA) | 94-06 | 714190 | -17.3 |  | -25.3 | 30.1 | 22.1 | 24.2 | 24.9 | 24 | 23.7333 |  | 19.8 | 22.2 | 22.8 | 22 | 21.6 |  |  | CanadaNova ScotiaHART ISLAND (AUT)
Canada | Nova Scotia | KEJIMKUJIK 1 | KEJIMKUJIK 1, NS, Canada | 44.43N | 65.20W | 165 | -4.00 (NAA) | 94-06 | 715990 | -21.5 |  | -27.3 | 36 | 31 | 30.8 | 31.1 | 31 | 30.9667 |  | 28.1 | 28.8 | 28.5 | 28 | 28.4667 |  |  | CanadaNova ScotiaKEJIMKUJIK 1
Canada | Nova Scotia | SABLE ISLAND | SABLE ISLAND, NS, Canada | 43.93N | 60.01W | 5 | -4.00 (NAA) | 82-06 | 716000 | -12 |  | -17 | 26.7 | 17.7 | 21.6 | 23.6 | 21 | 20.9667 |  | 16.4 | 20.2 | 22.2 | 20 | 19.6 |  |  | CanadaNova ScotiaSABLE ISLAND
Canada | Nova Scotia | SHEARWATER A | SHEARWATER A, NS, Canada | 44.63N | 63.50W | 51 | -4.00 (NAA) | 82-05 | 716010 | -20.6 |  | -28.1 | 34.1 | 27.7 | 28.3 | 27.7 | 28 | 27.9 |  | 24.2 | 25.7 | 25.7 | 25 | 25.2 |  |  | CanadaNova ScotiaSHEARWATER A
Canada | Nova Scotia | SHEARWATER JETTY | SHEARWATER JETTY, NS, Canada | 44.63N | 63.52W | 6 | -4.00 (NAA) | 94-06 | CAN35X | N/A |  | N/A | N/A | 27.2 | 27.6 | 27.5 | 27 | 27.4333 |  | 24 | 25.4 | 25.7 | 25 | 25.0333 |  |  | CanadaNova ScotiaSHEARWATER JETTY
Canada | Nova Scotia | ST PAUL ISLAND (AUT) | ST PAUL ISLAND (AUT), NS, Canada | 47.23N | 60.14W | 27 | -4.00 (NAA) | 94-06 | 714180 | -16.6 |  | -26.1 | 29.4 | 21.6 | 23.6 | 25 | 23 | 23.4 |  | 19.1 | 22.1 | 22.9 | 21 | 21.3667 |  |  | CanadaNova ScotiaST PAUL ISLAND (AUT)
Canada | Nova Scotia | SYDNEY A | SYDNEY A, NS, Canada | 46.17N | 60.05W | 62 | -4.00 (NAA) | 82-06 | 717070 | -20.9 |  | -29.7 | 34.7 | 28 | 29.3 | 29.7 | 29 | 29 |  | 25.4 | 27.2 | 27.1 | 27 | 26.5667 |  |  | CanadaNova ScotiaSYDNEY A
Canada | Nova Scotia | WESTERN HEAD | WESTERN HEAD, NS, Canada | 43.99N | 64.66W | 10 | -4.00 (NAA) | 87-06 | 714110 | -19.4 |  | -27 | 36.1 | 27.3 | 29 | 26.8 | 28 | 27.7 |  | 22.9 | 24.7 | 23.1 | 24 | 23.5667 |  |  | CanadaNova ScotiaWESTERN HEAD
Canada | Nova Scotia | YARMOUTH A | YARMOUTH A, NS, Canada | 43.83N | 66.09W | 43 | -4.00 (NAA) | 82-06 | 716030 | -17.1 |  | -23 | 29.2 | 23.1 | 24.8 | 25.1 | 24 | 24.3333 |  | 21 | 22.8 | 23.2 | 22 | 22.3333 |  |  | CanadaNova ScotiaYARMOUTH A
Canada | Nunavut | ALERT | ALERT, NU, Canada | 82.52N | 62.28W | 30 | -5.00 (NAE) | 82-06 | 710820 | -44.8 |  | -49.4 | 21.7 | 9.4 | 14.6 | 14.3 | 13 | 12.7667 |  | 6.9 | 12.9 | 10.8 | 10 | 10.2 |  |  | CanadaNunavutALERT
Canada | Nunavut | BAKER LAKE A | BAKER LAKE A, NU, Canada | 64.30N | 96.08W | 18 | -6.00 (NAC) | 82-06 | 719260 | -43.7 |  | -49.9 | 33.2 | 23.1 | 26.4 | 24.2 | 25 | 24.5667 |  | 17.1 | 23.6 | 20.3 | 20 | 20.3333 |  |  | CanadaNunavutBAKER LAKE A
Canada | Nunavut | BREVOORT ISLAND | BREVOORT ISLAND, NU, Canada | 63.34N | 64.15W | 376 | -5.00 (NAE) | 89-06 | 710970 | -33.5 |  | -40.2 | 22.7 | 10.2 | 18.4 | 16.2 | 15 | 14.9333 |  | 8.2 | 15.6 | 13.5 | 12 | 12.4333 |  |  | CanadaNunavutBREVOORT ISLAND
Canada | Nunavut | BYRON BAY A | BYRON BAY A, NU, Canada | 68.75N | 109.07W | 92 | -7.00 (NAM) | 82-93 | 719290 | -43.2 |  | -46.5 | 26.2 | 17.6 | 21.2 | 18.7 | 19 | 19.1667 |  | 14.8 | 18.1 | 16.2 | 16 | 16.3667 |  |  | CanadaNunavutBYRON BAY A
Canada | Nunavut | CAMBRIDGE BAY A | CAMBRIDGE BAY A, NU, Canada | 69.11N | 105.14W | 27 | -7.00 (NAM) | 82-06 | 719250 | -44.1 |  | -48.8 | 27.8 | 17.1 | 21.5 | 18.8 | 19 | 19.1333 |  | 13.4 | 18.3 | 15.4 | 16 | 15.7 |  |  | CanadaNunavutCAMBRIDGE BAY A
Canada | Nunavut | CAPE DORSET A | CAPE DORSET A, NU, Canada | 64.23N | 76.53W | 50 | -5.00 (NAE) | 82-06 | 719100 | -35.7 |  | -41.3 | 24.2 | 13.7 | 19.1 | 15.8 | 16 | 16.2 |  | 11.2 | 16.7 | 13.6 | 14 | 13.8333 |  |  | CanadaNunavutCAPE DORSET A
Canada | Nunavut | CAPE DYER | CAPE DYER, NU, Canada | 66.65N | 61.38W | 725 | -5.00 (NAE) | 82-06 | 710940 | -39.9 |  | -50.7 | 20.8 | 10.9 | 16.2 | 14.1 | 14 | 13.7333 |  | 8.8 | 14 | 11.6 | 11 | 11.4667 |  |  | CanadaNunavutCAPE DYER
Canada | Nunavut | CAPE HOOPER | CAPE HOOPER, NU, Canada | 68.47N | 66.82W | 390 | -5.00 (NAE) | 82-06 | 710930 | -37.1 |  | -43.7 | 21 | 11.1 | 17.4 | 14.8 | 14 | 14.4333 |  | 9.4 | 15.2 | 11.8 | 12 | 12.1333 |  |  | CanadaNunavutCAPE HOOPER
Canada | Nunavut | CAPE MERCY | CAPE MERCY, NU, Canada | 64.96N | 63.58W | 583 | -5.00 (NAE) | 94-06 | 719750 | N/A |  | N/A | N/A | 11.6 | 17.4 | 14.6 | 15 | 14.5333 |  | 7.7 | 14.1 | 11.3 | 11 | 11.0333 |  |  | CanadaNunavutCAPE MERCY
Canada | Nunavut | CAPE PEEL WEST | CAPE PEEL WEST, NU, Canada | 69.04N | 107.82W | 165 | -7.00 (NAM) | 94-06 | 710640 | N/A |  | N/A | N/A | 20 | 22.9 | 21 | 21 | 21.3 |  | 16.5 | 20.4 | 17.7 | 18 | 18.2 |  |  | CanadaNunavutCAPE PEEL WEST
Canada | Nunavut | CLINTON POINT | CLINTON POINT, NU, Canada | 69.58N | 120.80W | 101 | -7.00 (NAM) | 82-93 | 710530 | -38.9 |  | -45.1 | 30.4 | 19.6 | 22.9 | 21.3 | 21 | 21.2667 |  | 16.6 | 19.8 | 17.5 | 18 | 17.9667 |  |  | CanadaNunavutCLINTON POINT
Canada | Nunavut | CLYDE A | CLYDE A, NU, Canada | 70.49N | 68.52W | 27 | -5.00 (NAE) | 82-06 | 710900 | -42.9 |  | -48.5 | 23 | 10.4 | 17.2 | 14.8 | 14 | 14.1333 |  | 8.1 | 14.5 | 12.1 | 12 | 11.5667 |  |  | CanadaNunavutCLYDE A
Canada | Nunavut | CORAL HARBOUR A | CORAL HARBOUR A, NU, Canada | 64.19N | 83.36W | 64 | -5.00 (NAE) | 82-06 | 719150 | -43.4 |  | -49.4 | 28.6 | 17.1 | 24 | 20.2 | 20 | 20.4333 |  | 13.5 | 20.4 | 16.6 | 17 | 16.8333 |  |  | CanadaNunavutCORAL HARBOUR A
Canada | Nunavut | CROKER RIVER | CROKER RIVER, NU, Canada | 69.28N | 119.22W | 69 | -7.00 (NAM) | 94-06 | 710590 | -37.9 |  | -42.3 | 31.2 | 24 | 26.1 | 22.7 | 24 | 24.2667 |  | 19.1 | 22.2 | 19.6 | 20 | 20.3 |  |  | CanadaNunavutCROKER RIVER
Canada | Nunavut | DEWAR LAKES | DEWAR LAKES, NU, Canada | 68.65N | 71.17W | 527 | -5.00 (NAE) | 82-06 | 710920 | -42.8 |  | -49.6 | 22.6 | 12.2 | 18.4 | 14.3 | 15 | 14.9667 |  | 9.6 | 16.4 | 11.7 | 13 | 12.5667 |  |  | CanadaNunavutDEWAR LAKES
Canada | Nunavut | ENNADAI LAKE (AUT) | ENNADAI LAKE (AUT), NU, Canada | 61.13N | 100.88W | 353 | -6.00 (NAC) | 94-06 | 719230 | N/A |  | N/A | N/A | 25.1 | 27.1 | 24.7 | 26 | 25.6333 |  | 22.3 | 25 | 21.7 | 23 | 23 |  |  | CanadaNunavutENNADAI LAKE (AUT)
Canada | Nunavut | EUREKA | EUREKA, NU, Canada | 79.98N | 85.93W | 10 | -6.00 (NAC) | 82-06 | 719170 | -49.3 |  | -54 | 21.2 | 12.9 | 15.6 | 11.9 | 13 | 13.4667 |  | 9.8 | 12.6 | 9.6 | 11 | 10.6667 |  |  | CanadaNunavutEUREKA
Canada | Nunavut | FOX FIVE | FOX FIVE, NU, Canada | 67.54N | 63.79W | 584 | -5.00 (NAE) | 82-06 | 710960 | -36.4 |  | -42.5 | 21.1 | 11.2 | 17.2 | 15.4 | 15 | 14.6 |  | 9.2 | 15 | 12.4 | 12 | 12.2 |  |  | CanadaNunavutFOX FIVE
Canada | Nunavut | GLADMAN POINT A | GLADMAN POINT A, NU, Canada | 68.67N | 97.80W | 14 | -7.00 (NAM) | 82-92 | 719270 | -46.1 |  | -51.9 | 24.7 | 14.9 | 19.6 | 16.7 | 17 | 17.0667 |  | 11.2 | 16.5 | 13.2 | 14 | 13.6333 |  |  | CanadaNunavutGLADMAN POINT A
Canada | Nunavut | HALL BEACH A | HALL BEACH A, NU, Canada | 68.78N | 81.24W | 8 | -5.00 (NAE) | 82-06 | 710810 | -45.8 |  | -50.8 | 25.3 | 11.1 | 18.1 | 15.7 | 15 | 14.9667 |  | 8.4 | 15.3 | 12.1 | 12 | 11.9333 |  |  | CanadaNunavutHALL BEACH A
Canada | Nunavut | HAT ISLAND | HAT ISLAND, NU, Canada | 68.32N | 100.09W | 36 | -7.00 (NAM) | 94-06 | 710840 | -42.9 |  | -48.8 | 25.6 | 15.3 | 19.8 | 16.9 | 17 | 17.3333 |  | 10.9 | 16.4 | 13.6 | 14 | 13.6333 |  |  | CanadaNunavutHAT ISLAND
Canada | Nunavut | IQALUIT A | IQALUIT A, NU, Canada | 63.75N | 68.55W | 34 | -5.00 (NAE) | 82-06 | 719090 | -41.6 |  | -47.8 | 26.9 | 15.2 | 21.2 | 18.3 | 18 | 18.2333 |  | 11.9 | 18 | 15 | 15 | 14.9667 |  |  | CanadaNunavutIQALUIT A
Canada | Nunavut | JENNY LIND ISLAND A | JENNY LIND ISLAND A, NU, Canada | 68.65N | 101.73W | 18 | -7.00 (NAM) | 82-92 | 710710 | -43.9 |  | -47.9 | 21.8 | 13.4 | 16.2 | 15.8 | 15 | 15.1333 |  | 10.9 | 14 | 13.2 | 13 | 12.7 |  |  | CanadaNunavutJENNY LIND ISLAND A
Canada | Nunavut | KUGLUKTUK A | KUGLUKTUK A, NU, Canada | 67.82N | 115.14W | 23 | -7.00 (NAM) | 82-06 | 719380 | -43.1 |  | -47.6 | 34.6 | 24.3 | 28 | 25.1 | 26 | 25.8 |  | 20.2 | 24 | 21.4 | 22 | 21.8667 |  |  | CanadaNunavutKUGLUKTUK A
Canada | Nunavut | LADY FRANKLIN POINT A | LADY FRANKLIN POINT A, NU, Canada | 68.50N | 113.22W | 16 | -7.00 (NAM) | 82-99 | 719370 | -40.8 |  | -46.8 | 23 | 13.9 | 17.5 | 15.8 | 16 | 15.7333 |  | 11.1 | 15.1 | 13.4 | 13 | 13.2 |  |  | CanadaNunavutLADY FRANKLIN POINT A
Canada | Nunavut | LONGSTAFF BLUFF | LONGSTAFF BLUFF, NU, Canada | 68.90N | 75.14W | 161 | -5.00 (NAE) | 82-06 | 710910 | -43.6 |  | -48.9 | 23.6 | 13.3 | 18.1 | 14.7 | 15 | 15.3667 |  | 11 | 16.2 | 12.2 | 13 | 13.1333 |  |  | CanadaNunavutLONGSTAFF BLUFF
Canada | Nunavut | MACKAR INLET | MACKAR INLET, NU, Canada | 68.30N | 85.67W | 395 | -6.00 (NAC) | 82-92 | 710800 | -45 |  | -50 | 23 | 12.7 | 18.4 | 18.1 | 16 | 16.4 |  | 10.8 | 16.6 | 13.9 | 14 | 13.7667 |  |  | CanadaNunavutMACKAR INLET
Canada | Nunavut | PANGNIRTUNG | PANGNIRTUNG, NU, Canada | 66.15N | 65.72W | 23 | -5.00 (NAE) | 94-06 | 718260 | N/A |  | N/A | N/A | 13.7 | 17.9 | 17 | 16 | 16.2 |  | 11.4 | 14.8 | 14 | 13 | 13.4 |  |  | CanadaNunavutPANGNIRTUNG
Canada | Nunavut | PELLY BAY | PELLY BAY, NU, Canada | 68.43N | 89.72W | 326 | -6.00 (NAC) | 82-92 | 719190 | -45.5 |  | -50 | 27.2 | 15.1 | 20.3 | 19.1 | 18 | 18.1667 |  | 12.3 | 17.6 | 14.9 | 15 | 14.9333 |  |  | CanadaNunavutPELLY BAY
Canada | Nunavut | POND INLET A | POND INLET A, NU, Canada | 72.68N | 77.98W | 55 | -5.00 (NAE) | 82-06 | 710950 | -44.5 |  | -50.1 | 23 | 12.1 | 17.5 | 13.5 | 14 | 14.3667 |  | 9.6 | 14.6 | 11.2 | 12 | 11.8 |  |  | CanadaNunavutPOND INLET A
Canada | Nunavut | RANKIN INLET A | RANKIN INLET A, NU, Canada | 62.82N | 92.12W | 29 | -6.00 (NAC) | 82-06 | 710830 | -43 |  | -49.2 | 30.7 | 19.7 | 24.6 | 21.8 | 22 | 22.0333 |  | 15 | 21.7 | 18.7 | 18 | 18.4667 |  |  | CanadaNunavutRANKIN INLET A
Canada | Nunavut | RESOLUTE CARS | RESOLUTE CARS, NU, Canada | 74.72N | 94.99W | 66 | -6.00 (NAC) | 82-06 | 719240 | -44.5 |  | -49.5 | 18.9 | 9.5 | 13.8 | 11.7 | 12 | 11.6667 |  | 7.1 | 11.9 | 8.9 | 9 | 9.3 |  |  | CanadaNunavutRESOLUTE CARS
Canada | Nunavut | RESOLUTION ISLAND | RESOLUTION ISLAND, NU, Canada | 61.60N | 64.63W | 369 | -5.00 (NAE) | 94-06 | 719720 | N/A |  | N/A | N/A | 10.4 | 19 | 16.2 | 15 | 15.2 |  | 8 | 15.8 | 13.6 | 12 | 12.4667 |  |  | CanadaNunavutRESOLUTION ISLAND
Canada | Nunavut | ROBERTSON LAKE (AUT) | ROBERTSON LAKE (AUT), NU, Canada | 65.10N | 102.43W | 244 | -7.00 (NAM) | 94-06 | 714900 | -43.3 |  | -47 | 34.7 | 23.8 | 27.4 | 24.5 | 25 | 25.2333 |  | 19.7 | 24.9 | 20.6 | 22 | 21.7333 |  |  | CanadaNunavutROBERTSON LAKE (AUT)
Canada | Nunavut | SHEPHERD BAY A | SHEPHERD BAY A, NU, Canada | 68.82N | 93.43W | 43 | -7.00 (NAM) | 82-06 | 719110 | -49.3 |  | -54.7 | 27.8 | 17.1 | 21.5 | 18.6 | 19 | 19.0667 |  | 12.7 | 19 | 15.4 | 16 | 15.7 |  |  | CanadaNunavutSHEPHERD BAY A
Canada | Ontario | ARMSTRONG (AUT) | ARMSTRONG (AUT), ON, Canada | 50.29N | 88.91W | 323 | -5.00 (NAE) | 94-06 | 718410 | N/A |  | N/A | N/A | 29.8 | 31.2 | 30.5 | 31 | 30.5 |  | 27.5 | 28.7 | 27.7 | 28 | 27.9667 |  |  | CanadaOntarioARMSTRONG (AUT)
Canada | Ontario | ATIKOKAN (AUT) | ATIKOKAN (AUT), ON, Canada | 48.76N | 91.63W | 389 | -6.00 (NAC) | 94-06 | 717470 | -35.9 |  | -45.7 | 37.6 | 32.1 | 31.6 | 30.7 | 31 | 31.4667 |  | 28.7 | 29 | 28.1 | 29 | 28.6 |  |  | CanadaOntarioATIKOKAN (AUT)
Canada | Ontario | BANCROFT AUTO | BANCROFT AUTO, ON, Canada | 45.07N | 77.88W | 331 | -5.00 (NAE) | 95-06 | 712940 | -33.3 |  | -42.3 | 37.6 | 31 | 31.7 | 31.7 | 31 | 31.4667 |  | 28.8 | 29.5 | 28.5 | 29 | 28.9333 |  |  | CanadaOntarioBANCROFT AUTO
Canada | Ontario | BEAUSOLEIL | BEAUSOLEIL, ON, Canada | 44.85N | 79.87W | 183 | -5.00 (NAE) | 94-06 | 712720 | -28.1 |  | -40.3 | 37.4 | 31.5 | 31.8 | 32.6 | 32 | 31.9667 |  | 29.1 | 29.7 | 29.1 | 29 | 29.3 |  |  | CanadaOntarioBEAUSOLEIL
Canada | Ontario | BELLE RIVER | BELLE RIVER, ON, Canada | 42.30N | 82.70W | 184 | -5.00 (NAE) | 94-05 | 712730 | -16.7 |  | -25.5 | 40.3 | 33.5 | 34.2 | 32.2 | 33 | 33.3 |  | 31.5 | 31.8 | 29.8 | 31 | 31.0333 |  |  | CanadaOntarioBELLE RIVER
Canada | Ontario | BIG TROUT LAKE | BIG TROUT LAKE, ON, Canada | 53.83N | 89.87W | 224 | -6.00 (NAC) | 82-91 | 718480 | -40.4 |  | -45.7 | 34.2 | 27.2 | 28.3 | 29.5 | 28 | 28.3333 |  | 24.5 | 26.3 | 26.5 | 26 | 25.7667 |  |  | CanadaOntarioBIG TROUT LAKE
Canada | Ontario | BIG TROUT LAKE READAC | BIG TROUT LAKE READAC, ON, Canada | 53.82N | 89.90W | 222 | -6.00 (NAC) | 94-06 | 718440 | -41 |  | -48.8 | 37.2 | 29.6 | 29.6 | 29.3 | 30 | 29.5 |  | 26.5 | 26.9 | 26.7 | 27 | 26.7 |  |  | CanadaOntarioBIG TROUT LAKE READAC
Canada | Ontario | BURLINGTON PIERS (AUT) | BURLINGTON PIERS (AUT), ON, Canada | 43.30N | 79.80W | 77 | -5.00 (NAE) | 94-06 | 714370 | -17.4 |  | -25.6 | 36.3 | 31.5 | 32.2 | 32.1 | 32 | 31.9333 |  | 29.6 | 30.4 | 29.1 | 30 | 29.7 |  |  | CanadaOntarioBURLINGTON PIERS (AUT)
Canada | Ontario | COBOURG (AUT) | COBOURG (AUT), ON, Canada | 43.95N | 78.17W | 78 | -5.00 (NAE) | 93-06 | 714310 | -22.3 |  | -32.3 | 35.9 | 25.8 | 28.6 | 27.2 | 27 | 27.2 |  | 23.9 | 25.8 | 25.7 | 25 | 25.1333 |  |  | CanadaOntarioCOBOURG (AUT)
Canada | Ontario | COLLINGWOOD | COLLINGWOOD, ON, Canada | 44.50N | 80.22W | 180 | -5.00 (NAE) | 94-06 | 712700 | -22.1 |  | -32 | 38 | 32.1 | 32 | 33.3 | 32 | 32.4667 |  | 29.2 | 29.5 | 29.6 | 29 | 29.4333 |  |  | CanadaOntarioCOLLINGWOOD
Canada | Ontario | COVE ISLAND (AUT) | COVE ISLAND (AUT), ON, Canada | 45.33N | 81.73W | 181 | -5.00 (NAE) | 94-06 | 714390 | -21 |  | -30.1 | 29.3 | 25.2 | 24.6 | 25.1 | 25 | 24.9667 |  | 22.6 | 23.4 | 23.5 | 23 | 23.1667 |  |  | CanadaOntarioCOVE ISLAND (AUT)
Canada | Ontario | EARLTON A | EARLTON A, ON, Canada | 47.70N | 79.85W | 243 | -5.00 (NAE) | 82-91 | 717350 | -36.9 |  | -46.5 | 37.6 | 31.1 | 32.6 | 29.4 | 31 | 31.0333 |  | 27.9 | 29.7 | 27.7 | 28 | 28.4333 |  |  | CanadaOntarioEARLTON A
Canada | Ontario | ERIEAU (AUT) | ERIEAU (AUT), ON, Canada | 42.25N | 81.90W | 178 | -5.00 (NAE) | 94-06 | 714650 | -16.9 |  | -24.5 | 34.9 | 27.4 | 28.6 | 27.8 | 28 | 27.9333 |  | 25 | 26.7 | 27 | 26 | 26.2333 |  |  | CanadaOntarioERIEAU (AUT)
Canada | Ontario | GERALDTON A | GERALDTON A, ON, Canada | 49.78N | 86.93W | 349 | -5.00 (NAE) | 82-06 | 718340 | -41 |  | -48.5 | 37 | 30 | 30.8 | 30.4 | 30 | 30.4 |  | 27.5 | 28.2 | 27.3 | 28 | 27.6667 |  |  | CanadaOntarioGERALDTON A
Canada | Ontario | GODERICH | GODERICH, ON, Canada | 43.77N | 81.72W | 214 | -5.00 (NAE) | 87-06 | 712610 | -20.5 |  | -28.9 | 34.1 | 30.2 | 30 | 30.1 | 30 | 30.1 |  | 28.1 | 28 | 27.5 | 28 | 27.8667 |  |  | CanadaOntarioGODERICH
Canada | Ontario | GORE BAY A | GORE BAY A, ON, Canada | 45.88N | 82.57W | 194 | -5.00 (NAE) | 82-05 | 717330 | -29.9 |  | -38.5 | 35.4 | 28.1 | 30.2 | 29.1 | 29 | 29.1333 |  | 25.9 | 27.7 | 26.8 | 27 | 26.8 |  |  | CanadaOntarioGORE BAY A
Canada | Ontario | GREAT DUCK ISLAND (AUT) | GREAT DUCK ISLAND (AUT), ON, Canada | 45.63N | 82.95W | 183 | -5.00 (NAE) | 94-06 | 714620 | N/A |  | N/A | N/A | 23.8 | 25.2 | 26.7 | 25 | 25.2333 |  | 22 | 24 | 24.8 | 24 | 23.6 |  |  | CanadaOntarioGREAT DUCK ISLAND (AUT)
Canada | Ontario | GRENADIER ISLAND | GRENADIER ISLAND, ON, Canada | 44.42N | 75.85W | 82 | -5.00 (NAE) | 94-06 | 712810 | -25.3 |  | -34.3 | 36.2 | 30.8 | 30.9 | 31.6 | 31 | 31.1 |  | 28.4 | 29.4 | 29.4 | 29 | 29.0667 |  |  | CanadaOntarioGRENADIER ISLAND
Canada | Ontario | KAPUSKASING A | KAPUSKASING A, ON, Canada | 49.41N | 82.47W | 227 | -5.00 (NAE) | 82-06 | 718310 | -38 |  | -45.8 | 37.6 | 31.6 | 31.9 | 30.2 | 31 | 31.2333 |  | 28.7 | 29.1 | 27.9 | 29 | 28.5667 |  |  | CanadaOntarioKAPUSKASING A
Canada | Ontario | KENORA A | KENORA A, ON, Canada | 49.79N | 94.37W | 410 | -6.00 (NAC) | 82-06 | 718500 | -34.9 |  | -42.2 | 37.8 | 31.7 | 31.3 | 31.4 | 31 | 31.4667 |  | 28.2 | 28.8 | 28.7 | 29 | 28.5667 |  |  | CanadaOntarioKENORA A
Canada | Ontario | KILLARNEY (AUT) | KILLARNEY (AUT), ON, Canada | 45.97N | 81.48W | 196 | -5.00 (NAE) | 94-06 | 714600 | -26.5 |  | -34.8 | 33.9 | 26 | 27.3 | 27.8 | 27 | 27.0333 |  | 23.7 | 25.2 | 24.8 | 25 | 24.5667 |  |  | CanadaOntarioKILLARNEY (AUT)
Canada | Ontario | LAGOON CITY | LAGOON CITY, ON, Canada | 44.55N | 79.22W | 221 | -5.00 (NAE) | 94-06 | 712820 | -27.8 |  | -37 | 37.2 | 28.9 | 29.7 | 29.2 | 29 | 29.2667 |  | 26.6 | 27.8 | 26.8 | 27 | 27.0667 |  |  | CanadaOntarioLAGOON CITY
Canada | Ontario | LANSDOWNE HOUSE (AUT) | LANSDOWNE HOUSE (AUT), ON, Canada | 52.20N | 87.94W | 253 | -5.00 (NAE) | 82-06 | 718460 | -41.1 |  | -48.6 | 39.1 | 30.8 | 30.1 | 29.5 | 30 | 30.1333 |  | 27.5 | 27.3 | 27.2 | 27 | 27.3333 |  |  | CanadaOntarioLANSDOWNE HOUSE (AUT)
Canada | Ontario | LONDON INT'L AIRPORT | LONDON INT'L AIRPORT, ON, Canada | 43.03N | 81.15W | 278 | -5.00 (NAE) | 82-06 | 716230 | -22.6 |  | -31.3 | 38.5 | 31.5 | 32.6 | 31.4 | 32 | 31.8333 |  | 29.3 | 30.3 | 29 | 30 | 29.5333 |  |  | CanadaOntarioLONDON INT'L AIRPORT
Canada | Ontario | LONG POINT (AUT) | LONG POINT (AUT), ON, Canada | 42.57N | 80.05W | 175 | -5.00 (NAE) | 94-06 | 714640 | N/A |  | N/A | N/A | 27.1 | 27.1 | 27.2 | 27 | 27.1333 |  | 25.2 | 25.8 | 26 | 26 | 25.6667 |  |  | CanadaOntarioLONG POINT (AUT)
Canada | Ontario | MOOSONEE A | MOOSONEE A, ON, Canada | 51.29N | 80.61W | 9 | -5.00 (NAE) | 94-06 | 718360 | -38.3 |  | -46.8 | 38.2 | 32.5 | 32 | 30.3 | 32 | 31.6 |  | 29.1 | 28.8 | 28.2 | 29 | 28.7 |  |  | CanadaOntarioMOOSONEE A
Canada | Ontario | MOUNT FOREST (AUT) | MOUNT FOREST (AUT), ON, Canada | 43.98N | 80.75W | 415 | -5.00 (NAE) | 94-06 | 716310 | -26.6 |  | -35.2 | 35.1 | 30.4 | 30.3 | 30.1 | 30 | 30.2667 |  | 28.5 | 28.5 | 27.6 | 28 | 28.2 |  |  | CanadaOntarioMOUNT FOREST (AUT)
Canada | Ontario | NAGAGAMI (AUT) | NAGAGAMI (AUT), ON, Canada | 49.75N | 84.16W | 264 | -5.00 (NAE) | 94-06 | 718320 | N/A |  | N/A | N/A | 31.6 | 32.7 | 30.9 | 32 | 31.7333 |  | 28.7 | 29.2 | 28.3 | 29 | 28.7333 |  |  | CanadaOntarioNAGAGAMI (AUT)
Canada | Ontario | NORTH BAY A | NORTH BAY A, ON, Canada | 46.36N | 79.42W | 370 | -5.00 (NAE) | 82-06 | 717310 | -31.8 |  | -40.3 | 35.9 | 29.3 | 30.5 | 29.1 | 30 | 29.6333 |  | 27.2 | 27.9 | 26.6 | 27 | 27.2333 |  |  | CanadaOntarioNORTH BAY A
Canada | Ontario | OTTAWA MACDONALD-CARTIER INT' | OTTAWA MACDONALD-CARTIER INT', ON, Canada | 45.32N | 75.67W | 114 | -5.00 (NAE) | 82-06 | 716280 | -27.3 |  | -35 | 37.9 | 32.3 | 32.7 | 32.2 | 32 | 32.4 |  | 29.9 | 30.5 | 29.6 | 30 | 30 |  |  | CanadaOntarioOTTAWA MACDONALD-CARTIER INT'
Canada | Ontario | PEAWANUCK (AUT) | PEAWANUCK (AUT), ON, Canada | 54.98N | 85.43W | 53 | -5.00 (NAE) | 94-06 | 714340 | -40.2 |  | -47.3 | 39.1 | 30.2 | 31 | 31.4 | 31 | 30.8667 |  | 27.1 | 28 | 27.5 | 28 | 27.5333 |  |  | CanadaOntarioPEAWANUCK (AUT)
Canada | Ontario | PETAWAWA A | PETAWAWA A, ON, Canada | 45.95N | 77.32W | 130 | -5.00 (NAE) | 82-06 | 716250 | -34.3 |  | -43.4 | 37.8 | 32.1 | 33.1 | 32.2 | 32 | 32.4667 |  | 29.4 | 30.5 | 29.4 | 30 | 29.7667 |  |  | CanadaOntarioPETAWAWA A
Canada | Ontario | PETERBOROUGH A | PETERBOROUGH A, ON, Canada | 44.23N | 78.37W | 191 | -5.00 (NAE) | 96-04 | 716290 | -28 |  | -38.7 | 38 | 30.4 | 31.9 | 32 | 31 | 31.4333 |  | 28.7 | 29.6 | 28.6 | 29 | 28.9667 |  |  | CanadaOntarioPETERBOROUGH A
Canada | Ontario | PICKLE LAKE (AUT) | PICKLE LAKE (AUT), ON, Canada | 51.45N | 90.22W | 391 | -6.00 (NAC) | 82-06 | 718350 | -38.2 |  | -46.8 | 38.6 | 31.5 | 31.3 | 30.5 | 31 | 31.1 |  | 28 | 28.1 | 27.7 | 28 | 27.9333 |  |  | CanadaOntarioPICKLE LAKE (AUT)
Canada | Ontario | POINT PETRE (AUT) | POINT PETRE (AUT), ON, Canada | 43.83N | 77.15W | 79 | -5.00 (NAE) | 93-06 | 714300 | -22.7 |  | -32.5 | 33.6 | 25.4 | 27 | 27.9 | 27 | 26.7667 |  | 23.6 | 25.6 | 26.3 | 25 | 25.1667 |  |  | CanadaOntarioPOINT PETRE (AUT)
Canada | Ontario | PORT COLBORNE (AUT) | PORT COLBORNE (AUT), ON, Canada | 42.87N | 79.25W | 184 | -5.00 (NAE) | 94-06 | 714630 | N/A |  | N/A | N/A | 27 | 28 | 27.7 | 28 | 27.5667 |  | 24.8 | 25.6 | 26.1 | 26 | 25.5 |  |  | CanadaOntarioPORT COLBORNE (AUT)
Canada | Ontario | PORT WELLER (AUT) | PORT WELLER (AUT), ON, Canada | 43.25N | 79.22W | 79 | -5.00 (NAE) | 93-06 | 714320 | -14.1 |  | -21.2 | 36.9 | 30.3 | 31.5 | 31.8 | 31 | 31.2 |  | 27.8 | 29.3 | 28.9 | 29 | 28.6667 |  |  | CanadaOntarioPORT WELLER (AUT)
Canada | Ontario | PUKASKWA (AUT) | PUKASKWA (AUT), ON, Canada | 48.59N | 86.29W | 208 | -5.00 (NAE) | 94-06 | 717500 | -32.1 |  | -43 | 31.5 | 24.6 | 25.7 | 25.1 | 25 | 25.1333 |  | 20.8 | 22.8 | 22.4 | 22 | 22 |  |  | CanadaOntarioPUKASKWA (AUT)
Canada | Ontario | RED LAKE A | RED LAKE A, ON, Canada | 51.07N | 93.79W | 386 | -6.00 (NAC) | 82-93 | 718540 | -39.1 |  | -44.7 | 37.6 | 30.5 | 30.8 | 31.1 | 31 | 30.8 |  | 27.4 | 28.3 | 28.9 | 28 | 28.2 |  |  | CanadaOntarioRED LAKE A
Canada | Ontario | ROYAL ISLAND (AUT) | ROYAL ISLAND (AUT), ON, Canada | 49.47N | 94.76W | 329 | -6.00 (NAC) | 94-06 | CAN21X | N/A |  | N/A | N/A | 27.8 | 31.3 | 31.2 | 30 | 30.1 |  | 26.2 | 28.9 | 28.6 | 28 | 27.9 |  |  | CanadaOntarioROYAL ISLAND (AUT)
Canada | Ontario | SAULT STE MARIE A | SAULT STE MARIE A, ON, Canada | 46.48N | 84.51W | 192 | -5.00 (NAE) | 82-06 | 712600 | -30.2 |  | -40.8 | 36.1 | 29.9 | 31.5 | 29.5 | 30 | 30.3 |  | 27.2 | 28.7 | 27.2 | 28 | 27.7 |  |  | CanadaOntarioSAULT STE MARIE A
Canada | Ontario | SIOUX LOOKOUT A | SIOUX LOOKOUT A, ON, Canada | 50.12N | 91.90W | 383 | -6.00 (NAC) | 82-06 | 718420 | -38 |  | -45.4 | 38.3 | 32 | 31.4 | 31.1 | 32 | 31.5 |  | 28.4 | 28.8 | 28.7 | 29 | 28.6333 |  |  | CanadaOntarioSIOUX LOOKOUT A
Canada | Ontario | SUDBURY A | SUDBURY A, ON, Canada | 46.62N | 80.80W | 348 | -5.00 (NAE) | 82-06 | 717300 | -31.9 |  | -40.4 | 37.8 | 30.6 | 32.4 | 30.8 | 31 | 31.2667 |  | 28.4 | 29.4 | 28 | 29 | 28.6 |  |  | CanadaOntarioSUDBURY A
Canada | Ontario | THUNDER BAY A | THUNDER BAY A, ON, Canada | 48.37N | 89.33W | 199 | -5.00 (NAE) | 82-06 | 717490 | -34.2 |  | -42.8 | 39.3 | 31.3 | 31.5 | 31.2 | 31 | 31.3333 |  | 27.1 | 29.1 | 28.2 | 28 | 28.1333 |  |  | CanadaOntarioTHUNDER BAY A
Canada | Ontario | TIMMINS VICTOR POWER A | TIMMINS VICTOR POWER A, ON, Canada | 48.57N | 81.38W | 295 | -5.00 (NAE) | 82-06 | 717390 | -38.4 |  | -46.8 | 38.1 | 31.6 | 32.5 | 30.7 | 32 | 31.6 |  | 28.7 | 29.5 | 27.7 | 29 | 28.6333 |  |  | CanadaOntarioTIMMINS VICTOR POWER A
Canada | Ontario | TORONTO BUTTONVILLE A | TORONTO BUTTONVILLE A, ON, Canada | 43.86N | 79.37W | 198 | -5.00 (NAE) | 86-06 | 716390 | -24.3 |  | -34.3 | 39.5 | 33.3 | 34.1 | 33.6 | 34 | 33.6667 |  | 30.7 | 31.9 | 30.6 | 31 | 31.0667 |  |  | CanadaOntarioTORONTO BUTTONVILLE A
Canada | Ontario | TORONTO ISLAND A | TORONTO ISLAND A, ON, Canada | 43.63N | 79.40W | 77 | -5.00 (NAE) | 94-06 | 712650 | -20 |  | -27.8 | 37.7 | 30.1 | 31.4 | 30 | 31 | 30.5 |  | 26.8 | 28.7 | 27.7 | 28 | 27.7333 |  |  | CanadaOntarioTORONTO ISLAND A
Canada | Ontario | TORONTO LESTER B. PEARSON INT | TORONTO LESTER B. PEARSON INT, ON, Canada | 43.68N | 79.63W | 173 | -5.00 (NAE) | 82-06 | 716240 | -22.2 |  | -30.8 | 38.9 | 32.5 | 34.1 | 33.1 | 33 | 33.2333 |  | 30 | 31.5 | 30.1 | 31 | 30.5333 |  |  | CanadaOntarioTORONTO LESTER B. PEARSON INT
Canada | Ontario | TRENTON A | TRENTON A, ON, Canada | 44.12N | 77.53W | 86 | -5.00 (NAE) | 82-06 | 716210 | -25.9 |  | -35.6 | 36.7 | 30 | 31.4 | 30.9 | 31 | 30.7667 |  | 28 | 29.5 | 28.6 | 29 | 28.7 |  |  | CanadaOntarioTRENTON A
Canada | Ontario | UPSALA (AUT) | UPSALA (AUT), ON, Canada | 49.03N | 90.47W | 489 | -5.00 (NAE) | 94-06 | 714350 | N/A |  | N/A | N/A | 30.9 | 30.9 | 30.1 | 31 | 30.6333 |  | 28 | 28.4 | 27.1 | 28 | 27.8333 |  |  | CanadaOntarioUPSALA (AUT)
Canada | Ontario | WAWA (AUT) | WAWA (AUT), ON, Canada | 47.97N | 84.78W | 287 | -5.00 (NAE) | 94-06 | 717380 | -35.7 |  | -43.6 | 32.8 | 27.3 | 27.5 | 27.1 | 27 | 27.3 |  | 24.8 | 25.3 | 24.6 | 25 | 24.9 |  |  | CanadaOntarioWAWA (AUT)
Canada | Ontario | WELCOME ISLAND (AUT) | WELCOME ISLAND (AUT), ON, Canada | 48.37N | 89.12W | 211 | -5.00 (NAE) | 94-06 | 717510 | N/A |  | N/A | N/A | 24.8 | 27.4 | 26.5 | 26 | 26.2333 |  | 22.1 | 24.8 | 24.3 | 24 | 23.7333 |  |  | CanadaOntarioWELCOME ISLAND (AUT)
Canada | Ontario | WIARTON A | WIARTON A, ON, Canada | 44.75N | 81.11W | 222 | -5.00 (NAE) | 82-06 | 716330 | -23.8 |  | -33.8 | 34.7 | 29.6 | 30.4 | 30.5 | 30 | 30.1667 |  | 27.4 | 28.3 | 27.7 | 28 | 27.8 |  |  | CanadaOntarioWIARTON A
Canada | Ontario | WINDSOR A | WINDSOR A, ON, Canada | 42.28N | 82.96W | 190 | -5.00 (NAE) | 82-06 | 715380 | -19.5 |  | -30.3 | 39.3 | 33.3 | 34.5 | 33.1 | 34 | 33.6333 |  | 31.3 | 32.2 | 30.7 | 31 | 31.4 |  |  | CanadaOntarioWINDSOR A
Canada | Prince Edward Island | CHARLOTTETOWN A | CHARLOTTETOWN A, PE, Canada | 46.29N | 63.13W | 49 | -4.00 (NAA) | 82-06 | 717060 | -23.9 |  | -32 | 33.1 | 27.2 | 28.5 | 29 | 28 | 28.2333 |  | 25 | 26.6 | 26.7 | 26 | 26.1 |  |  | CanadaPrince Edward IslandCHARLOTTETOWN A
Canada | Prince Edward Island | EAST POINT (AUT) | EAST POINT (AUT), PE, Canada | 46.46N | 61.99W | 8 | -4.00 (NAA) | 94-06 | 714120 | -20.8 |  | -29.3 | 33.7 | 23.9 | 25.8 | 26.7 | 25 | 25.4667 |  | 21.3 | 23.8 | 24.6 | 23 | 23.2333 |  |  | CanadaPrince Edward IslandEAST POINT (AUT)
Canada | Prince Edward Island | NORTH CAPE | NORTH CAPE, PE, Canada | 47.06N | 64.00W | 8 | -4.00 (NAA) | 94-06 | 719870 | -20.8 |  | -28 | 34 | 26.1 | 28.3 | 28.5 | 28 | 27.6333 |  | 23.7 | 26 | 25.9 | 25 | 25.2 |  |  | CanadaPrince Edward IslandNORTH CAPE
Canada | Prince Edward Island | SUMMERSIDE | SUMMERSIDE, PE, Canada | 46.44N | 63.84W | 12 | -4.00 (NAA) | 82-06 | 717020 | -23.1 |  | -30.3 | 33.3 | 27.2 | 28.3 | 29 | 28 | 28.1667 |  | 24.8 | 26.7 | 26.6 | 26 | 26.0333 |  |  | CanadaPrince Edward IslandSUMMERSIDE
Canada | Quebec | AMQUI | AMQUI, QC, Canada | 48.47N | 67.43W | 166 | -5.00 (NAE) | 95-06 | 713860 | -31.6 |  | -37 | 35.8 | 31.4 | 29.5 | 30.7 | 31 | 30.5333 |  | 27.6 | 27.7 | 27.7 | 28 | 27.6667 |  |  | CanadaQuebecAMQUI
Canada | Quebec | BAGOTVILLE A | BAGOTVILLE A, QC, Canada | 48.33N | 71.00W | 159 | -5.00 (NAE) | 82-06 | 717270 | -33.5 |  | -39.8 | 37.6 | 32.1 | 31.7 | 30.2 | 31 | 31.3333 |  | 28.8 | 29.1 | 27.8 | 29 | 28.5667 |  |  | CanadaQuebecBAGOTVILLE A
Canada | Quebec | BAIE-COMEAU | BAIE-COMEAU, QC, Canada | 49.26N | 68.15W | 130 | -5.00 (NAE) | 97-06 | 718290 | -28.5 |  | -32.8 | 32 | 27.8 | 26.7 | 26.7 | 27 | 27.0667 |  | 24.8 | 24.8 | 24.7 | 25 | 24.7667 |  |  | CanadaQuebecBAIE-COMEAU
Canada | Quebec | BAIE-COMEAU A | BAIE-COMEAU A, QC, Canada | 49.13N | 68.20W | 22 | -5.00 (NAE) | 82-04 | 711870 | -32.1 |  | -38.8 | 32.4 | 25.2 | 26 | 26 | 26 | 25.7333 |  | 22.5 | 23.9 | 23.4 | 23 | 23.2667 |  |  | CanadaQuebecBAIE-COMEAU A
Canada | Quebec | BARRAGE TEMISCAMINGUE | BARRAGE TEMISCAMINGUE, QC, Canada | 46.71N | 79.10W | 181 | -5.00 (NAE) | 97-06 | 717320 | -28.9 |  | -35.2 | 37.4 | 30.7 | 32.6 | 31.8 | 32 | 31.7 |  | 28.8 | 29.9 | 28.9 | 29 | 29.2 |  |  | CanadaQuebecBARRAGE TEMISCAMINGUE
Canada | Quebec | BEAUCEVILLE | BEAUCEVILLE, QC, Canada | 46.20N | 70.78W | 229 | -5.00 (NAE) | 94-06 | 713230 | -31.7 |  | -41.9 | 35.8 | 31.2 | 30.4 | 29.7 | 30 | 30.4333 |  | 28.7 | 28.3 | 27.5 | 28 | 28.1667 |  |  | CanadaQuebecBEAUCEVILLE
Canada | Quebec | BLANC-SABLON A | BLANC-SABLON A, QC, Canada | 51.45N | 57.18W | 37 | -4.00 (NAA) | 82-06 | 718080 | -29 |  | -35.1 | 27 | 19.5 | 21.2 | 20.7 | 20 | 20.4667 |  | 16.3 | 18.6 | 18.7 | 18 | 17.8667 |  |  | CanadaQuebecBLANC-SABLON A
Canada | Quebec | BONNARD 1 | BONNARD 1, QC, Canada | 50.73N | 71.01W | 498 | -5.00 (NAE) | 94-06 | 713830 | -41.1 |  | -47.4 | 33.5 | 28.5 | 28.9 | 27.1 | 28 | 28.1667 |  | 25.7 | 25.7 | 24.8 | 25 | 25.4 |  |  | CanadaQuebecBONNARD 1
Canada | Quebec | CAP-CHAT | CAP-CHAT, QC, Canada | 49.11N | 66.65W | 5 | -5.00 (NAE) | 96-06 | 714280 | -24.3 |  | -30.3 | 33.1 | 25.2 | 24.6 | 24.6 | 25 | 24.8 |  | 21.2 | 22.5 | 22.1 | 22 | 21.9333 |  |  | CanadaQuebecCAP-CHAT
Canada | Quebec | CAP-D'ESPOIR | CAP-D'ESPOIR, QC, Canada | 48.42N | 64.32W | 15 | -5.00 (NAE) | 94-06 | 714290 | -24.3 |  | -28.9 | 30.9 | 21.6 | 23 | 23.7 | 23 | 22.7667 |  | 19.3 | 21.1 | 21.7 | 21 | 20.7 |  |  | CanadaQuebecCAP-D'ESPOIR
Canada | Quebec | CAP-MADELEINE | CAP-MADELEINE, QC, Canada | 49.25N | 65.32W | 29 | -5.00 (NAE) | 94-06 | 714250 | -23.7 |  | -28.6 | 34.4 | 25.4 | 26.6 | 25.6 | 26 | 25.8667 |  | 22.2 | 23.6 | 23.4 | 23 | 23.0667 |  |  | CanadaQuebecCAP-MADELEINE
Canada | Quebec | CAP-ROUGE | CAP-ROUGE, QC, Canada | 48.37N | 70.54W | 7 | -5.00 (NAE) | 94-06 | 711860 | -29.6 |  | -34.9 | 35.2 | 30.2 | 28.9 | 28.9 | 29 | 29.3333 |  | 27.2 | 26.7 | 26.5 | 27 | 26.8 |  |  | CanadaQuebecCAP-ROUGE
Canada | Quebec | CAP-TOURMENTE | CAP-TOURMENTE, QC, Canada | 47.08N | 70.78W | 6 | -5.00 (NAE) | 94-06 | 713840 | -28.1 |  | -35 | 36.3 | 30.5 | 30.6 | 30.3 | 30 | 30.4667 |  | 28.1 | 28.5 | 28.2 | 28 | 28.2667 |  |  | CanadaQuebecCAP-TOURMENTE
Canada | Quebec | CHARLEVOIX (MRC) | CHARLEVOIX (MRC), QC, Canada | 47.28N | 70.64W | 723 | -5.00 (NAE) | 97-06 | 713190 | N/A |  | N/A | N/A | 27.3 | 26.1 | 25.4 | 26 | 26.2667 |  | 24.6 | 23.8 | 23.3 | 24 | 23.9 |  |  | CanadaQuebecCHARLEVOIX (MRC)
Canada | Quebec | CHEVERY | CHEVERY, QC, Canada | 50.46N | 59.64W | 8 | -4.00 (NAA) | 94-06 | 718140 | -31.4 |  | -40.3 | 30.8 | 22 | 23.7 | 24.1 | 23 | 23.2667 |  | 18.1 | 19.9 | 20.9 | 20 | 19.6333 |  |  | CanadaQuebecCHEVERY
Canada | Quebec | CHIBOUGAMAU CHAPAIS A | CHIBOUGAMAU CHAPAIS A, QC, Canada | 49.77N | 74.53W | 387 | -5.00 (NAE) | 82-06 | 718220 | -39.4 |  | -45.2 | 34.3 | 30.7 | 30.3 | 27.9 | 30 | 29.6333 |  | 27.3 | 28.3 | 25.6 | 27 | 27.0667 |  |  | CanadaQuebecCHIBOUGAMAU CHAPAIS A
Canada | Quebec | CHUTE-DES-PASSES | CHUTE-DES-PASSES, QC, Canada | 49.84N | 71.17W | 398 | -5.00 (NAE) | 94-06 | 715220 | -35.9 |  | -43 | 35.9 | 30.3 | 28.7 | 28.4 | 29 | 29.1333 |  | 27.4 | 26.5 | 25.7 | 27 | 26.5333 |  |  | CanadaQuebecCHUTE-DES-PASSES
Canada | Quebec | DESCHAMBAULT | DESCHAMBAULT, QC, Canada | 46.69N | 71.97W | 61 | -5.00 (NAE) | 97-06 | 713890 | -33 |  | -40.5 | 36.1 | 31.5 | 30.7 | 29.8 | 31 | 30.6667 |  | 28.7 | 28.6 | 28 | 28 | 28.4333 |  |  | CanadaQuebecDESCHAMBAULT
Canada | Quebec | FRELIGHSBURG | FRELIGHSBURG, QC, Canada | 45.05N | 72.86W | 152 | -5.00 (NAE) | 94-06 | 713730 | -28 |  | -40 | 35.9 | 31.5 | 31 | 30.7 | 31 | 31.0667 |  | 29.2 | 29.2 | 28.6 | 29 | 29 |  |  | CanadaQuebecFRELIGHSBURG
Canada | Quebec | GASPE A | GASPE A, QC, Canada | 48.78N | 64.48W | 34 | -5.00 (NAE) | 82-06 | 711880 | -29.2 |  | -35 | 37.2 | 29.8 | 30.6 | 30 | 30 | 30.1333 |  | 26.2 | 27.6 | 27.1 | 27 | 26.9667 |  |  | CanadaQuebecGASPE A
Canada | Quebec | HAVRE-SAINT-PIERRE A | HAVRE-SAINT-PIERRE A, QC, Canada | 50.28N | 63.60W | 38 | -5.00 (NAE) | 94-06 | 713130 | -31.3 |  | -37.4 | 29.4 | 23.5 | 24.9 | 24.7 | 24 | 24.3667 |  | 21.2 | 22.9 | 22.4 | 22 | 22.1667 |  |  | CanadaQuebecHAVRE-SAINT-PIERRE A
Canada | Quebec | HEATH POINT | HEATH POINT, QC, Canada | 49.09N | 61.70W | 7 | -5.00 (NAE) | 94-06 | 714230 | -22.7 |  | -30.1 | 28.2 | 19.9 | 20.8 | 21.1 | 21 | 20.6 |  | 15.9 | 18.5 | 19.2 | 18 | 17.8667 |  |  | CanadaQuebecHEATH POINT
Canada | Quebec | ILE AUX PERROQUETS | ILE AUX PERROQUETS, QC, Canada | 50.22N | 64.21W | 9 | -5.00 (NAE) | 94-06 | 713750 | -24.4 |  | -30.2 | 25.2 | 16.7 | 18.7 | 18.1 | 18 | 17.8333 |  | 14.8 | 17.2 | 16.4 | 16 | 16.1333 |  |  | CanadaQuebecILE AUX PERROQUETS
Canada | Quebec | ILE ROUGE | ILE ROUGE, QC, Canada | 48.07N | 69.56W | 6 | -5.00 (NAE) | 94-06 | 714260 | -23.7 |  | -28.5 | 28 | 19.3 | 19.7 | 20 | 20 | 19.6667 |  | 16.9 | 17.9 | 17.8 | 18 | 17.5333 |  |  | CanadaQuebecILE ROUGE
Canada | Quebec | ILES DE LA MADELEINE | ILES DE LA MADELEINE, QC, Canada | 47.43N | 61.77W | 8 | -4.00 (NAA) | 93-06 | 717100 | -19.5 |  | -26.8 | 30.9 | 23.6 | 25 | 27.1 | 25 | 25.2333 |  | 21 | 23.5 | 24.2 | 23 | 22.9 |  |  | CanadaQuebecILES DE LA MADELEINE
Canada | Quebec | INUKJUAK A | INUKJUAK A, QC, Canada | 58.47N | 78.08W | 25 | -5.00 (NAE) | 82-06 | 719070 | -39.4 |  | -44 | 31.4 | 21.9 | 24.4 | 22.6 | 23 | 22.9667 |  | 18.1 | 21.2 | 18.6 | 19 | 19.3 |  |  | CanadaQuebecINUKJUAK A
Canada | Quebec | JONQUIERE | JONQUIERE, QC, Canada | 48.42N | 71.15W | 128 | -5.00 (NAE) | 94-06 | 716170 | -33.2 |  | -39.6 | 37.3 | 32.2 | 30.2 | 30.1 | 31 | 30.8333 |  | 29.2 | 28.3 | 27.7 | 28 | 28.4 |  |  | CanadaQuebecJONQUIERE
Canada | Quebec | KUUJJUAQ A | KUUJJUAQ A, QC, Canada | 58.10N | 68.42W | 39 | -5.00 (NAE) | 82-06 | 719060 | -40 |  | -45.6 | 33.9 | 26 | 27.1 | 26.3 | 26 | 26.4667 |  | 21.8 | 24.2 | 22.6 | 23 | 22.8667 |  |  | CanadaQuebecKUUJJUAQ A
Canada | Quebec | KUUJJUARAPIK A | KUUJJUARAPIK A, QC, Canada | 55.28N | 77.75W | 10 | -5.00 (NAE) | 82-06 | 719050 | -41.5 |  | -47.2 | 36.1 | 28.2 | 28.5 | 27.7 | 28 | 28.1333 |  | 23.4 | 24.6 | 24.1 | 24 | 24.0333 |  |  | CanadaQuebecKUUJJUARAPIK A
Canada | Quebec | LA BAIE | LA BAIE, QC, Canada | 48.30N | 70.92W | 152 | -5.00 (NAE) | 97-06 | 713880 | -34.5 |  | -38.9 | 37.8 | 32.2 | 30.7 | 30.1 | 31 | 31 |  | 29.1 | 28.3 | 27.8 | 28 | 28.4 |  |  | CanadaQuebecLA BAIE
Canada | Quebec | LA GRANDE IV A | LA GRANDE IV A, QC, Canada | 53.76N | 73.68W | 306 | -5.00 (NAE) | 85-05 | 718230 | -44.7 |  | -52.3 | 34.8 | 30.2 | 29.4 | 28 | 29 | 29.2 |  | 25.2 | 27 | 24.8 | 26 | 25.6667 |  |  | CanadaQuebecLA GRANDE IV A
Canada | Quebec | LA GRANDE RIVIERE A | LA GRANDE RIVIERE A, QC, Canada | 53.63N | 77.70W | 195 | -5.00 (NAE) | 82-06 | 718270 | -38.1 |  | -43.5 | 36.2 | 29.9 | 29.6 | 28.1 | 29 | 29.2 |  | 26.2 | 26.8 | 25.1 | 26 | 26.0333 |  |  | CanadaQuebecLA GRANDE RIVIERE A
Canada | Quebec | LA POCATIERE | LA POCATIERE, QC, Canada | 47.36N | 70.03W | 31 | -5.00 (NAE) | 96-06 | 717130 | -26.8 |  | -33.3 | 35.4 | 30.1 | 30 | 30.2 | 30 | 30.1 |  | 27.8 | 27.9 | 28 | 28 | 27.9 |  |  | CanadaQuebecLA POCATIERE
Canada | Quebec | LA TUQUE | LA TUQUE, QC, Canada | 47.41N | 72.79W | 169 | -5.00 (NAE) | 94-06 | 713780 | -35.3 |  | -42.9 | 39.4 | 33.5 | 32.3 | 31.4 | 32 | 32.4 |  | 30.7 | 29.4 | 28.8 | 30 | 29.6333 |  |  | CanadaQuebecLA TUQUE
Canada | Quebec | LAC BENOIT | LAC BENOIT, QC, Canada | 51.53N | 71.11W | 549 | -5.00 (NAE) | 94-06 | 715200 | -46.4 |  | -53.1 | 33.9 | 28.2 | 29.3 | 27.9 | 28 | 28.4667 |  | 25.3 | 26.2 | 25.1 | 26 | 25.5333 |  |  | CanadaQuebecLAC BENOIT
Canada | Quebec | LAC EON | LAC EON, QC, Canada | 51.87N | 63.28W | 589 | -5.00 (NAE) | 94-06 | 714210 | N/A |  | N/A | N/A | 28.4 | 32.7 | 28.4 | 30 | 29.8333 |  | 23.9 | 27.2 | 26.1 | 26 | 25.7333 |  |  | CanadaQuebecLAC EON
Canada | Quebec | LAC SAINT-PIERRE | LAC SAINT-PIERRE, QC, Canada | 46.18N | 72.92W | 16 | -5.00 (NAE) | 94-06 | 711980 | N/A |  | N/A | N/A | 29.5 | 29.6 | 28.7 | 29 | 29.2667 |  | 27.2 | 27.4 | 26.9 | 27 | 27.1667 |  |  | CanadaQuebecLAC SAINT-PIERRE
Canada | Quebec | L'ACADIE | L'ACADIE, QC, Canada | 45.29N | 73.35W | 44 | -5.00 (NAE) | 94-06 | 713720 | -26.9 |  | -36.5 | 36.9 | 32.5 | 31.4 | 31.1 | 32 | 31.6667 |  | 30.2 | 29.4 | 29.1 | 30 | 29.5667 |  |  | CanadaQuebecL'ACADIE
Canada | Quebec | L'ASSOMPTION | L'ASSOMPTION, QC, Canada | 45.81N | 73.43W | 21 | -5.00 (NAE) | 94-06 | 715240 | -29.8 |  | -40.2 | 37.1 | 32.3 | 31.7 | 31.6 | 32 | 31.8667 |  | 30.1 | 29.7 | 29.5 | 30 | 29.7667 |  |  | CanadaQuebecL'ASSOMPTION
Canada | Quebec | LENNOXVILLE | LENNOXVILLE, QC, Canada | 45.37N | 71.82W | 181 | -5.00 (NAE) | 96-06 | 716110 | -31.1 |  | -41.7 | 35.5 | 31.8 | 30.9 | 30.7 | 31 | 31.1333 |  | 29.1 | 28.9 | 28.6 | 29 | 28.8667 |  |  | CanadaQuebecLENNOXVILLE
Canada | Quebec | L'ETAPE | L'ETAPE, QC, Canada | 47.56N | 71.23W | 791 | -5.00 (NAE) | 94-06 | 713820 | -38.2 |  | -47 | 34 | 27.8 | 26.8 | 25.5 | 27 | 26.7 |  | 25.3 | 24.2 | 23.6 | 24 | 24.3667 |  |  | CanadaQuebecL'ETAPE
Canada | Quebec | LONGUE-POINTE-DE-MINGAN | LONGUE-POINTE-DE-MINGAN, QC, Canada | 50.27N | 64.23W | 11 | -5.00 (NAE) | 94-06 | 715120 | -31.7 |  | -38.6 | 33.6 | 22 | 23.3 | 22.9 | 23 | 22.7333 |  | 19.3 | 21.4 | 20.4 | 20 | 20.3667 |  |  | CanadaQuebecLONGUE-POINTE-DE-MINGAN
Canada | Quebec | MANIWAKI AIRPORT | MANIWAKI AIRPORT, QC, Canada | 46.27N | 75.99W | 200 | -5.00 (NAE) | 94-06 | 717210 | -31.6 |  | -39.8 | 37.9 | 32.6 | 32.2 | 31.4 | 32 | 32.0667 |  | 29.8 | 29.4 | 28.8 | 29 | 29.3333 |  |  | CanadaQuebecMANIWAKI AIRPORT
Canada | Quebec | MANIWAKI UA | MANIWAKI UA, QC, Canada | 46.30N | 76.01W | 192 | -5.00 (NAE) | 82-92 | 717220 | -35.2 |  | -42.7 | 37.2 | 31 | 32 | 29.2 | 31 | 30.7333 |  | 28.2 | 29.4 | 27.5 | 28 | 28.3667 |  |  | CanadaQuebecMANIWAKI UA
Canada | Quebec | MANOUANE EST | MANOUANE EST, QC, Canada | 50.66N | 70.53W | 497 | -5.00 (NAE) | 94-06 | 715210 | N/A |  | N/A | N/A | 28.2 | 28.4 | 27.6 | 28 | 28.0667 |  | 25.4 | 25.9 | 25 | 25 | 25.4333 |  |  | CanadaQuebecMANOUANE EST
Canada | Quebec | MATAGAMI A | MATAGAMI A, QC, Canada | 49.77N | 77.80W | 280 | -5.00 (NAE) | 94-06 | 718210 | -39.5 |  | -46.7 | 37.9 | 32.3 | 32.7 | 29.2 | 31 | 31.4 |  | 29.2 | 28.3 | 27.2 | 28 | 28.2333 |  |  | CanadaQuebecMATAGAMI A
Canada | Quebec | MCTAVISH | MCTAVISH, QC, Canada | 45.50N | 73.58W | 73 | -5.00 (NAE) | 94-06 | 716120 | -24.4 |  | -32.6 | 36.5 | 32 | 31.5 | 31.7 | 32 | 31.7333 |  | 29.6 | 29.6 | 29.4 | 30 | 29.5333 |  |  | CanadaQuebecMCTAVISH
Canada | Quebec | MISTOOK | MISTOOK, QC, Canada | 48.60N | 71.72W | 113 | -5.00 (NAE) | 94-06 | 713810 | -36.4 |  | -43.3 | 37.5 | 31.9 | 30.9 | 29.6 | 31 | 30.8 |  | 29.3 | 28.4 | 27.6 | 28 | 28.4333 |  |  | CanadaQuebecMISTOOK
Canada | Quebec | MONT-JOLI A | MONT-JOLI A, QC, Canada | 48.60N | 68.22W | 52 | -5.00 (NAE) | 82-06 | 717180 | -26.9 |  | -33.7 | 35.7 | 28.6 | 29 | 28.3 | 29 | 28.6333 |  | 25.6 | 26.7 | 25.9 | 26 | 26.0667 |  |  | CanadaQuebecMONT-JOLI A
Canada | Quebec | MONT-ORFORD | MONT-ORFORD, QC, Canada | 45.31N | 72.24W | 846 | -5.00 (NAE) | 94-06 | 716180 | -30 |  | -38.4 | 33.1 | 27.9 | 26.7 | 26.3 | 27 | 26.9667 |  | 25.1 | 24.4 | 24.1 | 25 | 24.5333 |  |  | CanadaQuebecMONT-ORFORD
Canada | Quebec | MONTREAL/MIRABEL INT'L A | MONTREAL/MIRABEL INT'L A, QC, Canada | 45.67N | 74.03W | 82 | -5.00 (NAE) | 82-06 | 716260 | -30.2 |  | -38.6 | 35.8 | 31.1 | 31.2 | 30.7 | 31 | 31 |  | 28.8 | 29.2 | 28.6 | 29 | 28.8667 |  |  | CanadaQuebecMONTREAL/MIRABEL INT'L A
Canada | Quebec | MONTREAL/PIERRE ELLIOTT TRUDE | MONTREAL/PIERRE ELLIOTT TRUDE, QC, Canada | 45.47N | 73.75W | 36 | -5.00 (NAE) | 82-06 | 716270 | -26.5 |  | -34.2 | 36.3 | 31.5 | 31.8 | 31.5 | 32 | 31.6 |  | 29.2 | 29.9 | 29.2 | 29 | 29.4333 |  |  | CanadaQuebecMONTREAL/PIERRE ELLIOTT TRUDE
Canada | Quebec | MONTREAL/ST-HUBERT A | MONTREAL/ST-HUBERT A, QC, Canada | 45.52N | 73.42W | 27 | -5.00 (NAE) | 82-04 | 713710 | -28 |  | -35.4 | 36.6 | 31.7 | 32.2 | 31.5 | 32 | 31.8 |  | 29.4 | 30 | 29.3 | 30 | 29.5667 |  |  | CanadaQuebecMONTREAL/ST-HUBERT A
Canada | Quebec | MONTREAL-EST | MONTREAL-EST, QC, Canada | 45.63N | 73.55W | 50 | -5.00 (NAE) | 94-06 | 716750 | -25.2 |  | -33.4 | 36.4 | 32.1 | 31.8 | 31.8 | 32 | 31.9 |  | 30.2 | 29.9 | 29.7 | 30 | 29.9333 |  |  | CanadaQuebecMONTREAL-EST
Canada | Quebec | NATASHQUAN A | NATASHQUAN A, QC, Canada | 50.18N | 61.82W | 11 | -5.00 (NAE) | 82-06 | 718130 | -31.6 |  | -39.5 | 29 | 21.9 | 23.7 | 23.4 | 23 | 23 |  | 19.1 | 21.6 | 21 | 21 | 20.5667 |  |  | CanadaQuebecNATASHQUAN A
Canada | Quebec | NEW CARLISLE 1 | NEW CARLISLE 1, QC, Canada | 48.01N | 65.33W | 46 | -5.00 (NAE) | 94-06 | 716190 | -24.8 |  | -29.6 | 35.2 | 28.1 | 28.2 | 29.3 | 29 | 28.5333 |  | 25.4 | 26 | 26 | 26 | 25.8 |  |  | CanadaQuebecNEW CARLISLE 1
Canada | Quebec | NICOLET | NICOLET, QC, Canada | 46.23N | 72.66W | 8 | -5.00 (NAE) | 94-06 | 717230 | -29.7 |  | -38.3 | 34.7 | 30.7 | 30.4 | 29.6 | 30 | 30.2333 |  | 28.6 | 28.6 | 27.4 | 28 | 28.2 |  |  | CanadaQuebecNICOLET
Canada | Quebec | NORMANDIN | NORMANDIN, QC, Canada | 48.84N | 72.55W | 137 | -5.00 (NAE) | 94-06 | 713790 | -37.9 |  | -44.4 | 39 | 32.4 | 30.8 | 29.8 | 31 | 31 |  | 28.7 | 28.2 | 27.6 | 28 | 28.1667 |  |  | CanadaQuebecNORMANDIN
Canada | Quebec | ONATCHIWAY | ONATCHIWAY, QC, Canada | 48.89N | 71.03W | 304 | -5.00 (NAE) | 97-06 | 713870 | -37.7 |  | -45.7 | 37.2 | 31.8 | 29.9 | 28.2 | 30 | 29.9667 |  | 28.7 | 27.8 | 26.3 | 28 | 27.6 |  |  | CanadaQuebecONATCHIWAY
Canada | Quebec | PARENT | PARENT, QC, Canada | 47.92N | 74.62W | 445 | -5.00 (NAE) | 94-06 | 717260 | -38.7 |  | -48.6 | 35.8 | 30.8 | 30.4 | 28.5 | 30 | 29.9 |  | 28.3 | 27.6 | 26.5 | 27 | 27.4667 |  |  | CanadaQuebecPARENT
Canada | Quebec | POINTE CLAVEAU | POINTE CLAVEAU, QC, Canada | 48.26N | 70.11W | 4 | -5.00 (NAE) | 94-06 | 711890 | -27.9 |  | -33.8 | 34.3 | 28.9 | 28.4 | 28.3 | 29 | 28.5333 |  | 26 | 25.9 | 25.4 | 26 | 25.7667 |  |  | CanadaQuebecPOINTE CLAVEAU
Canada | Quebec | POINTE NOIRE CS | POINTE NOIRE CS, QC, Canada | 50.16N | 66.43W | 24 | -5.00 (NAE) | 97-06 | 713900 | -26 |  | -30.7 | 31.8 | 27.1 | 26.9 | 26.4 | 27 | 26.8 |  | 23.6 | 24.5 | 23.5 | 24 | 23.8667 |  |  | CanadaQuebecPOINTE NOIRE CS
Canada | Quebec | POINTE-AU-PERE (INRS) | POINTE-AU-PERE (INRS), QC, Canada | 48.51N | 68.47W | 5 | -5.00 (NAE) | 96-06 | 715540 | -24.7 |  | -29.9 | 33.9 | 25.7 | 25.7 | 24.7 | 25 | 25.3667 |  | 22.8 | 22.7 | 22.2 | 23 | 22.5667 |  |  | CanadaQuebecPOINTE-AU-PERE (INRS)
Canada | Quebec | POINTE-DES-MONTS | POINTE-DES-MONTS, QC, Canada | 49.32N | 67.38W | 6 | -5.00 (NAE) | 94-06 | 714270 | -26.6 |  | -31.3 | 31.5 | 21 | 21.8 | 21 | 21 | 21.2667 |  | 18 | 19.9 | 18.7 | 19 | 18.8667 |  |  | CanadaQuebecPOINTE-DES-MONTS
Canada | Quebec | PORT-MENIER | PORT-MENIER, QC, Canada | 49.84N | 64.29W | 55 | -5.00 (NAE) | 94-06 | 718100 | N/A |  | N/A | N/A | 24.4 | 26.1 | 25.8 | 25 | 25.4333 |  | 21.9 | 24 | 23.3 | 23 | 23.0667 |  |  | CanadaQuebecPORT-MENIER
Canada | Quebec | QUEBEC/JEAN LESAGE INTL A | QUEBEC/JEAN LESAGE INTL A, QC, Canada | 46.80N | 71.38W | 74 | -5.00 (NAE) | 82-06 | 717080 | -29.7 |  | -36.6 | 35.6 | 30.9 | 31.2 | 29.7 | 31 | 30.6 |  | 28.2 | 28.9 | 27.9 | 28 | 28.3333 |  |  | CanadaQuebecQUEBEC/JEAN LESAGE INTL A
Canada | Quebec | RIVIERE-DU-LOUP | RIVIERE-DU-LOUP, QC, Canada | 47.81N | 69.55W | 147 | -5.00 (NAE) | 94-06 | 717150 | -27.1 |  | -32 | 33.4 | 28.5 | 28.4 | 27.8 | 28 | 28.2333 |  | 25.5 | 26.1 | 25.6 | 26 | 25.7333 |  |  | CanadaQuebecRIVIERE-DU-LOUP
Canada | Quebec | ROBERVAL A | ROBERVAL A, QC, Canada | 48.52N | 72.27W | 179 | -5.00 (NAE) | 82-06 | 717280 | -33.6 |  | -40.5 | 37.6 | 31.4 | 31.2 | 29.5 | 31 | 30.7 |  | 28.2 | 28.5 | 27.6 | 28 | 28.1 |  |  | CanadaQuebecROBERVAL A
Canada | Quebec | ROUYN | ROUYN, QC, Canada | 48.25N | 79.03W | 318 | -5.00 (NAE) | 94-06 | 717340 | -34 |  | -41.3 | 38.4 | 31 | 32.4 | 30 | 31 | 31.1333 |  | 28.4 | 29 | 27.2 | 28 | 28.2 |  |  | CanadaQuebecROUYN
Canada | Quebec | ROUYN A | ROUYN A, QC, Canada | 48.22N | 78.83W | 301 | -5.00 (NAE) | 82-06 | 717400 | -37.6 |  | -44.7 | 37.4 | 31.1 | 32.2 | 29.7 | 31 | 31 |  | 28.4 | 29.3 | 27.4 | 28 | 28.3667 |  |  | CanadaQuebecROUYN A
Canada | Quebec | SCHEFFERVILLE A | SCHEFFERVILLE A, QC, Canada | 54.80N | 66.82W | 522 | -5.00 (NAE) | 82-06 | 718280 | -41.6 |  | -48.5 | 32.9 | 27.3 | 26 | 25.7 | 26 | 26.3333 |  | 22.4 | 23.3 | 22.6 | 23 | 22.7667 |  |  | CanadaQuebecSCHEFFERVILLE A
Canada | Quebec | SEPT-ILES A | SEPT-ILES A, QC, Canada | 50.22N | 66.27W | 55 | -5.00 (NAE) | 82-06 | 718110 | -32 |  | -37.6 | 33 | 24 | 25.2 | 25 | 25 | 24.7333 |  | 21.3 | 22.8 | 22.4 | 22 | 22.1667 |  |  | CanadaQuebecSEPT-ILES A
Canada | Quebec | SHERBROOKE A | SHERBROOKE A, QC, Canada | 45.43N | 71.68W | 241 | -5.00 (NAE) | 82-04 | 716100 | -33.3 |  | -42.4 | 34.8 | 30.2 | 30.9 | 29.7 | 30 | 30.2667 |  | 27.9 | 28.6 | 27.6 | 28 | 28.0333 |  |  | CanadaQuebecSHERBROOKE A
Canada | Quebec | ST-ANICET 1 | ST-ANICET 1, QC, Canada | 45.12N | 74.29W | 49 | -5.00 (NAE) | 94-06 | 717120 | -29.2 |  | -39.4 | 36.3 | 32.2 | 31.2 | 31.4 | 32 | 31.6 |  | 29.9 | 29.7 | 29.3 | 30 | 29.6333 |  |  | CanadaQuebecST-ANICET 1
Canada | Quebec | STE AGATHE DES MONTS | STE AGATHE DES MONTS, QC, Canada | 46.05N | 74.28W | 395 | -5.00 (NAE) | 82-92 | 717200 | -32.3 |  | -36.1 | 34.2 | 29.2 | 30.1 | 27.6 | 29 | 28.9667 |  | 27 | 27.9 | 26.2 | 27 | 27.0333 |  |  | CanadaQuebecSTE AGATHE DES MONTS
Canada | Quebec | STE-ANNE-DE-BELLEVUE 1 | STE-ANNE-DE-BELLEVUE 1, QC, Canada | 45.43N | 73.93W | 39 | -5.00 (NAE) | 94-06 | 713770 | -27.4 |  | -34.9 | 36.3 | 31.7 | 31.3 | 31.6 | 32 | 31.5333 |  | 29.7 | 29.4 | 29.3 | 29 | 29.4667 |  |  | CanadaQuebecSTE-ANNE-DE-BELLEVUE 1
Canada | Quebec | STE-CLOTHILDE | STE-CLOTHILDE, QC, Canada | 45.17N | 73.68W | 53 | -5.00 (NAE) | 94-06 | 716140 | -29.8 |  | -40.4 | 37.2 | 32.4 | 32 | 32.2 | 32 | 32.2 |  | 30.2 | 29.8 | 29.8 | 30 | 29.9333 |  |  | CanadaQuebecSTE-CLOTHILDE
Canada | Quebec | STE-FOY (U. LAVAL) | STE-FOY (U. LAVAL), QC, Canada | 46.78N | 71.29W | 91 | -5.00 (NAE) | 97-06 | 713920 | N/A |  | N/A | N/A | 31.9 | 30.9 | 30.6 | 31 | 31.1333 |  | 28.8 | 28.7 | 28.4 | 29 | 28.6333 |  |  | CanadaQuebecSTE-FOY (U. LAVAL)
Canada | Quebec | ST-JOVITE | ST-JOVITE, QC, Canada | 46.08N | 74.56W | 239 | -5.00 (NAE) | 94-06 | 713760 | -35.5 |  | -43.9 | 37.6 | 31.7 | 31.1 | 30.4 | 31 | 31.0667 |  | 29 | 28.7 | 28.3 | 29 | 28.6667 |  |  | CanadaQuebecST-JOVITE
Canada | Quebec | TROIS-RIVIERES | TROIS-RIVIERES, QC, Canada | 46.35N | 72.52W | 6 | -5.00 (NAE) | 94-06 | 717240 | -26.7 |  | -36.1 | 35.9 | 28.5 | 29.4 | 28.7 | 29 | 28.8667 |  | 26.4 | 27.5 | 27.2 | 27 | 27.0333 |  |  | CanadaQuebecTROIS-RIVIERES
Canada | Quebec | VAL-D'OR A | VAL-D'OR A, QC, Canada | 48.06N | 77.79W | 337 | -5.00 (NAE) | 82-06 | 717250 | -37 |  | -43.8 | 36.4 | 30.8 | 31.6 | 29.3 | 31 | 30.5667 |  | 28.2 | 28.7 | 27.1 | 28 | 28 |  |  | CanadaQuebecVAL-D'OR A
Canada | Quebec | VARENNES | VARENNES, QC, Canada | 45.72N | 73.38W | 18 | -5.00 (NAE) | 94-06 | 711840 | -27.6 |  | -38 | 36.6 | 32.5 | 31.6 | 31.2 | 32 | 31.7667 |  | 30.4 | 29.5 | 29.3 | 30 | 29.7333 |  |  | CanadaQuebecVARENNES
Canada | Saskatchewan | ASSINIBOIA AIRPORT | ASSINIBOIA AIRPORT, SK, Canada | 49.73N | 105.93W | 726 | -6.00 (NAS) | 94-06 | 714870 | -33.8 |  | -42.9 | 39.9 | 31.7 | 34.2 | 35.2 | 34 | 33.7 |  | 28.5 | 31.6 | 32.9 | 31 | 31 |  |  | CanadaSaskatchewanASSINIBOIA AIRPORT
Canada | Saskatchewan | BROADVIEW | BROADVIEW, SK, Canada | 50.37N | 102.57W | 600 | -6.00 (NAS) | 82-06 | 718610 | -37.1 |  | -46.4 | 38.6 | 31.8 | 32.2 | 33.2 | 32 | 32.4 |  | 28.2 | 29.5 | 30.2 | 29 | 29.3 |  |  | CanadaSaskatchewanBROADVIEW
Canada | Saskatchewan | COLLINS BAY | COLLINS BAY, SK, Canada | 58.18N | 103.70W | 492 | -6.00 (NAS) | 82-06 | 710750 | -40.4 |  | -47.1 | 34.1 | 26.9 | 28.1 | 28.2 | 28 | 27.7333 |  | 24.3 | 25.6 | 24.9 | 25 | 24.9333 |  |  | CanadaSaskatchewanCOLLINS BAY
Canada | Saskatchewan | CORONACH SPC | CORONACH SPC, SK, Canada | 49.05N | 105.48W | 756 | -6.00 (NAS) | 96-06 | 715160 | -34.5 |  | -41.9 | 40 | 32.3 | 34.9 | 35.5 | 34 | 34.2333 |  | 28.5 | 32.8 | 33.2 | 32 | 31.5 |  |  | CanadaSaskatchewanCORONACH SPC
Canada | Saskatchewan | CREE LAKE | CREE LAKE, SK, Canada | 57.35N | 107.13W | 495 | -6.00 (NAS) | 82-96 | 719200 | -44.7 |  | -52.7 | 35.6 | 26.5 | 29.2 | 30.6 | 29 | 28.7667 |  | 24.1 | 26.6 | 27.4 | 26 | 26.0333 |  |  | CanadaSaskatchewanCREE LAKE
Canada | Saskatchewan | CYPRESS HILLS PARK | CYPRESS HILLS PARK, SK, Canada | 49.65N | 109.52W | 1271 | -6.00 (NAS) | 94-06 | 711390 | -31.5 |  | -43.2 | 35 | 26.9 | 30 | 30.9 | 29 | 29.2667 |  | 23.9 | 28.1 | 28.7 | 27 | 26.9 |  |  | CanadaSaskatchewanCYPRESS HILLS PARK
Canada | Saskatchewan | EASTEND CYPRESS (AUT) | EASTEND CYPRESS (AUT), SK, Canada | 49.43N | 108.98W | 1080 | -6.00 (NAS) | 94-06 | 711310 | -32.1 |  | -40.3 | 36.7 | 28.6 | 31.9 | 32.7 | 31 | 31.0667 |  | 25.6 | 30.2 | 30.9 | 29 | 28.9 |  |  | CanadaSaskatchewanEASTEND CYPRESS (AUT)
Canada | Saskatchewan | ELBOW CS | ELBOW CS, SK, Canada | 51.13N | 106.58W | 595 | -6.00 (NAS) | 94-06 | 714500 | -34.9 |  | -40.9 | 42.4 | 31.9 | 34.4 | 35.9 | 34 | 34.0667 |  | 28.5 | 31.6 | 32.5 | 31 | 30.8667 |  |  | CanadaSaskatchewanELBOW CS
Canada | Saskatchewan | ESTEVAN A | ESTEVAN A, SK, Canada | 49.22N | 102.97W | 581 | -6.00 (NAS) | 82-06 | 718620 | -35.6 |  | -45.4 | 41.1 | 34 | 34.5 | 35.2 | 35 | 34.5667 |  | 30.2 | 31.3 | 32.3 | 31 | 31.2667 |  |  | CanadaSaskatchewanESTEVAN A
Canada | Saskatchewan | HUDSON BAY | HUDSON BAY, SK, Canada | 52.82N | 102.32W | 358 | -6.00 (NAS) | 89-06 | 718680 | -39.6 |  | -44.6 | 37.5 | 30.7 | 31.3 | 31.9 | 31 | 31.3 |  | 27.2 | 28.8 | 29.1 | 28 | 28.3667 |  |  | CanadaSaskatchewanHUDSON BAY
Canada | Saskatchewan | INDIAN HEAD CDA | INDIAN HEAD CDA, SK, Canada | 50.55N | 103.65W | 579 | -6.00 (NAS) | 95-06 | 715150 | -37.8 |  | -45.4 | 38.8 | 31.2 | 31 | 33.2 | 32 | 31.8 |  | 27.7 | 29 | 30.9 | 29 | 29.2 |  |  | CanadaSaskatchewanINDIAN HEAD CDA
Canada | Saskatchewan | KEY LAKE A | KEY LAKE A, SK, Canada | 57.25N | 105.60W | 510 | -6.00 (NAS) | 94-06 | 714880 | -47.5 |  | -52.2 | 35.7 | 28.5 | 29.4 | 29.4 | 29 | 29.1 |  | 26.1 | 27.2 | 26.2 | 27 | 26.5 |  |  | CanadaSaskatchewanKEY LAKE A
Canada | Saskatchewan | KINDERSLEY A | KINDERSLEY A, SK, Canada | 51.52N | 109.18W | 694 | -6.00 (NAS) | 84-06 | 711290 | -36.1 |  | -46 | 39.7 | 32.4 | 33.3 | 34 | 33 | 33.2333 |  | 28.7 | 30.6 | 31.3 | 30 | 30.2 |  |  | CanadaSaskatchewanKINDERSLEY A
Canada | Saskatchewan | LA RONGE A | LA RONGE A, SK, Canada | 55.15N | 105.27W | 379 | -6.00 (NAS) | 82-06 | 719220 | -40.5 |  | -48.9 | 37.1 | 28.8 | 30.2 | 31.2 | 30 | 30.0667 |  | 26.1 | 27.9 | 28 | 27 | 27.3333 |  |  | CanadaSaskatchewanLA RONGE A
Canada | Saskatchewan | LAST MOUNTAIN CS | LAST MOUNTAIN CS, SK, Canada | 51.42N | 105.25W | 497 | -6.00 (NAS) | 96-06 | 715560 | -37.8 |  | -45.1 | 37.8 | 30.1 | 32.1 | 33.2 | 32 | 31.8 |  | 27 | 29.9 | 30.6 | 29 | 29.1667 |  |  | CanadaSaskatchewanLAST MOUNTAIN CS
Canada | Saskatchewan | LEADER AIRPORT | LEADER AIRPORT, SK, Canada | 50.90N | 109.50W | 676 | -6.00 (NAS) | 94-06 | 714590 | -35.6 |  | -45 | 40.2 | 31.3 | 35.1 | 35.2 | 34 | 33.8667 |  | 28.4 | 32.6 | 33.1 | 31 | 31.3667 |  |  | CanadaSaskatchewanLEADER AIRPORT
Canada | Saskatchewan | LUCKY LAKE | LUCKY LAKE, SK, Canada | 50.95N | 107.15W | 665 | -6.00 (NAS) | 94-06 | 714550 | -34 |  | -42.2 | 37.2 | 31 | 33 | 33.8 | 33 | 32.6 |  | 27.6 | 30.4 | 31.5 | 30 | 29.8333 |  |  | CanadaSaskatchewanLUCKY LAKE
Canada | Saskatchewan | MAPLE CREEK | MAPLE CREEK, SK, Canada | 49.90N | 109.47W | 767 | -6.00 (NAS) | 94-06 | 714530 | -35.2 |  | -44.1 | 38.2 | 30.5 | 33.9 | 34.4 | 33 | 32.9333 |  | 27.5 | 32.1 | 32.1 | 31 | 30.5667 |  |  | CanadaSaskatchewanMAPLE CREEK
Canada | Saskatchewan | MEADOW LAKE A | MEADOW LAKE A, SK, Canada | 54.13N | 108.52W | 480 | -6.00 (NAS) | 82-06 | 711250 | -41.8 |  | -52.7 | 38.2 | 29.4 | 30.7 | 31.4 | 31 | 30.5 |  | 26.5 | 27.9 | 28.5 | 28 | 27.6333 |  |  | CanadaSaskatchewanMEADOW LAKE A
Canada | Saskatchewan | MELFORT | MELFORT, SK, Canada | 52.82N | 104.60W | 490 | -6.00 (NAS) | 94-06 | 714560 | -37.2 |  | -45 | 38.6 | 31.4 | 30.6 | 32.6 | 32 | 31.5333 |  | 27.4 | 28.1 | 29.7 | 28 | 28.4 |  |  | CanadaSaskatchewanMELFORT
Canada | Saskatchewan | MOOSE JAW A | MOOSE JAW A, SK, Canada | 50.33N | 105.55W | 577 | -6.00 (NAS) | 82-97 | 718640 | -36.4 |  | -46.2 | 41.7 | 35.2 | 34.3 | 35 | 35 | 34.8333 |  | 31.1 | 31.6 | 32.5 | 32 | 31.7333 |  |  | CanadaSaskatchewanMOOSE JAW A
Canada | Saskatchewan | MOOSE JAW CS | MOOSE JAW CS, SK, Canada | 50.33N | 105.56W | 577 | -6.00 (NAS) | 98-06 | 715390 | -34.3 |  | -44.9 | 41.5 | 32.4 | 34 | 36 | 34 | 34.1333 |  | 28.4 | 31.4 | 32.8 | 31 | 30.8667 |  |  | CanadaSaskatchewanMOOSE JAW CS
Canada | Saskatchewan | NIPAWIN A | NIPAWIN A, SK, Canada | 53.33N | 104.00W | 372 | -6.00 (NAS) | 82-94 | 711300 | -39 |  | -46.7 | 39.6 | 31.8 | 31.1 | 31.8 | 32 | 31.5667 |  | 28 | 28 | 29.2 | 28 | 28.4 |  |  | CanadaSaskatchewanNIPAWIN A
Canada | Saskatchewan | NORTH BATTLEFORD A | NORTH BATTLEFORD A, SK, Canada | 52.77N | 108.26W | 548 | -6.00 (NAS) | 82-05 | 718760 | -38.4 |  | -48.2 | 40.5 | 31.5 | 32.2 | 33.2 | 32 | 32.3 |  | 27.7 | 28.9 | 30 | 29 | 28.8667 |  |  | CanadaSaskatchewanNORTH BATTLEFORD A
Canada | Saskatchewan | OUTLOOK PFRA | OUTLOOK PFRA, SK, Canada | 51.48N | 107.05W | 541 | -6.00 (NAS) | 96-06 | 715510 | -33.9 |  | -42.6 | 39.7 | 31.5 | 33.9 | 34.8 | 33 | 33.4 |  | 27.7 | 30.7 | 31.6 | 30 | 30 |  |  | CanadaSaskatchewanOUTLOOK PFRA
Canada | Saskatchewan | PRINCE ALBERT A | PRINCE ALBERT A, SK, Canada | 53.22N | 105.67W | 428 | -6.00 (NAS) | 82-06 | 718690 | -39.7 |  | -49.3 | 39.3 | 31.3 | 31.1 | 32.2 | 32 | 31.5333 |  | 27.5 | 28.4 | 29.4 | 28 | 28.4333 |  |  | CanadaSaskatchewanPRINCE ALBERT A
Canada | Saskatchewan | REGINA A | REGINA A, SK, Canada | 50.43N | 104.67W | 577 | -6.00 (NAS) | 82-06 | 718630 | -37.3 |  | -45.4 | 40.4 | 33.4 | 33.4 | 34 | 34 | 33.6 |  | 29.9 | 30.5 | 31.5 | 31 | 30.6333 |  |  | CanadaSaskatchewanREGINA A
Canada | Saskatchewan | ROCKGLEN (AUT) | ROCKGLEN (AUT), SK, Canada | 49.17N | 105.98W | 917 | -6.00 (NAS) | 94-06 | 711350 | -34.1 |  | -43.5 | 38.7 | 29.9 | 33.1 | 34.5 | 33 | 32.5 |  | 26.7 | 30.7 | 31.9 | 30 | 29.7667 |  |  | CanadaSaskatchewanROCKGLEN (AUT)
Canada | Saskatchewan | ROSETOWN EAST | ROSETOWN EAST, SK, Canada | 51.57N | 107.92W | 586 | -6.00 (NAS) | 94-06 | 715100 | -37.4 |  | -46.7 | 40.3 | 31.2 | 33.6 | 34.2 | 33 | 33 |  | 27.9 | 30.5 | 31.4 | 30 | 29.9333 |  |  | CanadaSaskatchewanROSETOWN EAST
Canada | Saskatchewan | SASKATOON DIEFENBAKER INT'L A | SASKATOON DIEFENBAKER INT'L A, SK, Canada | 52.17N | 106.72W | 504 | -6.00 (NAS) | 82-06 | 718660 | -38 |  | -48.4 | 41.7 | 33.4 | 33 | 34.1 | 34 | 33.5 |  | 28.9 | 30.1 | 31 | 30 | 30 |  |  | CanadaSaskatchewanSASKATOON DIEFENBAKER INT'L A
Canada | Saskatchewan | SASKATOON KERNEN FARM | SASKATOON KERNEN FARM, SK, Canada | 52.15N | 106.55W | 510 | -6.00 (NAS) | 96-05 | 715130 | -36.9 |  | -41.9 | 41.1 | 31.8 | 32.9 | 34.5 | 33 | 33.0667 |  | 27.7 | 30.1 | 31.1 | 30 | 29.6333 |  |  | CanadaSaskatchewanSASKATOON KERNEN FARM
Canada | Saskatchewan | SCOTT CDA | SCOTT CDA, SK, Canada | 52.36N | 108.83W | 660 | -6.00 (NAS) | 97-06 | 714890 | -36.4 |  | -46.5 | 42.4 | 31.3 | 33.2 | 33.7 | 33 | 32.7333 |  | 27 | 30 | 30.5 | 29 | 29.1667 |  |  | CanadaSaskatchewanSCOTT CDA
Canada | Saskatchewan | SOUTHEND | SOUTHEND, SK, Canada | 56.33N | 103.28W | 344 | -6.00 (NAS) | 94-06 | 714510 | -41.6 |  | -49.1 | 36.5 | 28.9 | 30.4 | 30.6 | 30 | 29.9667 |  | 26.2 | 27.6 | 27.1 | 27 | 26.9667 |  |  | CanadaSaskatchewanSOUTHEND
Canada | Saskatchewan | SPIRITWOOD WEST | SPIRITWOOD WEST, SK, Canada | 53.37N | 107.55W | 584 | -6.00 (NAS) | 94-06 | 711330 | -39.3 |  | -48.5 | 40.2 | 29.4 | 30.6 | 31.5 | 31 | 30.5 |  | 26.1 | 27.8 | 28.5 | 27 | 27.4667 |  |  | CanadaSaskatchewanSPIRITWOOD WEST
Canada | Saskatchewan | STONY RAPIDS A | STONY RAPIDS A, SK, Canada | 59.25N | 105.83W | 245 | -6.00 (NAS) | 86-06 | 711320 | -44 |  | -51.1 | 36.8 | 29.2 | 30.9 | 30.5 | 30 | 30.2 |  | 26.7 | 28 | 27 | 27 | 27.2333 |  |  | CanadaSaskatchewanSTONY RAPIDS A
Canada | Saskatchewan | SWIFT CURRENT A | SWIFT CURRENT A, SK, Canada | 50.30N | 107.68W | 818 | -6.00 (NAS) | 86-06 | 718700 | -34.5 |  | -44.1 | 39 | 32.1 | 32.8 | 34.2 | 33 | 33.0333 |  | 28.7 | 30.5 | 31.7 | 30 | 30.3 |  |  | CanadaSaskatchewanSWIFT CURRENT A
Canada | Saskatchewan | SWIFT CURRENT CDA | SWIFT CURRENT CDA, SK, Canada | 50.27N | 107.73W | 825 | -6.00 (NAS) | 94-06 | 714460 | -33.5 |  | -42.3 | 38.7 | 30.3 | 32.9 | 34.2 | 32 | 32.4667 |  | 27.2 | 30.6 | 32.1 | 30 | 29.9667 |  |  | CanadaSaskatchewanSWIFT CURRENT CDA
Canada | Saskatchewan | URANIUM CITY (AUT) | URANIUM CITY (AUT), SK, Canada | 59.57N | 108.48W | 318 | -6.00 (NAS) | 94-06 | 710760 | N/A |  | N/A | N/A | 28.5 | 29 | 26.8 | 28 | 28.1 |  | 25.8 | 26.7 | 24.7 | 26 | 25.7333 |  |  | CanadaSaskatchewanURANIUM CITY (AUT)
Canada | Saskatchewan | VAL MARIE SOUTHEAST | VAL MARIE SOUTHEAST, SK, Canada | 49.07N | 107.58W | 796 | -6.00 (NAS) | 94-06 | 711370 | -37.4 |  | -47.2 | 40.3 | 32.1 | 35.9 | 36.2 | 35 | 34.7333 |  | 28.8 | 33.6 | 34 | 32 | 32.1333 |  |  | CanadaSaskatchewanVAL MARIE SOUTHEAST
Canada | Saskatchewan | WASKESIU LAKE | WASKESIU LAKE, SK, Canada | 53.92N | 106.07W | 569 | -6.00 (NAS) | 94-06 | 714540 | -36.4 |  | -43.4 | 36.4 | 29.2 | 30 | 30.4 | 30 | 29.8667 |  | 26 | 27.4 | 27.6 | 27 | 27 |  |  | CanadaSaskatchewanWASKESIU LAKE
Canada | Saskatchewan | WATROUS EAST | WATROUS EAST, SK, Canada | 51.67N | 105.40W | 526 | -6.00 (NAS) | 94-06 | 715110 | -38.3 |  | -47.3 | 38.9 | 30.9 | 31.2 | 33.9 | 32 | 32 |  | 27.8 | 29.1 | 30.7 | 29 | 29.2 |  |  | CanadaSaskatchewanWATROUS EAST
Canada | Saskatchewan | WEYBURN | WEYBURN, SK, Canada | 49.70N | 103.80W | 589 | -6.00 (NAS) | 94-06 | 714520 | -35.5 |  | -45.9 | 39.7 | 32.2 | 33.6 | 35.2 | 34 | 33.6667 |  | 28.9 | 31.1 | 32.5 | 31 | 30.8333 |  |  | CanadaSaskatchewanWEYBURN
Canada | Saskatchewan | WYNYARD (AUT) | WYNYARD (AUT), SK, Canada | 51.77N | 104.20W | 560 | -6.00 (NAS) | 82-06 | 718650 | -36.4 |  | -46.4 | 39.6 | 31.7 | 32.2 | 32 | 32 | 31.9667 |  | 28.1 | 28.9 | 29.4 | 29 | 28.8 |  |  | CanadaSaskatchewanWYNYARD (AUT)
Canada | Saskatchewan | YORKTON A | YORKTON A, SK, Canada | 51.27N | 102.47W | 498 | -6.00 (NAS) | 82-05 | 711380 | -38.2 |  | -47.5 | 37.6 | 31.7 | 31.6 | 32.5 | 32 | 31.9333 |  | 28 | 29 | 29.9 | 29 | 28.9667 |  |  | CanadaSaskatchewanYORKTON A
Canada | Yukon | BURWASH A | BURWASH A, YT, Canada | 61.37N | 139.05W | 807 | -8.00 (NAP) | 82-06 | 719670 | -45.5 |  | -54.9 | 31.7 | 27 | 24.9 | 26.2 | 26 | 26.0333 |  | 23.4 | 22.8 | 22.6 | 23 | 22.9333 |  |  | CanadaYukonBURWASH A
Canada | Yukon | FARO (AUT) | FARO (AUT), YT, Canada | 62.23N | 133.35W | 717 | -8.00 (NAP) | 94-06 | 719490 | -45.2 |  | -55.1 | 34.7 | 29.3 | 27.6 | 28.9 | 29 | 28.6 |  | 26.1 | 25.1 | 25.8 | 26 | 25.6667 |  |  | CanadaYukonFARO (AUT)
Canada | Yukon | HAINES JUNCTION | HAINES JUNCTION, YT, Canada | 60.77N | 137.58W | 599 | -8.00 (NAP) | 94-06 | 715050 | -44.9 |  | -51.5 | 34.7 | 28.2 | 25.8 | 27.7 | 27 | 27.2333 |  | 24.1 | 23.8 | 25.1 | 24 | 24.3333 |  |  | CanadaYukonHAINES JUNCTION
Canada | Yukon | HERSCHEL ISLAND | HERSCHEL ISLAND, YT, Canada | 69.57N | 138.91W | 1 | -8.00 (NAP) | 94-06 | 715010 | N/A |  | N/A | N/A | 15.9 | 24.4 | 18.4 | 20 | 19.5667 |  | 12.8 | 19.1 | 15.4 | 16 | 15.7667 |  |  | CanadaYukonHERSCHEL ISLAND
Canada | Yukon | IVVAVIK NAT. PARK | IVVAVIK NAT. PARK, YT, Canada | 69.16N | 140.15W | 244 | -8.00 (NAP) | 95-06 | 719780 | -41.6 |  | -48.1 | 32.7 | 26.4 | 27.1 | 24.7 | 26 | 26.0667 |  | 22.9 | 24.6 | 20.9 | 23 | 22.8 |  |  | CanadaYukonIVVAVIK NAT. PARK
Canada | Yukon | KOMAKUK BEACH | KOMAKUK BEACH, YT, Canada | 69.61N | 140.20W | 13 | -8.00 (NAP) | 94-06 | 710460 | -39.8 |  | -43.3 | 28.7 | 18.2 | 21.7 | 20.7 | 20 | 20.2 |  | 14.3 | 18.9 | 16.7 | 17 | 16.6333 |  |  | CanadaYukonKOMAKUK BEACH
Canada | Yukon | MAYO A | MAYO A, YT, Canada | 63.62N | 135.87W | 504 | -8.00 (NAP) | 82-06 | 719650 | -49.2 |  | -58.1 | 34.9 | 29.9 | 29.3 | 29.1 | 29 | 29.4333 |  | 26.8 | 26.8 | 25.3 | 26 | 26.3 |  |  | CanadaYukonMAYO A
Canada | Yukon | ROCK RIVER | ROCK RIVER, YT, Canada | 66.98N | 136.22W | 731 | -8.00 (NAP) | 94-06 | 715060 | -34.5 |  | -41.4 | 31.9 | 24.7 | 25 | 25.8 | 25 | 25.1667 |  | 22 | 22.5 | 21.1 | 22 | 21.8667 |  |  | CanadaYukonROCK RIVER
Canada | Yukon | SHINGLE POINT A | SHINGLE POINT A, YT, Canada | 68.95N | 137.22W | 49 | -8.00 (NAP) | 82-06 | 719680 | -42.3 |  | -49.2 | 31.2 | 24.2 | 25.9 | 22.6 | 24 | 24.2333 |  | 21.1 | 23.2 | 19.2 | 21 | 21.1667 |  |  | CanadaYukonSHINGLE POINT A
Canada | Yukon | TESLIN (AUT) | TESLIN (AUT), YT, Canada | 60.17N | 132.73W | 705 | -8.00 (NAP) | 94-06 | 710450 | -42.4 |  | -52.3 | 34.1 | 29 | 27.2 | 27.6 | 28 | 27.9333 |  | 25.1 | 24.2 | 24.3 | 25 | 24.5333 |  |  | CanadaYukonTESLIN (AUT)
Canada | Yukon | WATSON LAKE A | WATSON LAKE A, YT, Canada | 60.12N | 128.82W | 687 | -8.00 (NAP) | 82-06 | 719530 | -47.6 |  | -56.3 | 34.8 | 28.9 | 28.1 | 29 | 29 | 28.6667 |  | 25.7 | 25.8 | 25.3 | 26 | 25.6 |  |  | CanadaYukonWATSON LAKE A
Canada | Yukon | WHITEHORSE A | WHITEHORSE A, YT, Canada | 60.71N | 135.07W | 706 | -8.00 (NAP) | 82-06 | 719640 | -41.7 |  | -50.8 | 34.4 | 28.9 | 27.6 | 28.1 | 28 | 28.2 |  | 24.8 | 25.1 | 25 | 25 | 24.9667 |  |  | CanadaYukonWHITEHORSE A
Cape Verde |  | SAL | SAL, Cape Verde | 16.73N | 22.95W | 53 | -1.00 (CVI) | 82-06 | 85940 | 15 |  | 8.3 | 37.5 | 29.1 | 29.9 | 31 | 30 | 30 |  | 27.8 | 28.8 | 30 | 29 | 28.8667
Chad |  | NDJAMENA | NDJAMENA, Chad | 12.13N | 15.03E | 295 | 1.00 (AFW) | 88-06 | 647000 | 10.3 |  | 7.6 | 46.3 | 41.2 | 38.5 | 34.6 | 38 | 38.1 |  | 40 | 36.7 | 33.2 | 37 | 36.6333
Chile |  | ANTOFAGASTA | ANTOFAGASTA, Chile | 23.43S | 70.45W | 140 | -4.00 (SAC) | 82-06 | 854420 | 7.8 |  | 4.7 | 30.5 | 20.2 | 19.8 | 19.9 | 20 | 19.9667 |  | 18.9 | 18.1 | 17.9 | 18 | 18.3
Chile |  | ARICA | ARICA, Chile | 18.47S | 70.17W | 58 | -4.00 (SAC) | 82-06 | 854060 | 8.9 |  | 4.2 | 32.2 | 23 | 21.2 | 21.2 | 22 | 21.8 |  | 21.1 | 19.9 | 19.8 | 20 | 20.2667
Chile |  | BALMACEDA | BALMACEDA, Chile | 45.92S | 71.70W | 522 | -4.00 (SAC) | 82-06 | 858740 | N/A |  | N/A | N/A | 10.2 | 10 | 11.2 | 10 | 10.4667 |  | 8.7 | 8.2 | 9.3 | 9 | 8.7333
Chile |  | CONCEPCION | CONCEPCION, Chile | 36.77S | 73.07W | 148 | -4.00 (SAC) | 82-06 | 856820 | -0.9 |  | -3.2 | 33.7 | 16.2 | 16.2 | 18 | 17 | 16.8 |  | 15.1 | 14.6 | 15.4 | 15 | 15.0333
Chile |  | FARO EVANGELISTAS | FARO EVANGELISTAS, Chile | 52.40S | 75.10W | 52 | -4.00 (SAC) | 84-05 | 859300 | N/A |  | N/A | N/A | 10.7 | 9.2 | 9.6 | 10 | 9.8333 |  | 10 | 8.8 | 8.7 | 9 | 9.1667
Chile |  | IQUIQUE | IQUIQUE, Chile | 20.53S | 70.18W | 48 | -4.00 (SAC) | 84-06 | 854180 | 10.4 |  | 8 | 31.7 | 21.1 | 20.1 | 20.2 | 20 | 20.4667 |  | 20.1 | 19.1 | 19.1 | 19 | 19.4333
Chile |  | ISLA DIEGO RAMIREZ | ISLA DIEGO RAMIREZ, Chile | 56.50S | 68.67W | 42 | -5.00 (XXX) | 83-05 | 859720 | N/A |  | N/A | N/A | 9.4 | 8.7 | 9.5 | 9 | 9.2 |  | 8.4 | 7.6 | 7.8 | 8 | 7.9333
Chile |  | LA SERENA | LA SERENA, Chile | 29.92S | 71.20W | 146 | -4.00 (SAC) | 83-06 | 854880 | 3.5 |  | -0.2 | 28.1 | 18.7 | 18.9 | 18.7 | 19 | 18.7667 |  | 17 | 16.9 | 16.9 | 17 | 16.9333
Chile |  | PUDAHUEL | PUDAHUEL, Chile | 33.38S | 70.78W | 474 | -4.00 (SAC) | 82-06 | 855740 | -3.5 |  | -6.8 | 37.4 | 22.1 | 22.2 | 24.2 | 23 | 22.8333 |  | 19.4 | 19.2 | 21.3 | 20 | 19.9667
Chile |  | PUERTO MONTT | PUERTO MONTT, Chile | 41.43S | 73.10W | 90 | -4.00 (SAC) | 82-06 | 857990 | -4 |  | -7.2 | 32 | 14.3 | 14 | 15.8 | 15 | 14.7 |  | 13.2 | 12.6 | 13.6 | 13 | 13.1333
Chile |  | PUNTA ARENAS | PUNTA ARENAS, Chile | 53.00S | 70.97W | 37 | -4.00 (SAC) | 82-06 | 859340 | -8.5 |  | -14.5 | 28.1 | 8.4 | 9.1 | 10 | 9 | 9.1667 |  | 7 | 7.1 | 8.2 | 7 | 7.4333
Chile |  | TEMUCO | TEMUCO, Chile | 38.75S | 72.63W | 114 | -4.00 (SAC) | 82-06 | 857430 | -3.9 |  | -6.4 | 39.5 | 16.1 | 15.9 | 18.4 | 17 | 16.8 |  | 14.6 | 13.8 | 15.7 | 15 | 14.7
China |  | ABAG QI | ABAG QI, China | 44.02N | 114.95E | 1128 | 8.00 (CHN) | 82-06 | 531920 | -33.3 |  | -38.5 | 38.8 | 32.1 | 34.5 | 32.2 | 33 | 32.9333 |  | 29.9 | 31.7 | 29.9 | 31 | 30.5
China |  | AIHUI | AIHUI, China | 50.25N | 127.45E | 166 | 8.00 (CHN) | 82-06 | 504680 | -34.8 |  | -42.4 | 39.7 | 32.2 | 33.1 | 30.3 | 32 | 31.8667 |  | 29.7 | 30.3 | 28.5 | 30 | 29.5
China |  | AKQI | AKQI, China | 40.93N | 78.45E | 1986 | 8.00 (CHN) | 82-06 | 517110 | -20.1 |  | -25.8 | 37.4 | 29.5 | 30.8 | 30.7 | 30 | 30.3333 |  | 27.4 | 28.8 | 28.5 | 28 | 28.2333
China |  | ALAR | ALAR, China | 40.50N | 81.05E | 1013 | 8.00 (CHN) | 82-06 | 517300 | -17.8 |  | -23.1 | 40 | 35.5 | 36 | 35.6 | 36 | 35.7 |  | 33.8 | 34.4 | 33.8 | 34 | 34
China |  | ALTAY | ALTAY, China | 47.73N | 88.08E | 737 | 8.00 (CHN) | 82-06 | 510760 | -31.8 |  | -43.6 | 38.3 | 32.2 | 34.3 | 33 | 33 | 33.1667 |  | 30.4 | 31.7 | 30.7 | 31 | 30.9333
China |  | ANDA | ANDA, China | 46.38N | 125.32E | 150 | 8.00 (CHN) | 82-06 | 508540 | -29.9 |  | -37.2 | 39 | 33.7 | 34.3 | 32.1 | 33 | 33.3667 |  | 31.2 | 31.8 | 29.9 | 31 | 30.9667
China |  | ANDIR | ANDIR, China | 37.93N | 83.65E | 1264 | 8.00 (CHN) | 82-98 | 518480 | -20.4 |  | -24.7 | 43.5 | 37.8 | 39 | 38.6 | 38 | 38.4667 |  | 35.5 | 37.3 | 36.8 | 37 | 36.5333
China |  | ANKANG | ANKANG, China | 32.72N | 109.03E | 291 | 8.00 (CHN) | 82-06 | 572450 | -4.5 |  | -8.5 | 43.4 | 36.4 | 37.6 | 37.7 | 37 | 37.2333 |  | 34.2 | 35.6 | 35.5 | 35 | 35.1
China |  | ANQING | ANQING, China | 30.53N | 117.05E | 20 | 8.00 (CHN) | 82-06 | 584240 | -4 |  | -8 | 40.3 | 34.6 | 37.2 | 36.5 | 36 | 36.1 |  | 33.1 | 36.1 | 35.1 | 35 | 34.7667
China |  | ANYANG | ANYANG, China | 36.05N | 114.40E | 64 | 8.00 (CHN) | 82-06 | 538980 | -10.9 |  | -17.9 | 41.9 | 37.7 | 36.8 | 34.5 | 36 | 36.3333 |  | 35.5 | 34.8 | 33 | 34 | 34.4333
China |  | ARXAN | ARXAN, China | 47.17N | 119.93E | 997 | 8.00 (CHN) | 82-06 | 507270 | -38.6 |  | -45.6 | 34.4 | 28.6 | 29.9 | 28.5 | 29 | 29 |  | 25.9 | 27.2 | 26.3 | 26 | 26.4667
China |  | BACHU | BACHU, China | 39.80N | 78.57E | 1117 | 8.00 (CHN) | 82-06 | 517160 | -16.1 |  | -22.5 | 41.9 | 37 | 38 | 36.8 | 37 | 37.2667 |  | 34.9 | 35.9 | 34.9 | 35 | 35.2333
China |  | BAILING-MIAO | BAILING-MIAO, China | 41.70N | 110.43E | 1377 | 8.00 (CHN) | 82-06 | 533520 | -30 |  | -37.5 | 37.6 | 32 | 33.8 | 31.6 | 32 | 32.4667 |  | 29.9 | 31.6 | 29.5 | 30 | 30.3333
China |  | BAINGOIN | BAINGOIN, China | 31.37N | 90.02E | 4701 | 8.00 (CHN) | 82-06 | 552790 | -25.6 |  | -32.1 | 23.8 | 19.1 | 17.9 | 17 | 18 | 18 |  | 17 | 16.5 | 15.5 | 16 | 16.3333
China |  | BAISE | BAISE, China | 23.90N | 106.60E | 177 | 8.00 (CHN) | 82-06 | 592110 | 3.7 |  | 0.1 | 41.9 | 36.9 | 37.4 | 36.9 | 37 | 37.0667 |  | 35.2 | 35.8 | 35.4 | 35 | 35.4667
China |  | BALGUNTAY | BALGUNTAY, China | 42.67N | 86.33E | 1753 | 8.00 (CHN) | 82-06 | 514670 | -18.8 |  | -23.6 | 34.8 | 29.2 | 31 | 30.2 | 30 | 30.1333 |  | 27.3 | 28.6 | 28.4 | 28 | 28.1
China |  | BAODING | BAODING, China | 38.85N | 115.57E | 19 | 8.00 (CHN) | 82-06 | 546020 | -12.6 |  | -18.2 | 42.8 | 37.4 | 37.9 | 34.1 | 36 | 36.4667 |  | 35.3 | 35.5 | 32.6 | 34 | 34.4667
China |  | BAOJI | BAOJI, China | 34.35N | 107.13E | 610 | 8.00 (CHN) | 82-04 | 570160 | -8.8 |  | -14.5 | 41 | 36.6 | 36.7 | 35.3 | 36 | 36.2 |  | 34.2 | 34.9 | 33.1 | 34 | 34.0667
China |  | BAOQING | BAOQING, China | 46.32N | 132.18E | 83 | 8.00 (CHN) | 82-06 | 508880 | -29.2 |  | -37.5 | 38.8 | 32.4 | 33.7 | 32.6 | 33 | 32.9 |  | 30.2 | 31.2 | 29.9 | 30 | 30.4333
China |  | BAOSHAN | BAOSHAN, China | 25.12N | 99.18E | 1649 | 8.00 (CHN) | 83-06 | 567480 | -0.2 |  | -4.3 | 32.9 | 29 | 28.1 | 28.4 | 29 | 28.5 |  | 27.4 | 26.9 | 27.2 | 27 | 27.1667
China |  | BARKAM | BARKAM, China | 31.90N | 102.23E | 2666 | 8.00 (CHN) | 82-06 | 561720 | -13.3 |  | -17.1 | 35.2 | 29.3 | 30.7 | 30.3 | 30 | 30.1 |  | 26.5 | 27.8 | 27.8 | 27 | 27.3667
China |  | BATANG | BATANG, China | 30.00N | 99.10E | 2589 | 8.00 (CHN) | 82-06 | 562470 | -8 |  | -11.6 | 37.7 | 33.2 | 33.6 | 31.2 | 33 | 32.6667 |  | 31.4 | 30.6 | 29 | 30 | 30.3333
China |  | BAYAN MOD | BAYAN MOD, China | 40.75N | 104.50E | 1329 | 8.00 (CHN) | 82-06 | 524950 | -25.2 |  | -33.9 | 40.4 | 34 | 36.1 | 34.2 | 35 | 34.7667 |  | 32.1 | 34 | 32.2 | 33 | 32.7667
China |  | BAYANBULAK | BAYANBULAK, China | 43.03N | 84.15E | 2459 | 8.00 (CHN) | 82-06 | 515420 | -39.5 |  | -47 | 29 | 21 | 23.8 | 22.9 | 23 | 22.5667 |  | 19.1 | 20.9 | 20.9 | 20 | 20.3
China |  | BAYTIK SHAN | BAYTIK SHAN, China | 45.37N | 90.53E | 1651 | 8.00 (CHN) | 82-06 | 512880 | -26.6 |  | -35.5 | 35 | 28.2 | 30.5 | 29.2 | 29 | 29.3 |  | 26.2 | 28 | 26.8 | 27 | 27
China |  | BEIHAI | BEIHAI, China | 21.48N | 109.10E | 16 | 8.00 (CHN) | 82-06 | 596440 | 5.1 |  | 1.3 | 39.6 | 33.3 | 33.8 | 34.3 | 34 | 33.8 |  | 32.5 | 32.9 | 32.8 | 33 | 32.7333
China |  | BEIJING | BEIJING, China | 39.93N | 116.28E | 55 | 8.00 (CHN) | 82-06 | 545110 | -13.7 |  | -19.4 | 42.7 | 36.9 | 37.2 | 34.9 | 36 | 36.3333 |  | 34.8 | 35 | 32.8 | 34 | 34.2
China |  | BENGBU | BENGBU, China | 32.95N | 117.37E | 22 | 8.00 (CHN) | 82-06 | 582210 | -8.1 |  | -13.4 | 40.4 | 36.2 | 37.7 | 36.2 | 37 | 36.7 |  | 34.2 | 36.2 | 34.5 | 35 | 34.9667
China |  | BENXI | BENXI, China | 41.32N | 123.78E | 185 | 8.00 (CHN) | 89-06 | 543460 | -25.5 |  | -34.6 | 38.3 | 33.8 | 33.7 | 31.9 | 33 | 33.1333 |  | 31.3 | 31.7 | 30.5 | 31 | 31.1667
China |  | BIJIE | BIJIE, China | 27.30N | 105.23E | 1511 | 8.00 (CHN) | 82-06 | 577070 | -4.4 |  | -7.5 | 36.7 | 29.9 | 30.8 | 30.9 | 31 | 30.5333 |  | 28 | 29.2 | 29.3 | 29 | 28.8333 |  |  | Yukon
China |  | BINHAI | BINHAI, China | 39.12N | 117.33E | 2 | 8.00 (CHN) | 90-06 | 545273 | -13.3 |  | -18.7 | 43 | 35.9 | 37.1 | 34.2 | 36 | 35.7333 |  | 33.9 | 34.9 | 33 | 34 | 33.9333
China |  | BOXIAN | BOXIAN, China | 33.88N | 115.77E | 42 | 8.00 (CHN) | 82-06 | 581020 | -10 |  | -16 | 40.6 | 37 | 37.2 | 35.2 | 36 | 36.4667 |  | 35.4 | 35.5 | 33.6 | 35 | 34.8333
China |  | BUGT | BUGT, China | 48.77N | 121.92E | 739 | 8.00 (CHN) | 82-06 | 506320 | -31.3 |  | -36.6 | 36.6 | 30 | 31.3 | 29 | 30 | 30.1 |  | 27.1 | 28.2 | 26.4 | 27 | 27.2333
China |  | BUGT | BUGT, China | 42.33N | 120.70E | 401 | 8.00 (CHN) | 82-06 | 542260 | -22.5 |  | -28.8 | 42 | 34.5 | 34.3 | 32.7 | 34 | 33.8333 |  | 31.9 | 32.1 | 30.5 | 32 | 31.5
China |  | CANGZHOU | CANGZHOU, China | 38.33N | 116.83E | 11 | 8.00 (CHN) | 82-95 | 546160 | -12.8 |  | -19.3 | 40.8 | 36.6 | 35.7 | 34.2 | 36 | 35.5 |  | 34.4 | 34.1 | 32.8 | 34 | 33.7667
China |  | CHANG DAO | CHANG DAO, China | 37.93N | 120.72E | 40 | 8.00 (CHN) | 88-06 | 547510 | -8.1 |  | -13.2 | 36.5 | 30.6 | 32.6 | 31.9 | 32 | 31.7 |  | 28.8 | 31 | 29.9 | 30 | 29.9
China |  | CHANGBAI | CHANGBAI, China | 41.35N | 128.17E | 1018 | 8.00 (CHN) | 82-06 | 543860 | -30.1 |  | -36.5 | 34.7 | 28.2 | 30.7 | 29.5 | 29 | 29.4667 |  | 25.7 | 28.2 | 27.4 | 27 | 27.1
China |  | CHANGCHUN | CHANGCHUN, China | 43.90N | 125.22E | 238 | 8.00 (CHN) | 82-06 | 541610 | -27.2 |  | -34.6 | 37 | 33.1 | 32.2 | 31.4 | 32 | 32.2333 |  | 30.6 | 30.6 | 29.7 | 30 | 30.3
China |  | CHANGDE | CHANGDE, China | 29.05N | 111.68E | 35 | 8.00 (CHN) | 82-06 | 576620 | -2.9 |  | -6.8 | 40.4 | 35.4 | 37.6 | 37.1 | 37 | 36.7 |  | 34 | 36.5 | 35.7 | 35 | 35.4 |  |  | Yukon
China |  | CHANGLING | CHANGLING, China | 44.25N | 123.97E | 190 | 8.00 (CHN) | 82-06 | 540490 | -26.9 |  | -34.9 | 37.8 | 33.7 | 33.2 | 31.7 | 33 | 32.8667 |  | 31.4 | 31.5 | 30 | 31 | 30.9667
China |  | CHANGSHA | CHANGSHA, China | 28.23N | 112.87E | 68 | 8.00 (CHN) | 87-06 | 576870 | -3.7 |  | -10.6 | 42.6 | 34.7 | 37.6 | 37.4 | 37 | 36.5667 |  | 33.6 | 36.3 | 35.7 | 35 | 35.2 |  |  | Yukon
China |  | CHANGTING | CHANGTING, China | 25.85N | 116.37E | 311 | 8.00 (CHN) | 82-06 | 589110 | -3.4 |  | -7.4 | 38.7 | 33.6 | 35.7 | 35.1 | 35 | 34.8 |  | 32.2 | 34.4 | 33.9 | 34 | 33.5
China |  | CHAOYANG | CHAOYANG, China | 41.55N | 120.45E | 176 | 8.00 (CHN) | 82-06 | 543240 | -22.2 |  | -31.9 | 42.1 | 36.2 | 36.1 | 34.3 | 36 | 35.5333 |  | 33.6 | 33.4 | 32.1 | 33 | 33.0333
China |  | CHENGDE | CHENGDE, China | 40.98N | 117.95E | 386 | 8.00 (CHN) | 82-06 | 544230 | -20.5 |  | -26 | 41.1 | 34.8 | 36 | 33.3 | 35 | 34.7 |  | 32.7 | 33.1 | 31.4 | 32 | 32.4
China |  | CHENGDU | CHENGDU, China | 30.67N | 104.02E | 508 | 8.00 (CHN) | 82-06 | 562940 | -1.7 |  | -4.4 | 39.2 | 33.2 | 34.8 | 34.8 | 34 | 34.2667 |  | 31.2 | 33 | 33 | 32 | 32.4
China |  | CHENGSHANTOU | CHENGSHANTOU, China | 37.40N | 122.68E | 47 | 8.00 (CHN) | 82-06 | 547760 | -8 |  | -13.8 | 32.7 | 26.1 | 28.6 | 28.5 | 28 | 27.7333 |  | 24.1 | 26.7 | 27.3 | 26 | 26.0333
China |  | CHENZHOU | CHENZHOU, China | 25.80N | 113.03E | 185 | 8.00 (CHN) | 82-06 | 579720 | -2.1 |  | -4.9 | 40.8 | 35 | 37.7 | 37.2 | 37 | 36.6333 |  | 33.8 | 36.2 | 35.6 | 35 | 35.2
China |  | CHIFENG | CHIFENG, China | 42.27N | 118.97E | 572 | 8.00 (CHN) | 82-06 | 542180 | -22.6 |  | -28.2 | 40.2 | 34 | 35.3 | 33.4 | 34 | 34.2333 |  | 31.9 | 32.9 | 31.3 | 32 | 32.0333
China |  | CHONGQING | CHONGQING, China | 29.58N | 106.47E | 260 | 8.00 (CHN) | 87-06 | 575160 | 1.1 |  | -2.3 | 43 | 35.6 | 37.6 | 39.6 | 38 | 37.6 |  | 33.8 | 36.3 | 37.5 | 36 | 35.8667
China |  | CHUXIONG | CHUXIONG, China | 25.02N | 101.52E | 1820 | 8.00 (CHN) | 82-06 | 567680 | -0.9 |  | -4.7 | 36 | 29.9 | 28.5 | 28 | 29 | 28.8 |  | 28.4 | 27.2 | 26.8 | 27 | 27.4667
China |  | DA XIAN | DA XIAN, China | 31.20N | 107.50E | 344 | 8.00 (CHN) | 82-06 | 573280 | -0.7 |  | -4 | 43.4 | 35.3 | 37.2 | 38 | 37 | 36.8333 |  | 33.2 | 35.5 | 36.4 | 35 | 35.0333
China |  | DACHEN DAO | DACHEN DAO, China | 28.45N | 121.88E | 84 | 8.00 (CHN) | 82-06 | 586660 | -0.9 |  | -3.8 | 33.4 | 28 | 30.3 | 30.8 | 30 | 29.7 |  | 27 | 29.6 | 30 | 29 | 28.8667
China |  | DALI | DALI, China | 25.70N | 100.18E | 1992 | 8.00 (CHN) | 82-06 | 567510 | -1.1 |  | -4.2 | 31.4 | 28.2 | 27.2 | 26.9 | 27 | 27.4333 |  | 26.8 | 26 | 25.8 | 26 | 26.2
China |  | DALIAN | DALIAN, China | 38.90N | 121.63E | 97 | 8.00 (CHN) | 82-06 | 546620 | -14.6 |  | -20.9 | 38.4 | 32.9 | 33.8 | 32.1 | 33 | 32.9333 |  | 29.9 | 31.2 | 30.9 | 31 | 30.6667
China |  | DANDONG | DANDONG, China | 40.05N | 124.33E | 14 | 8.00 (CHN) | 82-06 | 544970 | -19 |  | -26.9 | 35.4 | 29.8 | 32 | 31.7 | 31 | 31.1667 |  | 27.5 | 29.7 | 30.1 | 29 | 29.1
China |  | DANXIAN | DANXIAN, China | 19.52N | 109.58E | 169 | 8.00 (CHN) | 82-06 | 598450 | 7.7 |  | 3.7 | 40.6 | 35.7 | 35.7 | 34.5 | 35 | 35.3 |  | 34.6 | 34.4 | 33.4 | 34 | 34.1333
China |  | DAOCHENG | DAOCHENG, China | 29.05N | 100.30E | 3729 | 8.00 (CHN) | 83-06 | 563570 | -17.9 |  | -22.1 | 26.7 | 23 | 21.7 | 20.9 | 22 | 21.8667 |  | 21.5 | 19.9 | 19.2 | 20 | 20.2
China |  | DA-QAIDAM | DA-QAIDAM, China | 37.85N | 95.37E | 3174 | 8.00 (CHN) | 82-06 | 527130 | -26.7 |  | -33.1 | 33.6 | 25.1 | 29.3 | 27.9 | 27 | 27.4333 |  | 22.7 | 26.1 | 25.3 | 25 | 24.7
China |  | DARLAG | DARLAG, China | 33.75N | 99.65E | 3968 | 8.00 (CHN) | 82-06 | 560460 | -28.8 |  | -33.3 | 25.2 | 18.3 | 20.7 | 19.8 | 20 | 19.6 |  | 16.3 | 18.2 | 17.8 | 17 | 17.4333
China |  | DATONG | DATONG, China | 40.10N | 113.33E | 1069 | 8.00 (CHN) | 82-06 | 534870 | -24.1 |  | -28.6 | 37.4 | 33 | 33.6 | 31.9 | 33 | 32.8333 |  | 31 | 31.6 | 29.6 | 31 | 30.7333
China |  | DAWU | DAWU, China | 30.98N | 101.12E | 2959 | 8.00 (CHN) | 83-06 | 561670 | -14.7 |  | -19 | 33.4 | 26.8 | 28.4 | 28.4 | 28 | 27.8667 |  | 25.1 | 26.2 | 26.4 | 26 | 25.9
China |  | DEGE | DEGE, China | 31.80N | 98.57E | 3185 | 8.00 (CHN) | 82-06 | 561440 | -13.7 |  | -17.4 | 31.7 | 27.1 | 27.6 | 27.1 | 27 | 27.2667 |  | 24.6 | 25.3 | 25 | 25 | 24.9667
China |  | DELINGHA | DELINGHA, China | 37.37N | 97.37E | 2982 | 8.00 (CHN) | 82-06 | 527370 | -22.6 |  | -28.9 | 34.1 | 26.2 | 29.9 | 28.6 | 28 | 28.2333 |  | 24 | 27.1 | 26.2 | 26 | 25.7667
China |  | DENGQEN | DENGQEN, China | 31.42N | 95.60E | 3874 | 8.00 (CHN) | 82-06 | 561160 | -18.7 |  | -22.8 | 27.9 | 22.6 | 23.2 | 22.7 | 23 | 22.8333 |  | 20.7 | 21.6 | 21.1 | 21 | 21.1333
China |  | DEQEN | DEQEN, China | 28.45N | 98.88E | 3320 | 8.00 (CHN) | 82-06 | 564440 | -10.1 |  | -15.3 | 30.2 | 21.8 | 22.1 | 21.5 | 22 | 21.8 |  | 20 | 20.2 | 19.6 | 20 | 19.9333
China |  | DEZHOU | DEZHOU, China | 37.43N | 116.32E | 22 | 8.00 (CHN) | 82-94 | 547140 | -11.9 |  | -18 | 39.8 | 36.4 | 35.6 | 34 | 35 | 35.3333 |  | 34.2 | 34.1 | 32.6 | 34 | 33.6333
China |  | DINGHAI | DINGHAI, China | 30.03N | 122.12E | 37 | 8.00 (CHN) | 82-06 | 584770 | -2.4 |  | -5.4 | 39.4 | 31.8 | 34.9 | 34.2 | 34 | 33.6333 |  | 30 | 32.9 | 32.5 | 32 | 31.8
China |  | DINGTAO | DINGTAO, China | 35.07N | 115.57E | 49 | 8.00 (CHN) | 95-06 | 549090 | -12 |  | -17.5 | 41.5 | 36.8 | 36 | 34.1 | 36 | 35.6333 |  | 34.9 | 34.6 | 32.7 | 34 | 34.0667
China |  | DIWOPU | DIWOPU, China | 43.90N | 87.47E | 664 | 8.00 (CHN) | 88-06 | 514635 | -25.2 |  | -33.2 | 43.3 | 36.1 | 38.2 | 37.1 | 37 | 37.1333 |  | 34.2 | 36 | 35 | 35 | 35.0667
China |  | DONGFANG | DONGFANG, China | 19.10N | 108.62E | 8 | 8.00 (CHN) | 82-06 | 598380 | 10.5 |  | 6.5 | 39 | 33.7 | 33.7 | 33.4 | 34 | 33.6 |  | 33 | 33 | 32.6 | 33 | 32.8667
China |  | DONGSHENG | DONGSHENG, China | 39.83N | 109.98E | 1459 | 8.00 (CHN) | 82-06 | 535430 | -22.2 |  | -26.8 | 36.1 | 30.6 | 32.2 | 29.7 | 31 | 30.8333 |  | 28.6 | 30.2 | 28 | 29 | 28.9333
China |  | DONGTAI | DONGTAI, China | 32.85N | 120.28E | 5 | 8.00 (CHN) | 82-06 | 582510 | -7 |  | -10.4 | 39.1 | 34.1 | 35.9 | 34.8 | 35 | 34.9333 |  | 32 | 34.5 | 33.3 | 33 | 33.2667
China |  | DULAN | DULAN, China | 36.30N | 98.10E | 3192 | 8.00 (CHN) | 82-06 | 528360 | -20.9 |  | -27.2 | 32.7 | 25.2 | 28.5 | 27.7 | 27 | 27.1333 |  | 22.7 | 25.8 | 25 | 25 | 24.5
China |  | DUNHUA | DUNHUA, China | 43.37N | 128.20E | 525 | 8.00 (CHN) | 82-06 | 541860 | -29.7 |  | -37.4 | 34.9 | 29.6 | 31.4 | 30.3 | 30 | 30.4333 |  | 27.7 | 29.1 | 28.3 | 28 | 28.3667
China |  | DUNHUANG | DUNHUANG, China | 40.15N | 94.68E | 1140 | 8.00 (CHN) | 82-06 | 524180 | -20.7 |  | -28.1 | 41.1 | 35.2 | 37.2 | 36.4 | 36 | 36.2667 |  | 33.6 | 35.4 | 34.4 | 34 | 34.4667
China |  | DUOLUN | DUOLUN, China | 42.18N | 116.47E | 1247 | 8.00 (CHN) | 82-06 | 542080 | -31.1 |  | -37.9 | 36.7 | 30 | 31.5 | 29.5 | 30 | 30.3333 |  | 27.6 | 28.7 | 27.4 | 28 | 27.9
China |  | DUSHAN | DUSHAN, China | 25.83N | 107.55E | 971 | 8.00 (CHN) | 83-06 | 579220 | -3.7 |  | -7.3 | 36.8 | 29.1 | 30.5 | 30.6 | 30 | 30.0667 |  | 28 | 29.2 | 29.3 | 29 | 28.8333
China |  | EJIN QI | EJIN QI, China | 41.95N | 101.07E | 941 | 8.00 (CHN) | 82-06 | 522670 | -24.2 |  | -31.3 | 43.1 | 37.4 | 39.7 | 37.6 | 38 | 38.2333 |  | 35.4 | 37.7 | 35.7 | 36 | 36.2667
China |  | EMEI SHAN | EMEI SHAN, China | 29.52N | 103.33E | 3049 | 8.00 (CHN) | 82-06 | 563850 | -14.9 |  | -19.6 | 27.4 | 18.2 | 18.3 | 18.6 | 18 | 18.3667 |  | 16 | 16.8 | 16.8 | 17 | 16.5333
China |  | ENSHI | ENSHI, China | 30.28N | 109.47E | 458 | 8.00 (CHN) | 82-06 | 574470 | -2 |  | -5 | 39.9 | 35.1 | 36.2 | 36.8 | 36 | 36.0333 |  | 32.8 | 34.6 | 35.2 | 34 | 34.2
China |  | ERENHOT | ERENHOT, China | 43.65N | 112.00E | 966 | 8.00 (CHN) | 82-06 | 530680 | -30.9 |  | -37 | 41 | 35.1 | 37.2 | 34.6 | 36 | 35.6333 |  | 32.5 | 34.8 | 32.5 | 33 | 33.2667
China |  | FANGXIAN | FANGXIAN, China | 32.03N | 110.77E | 435 | 8.00 (CHN) | 82-06 | 572590 | -7.1 |  | -12.1 | 41.1 | 35.2 | 36.4 | 35.9 | 36 | 35.8333 |  | 33.2 | 34.6 | 33.7 | 34 | 33.8333
China |  | FENGJIE | FENGJIE, China | 31.02N | 109.53E | 303 | 8.00 (CHN) | 82-06 | 573480 | -1.1 |  | -4.9 | 41.5 | 36.6 | 36.7 | 37.8 | 37 | 37.0333 |  | 32.8 | 34.7 | 35.7 | 34 | 34.4
China |  | FENGNING | FENGNING, China | 41.22N | 116.63E | 661 | 8.00 (CHN) | 82-06 | 543080 | -23 |  | -27.8 | 40.1 | 32.9 | 34.6 | 32.1 | 33 | 33.2 |  | 31 | 31.7 | 29.8 | 31 | 30.8333
China |  | FEZXZAN | FEZXZAN, China | 35.25N | 117.95E | 120 | 8.00 (CHN) | 98-06 | 549290 | -10.6 |  | -12.7 | 42.5 | 35.6 | 36.3 | 34.4 | 35 | 35.4333 |  | 33.9 | 33.9 | 32.7 | 34 | 33.5
China |  | FOGANG | FOGANG, China | 23.87N | 113.53E | 68 | 8.00 (CHN) | 82-06 | 590870 | 1.5 |  | -1.6 | 39.2 | 34.5 | 36 | 35.7 | 35 | 35.4 |  | 33.1 | 34.6 | 34.5 | 34 | 34.0667
China |  | FUDING | FUDING, China | 27.33N | 120.20E | 38 | 8.00 (CHN) | 82-06 | 587540 | -1.5 |  | -4.9 | 40.9 | 34.4 | 36.7 | 35.5 | 36 | 35.5333 |  | 33 | 34.9 | 34.1 | 34 | 34
China |  | FUJIN | FUJIN, China | 47.23N | 131.98E | 65 | 8.00 (CHN) | 82-06 | 507880 | -30.6 |  | -35.5 | 38.1 | 32.3 | 34 | 32.1 | 33 | 32.8 |  | 30.1 | 31.2 | 29.2 | 30 | 30.1667
China |  | FUYANG | FUYANG, China | 32.87N | 115.73E | 33 | 8.00 (CHN) | 82-06 | 582030 | -8.7 |  | -14.8 | 40 | 35.9 | 37.2 | 35.5 | 36 | 36.2 |  | 34.2 | 35.7 | 34.1 | 35 | 34.6667
China |  | FUYUN | FUYUN, China | 46.98N | 89.52E | 827 | 8.00 (CHN) | 82-06 | 510870 | -35.6 |  | -45.9 | 41.6 | 34.3 | 37.1 | 35.1 | 36 | 35.5 |  | 32.2 | 34.1 | 32.6 | 33 | 32.9667
China |  | FUZHOU | FUZHOU, China | 26.08N | 119.28E | 85 | 8.00 (CHN) | 82-06 | 588470 | 2.4 |  | -1.2 | 40.5 | 35.4 | 37.2 | 36.7 | 36 | 36.4333 |  | 33.9 | 35.9 | 35.2 | 35 | 35
China |  | GANGCA | GANGCA, China | 37.33N | 100.13E | 3302 | 8.00 (CHN) | 82-06 | 527540 | -25 |  | -30.3 | 26.7 | 19 | 22.7 | 21.2 | 21 | 20.9667 |  | 17 | 19.9 | 19.4 | 19 | 18.7667
China |  | GANYU | GANYU, China | 34.83N | 119.13E | 10 | 8.00 (CHN) | 82-06 | 580400 | -9.5 |  | -14.2 | 38.8 | 33.9 | 35.3 | 34.2 | 34 | 34.4667 |  | 31.6 | 33.5 | 32.1 | 32 | 32.4
China |  | GANZHOU | GANZHOU, China | 25.87N | 115.00E | 138 | 8.00 (CHN) | 82-06 | 579930 | -1.1 |  | -4.5 | 40.6 | 35.4 | 37.7 | 37 | 37 | 36.7 |  | 34 | 36.3 | 35.6 | 35 | 35.3
China |  | GAOYAO | GAOYAO, China | 23.05N | 112.47E | 12 | 8.00 (CHN) | 82-06 | 592780 | 4.9 |  | 1.9 | 39.1 | 35.1 | 36.3 | 36.1 | 36 | 35.8333 |  | 33.9 | 35 | 34.9 | 35 | 34.6
China |  | GARZE | GARZE, China | 31.62N | 100.00E | 3394 | 8.00 (CHN) | 82-06 | 561460 | -18.4 |  | -26.6 | 30.3 | 25.7 | 25.6 | 25.2 | 26 | 25.5 |  | 23.1 | 23.4 | 23.1 | 23 | 23.2
China |  | GENGMA | GENGMA, China | 23.55N | 99.40E | 1104 | 8.00 (CHN) | 90-06 | 569460 | 1.5 |  | -1.5 | 36.1 | 32.9 | 31 | 31.5 | 32 | 31.8 |  | 30.5 | 29.4 | 30.2 | 30 | 30.0333
China |  | GOLMUD | GOLMUD, China | 36.42N | 94.90E | 2809 | 8.00 (CHN) | 82-06 | 528180 | -19.8 |  | -25.6 | 35.3 | 27.6 | 30.6 | 29.7 | 29 | 29.3 |  | 25.6 | 28.3 | 27.3 | 27 | 27.0667
China |  | GUAIZIHU | GUAIZIHU, China | 41.37N | 102.37E | 960 | 8.00 (CHN) | 82-06 | 523780 | -24.4 |  | -29.3 | 45.3 | 37.7 | 40.4 | 38.1 | 39 | 38.7333 |  | 35.8 | 38.3 | 36.2 | 37 | 36.7667
China |  | GUANGCHANG | GUANGCHANG, China | 26.85N | 116.33E | 142 | 8.00 (CHN) | 82-06 | 588130 | -3.4 |  | -8 | 41.9 | 35.3 | 37.9 | 37.2 | 37 | 36.8 |  | 34 | 36.3 | 35.9 | 35 | 35.4
China |  | GUANGHUA | GUANGHUA, China | 32.38N | 111.67E | 91 | 8.00 (CHN) | 82-06 | 572650 | -5.6 |  | -10.4 | 39.9 | 35.9 | 36.8 | 36.2 | 36 | 36.3 |  | 34.3 | 35.3 | 34.4 | 35 | 34.6667
China |  | GUANGNAN | GUANGNAN, China | 24.07N | 105.07E | 1251 | 8.00 (CHN) | 82-06 | 590070 | -1.2 |  | -4.9 | 38 | 31.4 | 30.8 | 30.5 | 31 | 30.9 |  | 29.8 | 29.5 | 29.1 | 29 | 29.4667
China |  | GUANGZHOU | GUANGZHOU, China | 23.17N | 113.33E | 42 | 8.00 (CHN) | 82-06 | 592870 | 3.3 |  | -1 | 40 | 35.1 | 36.5 | 36.2 | 36 | 35.9333 |  | 33.9 | 35 | 35 | 35 | 34.6333
China |  | GUILIN | GUILIN, China | 25.33N | 110.30E | 166 | 8.00 (CHN) | 82-06 | 579570 | -0.5 |  | -3.3 | 39.3 | 34 | 35.9 | 36.1 | 35 | 35.3333 |  | 32.8 | 34.6 | 34.8 | 34 | 34.0667
China |  | GUIPING | GUIPING, China | 23.40N | 110.08E | 44 | 8.00 (CHN) | 82-06 | 592540 | 3.7 |  | 0.5 | 40.3 | 34.7 | 36.1 | 36.1 | 36 | 35.6333 |  | 33.7 | 34.9 | 34.9 | 35 | 34.5
China |  | GUIYANG | GUIYANG, China | 26.58N | 106.73E | 1223 | 8.00 (CHN) | 82-06 | 578160 | -3.2 |  | -7 | 36.4 | 30.2 | 31.2 | 31.8 | 31 | 31.0667 |  | 28.9 | 29.9 | 30.4 | 30 | 29.7333
China |  | GUSHI | GUSHI, China | 32.17N | 115.67E | 58 | 8.00 (CHN) | 82-06 | 582080 | -6.9 |  | -12.5 | 39.5 | 34.3 | 36.5 | 35.3 | 35 | 35.3667 |  | 32.8 | 35.2 | 34 | 34 | 34
China |  | HAIKOU | HAIKOU, China | 20.03N | 110.35E | 24 | 8.00 (CHN) | 82-06 | 597580 | 8.9 |  | 4.7 | 40.2 | 35.7 | 35.7 | 34.5 | 35 | 35.3 |  | 34.6 | 34.7 | 33.5 | 34 | 34.2667
China |  | HAILAR | HAILAR, China | 49.22N | 119.75E | 611 | 8.00 (CHN) | 82-06 | 505270 | -37.1 |  | -45 | 39.6 | 31.9 | 33.2 | 31.6 | 32 | 32.2333 |  | 29.2 | 30.3 | 29 | 30 | 29.5
China |  | HAILS | HAILS, China | 41.45N | 106.38E | 1510 | 8.00 (CHN) | 82-06 | 532310 | -27.1 |  | -32 | 38.7 | 31.6 | 34.2 | 32.1 | 33 | 32.6333 |  | 29.8 | 32 | 30.1 | 31 | 30.6333
China |  | HAILUN | HAILUN, China | 47.43N | 126.97E | 240 | 8.00 (CHN) | 82-06 | 507560 | -32.3 |  | -38.9 | 37.8 | 32.3 | 32.4 | 30.6 | 32 | 31.7667 |  | 30.1 | 29.9 | 28.3 | 29 | 29.4333
China |  | HAIYANG | HAIYANG, China | 36.77N | 121.17E | 64 | 8.00 (CHN) | 82-06 | 548630 | -10.8 |  | -14.2 | 37.5 | 31.3 | 32.9 | 31.4 | 32 | 31.8667 |  | 29 | 30.7 | 30.1 | 30 | 29.9333
China |  | HAIYANG DAO | HAIYANG DAO, China | 39.05N | 123.22E | 10 | 8.00 (CHN) | 82-04 | 545870 | -14.1 |  | -24.5 | 32.6 | 27.2 | 30.1 | 31 | 29 | 29.4333 |  | 25.8 | 28.4 | 29.5 | 28 | 27.9
China |  | HALIUT | HALIUT, China | 41.57N | 108.52E | 1290 | 8.00 (CHN) | 82-06 | 533360 | -25.5 |  | -30.4 | 37.8 | 32.3 | 33.6 | 31.3 | 32 | 32.4 |  | 30.2 | 31.8 | 29.5 | 31 | 30.5
China |  | HAMI | HAMI, China | 42.82N | 93.52E | 739 | 8.00 (CHN) | 82-06 | 522030 | -21 |  | -28.3 | 42.9 | 37 | 39.1 | 38.3 | 38 | 38.1333 |  | 35.3 | 37.3 | 36 | 36 | 36.2
China |  | HANGZHOU | HANGZHOU, China | 30.23N | 120.17E | 43 | 8.00 (CHN) | 82-06 | 584570 | -4.8 |  | -8.8 | 40.9 | 35.8 | 37.9 | 37.2 | 37 | 36.9667 |  | 33.8 | 36.7 | 35.9 | 35 | 35.4667
China |  | HANZHONG | HANZHONG, China | 33.07N | 107.03E | 509 | 8.00 (CHN) | 82-06 | 571270 | -4.8 |  | -8.1 | 39.1 | 33.4 | 35.2 | 34.6 | 34 | 34.4 |  | 31.7 | 33.3 | 32.9 | 33 | 32.6333
China |  | HARBIN | HARBIN, China | 45.75N | 126.77E | 143 | 8.00 (CHN) | 82-06 | 509530 | -30.9 |  | -39.7 | 38.1 | 33.3 | 33.2 | 31.5 | 33 | 32.6667 |  | 31 | 31.1 | 29.6 | 31 | 30.5667
China |  | HECHI | HECHI, China | 24.70N | 108.05E | 214 | 8.00 (CHN) | 82-06 | 590230 | 2.6 |  | -0.7 | 39.4 | 34.7 | 36.2 | 36.4 | 36 | 35.7667 |  | 33.4 | 34.9 | 35.1 | 34 | 34.4667
China |  | HEFEI | HEFEI, China | 31.87N | 117.23E | 36 | 8.00 (CHN) | 82-06 | 583210 | -7.2 |  | -13.5 | 40.2 | 34.3 | 37.1 | 36 | 36 | 35.8 |  | 32.7 | 35.8 | 34.7 | 34 | 34.4
China |  | HENAN | HENAN, China | 34.73N | 101.60E | 3501 | 8.00 (CHN) | 82-06 | 560650 | -31.4 |  | -37.4 | 26.2 | 19.3 | 22.2 | 21.1 | 21 | 20.8667 |  | 17.3 | 19.7 | 19.1 | 19 | 18.7
China |  | HEQU | HEQU, China | 39.38N | 111.15E | 861 | 8.00 (CHN) | 82-06 | 535640 | -24.3 |  | -31.1 | 39.8 | 35.2 | 35.7 | 33.5 | 35 | 34.8 |  | 33.1 | 33.8 | 31.6 | 33 | 32.8333
China |  | HEYUAN | HEYUAN, China | 23.80N | 114.73E | 41 | 8.00 (CHN) | 82-06 | 592930 | 2.7 |  | -0.3 | 39.6 | 35.2 | 36.4 | 36.1 | 36 | 35.9 |  | 33.8 | 35 | 34.9 | 35 | 34.5667
China |  | HEZE/CAOZHOU | HEZE/CAOZHOU, China | 35.25N | 115.43E | 51 | 8.00 (CHN) | 82-94 | 549060 | -10.9 |  | -18.1 | 39.3 | 35.8 | 35.6 | 34.4 | 35 | 35.2667 |  | 34.3 | 34.4 | 32.7 | 34 | 33.8
China |  | HEZUO | HEZUO, China | 35.00N | 102.90E | 2910 | 8.00 (CHN) | 82-06 | 560800 | -23.8 |  | -29.1 | 29.8 | 22.6 | 25.1 | 24.6 | 24 | 24.1 |  | 20.5 | 23.1 | 22.6 | 22 | 22.0667
China |  | HOBOKSAR | HOBOKSAR, China | 46.78N | 85.72E | 1294 | 8.00 (CHN) | 82-06 | 511560 | -24.4 |  | -32.6 | 35.8 | 29.6 | 31.5 | 30.5 | 31 | 30.5333 |  | 28 | 29.5 | 28.3 | 29 | 28.6
China |  | HOHHOT | HOHHOT, China | 40.82N | 111.68E | 1065 | 8.00 (CHN) | 82-06 | 534630 | -24.5 |  | -37.7 | 38 | 32.9 | 34.2 | 31.8 | 33 | 32.9667 |  | 31 | 32.1 | 29.8 | 31 | 30.9667
China |  | HONG KONG INTERNATI | HONG KONG INTERNATI, China | 22.32N | 113.92E | 8 | 8.00 (CHN) | 82-06 | 450070 | 7.2 |  | 3.4 | 38.5 | 33.9 | 34.9 | 34.9 | 35 | 34.5667 |  | 32.8 | 33.2 | 33.6 | 33 | 33.2
China |  | HONG KONG OBSERVATO | HONG KONG OBSERVATO, China | 22.30N | 114.17E | 62 | 8.00 (CHN) | 82-92 | 450050 | 7.6 |  | 3.1 | 34.4 | 32.2 | 33 | 32.9 | 33 | 32.7 |  | 31.5 | 32.2 | 32.1 | 32 | 31.9333
China |  | HOTAN | HOTAN, China | 37.13N | 79.93E | 1375 | 8.00 (CHN) | 82-06 | 518280 | -13.3 |  | -21.2 | 41.5 | 36.3 | 36.8 | 36.2 | 36 | 36.4333 |  | 33.9 | 35.1 | 34.2 | 34 | 34.4
China |  | HUA SHAN | HUA SHAN, China | 34.48N | 110.08E | 2063 | 8.00 (CHN) | 82-06 | 570460 | -18.3 |  | -24.5 | 29.4 | 24.9 | 24.7 | 24 | 25 | 24.5333 |  | 22.8 | 23.5 | 22.5 | 23 | 22.9333
China |  | HUADE | HUADE, China | 41.90N | 114.00E | 1484 | 8.00 (CHN) | 82-06 | 533910 | -27.7 |  | -33.5 | 35.7 | 30.1 | 30.5 | 29.2 | 30 | 29.9333 |  | 27.6 | 28.7 | 26.9 | 28 | 27.7333
China |  | HUADIAN | HUADIAN, China | 42.98N | 126.75E | 264 | 8.00 (CHN) | 82-06 | 542730 | -34.6 |  | -44.5 | 35.3 | 31.3 | 32.5 | 31.4 | 32 | 31.7333 |  | 29.3 | 30.2 | 29.8 | 30 | 29.7667
China |  | HUAILAI | HUAILAI, China | 40.40N | 115.50E | 538 | 8.00 (CHN) | 82-06 | 544050 | -17.7 |  | -22.5 | 39.8 | 35.1 | 35.8 | 33.2 | 35 | 34.7 |  | 33 | 33.4 | 31.4 | 33 | 32.6
China |  | HUAJIALING | HUAJIALING, China | 35.38N | 105.00E | 2450 | 8.00 (CHN) | 82-06 | 529960 | -19.2 |  | -24.7 | 31.4 | 22.9 | 24.8 | 23.2 | 24 | 23.6333 |  | 21 | 22.5 | 21.7 | 22 | 21.7333
China |  | HUANG SHAN | HUANG SHAN, China | 30.13N | 118.15E | 1836 | 8.00 (CHN) | 82-06 | 584370 | -15.8 |  | -21.4 | 30.7 | 21.5 | 24.6 | 23.6 | 23 | 23.2333 |  | 20.1 | 22.8 | 22.1 | 22 | 21.6667
China |  | HUILI | HUILI, China | 26.65N | 102.25E | 1788 | 8.00 (CHN) | 82-06 | 566710 | -2.8 |  | -5.1 | 33.2 | 30.2 | 28.7 | 28.5 | 29 | 29.1333 |  | 28.5 | 27.4 | 27.3 | 28 | 27.7333
China |  | HUIMIN | HUIMIN, China | 37.50N | 117.53E | 12 | 8.00 (CHN) | 82-06 | 547250 | -13.5 |  | -19.5 | 40.7 | 36.4 | 35.9 | 34.1 | 35 | 35.4667 |  | 34.3 | 34.3 | 32.5 | 34 | 33.7
China |  | HUIZE | HUIZE, China | 26.42N | 103.28E | 2110 | 8.00 (CHN) | 83-06 | 566840 | -5.4 |  | -10.4 | 31.3 | 27.7 | 27 | 26.7 | 27 | 27.1333 |  | 26.3 | 25.5 | 25.3 | 26 | 25.7
China |  | HULIN | HULIN, China | 45.77N | 132.97E | 103 | 8.00 (CHN) | 82-06 | 509830 | -29.2 |  | -34.2 | 36 | 30.6 | 31.5 | 31.3 | 31 | 31.1333 |  | 28.5 | 29.4 | 29 | 29 | 28.9667
China |  | HUMA | HUMA, China | 51.72N | 126.65E | 179 | 8.00 (CHN) | 82-06 | 503530 | -39.4 |  | -47.3 | 39.8 | 31.7 | 34.5 | 31.2 | 32 | 32.4667 |  | 29.9 | 31 | 28.9 | 30 | 29.9333
China |  | HUOSHAN | HUOSHAN, China | 31.40N | 116.33E | 68 | 8.00 (CHN) | 82-06 | 583140 | -7.3 |  | -12.3 | 41 | 35.7 | 37.8 | 36.6 | 37 | 36.7 |  | 33.7 | 36.4 | 35 | 35 | 35.0333
China |  | JARTAI | JARTAI, China | 39.78N | 105.75E | 1143 | 8.00 (CHN) | 82-06 | 535020 | -23.5 |  | -29.2 | 41.7 | 36 | 37.8 | 36.2 | 37 | 36.6667 |  | 34.2 | 35.9 | 34.2 | 35 | 34.7667
China |  | JARUD QI | JARUD QI, China | 44.57N | 120.90E | 266 | 8.00 (CHN) | 82-06 | 540260 | -23.2 |  | -30.7 | 40.7 | 35.5 | 35.9 | 34.2 | 35 | 35.2 |  | 32.7 | 33.3 | 31.9 | 33 | 32.6333
China |  | JIAN | JIAN, China | 41.10N | 126.15E | 179 | 8.00 (CHN) | 82-06 | 543770 | -24.4 |  | -31.6 | 38.6 | 32.9 | 34.6 | 33.4 | 34 | 33.6333 |  | 30.4 | 32 | 31.4 | 31 | 31.2667
China |  | JIAN | JIAN, China | 27.12N | 114.97E | 78 | 8.00 (CHN) | 82-06 | 577990 | -2.3 |  | -5.9 | 41 | 35.1 | 38.2 | 37.5 | 37 | 36.9333 |  | 33.7 | 36.7 | 35.9 | 35 | 35.4333
China |  | JIANGCHENG | JIANGCHENG, China | 22.62N | 101.82E | 1121 | 8.00 (CHN) | 83-06 | 569770 | 3.6 |  | -1.9 | 34.8 | 30 | 29.5 | 29.8 | 30 | 29.7667 |  | 28.7 | 28.2 | 28.7 | 29 | 28.5333
China |  | JIANGLING | JIANGLING, China | 30.33N | 112.18E | 33 | 8.00 (CHN) | 82-06 | 574760 | -3.3 |  | -7.6 | 39.1 | 34.2 | 36.4 | 35.9 | 36 | 35.5 |  | 33 | 35.2 | 34.6 | 34 | 34.2667
China |  | JIEXIU | JIEXIU, China | 37.03N | 111.92E | 745 | 8.00 (CHN) | 82-06 | 538630 | -17.2 |  | -22.4 | 40.5 | 35.2 | 35.7 | 33.1 | 35 | 34.6667 |  | 33.2 | 33.5 | 31.3 | 33 | 32.6667
China |  | JINAN | JINAN, China | 36.60N | 117.05E | 169 | 8.00 (CHN) | 82-06 | 548230 | -10.7 |  | -16.2 | 41.2 | 37 | 36.4 | 35 | 36 | 36.1333 |  | 35.1 | 34.9 | 33.3 | 34 | 34.4333
China |  | JINGDEZHEN | JINGDEZHEN, China | 29.30N | 117.20E | 60 | 8.00 (CHN) | 82-06 | 585270 | -3.9 |  | -8.3 | 41 | 34.7 | 37.8 | 37.2 | 37 | 36.5667 |  | 33.5 | 36.4 | 35.9 | 35 | 35.2667
China |  | JINGHE | JINGHE, China | 44.62N | 82.90E | 321 | 8.00 (CHN) | 82-06 | 513340 | -27.2 |  | -35.7 | 41.4 | 37.1 | 38 | 36.6 | 37 | 37.2333 |  | 35.2 | 35.8 | 34.7 | 35 | 35.2333
China |  | JINGHONG | JINGHONG, China | 22.00N | 100.78E | 579 | 8.00 (CHN) | 83-06 | 569590 | 7.3 |  | 1.9 | 40.5 | 35.2 | 33.6 | 33.6 | 34 | 34.1333 |  | 33.2 | 32.1 | 32.1 | 32 | 32.4667
China |  | JINING | JINING, China | 41.03N | 113.07E | 1416 | 8.00 (CHN) | 82-06 | 534800 | -25.5 |  | -30.4 | 34.8 | 30.1 | 30.7 | 29.4 | 30 | 30.0667 |  | 28.1 | 28.9 | 27.1 | 28 | 28.0333
China |  | JINZHOU | JINZHOU, China | 41.13N | 121.12E | 70 | 8.00 (CHN) | 82-06 | 543370 | -18 |  | -24.9 | 39.4 | 34.3 | 33.8 | 32.4 | 34 | 33.5 |  | 31 | 31.7 | 30.8 | 31 | 31.1667
China |  | JIULONG | JIULONG, China | 29.00N | 101.50E | 2994 | 8.00 (CHN) | 82-06 | 564620 | -10.6 |  | -14.9 | 32 | 26.8 | 25.6 | 25.6 | 26 | 26 |  | 24.6 | 23.9 | 23.6 | 24 | 24.0333
China |  | JIUQUAN | JIUQUAN, China | 39.77N | 98.48E | 1478 | 8.00 (CHN) | 82-06 | 525330 | -22.8 |  | -30.2 | 38 | 31.5 | 33.5 | 32.6 | 33 | 32.5333 |  | 29.8 | 31.6 | 31 | 31 | 30.8
China |  | JIUXIAN SHAN | JIUXIAN SHAN, China | 25.72N | 118.10E | 1651 | 8.00 (CHN) | 82-06 | 589310 | -8 |  | -13.3 | 32.3 | 24.6 | 26.1 | 25.2 | 25 | 25.3 |  | 23 | 24.7 | 24 | 24 | 23.9
China |  | JIXI | JIXI, China | 45.28N | 130.95E | 234 | 8.00 (CHN) | 82-06 | 509780 | -27 |  | -32.7 | 37.8 | 31.9 | 33.7 | 31.7 | 32 | 32.4333 |  | 29.7 | 31 | 29.3 | 30 | 30
China |  | JURH | JURH, China | 42.40N | 112.90E | 1152 | 8.00 (CHN) | 82-06 | 532760 | -27.6 |  | -32.7 | 40 | 33.8 | 34.9 | 33.3 | 34 | 34 |  | 31.1 | 33 | 31.1 | 32 | 31.7333
China |  | KABA HE | KABA HE, China | 48.05N | 86.35E | 534 | 8.00 (CHN) | 82-06 | 510530 | -29.9 |  | -41.6 | 39.8 | 33 | 35.2 | 33.9 | 34 | 34.0333 |  | 31.1 | 32.7 | 31.4 | 32 | 31.7333
China |  | KANGDING | KANGDING, China | 30.05N | 101.97E | 2617 | 8.00 (CHN) | 82-06 | 563740 | -10.6 |  | -14.6 | 32.5 | 23.4 | 24.5 | 24.7 | 24 | 24.2 |  | 21.3 | 22.9 | 23 | 22 | 22.4
China |  | KARAMAY | KARAMAY, China | 45.60N | 84.85E | 428 | 8.00 (CHN) | 82-06 | 512430 | -25.8 |  | -35.1 | 42.8 | 37.4 | 39.1 | 37.9 | 38 | 38.1333 |  | 35.7 | 37.2 | 35.7 | 36 | 36.2
China |  | KASHI | KASHI, China | 39.47N | 75.98E | 1291 | 8.00 (CHN) | 82-06 | 517090 | -14.8 |  | -22.5 | 40.3 | 34.7 | 35.7 | 35.1 | 35 | 35.1667 |  | 32.7 | 34 | 33.2 | 33 | 33.3
China |  | KESHAN | KESHAN, China | 48.05N | 125.88E | 237 | 8.00 (CHN) | 82-06 | 506580 | -33.4 |  | -41.6 | 38.7 | 33 | 33.2 | 30.7 | 32 | 32.3 |  | 30.4 | 30.6 | 28.8 | 30 | 29.9333
China |  | KORLA | KORLA, China | 41.75N | 86.13E | 933 | 8.00 (CHN) | 82-06 | 516560 | -16.2 |  | -23.3 | 41 | 35.4 | 37.3 | 36.5 | 36 | 36.4 |  | 33.9 | 35.5 | 34.7 | 35 | 34.7
China |  | KUANDIAN | KUANDIAN, China | 40.72N | 124.78E | 261 | 8.00 (CHN) | 82-06 | 544930 | -26 |  | -35.4 | 36.3 | 31.5 | 32.6 | 31.6 | 32 | 31.9 |  | 28.7 | 30.2 | 29.8 | 30 | 29.5667
China |  | KUNMING | KUNMING, China | 25.02N | 102.68E | 1892 | 8.00 (CHN) | 82-06 | 567780 | -2.1 |  | -6.9 | 31.7 | 27.9 | 27 | 27 | 27 | 27.3 |  | 26.4 | 25.7 | 25.8 | 26 | 25.9667
China |  | KUOCANG SHAN | KUOCANG SHAN, China | 28.82N | 120.92E | 1371 | 8.00 (CHN) | 82-94 | 586530 | -13.5 |  | -17.5 | 31.3 | 25.9 | 28.2 | 26.9 | 27 | 27 |  | 24.1 | 26.7 | 25.5 | 25 | 25.4333
China |  | KUQA | KUQA, China | 41.72N | 82.95E | 1100 | 8.00 (CHN) | 82-06 | 516440 | -16.6 |  | -24.4 | 40.6 | 34.4 | 36.5 | 35.7 | 36 | 35.5333 |  | 33 | 34.7 | 33.6 | 34 | 33.7667
China |  | LANCANG | LANCANG, China | 22.57N | 99.93E | 1054 | 8.00 (CHN) | 82-06 | 569540 | 3.1 |  | 0.1 | 37.3 | 32.2 | 30.8 | 31.1 | 31 | 31.3667 |  | 30.2 | 29.3 | 29.8 | 30 | 29.7667
China |  | LANGZHONG | LANGZHONG, China | 31.58N | 105.97E | 385 | 8.00 (CHN) | 82-06 | 573060 | -1.4 |  | -4.9 | 41 | 34 | 36.8 | 37.2 | 36 | 36 |  | 32.3 | 34.7 | 35.2 | 34 | 34.0667
China |  | LANZHOU | LANZHOU, China | 36.05N | 103.88E | 1518 | 8.00 (CHN) | 82-03 | 528890 | -13.9 |  | -18.8 | 39.7 | 32.7 | 35.2 | 33.6 | 34 | 33.8333 |  | 30.6 | 32.7 | 31.5 | 32 | 31.6
China |  | LENGHU | LENGHU, China | 38.83N | 93.38E | 2771 | 8.00 (CHN) | 82-06 | 526020 | -26 |  | -30.6 | 35.3 | 26.8 | 30.9 | 29.8 | 29 | 29.1667 |  | 24.8 | 28.1 | 27.1 | 27 | 26.6667
China |  | LETING | LETING, China | 39.43N | 118.90E | 12 | 8.00 (CHN) | 82-06 | 545390 | -15.9 |  | -22.6 | 39.8 | 33.4 | 34 | 32.4 | 33 | 33.2667 |  | 30.9 | 32.2 | 31 | 31 | 31.3667
China |  | LHASA | LHASA, China | 29.67N | 91.13E | 3650 | 8.00 (CHN) | 82-06 | 555910 | -12.3 |  | -17.2 | 29.3 | 26.6 | 26.1 | 24.5 | 26 | 25.7333 |  | 25 | 24.4 | 23 | 24 | 24.1333
China |  | LHUNZE | LHUNZE, China | 28.42N | 92.47E | 3861 | 8.00 (CHN) | 82-06 | 556960 | -16.6 |  | -20.7 | 28 | 23 | 22.7 | 21.8 | 23 | 22.5 |  | 21.4 | 21.1 | 20.4 | 21 | 20.9667
China |  | LIAN XIAN | LIAN XIAN, China | 24.78N | 112.38E | 98 | 8.00 (CHN) | 82-06 | 590720 | -0.6 |  | -3.7 | 40.4 | 35.7 | 37.3 | 37.1 | 37 | 36.7 |  | 34.2 | 35.9 | 35.6 | 35 | 35.2333
China |  | LIANGPING | LIANGPING, China | 30.68N | 107.80E | 455 | 8.00 (CHN) | 82-06 | 574260 | -1.7 |  | -3.9 | 40.1 | 34.3 | 36.1 | 37.2 | 36 | 35.8667 |  | 32.3 | 34.6 | 35.5 | 34 | 34.1333
China |  | LIANPING | LIANPING, China | 24.37N | 114.48E | 214 | 8.00 (CHN) | 82-06 | 590960 | 0.3 |  | -2.4 | 40 | 34.6 | 36.1 | 35.9 | 36 | 35.5333 |  | 33.2 | 34.7 | 34.6 | 34 | 34.1667
China |  | LIJING | LIJING, China | 26.83N | 100.47E | 2394 | 8.00 (CHN) | 82-06 | 566510 | -4.3 |  | -8.9 | 31.9 | 28.4 | 27 | 25.7 | 27 | 27.0333 |  | 26.7 | 24.9 | 24.3 | 25 | 25.3
China |  | LINCANG | LINCANG, China | 23.95N | 100.22E | 1503 | 8.00 (CHN) | 82-06 | 569510 | 1.8 |  | -1.5 | 37 | 30.1 | 28.6 | 29.2 | 29 | 29.3 |  | 28 | 27.2 | 27.8 | 28 | 27.6667
China |  | LINDONG | LINDONG, China | 43.98N | 119.40E | 485 | 8.00 (CHN) | 82-06 | 540270 | -25.1 |  | -32.3 | 39.7 | 33.8 | 34.6 | 33.2 | 34 | 33.8667 |  | 31.5 | 32.1 | 31 | 32 | 31.5333
China |  | LINGLING | LINGLING, China | 26.23N | 111.62E | 174 | 8.00 (CHN) | 82-06 | 578660 | -2.1 |  | -5.6 | 39.8 | 34.4 | 37 | 36.9 | 36 | 36.1 |  | 33.1 | 35.6 | 35.2 | 35 | 34.6333
China |  | LINGXIAN | LINGXIAN, China | 37.33N | 116.57E | 19 | 8.00 (CHN) | 95-06 | 547150 | -15.5 |  | -23.9 | 42.7 | 37.3 | 36.9 | 34.2 | 36 | 36.1333 |  | 35.6 | 35.1 | 32.7 | 34 | 34.4667
China |  | LINHAI | LINHAI, China | 28.85N | 121.13E | 9 | 8.00 (CHN) | 94-06 | 586600 | -2.5 |  | -5.4 | 42.2 | 36.1 | 38.6 | 37 | 37 | 37.2333 |  | 33.9 | 36.5 | 35.3 | 35 | 35.2333
China |  | LINHE | LINHE, China | 40.77N | 107.40E | 1041 | 8.00 (CHN) | 82-06 | 535130 | -21.2 |  | -27.2 | 39.5 | 34.5 | 35.6 | 33.4 | 35 | 34.5 |  | 32.5 | 33.6 | 31.6 | 33 | 32.5667
China |  | LINJIANG | LINJIANG, China | 41.72N | 126.92E | 333 | 8.00 (CHN) | 82-06 | 543740 | -28.5 |  | -35.2 | 37.9 | 31.3 | 33.7 | 32.7 | 33 | 32.5667 |  | 29.3 | 31.1 | 30.5 | 30 | 30.3
China |  | LINXI | LINXI, China | 43.60N | 118.07E | 800 | 8.00 (CHN) | 82-06 | 541150 | -25.7 |  | -32.2 | 38.7 | 32.6 | 34.1 | 32.3 | 33 | 33 |  | 30.3 | 31.1 | 30 | 30 | 30.4667
China |  | LINYI | LINYI, China | 35.05N | 118.35E | 86 | 8.00 (CHN) | 82-97 | 549380 | -9.7 |  | -14.6 | 39.1 | 34.7 | 35.6 | 34 | 35 | 34.7667 |  | 32.7 | 33.8 | 32.2 | 33 | 32.9
China |  | LISHI | LISHI, China | 37.50N | 111.10E | 951 | 8.00 (CHN) | 82-06 | 537640 | -20.7 |  | -26.7 | 39.2 | 35 | 35.2 | 33.1 | 34 | 34.4333 |  | 32.5 | 33.4 | 31.1 | 32 | 32.3333
China |  | LISHUI | LISHUI, China | 28.45N | 119.92E | 60 | 8.00 (CHN) | 82-06 | 586460 | -3.6 |  | -7.3 | 42 | 36.7 | 39 | 38.2 | 38 | 37.9667 |  | 34.8 | 37.4 | 36.6 | 36 | 36.2667
China |  | LITANG | LITANG, China | 30.00N | 100.27E | 3950 | 8.00 (CHN) | 82-06 | 562570 | -20.6 |  | -29.3 | 27.1 | 21.4 | 20.7 | 19.7 | 21 | 20.6 |  | 19.8 | 18.8 | 18.1 | 19 | 18.9
China |  | LIUZHOU | LIUZHOU, China | 24.35N | 109.40E | 97 | 8.00 (CHN) | 82-06 | 590460 | 1.9 |  | -1.2 | 39.8 | 34.9 | 36.2 | 36.4 | 36 | 35.8333 |  | 33.8 | 35.1 | 35.2 | 35 | 34.7
China |  | LIYANG | LIYANG, China | 31.43N | 119.48E | 8 | 8.00 (CHN) | 82-06 | 583450 | -6.2 |  | -12.3 | 39.9 | 34.9 | 37 | 36.2 | 36 | 36.0333 |  | 33 | 35.8 | 34.6 | 34 | 34.4667
China |  | LONGKOU | LONGKOU, China | 37.62N | 120.32E | 5 | 8.00 (CHN) | 82-06 | 547530 | -10.7 |  | -16.1 | 40.2 | 33.5 | 34.5 | 33.1 | 34 | 33.7 |  | 31.4 | 33 | 31.5 | 32 | 31.9667
China |  | LONGYAN | LONGYAN, China | 25.10N | 117.02E | 341 | 8.00 (CHN) | 82-93 | 589270 | -0.1 |  | -4.6 | 39.1 | 34.6 | 36.4 | 35.2 | 35 | 35.4 |  | 33 | 34.9 | 34.2 | 34 | 34.0333
China |  | LONGZHOU | LONGZHOU, China | 22.37N | 106.75E | 129 | 8.00 (CHN) | 82-06 | 594170 | 3.7 |  | -0.8 | 40.9 | 36.3 | 36.6 | 36.2 | 36 | 36.3667 |  | 34.8 | 35.2 | 34.9 | 35 | 34.9667
China |  | LU SHAN | LU SHAN, China | 29.58N | 115.98E | 1165 | 8.00 (CHN) | 82-06 | 585060 | -11 |  | -16.1 | 31.4 | 26.9 | 29.1 | 28.5 | 28 | 28.1667 |  | 25.5 | 27.8 | 27.2 | 27 | 26.8333
China |  | LUODIAN | LUODIAN, China | 25.43N | 106.77E | 441 | 8.00 (CHN) | 82-06 | 579160 | 0.8 |  | -2 | 42 | 34.9 | 35.7 | 35.8 | 35 | 35.4667 |  | 33.4 | 34.2 | 34.5 | 34 | 34.0333
China |  | LUSHI | LUSHI, China | 34.05N | 111.03E | 570 | 8.00 (CHN) | 82-06 | 570670 | -11.9 |  | -17.2 | 40.2 | 35.6 | 35.7 | 34.8 | 35 | 35.3667 |  | 33.3 | 33.9 | 32.9 | 33 | 33.3667
China |  | LUSI | LUSI, China | 32.07N | 121.60E | 10 | 8.00 (CHN) | 82-06 | 582650 | -5.3 |  | -9 | 38 | 33.7 | 35.3 | 34.3 | 34 | 34.4333 |  | 31 | 33.9 | 32.6 | 33 | 32.5
China |  | LUXI | LUXI, China | 24.53N | 103.77E | 1708 | 8.00 (CHN) | 83-06 | 568860 | -3.5 |  | -9.4 | 33.5 | 28.4 | 27.9 | 27.5 | 28 | 27.9333 |  | 27.1 | 26.5 | 26.3 | 27 | 26.6333
China |  | LUZHOU | LUZHOU, China | 28.88N | 105.43E | 336 | 8.00 (CHN) | 83-02 | 576020 | 1.9 |  | -1.4 | 40.4 | 34.4 | 36.3 | 37.1 | 36 | 35.9333 |  | 32.4 | 35 | 35.5 | 34 | 34.3 |  |  | Yukon
China |  | MACHENG | MACHENG, China | 31.18N | 114.97E | 59 | 8.00 (CHN) | 82-06 | 573990 | -5.8 |  | -12.4 | 40.7 | 35.1 | 37.4 | 36.7 | 36 | 36.4 |  | 33.6 | 36.2 | 35.4 | 35 | 35.0667
China |  | MADOI | MADOI, China | 34.92N | 98.22E | 4273 | 8.00 (CHN) | 82-06 | 560330 | -30.5 |  | -38.1 | 24.3 | 16.2 | 19.4 | 18.8 | 18 | 18.1333 |  | 14.2 | 16.9 | 16.4 | 16 | 15.8333
China |  | MANDAL | MANDAL, China | 42.53N | 110.13E | 1223 | 8.00 (CHN) | 82-06 | 531490 | -26.3 |  | -31.7 | 39.5 | 33.2 | 35.8 | 33.1 | 34 | 34.0333 |  | 31.2 | 33.2 | 31.1 | 32 | 31.8333
China |  | MANGNAI | MANGNAI, China | 38.25N | 90.85E | 2945 | 8.00 (CHN) | 82-06 | 518860 | -22.4 |  | -27.8 | 33.4 | 25.4 | 28.7 | 27.6 | 27 | 27.2333 |  | 23.3 | 26.4 | 25.2 | 25 | 24.9667
China |  | MAZONG SHAN | MAZONG SHAN, China | 41.80N | 97.03E | 1770 | 8.00 (CHN) | 82-06 | 523230 | -28.2 |  | -37.3 | 35.9 | 30.2 | 32.5 | 31.4 | 31 | 31.3667 |  | 28.5 | 30.7 | 29.4 | 30 | 29.5333
China |  | MEI XIAN | MEI XIAN, China | 24.30N | 116.12E | 84 | 8.00 (CHN) | 82-06 | 591170 | 1.4 |  | -2.9 | 40 | 35.6 | 36.9 | 36.2 | 36 | 36.2333 |  | 34.3 | 35.6 | 35.1 | 35 | 35
China |  | MENGDING | MENGDING, China | 23.57N | 99.08E | 512 | 8.00 (CHN) | 82-89 | 569450 | 6 |  | 3.1 | 40.4 | 36.5 | 33.5 | 33.1 | 34 | 34.3667 |  | 33.3 | 32 | 32 | 32 | 32.4333
China |  | MENGJIN | MENGJIN, China | 34.82N | 112.43E | 333 | 8.00 (CHN) | 83-06 | 570710 | -9.5 |  | -14.7 | 41.5 | 36.8 | 36.7 | 34.6 | 36 | 36.0333 |  | 35 | 34.3 | 32.8 | 34 | 34.0333
China |  | MENGLA | MENGLA, China | 21.50N | 101.58E | 633 | 8.00 (CHN) | 82-06 | 569690 | 7.1 |  | 2.7 | 40.3 | 33.6 | 32.6 | 32.5 | 33 | 32.9 |  | 32 | 31.2 | 31.2 | 31 | 31.4667
China |  | MENGSHAN | MENGSHAN, China | 24.20N | 110.52E | 145 | 8.00 (CHN) | 82-06 | 590580 | 0.2 |  | -2.5 | 40.5 | 34 | 36 | 35.8 | 35 | 35.2667 |  | 32.9 | 34.4 | 34.4 | 34 | 33.9
China |  | MENGZI | MENGZI, China | 23.38N | 103.38E | 1302 | 8.00 (CHN) | 82-06 | 569850 | 1.3 |  | -4.3 | 36 | 31.1 | 30.5 | 29.8 | 30 | 30.4667 |  | 29.6 | 29 | 28.7 | 29 | 29.1
China |  | MIANYANG | MIANYANG, China | 31.45N | 104.73E | 522 | 8.00 (CHN) | 82-06 | 561960 | -2.5 |  | -5.3 | 38.9 | 33.9 | 35.6 | 35.3 | 35 | 34.9333 |  | 32 | 33.5 | 33.6 | 33 | 33.0333
China |  | MINFENG | MINFENG, China | 37.07N | 82.72E | 1409 | 8.00 (CHN) | 82-98 | 518390 | N/A |  | N/A | N/A | 37.3 | 37.4 | 37.1 | 37 | 37.2667 |  | 34.3 | 35.7 | 35.2 | 35 | 35.0667
China |  | MINQIN | MINQIN, China | 38.63N | 103.08E | 1367 | 8.00 (CHN) | 82-06 | 526810 | -21.5 |  | -27.1 | 42.1 | 33.5 | 36.2 | 34.6 | 35 | 34.7667 |  | 31.8 | 33.9 | 32.7 | 33 | 32.8
China |  | MOHE | MOHE, China | 52.13N | 122.52E | 433 | 8.00 (CHN) | 82-06 | 501360 | -44 |  | -49.7 | 37.7 | 30.8 | 32.9 | 30.5 | 31 | 31.4 |  | 28.7 | 30.2 | 28 | 29 | 28.9667
China |  | MUDANJIANG | MUDANJIANG, China | 44.57N | 129.60E | 242 | 8.00 (CHN) | 82-06 | 540940 | -28.2 |  | -35.7 | 37.7 | 31.9 | 33.9 | 33 | 33 | 32.9333 |  | 30.1 | 31.4 | 30.4 | 31 | 30.6333
China |  | NAGQU | NAGQU, China | 31.48N | 92.07E | 4508 | 8.00 (CHN) | 82-06 | 552990 | -26.8 |  | -32.9 | 23.1 | 20.2 | 18.7 | 18.6 | 19 | 19.1667 |  | 17.6 | 17.2 | 16.9 | 17 | 17.2333
China |  | NANCHANG | NANCHANG, China | 28.60N | 115.92E | 50 | 8.00 (CHN) | 82-06 | 586060 | -2.8 |  | -7.2 | 40.7 | 34.2 | 37.6 | 36.6 | 36 | 36.1333 |  | 33 | 36.2 | 35.2 | 35 | 34.8
China |  | NANCHENG | NANCHENG, China | 27.58N | 116.65E | 82 | 8.00 (CHN) | 82-06 | 587150 | -3.1 |  | -8.1 | 40.2 | 34.6 | 37.5 | 36.6 | 36 | 36.2333 |  | 33.4 | 36.1 | 35.3 | 35 | 34.9333
China |  | NANCHONG | NANCHONG, China | 30.80N | 106.08E | 310 | 8.00 (CHN) | 82-06 | 574110 | -0.6 |  | -4.2 | 42.5 | 34.4 | 37 | 38.4 | 37 | 36.6 |  | 32.7 | 35.3 | 36.5 | 35 | 34.8333
China |  | NANJING | NANJING, China | 32.00N | 118.80E | 7 | 8.00 (CHN) | 82-06 | 582380 | -7.2 |  | -11.8 | 40.5 | 34.9 | 37.1 | 36.1 | 36 | 36.0333 |  | 32.9 | 35.7 | 34.6 | 34 | 34.4
China |  | NANNING | NANNING, China | 22.82N | 108.35E | 126 | 8.00 (CHN) | 82-06 | 594310 | 2.7 |  | -1.5 | 39.9 | 35.2 | 35.9 | 36 | 36 | 35.7 |  | 34 | 34.7 | 34.7 | 34 | 34.4667
China |  | NANPING | NANPING, China | 26.63N | 118.00E | 128 | 8.00 (CHN) | 82-06 | 588340 | -0.6 |  | -4.7 | 40.7 | 36 | 38.2 | 37.5 | 37 | 37.2333 |  | 34.6 | 36.7 | 36 | 36 | 35.7667
China |  | NANYANG | NANYANG, China | 33.03N | 112.58E | 131 | 8.00 (CHN) | 82-06 | 571780 | -8.5 |  | -15.9 | 39.5 | 36 | 36 | 34.9 | 36 | 35.6333 |  | 34.5 | 34.4 | 33.3 | 34 | 34.0667
China |  | NANYUE | NANYUE, China | 27.30N | 112.70E | 1268 | 8.00 (CHN) | 82-06 | 577760 | -9.9 |  | -14.7 | 32.1 | 25.5 | 27.7 | 27.6 | 27 | 26.9333 |  | 24.2 | 26.5 | 26.1 | 26 | 25.6
China |  | NAPO | NAPO, China | 23.30N | 105.95E | 794 | 8.00 (CHN) | 82-06 | 592090 | 0.6 |  | -4 | 36.9 | 32 | 32.3 | 32.5 | 32 | 32.2667 |  | 30.7 | 31.1 | 31.1 | 31 | 30.9667
China |  | NARAN BULAG | NARAN BULAG, China | 44.62N | 114.15E | 1183 | 8.00 (CHN) | 82-06 | 530830 | -33.1 |  | -37.8 | 39.6 | 31.7 | 34.4 | 32.3 | 33 | 32.8 |  | 29.5 | 31.6 | 29.5 | 30 | 30.2
China |  | NEIJIANG | NEIJIANG, China | 29.58N | 105.05E | 357 | 8.00 (CHN) | 82-01 | 575040 | 0.1 |  | -4.4 | 40.5 | 34.5 | 36.2 | 36.9 | 36 | 35.8667 |  | 32.7 | 34.9 | 35.4 | 34 | 34.3333
China |  | NENJIANG | NENJIANG, China | 49.17N | 125.23E | 243 | 8.00 (CHN) | 82-06 | 505570 | -36.7 |  | -45 | 40 | 33.1 | 33.3 | 30 | 32 | 32.1333 |  | 30.4 | 30.6 | 28.1 | 30 | 29.7
China |  | NYINGCHI | NYINGCHI, China | 29.57N | 94.47E | 3001 | 8.00 (CHN) | 82-06 | 563120 | -9.9 |  | -13.6 | 30.8 | 25.1 | 26.3 | 25.5 | 26 | 25.6333 |  | 23 | 24.2 | 23.5 | 24 | 23.5667
China |  | OTOG QI | OTOG QI, China | 39.10N | 107.98E | 1381 | 8.00 (CHN) | 82-06 | 535290 | -24.1 |  | -30.1 | 38.1 | 32.6 | 34.4 | 32.2 | 33 | 33.0667 |  | 30.6 | 32.4 | 30.4 | 31 | 31.1333
China |  | PAGRI | PAGRI, China | 27.73N | 89.08E | 4300 | 8.00 (CHN) | 82-06 | 557730 | -22.9 |  | -28.4 | 22.4 | 14.9 | 14.6 | 14.3 | 15 | 14.6 |  | 13 | 13.2 | 13 | 13 | 13.0667
China |  | PINGLIANG | PINGLIANG, China | 35.55N | 106.67E | 1348 | 8.00 (CHN) | 82-06 | 539150 | -15.9 |  | -21.1 | 36.2 | 32 | 32.3 | 30.9 | 32 | 31.7333 |  | 29.9 | 30.5 | 29.3 | 30 | 29.9
China |  | PINGTAN | PINGTAN, China | 25.52N | 119.78E | 31 | 8.00 (CHN) | 82-06 | 589440 | 4.6 |  | -0.1 | 38.4 | 31.9 | 32.7 | 32.8 | 32 | 32.4667 |  | 30.5 | 31.7 | 31.7 | 31 | 31.3
China |  | PINGWU | PINGWU, China | 32.42N | 104.52E | 894 | 8.00 (CHN) | 82-06 | 561930 | -4.3 |  | -10.4 | 38.5 | 33.3 | 34.7 | 34 | 34 | 34 |  | 31.2 | 32.9 | 32.1 | 32 | 32.0667
China |  | PISHAN | PISHAN, China | 37.62N | 78.28E | 1376 | 8.00 (CHN) | 82-06 | 518180 | -15.4 |  | -22.7 | 41.8 | 36.5 | 37.8 | 37.1 | 37 | 37.1333 |  | 34.4 | 35.8 | 34.9 | 35 | 35.0333
China |  | POTOU | POTOU, China | 38.08N | 116.55E | 13 | 8.00 (CHN) | 97-06 | 546180 | -14.4 |  | -18.7 | 42.6 | 37.8 | 37.7 | 34.3 | 37 | 36.6 |  | 36 | 35.5 | 32.8 | 35 | 34.7667
China |  | PUCHENG | PUCHENG, China | 27.92N | 118.53E | 275 | 8.00 (CHN) | 82-06 | 587310 | -4.3 |  | -7.5 | 40.6 | 34 | 36.9 | 36.4 | 36 | 35.7667 |  | 32.6 | 35.2 | 34.9 | 34 | 34.2333
China |  | QAMDO | QAMDO, China | 31.15N | 97.17E | 3307 | 8.00 (CHN) | 82-06 | 561370 | -15.3 |  | -19.1 | 32 | 28.5 | 28.5 | 27.7 | 28 | 28.2333 |  | 26.5 | 26.5 | 25.9 | 26 | 26.3
China |  | QIAN GORLOS | QIAN GORLOS, China | 45.08N | 124.87E | 136 | 8.00 (CHN) | 82-06 | 509490 | -27.7 |  | -38 | 37.9 | 33.6 | 33.3 | 32.1 | 33 | 33 |  | 31.4 | 31.4 | 30.4 | 31 | 31.0667
China |  | QIEMO/QARQAN | QIEMO/QARQAN, China | 38.15N | 85.55E | 1248 | 8.00 (CHN) | 82-98 | 518550 | -18.6 |  | -24.4 | 41.6 | 36.6 | 37.1 | 36.9 | 37 | 36.8667 |  | 33.9 | 35.4 | 35.1 | 35 | 34.8
China |  | QINGDAO | QINGDAO, China | 36.07N | 120.33E | 77 | 8.00 (CHN) | 82-06 | 548570 | -10.5 |  | -15.4 | 40.9 | 33.6 | 35 | 33.1 | 34 | 33.9 |  | 30.2 | 32.2 | 31.2 | 31 | 31.2
China |  | QINGJIANG | QINGJIANG, China | 33.60N | 119.03E | 19 | 8.00 (CHN) | 82-00 | 581440 | -9 |  | -14.5 | 40 | 33.7 | 35.7 | 34.2 | 35 | 34.5333 |  | 31.9 | 34.2 | 32.6 | 33 | 32.9
China |  | QINGLONG | QINGLONG, China | 40.40N | 118.95E | 228 | 8.00 (CHN) | 82-06 | 544360 | -20.4 |  | -26.9 | 39.3 | 34.6 | 35.2 | 32.4 | 34 | 34.0667 |  | 32.3 | 32.5 | 31 | 32 | 31.9333
China |  | QINGYUAN | QINGYUAN, China | 42.10N | 124.95E | 235 | 8.00 (CHN) | 82-06 | 542590 | -29.8 |  | -36.9 | 38.3 | 33.2 | 34.1 | 33.1 | 33 | 33.4667 |  | 30.9 | 31.7 | 31.1 | 31 | 31.2333
China |  | QINZHOU | QINZHOU, China | 21.95N | 108.62E | 6 | 8.00 (CHN) | 82-06 | 596320 | 4.3 |  | -0.1 | 38.3 | 33.9 | 35 | 35 | 35 | 34.6333 |  | 32.8 | 33.5 | 33.8 | 33 | 33.3667
China |  | QIONGHAI | QIONGHAI, China | 19.23N | 110.47E | 25 | 8.00 (CHN) | 82-06 | 598550 | 9 |  | 3.9 | 38.8 | 35.3 | 35.7 | 35 | 35 | 35.3333 |  | 34 | 34.4 | 33.8 | 34 | 34.0667
China |  | QIQIHAR | QIQIHAR, China | 47.38N | 123.92E | 148 | 8.00 (CHN) | 82-06 | 507450 | -29.7 |  | -36.8 | 40.3 | 33.9 | 34.6 | 31.9 | 33 | 33.4667 |  | 31.3 | 32.1 | 29.8 | 31 | 31.0667
China |  | QITAI | QITAI, China | 44.02N | 89.57E | 794 | 8.00 (CHN) | 82-06 | 513790 | -31.3 |  | -39.9 | 43 | 34.4 | 36.8 | 36 | 36 | 35.7333 |  | 32.4 | 34.2 | 33.8 | 33 | 33.4667
China |  | QIXIAN SHAN | QIXIAN SHAN, China | 27.95N | 117.83E | 1415 | 8.00 (CHN) | 82-91 | 587260 | -10.2 |  | -13.9 | 33.8 | 25.9 | 27.6 | 26.5 | 27 | 26.6667 |  | 24.3 | 26.4 | 25.2 | 25 | 25.3
China |  | QU XIAN | QU XIAN, China | 28.97N | 118.87E | 71 | 8.00 (CHN) | 82-06 | 586330 | -3.8 |  | -8.3 | 41.9 | 35.2 | 38.1 | 37.5 | 37 | 36.9333 |  | 33.7 | 36.5 | 35.9 | 35 | 35.3667
China |  | QUMARLEB | QUMARLEB, China | 34.13N | 95.78E | 4176 | 8.00 (CHN) | 82-06 | 560210 | -29.5 |  | -35 | 25.2 | 18.6 | 20.4 | 20.1 | 20 | 19.7 |  | 16.1 | 18.2 | 17.8 | 17 | 17.3667
China |  | RIZHAO | RIZHAO, China | 35.43N | 119.53E | 37 | 8.00 (CHN) | 82-06 | 549450 | -9.2 |  | -12.6 | 39.8 | 31.6 | 32.7 | 31.6 | 32 | 31.9667 |  | 28.5 | 30.9 | 30.3 | 30 | 29.9
China |  | RONGJIANG | RONGJIANG, China | 25.97N | 108.53E | 287 | 8.00 (CHN) | 82-06 | 579320 | -0.9 |  | -3.5 | 39.7 | 34.3 | 36.3 | 36.4 | 36 | 35.6667 |  | 33 | 34.8 | 35 | 34 | 34.2667
China |  | RUILI | RUILI, China | 24.02N | 97.83E | 776 | 8.00 (CHN) | 82-06 | 568380 | 4.3 |  | 0.9 | 37.1 | 32.2 | 31.1 | 32 | 32 | 31.7667 |  | 30.5 | 29.6 | 30.5 | 30 | 30.2
China |  | RUOERGAI | RUOERGAI, China | 33.58N | 102.97E | 3441 | 8.00 (CHN) | 82-06 | 560790 | -25.8 |  | -30.1 | 26.4 | 19.8 | 22.1 | 21.5 | 21 | 21.1333 |  | 17.9 | 20.1 | 19.5 | 19 | 19.1667
China |  | RUOQIANG | RUOQIANG, China | 39.03N | 88.17E | 889 | 8.00 (CHN) | 82-06 | 517770 | -17.3 |  | -22.8 | 44 | 38.8 | 40 | 39.1 | 39 | 39.3 |  | 36.9 | 38.3 | 37.3 | 38 | 37.5
China |  | SANGZHI | SANGZHI, China | 29.40N | 110.17E | 322 | 8.00 (CHN) | 82-06 | 575540 | -2.7 |  | -6.2 | 40.4 | 34.4 | 36.6 | 36.7 | 36 | 35.9 |  | 32.7 | 34.9 | 35.2 | 34 | 34.2667
China |  | SANHU DAO | SANHU DAO, China | 16.53N | 111.62E | 5 | 8.00 (CHN) | 82-06 | 599850 | 18.6 |  | 12.3 | 42.7 | 34.5 | 34.2 | 33.6 | 34 | 34.1 |  | 33.3 | 33.1 | 32.7 | 33 | 33.0333
China |  | SANSUI | SANSUI, China | 26.97N | 108.67E | 631 | 8.00 (CHN) | 82-06 | 578320 | -4.6 |  | -8.5 | 37.6 | 32 | 33.9 | 34 | 33 | 33.3 |  | 30.7 | 32.5 | 32.6 | 32 | 31.9333
China |  | SERTAR | SERTAR, China | 32.28N | 100.33E | 3896 | 8.00 (CHN) | 82-06 | 561520 | -26.6 |  | -31 | 24.2 | 20.7 | 21.3 | 20.5 | 21 | 20.8333 |  | 18.3 | 19.6 | 18.8 | 19 | 18.9
China |  | SHACHE | SHACHE, China | 38.43N | 77.27E | 1232 | 8.00 (CHN) | 82-06 | 518110 | -15.3 |  | -23.5 | 40 | 35.7 | 36.1 | 35 | 36 | 35.6 |  | 33.7 | 34.5 | 32.9 | 34 | 33.7
China |  | SHANGCHUAN DAO | SHANGCHUAN DAO, China | 21.73N | 112.77E | 18 | 8.00 (CHN) | 82-06 | 596730 | 6.2 |  | 1.8 | 37.7 | 32.8 | 33.5 | 33.6 | 33 | 33.3 |  | 31.6 | 32.3 | 32.5 | 32 | 32.1333
China |  | SHANGHAI | SHANGHAI, China | 31.40N | 121.47E | 4 | 8.00 (CHN) | 91-06 | 583620 | -3.7 |  | -6.7 | 39 | 35.1 | 36.5 | 35.9 | 36 | 35.8333 |  | 32.6 | 35.3 | 34.3 | 34 | 34.0667
China |  | SHANGHAI/HONGQIAO | SHANGHAI/HONGQIAO, China | 31.17N | 121.43E | 7 | 8.00 (CHN) | 82-06 | 583670 | -5.6 |  | -9.4 | 40.1 | 35 | 37.1 | 36.2 | 36 | 36.1 |  | 32.8 | 35.6 | 34.2 | 34 | 34.2
China |  | SHANGZHI | SHANGZHI, China | 45.22N | 127.97E | 191 | 8.00 (CHN) | 82-06 | 509680 | -34.9 |  | -43.7 | 35.1 | 31.2 | 32.1 | 31.3 | 32 | 31.5333 |  | 29.6 | 30.2 | 29.2 | 30 | 29.6667
China |  | SHANTOU | SHANTOU, China | 23.40N | 116.68E | 3 | 8.00 (CHN) | 82-06 | 593160 | 4.5 |  | 0.2 | 39.1 | 33.8 | 35.1 | 34.8 | 35 | 34.5667 |  | 32.1 | 33.6 | 33.3 | 33 | 33
China |  | SHANWEI | SHANWEI, China | 22.78N | 115.37E | 5 | 8.00 (CHN) | 82-06 | 595010 | 5.8 |  | 2.2 | 38.4 | 32.1 | 33.2 | 33.4 | 33 | 32.9 |  | 31.2 | 32 | 32.3 | 32 | 31.8333
China |  | SHAOGUAN | SHAOGUAN, China | 24.80N | 113.58E | 68 | 8.00 (CHN) | 82-06 | 590820 | 0.3 |  | -3.3 | 40.4 | 35.3 | 37.1 | 36.6 | 36 | 36.3333 |  | 33.9 | 35.6 | 35.3 | 35 | 34.9333
China |  | SHAOWU | SHAOWU, China | 27.33N | 117.47E | 219 | 8.00 (CHN) | 82-06 | 587250 | -4.1 |  | -8.3 | 41 | 35.1 | 37.5 | 36.6 | 36 | 36.4 |  | 33.7 | 35.8 | 35.2 | 35 | 34.9
China |  | SHAOYANG | SHAOYANG, China | 27.23N | 111.47E | 248 | 8.00 (CHN) | 82-06 | 577660 | -3.4 |  | -8.3 | 39.5 | 33.8 | 36.4 | 36.2 | 35 | 35.4667 |  | 32.6 | 35.2 | 34.7 | 34 | 34.1667
China |  | SHENG SHANG | SHENG SHANG, China | 30.72N | 122.82E | 197 | 8.00 (CHN) | 82-90 | 584730 | -2 |  | -6.2 | 33.7 | 27.3 | 30.6 | 30.6 | 30 | 29.5 |  | 25.7 | 28.8 | 29.4 | 28 | 27.9667
China |  | SHENGSI | SHENGSI, China | 30.73N | 122.45E | 81 | 8.00 (CHN) | 82-06 | 584720 | -2.4 |  | -6.6 | 36.6 | 30.7 | 32.8 | 32.9 | 32 | 32.1333 |  | 28.6 | 31.6 | 31.2 | 30 | 30.4667
China |  | SHENGXIAN | SHENGXIAN, China | 29.60N | 120.82E | 108 | 8.00 (CHN) | 82-06 | 585560 | -5.3 |  | -9.1 | 41.2 | 35.3 | 38 | 37.5 | 37 | 36.9333 |  | 33.6 | 36.5 | 35.6 | 35 | 35.2333
China |  | SHENYANG | SHENYANG, China | 41.73N | 123.52E | 43 | 8.00 (CHN) | 82-06 | 543420 | -24.8 |  | -32.2 | 37 | 32.6 | 33.2 | 32.8 | 33 | 32.8667 |  | 30.8 | 31.7 | 31.2 | 31 | 31.2333
China |  | SHENZHEN | SHENZHEN, China | 22.55N | 114.10E | 18 | 8.00 (CHN) | 82-06 | 594930 | 5 |  | 0.7 | 38.6 | 33.9 | 35 | 34.8 | 35 | 34.5667 |  | 32.8 | 33.7 | 33.6 | 33 | 33.3667
China |  | SHEYANG | SHEYANG, China | 33.77N | 120.25E | 7 | 8.00 (CHN) | 82-06 | 581500 | -8.1 |  | -12 | 39.5 | 33.9 | 35.7 | 34.2 | 35 | 34.6 |  | 31.6 | 34.1 | 32.8 | 33 | 32.8333
China |  | SHIJIAZHUANG | SHIJIAZHUANG, China | 38.03N | 114.42E | 81 | 8.00 (CHN) | 82-06 | 536980 | -11.5 |  | -17.5 | 42.8 | 38 | 38.4 | 34.9 | 37 | 37.1 |  | 35.9 | 35.8 | 33.1 | 35 | 34.9333
China |  | SHIPU | SHIPU, China | 29.20N | 121.95E | 127 | 8.00 (CHN) | 82-06 | 585690 | -3.1 |  | -6.6 | 37.8 | 31.1 | 33.9 | 33.7 | 33 | 32.9 |  | 29.4 | 32.2 | 32.2 | 31 | 31.2667
China |  | SHIQUANHE | SHIQUANHE, China | 32.50N | 80.08E | 4280 | 8.00 (CHN) | 82-06 | 552280 | -27.3 |  | -36.3 | 28.5 | 22.7 | 24.2 | 23.2 | 23 | 23.3667 |  | 21 | 22.9 | 21.6 | 22 | 21.8333
China |  | SHISANJIANFANG | SHISANJIANFANG, China | 43.22N | 91.73E | 792 | 8.00 (CHN) | 82-06 | 514950 | -21 |  | -28.2 | 44.5 | 38 | 40 | 38.6 | 39 | 38.8667 |  | 35.5 | 37.5 | 36.5 | 37 | 36.5
China |  | SIMAO | SIMAO, China | 22.77N | 100.98E | 1303 | 8.00 (CHN) | 82-06 | 569640 | 3.6 |  | -0.6 | 35.9 | 30.3 | 29.3 | 29.2 | 30 | 29.6 |  | 28.6 | 27.8 | 27.9 | 28 | 28.1
China |  | SINAN | SINAN, China | 27.95N | 108.25E | 418 | 8.00 (CHN) | 82-06 | 577310 | 0.2 |  | -2.3 | 40.3 | 34.6 | 36.6 | 37 | 36 | 36.0667 |  | 33.2 | 35.1 | 35.5 | 35 | 34.6 |  |  | Yukon
China |  | SIPING | SIPING, China | 43.18N | 124.33E | 167 | 8.00 (CHN) | 82-06 | 541570 | -25.5 |  | -32.9 | 36.7 | 32.9 | 32.7 | 32 | 33 | 32.5333 |  | 30.8 | 30.9 | 30.2 | 31 | 30.6333
China |  | SOG XIAN | SOG XIAN, China | 31.88N | 93.78E | 4024 | 8.00 (CHN) | 82-06 | 561060 | -22.9 |  | -30.8 | 28.5 | 22.8 | 22.3 | 22.2 | 22 | 22.4333 |  | 19.7 | 20.6 | 20.4 | 20 | 20.2333
China |  | SONGPAN | SONGPAN, China | 32.65N | 103.57E | 2852 | 8.00 (CHN) | 83-06 | 561820 | -16 |  | -19.4 | 30.7 | 25.4 | 26.8 | 26.5 | 26 | 26.2333 |  | 22.9 | 24.8 | 24.6 | 24 | 24.1
China |  | SUIFENHE | SUIFENHE, China | 44.38N | 131.15E | 498 | 8.00 (CHN) | 82-06 | 540960 | -28.7 |  | -35.7 | 36.9 | 29.4 | 31.4 | 30.6 | 30 | 30.4667 |  | 27.1 | 28.9 | 28.1 | 28 | 28.0333
China |  | SUNWU | SUNWU, China | 49.43N | 127.35E | 235 | 8.00 (CHN) | 82-06 | 505640 | -36.7 |  | -43.4 | 38.3 | 32.1 | 32.3 | 30.1 | 32 | 31.5 |  | 29.8 | 29.8 | 28.1 | 29 | 29.2333
China |  | TACHENG | TACHENG, China | 46.73N | 83.00E | 535 | 8.00 (CHN) | 82-06 | 511330 | -26.3 |  | -34.6 | 41.3 | 34.2 | 36.6 | 36.3 | 36 | 35.7 |  | 32.4 | 34.3 | 33.8 | 34 | 33.5
China |  | TAI SHAN | TAI SHAN, China | 36.25N | 117.10E | 1536 | 8.00 (CHN) | 82-06 | 548260 | -20 |  | -24.5 | 28.7 | 23.6 | 24.2 | 22.7 | 24 | 23.5 |  | 21.9 | 22.7 | 21.6 | 22 | 22.0667
China |  | TAILAI | TAILAI, China | 46.40N | 123.42E | 150 | 8.00 (CHN) | 82-06 | 508440 | -27.7 |  | -35.7 | 40.2 | 35 | 35.2 | 32.8 | 34 | 34.3333 |  | 32.1 | 32.4 | 30.7 | 32 | 31.7333
China |  | TAISHAN | TAISHAN, China | 27.00N | 120.70E | 107 | 8.00 (CHN) | 82-92 | 588530 | 1.5 |  | -2.9 | 35.8 | 28.2 | 30.5 | 31.4 | 30 | 30.0333 |  | 27.2 | 29.4 | 30.3 | 29 | 28.9667
China |  | TAIYUAN | TAIYUAN, China | 37.78N | 112.55E | 779 | 8.00 (CHN) | 82-06 | 537720 | -19.1 |  | -23.4 | 39.6 | 35.1 | 34.9 | 33.2 | 34 | 34.4 |  | 32.3 | 33 | 31.2 | 32 | 32.1667
China |  | TANGSHAN | TANGSHAN, China | 39.67N | 118.15E | 29 | 8.00 (CHN) | 82-06 | 545340 | -15.5 |  | -22.5 | 40.3 | 35.2 | 35.9 | 33 | 35 | 34.7 |  | 32.9 | 33.6 | 31.6 | 33 | 32.7
China |  | TAOXIAN | TAOXIAN, China | 41.63N | 123.48E | 62 | 8.00 (CHN) | 92-06 | 543424 | -28.7 |  | -37 | 38.3 | 34 | 33.9 | 32.1 | 33 | 33.3333 |  | 32 | 32.2 | 30.9 | 32 | 31.7
China |  | TENGCHONG | TENGCHONG, China | 25.12N | 98.48E | 1649 | 8.00 (CHN) | 82-06 | 567390 | -0.3 |  | -2.5 | 30.9 | 27.5 | 27 | 28 | 28 | 27.5 |  | 25.5 | 25.3 | 26.4 | 26 | 25.7333
China |  | TIANJIN | TIANJIN, China | 39.10N | 117.17E | 5 | 8.00 (CHN) | 82-06 | 545270 | -13.1 |  | -18.7 | 41.2 | 36.2 | 36.4 | 33.9 | 36 | 35.5 |  | 34.1 | 34.4 | 32.6 | 34 | 33.7
China |  | TIANMU SHAN (MTNS) | TIANMU SHAN (MTNS), China | 30.35N | 119.42E | 1494 | 8.00 (CHN) | 82-98 | 584450 | -14.7 |  | -19.2 | 31.4 | 24.3 | 27.2 | 26.7 | 26 | 26.0667 |  | 22.5 | 25.7 | 24.7 | 24 | 24.3
China |  | TIANSHUI | TIANSHUI, China | 34.58N | 105.75E | 1143 | 8.00 (CHN) | 82-03 | 570060 | -11.4 |  | -16.2 | 39 | 32.2 | 34.4 | 33.2 | 33 | 33.2667 |  | 30.3 | 32.1 | 31.1 | 31 | 31.1667
China |  | TIKANLIK | TIKANLIK, China | 40.63N | 87.70E | 847 | 8.00 (CHN) | 82-06 | 517650 | -19.3 |  | -23 | 43.2 | 38 | 39.2 | 38.6 | 39 | 38.6 |  | 36.2 | 37.3 | 36.6 | 37 | 36.7
China |  | TINGRI | TINGRI, China | 28.63N | 87.08E | 4300 | 8.00 (CHN) | 82-06 | 556640 | -21.7 |  | -27.1 | 24.9 | 22.1 | 21.5 | 20 | 21 | 21.2 |  | 20.6 | 20.2 | 18.7 | 20 | 19.8333
China |  | TONGCHUAN | TONGCHUAN, China | 35.17N | 109.05E | 914 | 8.00 (CHN) | 82-98 | 539470 | N/A |  | N/A | N/A | 33.2 | 33.5 | 33.3 | 33 | 33.3333 |  | 31.5 | 31.6 | 30.6 | 31 | 31.2333
China |  | TONGDAO | TONGDAO, China | 26.17N | 109.78E | 397 | 8.00 (CHN) | 82-06 | 578450 | -3.6 |  | -6.4 | 38.2 | 33 | 34.5 | 34.6 | 34 | 34.0333 |  | 31.5 | 33.1 | 33.4 | 33 | 32.6667
China |  | TONGDE | TONGDE, China | 35.27N | 100.65E | 3290 | 8.00 (CHN) | 82-98 | 529570 | -29.7 |  | -35.2 | 29 | 21.7 | 23.3 | 23.7 | 23 | 22.9 |  | 19.5 | 21 | 21.6 | 21 | 20.7
China |  | TONGHE | TONGHE, China | 45.97N | 128.73E | 110 | 8.00 (CHN) | 82-06 | 509630 | -34.1 |  | -40 | 36.6 | 31.8 | 32.7 | 31.5 | 32 | 32 |  | 29.8 | 30.4 | 29.1 | 30 | 29.7667
China |  | TONGLIAO | TONGLIAO, China | 43.60N | 122.27E | 180 | 8.00 (CHN) | 82-06 | 541350 | -24.8 |  | -32.8 | 39.2 | 34.7 | 34.4 | 33.5 | 34 | 34.2 |  | 32.1 | 32.5 | 31.4 | 32 | 32
China |  | TRUONG SA | TRUONG SA, China | 8.65N | 111.92E | 3 | 8.00 (CHN) | 92-06 | 489200 | 18.3 |  | 9.9 | 41 | 33.1 | 32 | 32 | 32 | 32.3667 |  | 32 | 31.2 | 31.2 | 31 | 31.4667
China |  | TULIHE | TULIHE, China | 50.45N | 121.70E | 733 | 8.00 (CHN) | 82-06 | 504340 | -43.5 |  | -49.3 | 36.7 | 29.3 | 30.4 | 29.7 | 30 | 29.8 |  | 27.2 | 28 | 26.7 | 27 | 27.3
China |  | TUOTUOHE | TUOTUOHE, China | 34.22N | 92.43E | 4535 | 8.00 (CHN) | 82-06 | 560040 | -32.1 |  | -43.9 | 24.4 | 18.8 | 19.5 | 18.7 | 19 | 19 |  | 15.9 | 17.1 | 16.6 | 17 | 16.5333
China |  | TURPAN | TURPAN, China | 42.93N | 89.20E | 37 | 8.00 (CHN) | 82-06 | 515730 | -14.6 |  | -20.7 | 48.5 | 42.1 | 43.4 | 42.4 | 43 | 42.6333 |  | 40.4 | 41.8 | 40.4 | 41 | 40.8667
China |  | ULIASTAI | ULIASTAI, China | 45.52N | 116.97E | 840 | 8.00 (CHN) | 82-06 | 509150 | -33.2 |  | -40 | 40 | 33.2 | 35.2 | 33.5 | 34 | 33.9667 |  | 30.8 | 32 | 30.9 | 31 | 31.2333
China |  | WANYUAN | WANYUAN, China | 32.07N | 108.03E | 674 | 8.00 (CHN) | 82-06 | 572370 | -4.7 |  | -7.9 | 39.2 | 33.4 | 34.7 | 35.4 | 35 | 34.5 |  | 31.7 | 33.2 | 33.7 | 33 | 32.8667
China |  | WEICHANG | WEICHANG, China | 41.93N | 117.75E | 844 | 8.00 (CHN) | 82-06 | 543110 | -23.6 |  | -28.1 | 38.4 | 31.5 | 33.4 | 30.8 | 32 | 31.9 |  | 29.3 | 30.4 | 28.8 | 30 | 29.5
China |  | WEIFANG | WEIFANG, China | 36.77N | 119.18E | 22 | 8.00 (CHN) | 82-06 | 548430 | -13.7 |  | -17.8 | 41.1 | 36.1 | 36.2 | 34.2 | 36 | 35.5 |  | 33.9 | 34.5 | 32.5 | 34 | 33.6333
China |  | WEINING | WEINING, China | 26.87N | 104.28E | 2236 | 8.00 (CHN) | 82-06 | 566910 | -7.9 |  | -12.5 | 30.6 | 26 | 25.6 | 25.7 | 26 | 25.7667 |  | 24 | 24.2 | 24.2 | 24 | 24.1333
China |  | WENZHOU | WENZHOU, China | 28.02N | 120.67E | 7 | 8.00 (CHN) | 82-01 | 586590 | -1.1 |  | -4 | 39.6 | 34 | 36 | 34.8 | 35 | 34.9333 |  | 32.2 | 34.2 | 33.5 | 33 | 33.3
China |  | WU LU MU QI | WU LU MU QI, China | 43.80N | 87.65E | 947 | 8.00 (CHN) | 82-06 | 514630 | -23.9 |  | -31 | 41.5 | 33.7 | 35.9 | 35.1 | 35 | 34.9 |  | 31.9 | 33.6 | 33 | 33 | 32.8333
China |  | WUDAOLIANG | WUDAOLIANG, China | 35.22N | 93.08E | 4613 | 8.00 (CHN) | 82-06 | 529080 | -30 |  | -36.3 | 22.6 | 16.4 | 18 | 17.2 | 17 | 17.2 |  | 13.1 | 15.3 | 14.9 | 14 | 14.4333
China |  | WUDU | WUDU, China | 33.40N | 104.92E | 1079 | 8.00 (CHN) | 82-06 | 560960 | -4.7 |  | -8.3 | 39.4 | 34.4 | 35.9 | 35.1 | 35 | 35.1333 |  | 32.1 | 34.1 | 33.2 | 33 | 33.1333
China |  | WUGANG | WUGANG, China | 26.73N | 110.63E | 340 | 8.00 (CHN) | 82-06 | 578530 | -3.6 |  | -9.4 | 39.1 | 33.7 | 36.1 | 35.7 | 35 | 35.1667 |  | 32.4 | 34.9 | 34.3 | 34 | 33.8667
China |  | WUHAN | WUHAN, China | 30.62N | 114.13E | 23 | 8.00 (CHN) | 82-06 | 574940 | -4.9 |  | -11.8 | 40.3 | 35 | 37.2 | 36.8 | 36 | 36.3333 |  | 33.5 | 36.1 | 35.4 | 35 | 35
China |  | WUHU | WUHU, China | 31.33N | 118.35E | 16 | 8.00 (CHN) | 82-06 | 583380 | -6 |  | -10.4 | 42.4 | 35 | 37.6 | 36.7 | 36 | 36.4333 |  | 33.2 | 36.3 | 35.2 | 35 | 34.9
China |  | WUSHAOLING | WUSHAOLING, China | 37.20N | 102.87E | 3044 | 8.00 (CHN) | 82-06 | 527870 | -23.2 |  | -28.9 | 28.6 | 19.4 | 22.4 | 21.2 | 21 | 21 |  | 17.6 | 20 | 19.1 | 19 | 18.9
China |  | WUTAI SHAN | WUTAI SHAN, China | 38.95N | 113.52E | 2210 | 8.00 (CHN) | 82-06 | 535880 | -30.2 |  | -39.7 | 29.1 | 21.7 | 22.4 | 20.6 | 22 | 21.5667 |  | 19.3 | 20.2 | 18.6 | 19 | 19.3667
China |  | WUYISHAN | WUYISHAN, China | 27.77N | 118.03E | 221 | 8.00 (CHN) | 92-06 | 587300 | -4.2 |  | -12.2 | 39.4 | 34.9 | 36.9 | 36.2 | 36 | 36 |  | 33.2 | 35.3 | 34.9 | 34 | 34.4667
China |  | WUZHOU | WUZHOU, China | 23.48N | 111.30E | 120 | 8.00 (CHN) | 82-06 | 592650 | 1.5 |  | -1.6 | 39.6 | 35.2 | 36.1 | 36 | 36 | 35.7667 |  | 34 | 35.1 | 34.8 | 35 | 34.6333
China |  | XAINZA | XAINZA, China | 30.95N | 88.63E | 4670 | 8.00 (CHN) | 82-06 | 554720 | -24.3 |  | -30.3 | 23.4 | 20.1 | 19.1 | 18.1 | 19 | 19.1 |  | 18.1 | 17.6 | 16.5 | 17 | 17.4
China |  | XI UJIMQIN QI | XI UJIMQIN QI, China | 44.58N | 117.60E | 997 | 8.00 (CHN) | 82-06 | 540120 | -32.5 |  | -39.3 | 38 | 31.3 | 33.5 | 31.7 | 32 | 32.1667 |  | 29.1 | 30 | 29.2 | 29 | 29.4333
China |  | XIAMEN | XIAMEN, China | 24.48N | 118.08E | 139 | 8.00 (CHN) | 82-06 | 591340 | 4.5 |  | 1.1 | 39.4 | 34 | 35.7 | 35.2 | 35 | 34.9667 |  | 32.2 | 34.1 | 34 | 33 | 33.4333
China |  | XIAN | XIAN, China | 34.30N | 108.93E | 398 | 8.00 (CHN) | 82-06 | 570360 | -9.9 |  | -16.5 | 42.6 | 38 | 37.8 | 36.1 | 37 | 37.3 |  | 35.8 | 36.1 | 33.9 | 35 | 35.2667
China |  | XIAOERGOU | XIAOERGOU, China | 49.20N | 123.72E | 288 | 8.00 (CHN) | 82-06 | 505480 | N/A |  | N/A | N/A | 34.4 | 34.6 | 30.9 | 33 | 33.3 |  | 31.6 | 32.1 | 29.2 | 31 | 30.9667
China |  | XICHANG | XICHANG, China | 27.90N | 102.27E | 1599 | 8.00 (CHN) | 82-06 | 565710 | -0.2 |  | -3.4 | 37.4 | 33 | 31.9 | 31.6 | 32 | 32.1667 |  | 31.1 | 30.3 | 30.1 | 31 | 30.5
China |  | XIFENGZHEN | XIFENGZHEN, China | 35.73N | 107.63E | 1423 | 8.00 (CHN) | 82-06 | 539230 | -15.4 |  | -21 | 35.8 | 31.1 | 31.2 | 30.1 | 31 | 30.8 |  | 29 | 29.6 | 28.1 | 29 | 28.9
China |  | XIGAZE | XIGAZE, China | 29.25N | 88.88E | 3837 | 8.00 (CHN) | 82-06 | 555780 | -17.3 |  | -20.6 | 30.3 | 25.6 | 24.8 | 23.7 | 25 | 24.7 |  | 24 | 23.1 | 22 | 23 | 23.0333
China |  | XIHUA | XIHUA, China | 33.78N | 114.52E | 53 | 8.00 (CHN) | 82-06 | 571930 | -9.7 |  | -15.4 | 41.4 | 36.7 | 36.5 | 34.8 | 36 | 36 |  | 35.1 | 35 | 33.2 | 34 | 34.4333
China |  | XILIN HOT | XILIN HOT, China | 43.95N | 116.12E | 1004 | 8.00 (CHN) | 82-06 | 541020 | -31.4 |  | -37.5 | 41.5 | 32.9 | 35.2 | 32.9 | 34 | 33.6667 |  | 30.7 | 32.2 | 30.6 | 31 | 31.1667
China |  | XIN BARAG YOUQI | XIN BARAG YOUQI, China | 48.67N | 116.82E | 556 | 8.00 (CHN) | 82-06 | 506030 | -32.1 |  | -39.7 | 43 | 34.1 | 35.6 | 33.9 | 35 | 34.5333 |  | 31 | 32.2 | 30.8 | 31 | 31.3333
China |  | XINGREN | XINGREN, China | 25.43N | 105.18E | 1379 | 8.00 (CHN) | 82-06 | 579020 | -2 |  | -4.8 | 34.7 | 30 | 29.6 | 29.4 | 30 | 29.6667 |  | 28.2 | 28.3 | 28.2 | 28 | 28.2333
China |  | XINGTAI | XINGTAI, China | 37.07N | 114.50E | 78 | 8.00 (CHN) | 82-06 | 537980 | -10.2 |  | -15 | 41.7 | 38.1 | 37.5 | 34.9 | 37 | 36.8333 |  | 35.8 | 35.5 | 33.3 | 35 | 34.8667
China |  | XINING | XINING, China | 36.62N | 101.77E | 2296 | 8.00 (CHN) | 82-06 | 528660 | -19.2 |  | -24 | 34.8 | 27.3 | 30.3 | 29.3 | 29 | 28.9667 |  | 25.4 | 27.8 | 27.1 | 27 | 26.7667
China |  | XINXIAN | XINXIAN, China | 36.23N | 115.67E | 38 | 8.00 (CHN) | 82-06 | 548080 | -13.4 |  | -21.4 | 41.3 | 37.4 | 36.2 | 34 | 36 | 35.8667 |  | 35.1 | 34.5 | 32.5 | 34 | 34.0333
China |  | XINYANG | XINYANG, China | 32.13N | 114.05E | 115 | 8.00 (CHN) | 82-06 | 572970 | -7.6 |  | -13.3 | 40 | 34.5 | 36.5 | 35.6 | 36 | 35.5333 |  | 32.9 | 35 | 33.8 | 34 | 33.9
China |  | XINYI | XINYI, China | 22.35N | 110.93E | 84 | 8.00 (CHN) | 82-06 | 594560 | 4.4 |  | 0.5 | 38.5 | 34.9 | 35.7 | 35.5 | 35 | 35.3667 |  | 33.7 | 34.7 | 34.4 | 34 | 34.2667
China |  | XISHA DAO | XISHA DAO, China | 16.83N | 112.33E | 5 | 8.00 (CHN) | 82-06 | 599810 | 18.6 |  | 12.5 | 39.4 | 32.5 | 32.2 | 32.4 | 32 | 32.3667 |  | 31.9 | 31.6 | 31.6 | 32 | 31.7
China |  | XIUSHUI | XIUSHUI, China | 29.03N | 114.58E | 147 | 8.00 (CHN) | 82-06 | 575980 | -5.3 |  | -10 | 41.3 | 35.1 | 38.2 | 37.2 | 37 | 36.8333 |  | 33.7 | 36.6 | 35.8 | 35 | 35.3667 |  |  | Yukon
China |  | XUNWU | XUNWU, China | 24.95N | 115.65E | 299 | 8.00 (CHN) | 82-06 | 591020 | -1.8 |  | -5.6 | 39.2 | 34.3 | 35.9 | 35.1 | 35 | 35.1 |  | 32.6 | 34.4 | 34 | 34 | 33.6667
China |  | XUZHOU | XUZHOU, China | 34.28N | 117.15E | 42 | 8.00 (CHN) | 82-06 | 580270 | -9.3 |  | -14.5 | 39.9 | 36 | 36.7 | 34.8 | 36 | 35.8333 |  | 34.3 | 34.8 | 33.2 | 34 | 34.1
China |  | YAAN | YAAN, China | 29.98N | 103.00E | 629 | 8.00 (CHN) | 83-06 | 562870 | 0.2 |  | -2.3 | 37.1 | 33 | 34.4 | 34.3 | 34 | 33.9 |  | 31.3 | 32.8 | 32.9 | 32 | 32.3333
China |  | YAN AN | YAN AN, China | 36.60N | 109.50E | 959 | 8.00 (CHN) | 82-06 | 538450 | -18.3 |  | -24.3 | 39.9 | 34.9 | 35.3 | 33.5 | 35 | 34.5667 |  | 32.6 | 33.4 | 31.4 | 32 | 32.4667
China |  | YANCHI | YANCHI, China | 37.80N | 107.38E | 1356 | 8.00 (CHN) | 82-06 | 537230 | -22.7 |  | -30 | 37.9 | 33.4 | 34.6 | 32.6 | 34 | 33.5333 |  | 31.5 | 32.8 | 31 | 32 | 31.7667
China |  | YANGCHENG | YANGCHENG, China | 35.48N | 112.40E | 659 | 8.00 (CHN) | 82-06 | 539750 | -13.5 |  | -18.1 | 40 | 34.5 | 35.4 | 33.2 | 34 | 34.3667 |  | 32.4 | 32.7 | 31.3 | 32 | 32.1333
China |  | YANGJIANG | YANGJIANG, China | 21.87N | 111.97E | 22 | 8.00 (CHN) | 82-06 | 596630 | 5.6 |  | 2.8 | 39.5 | 32.9 | 34.2 | 34.4 | 34 | 33.8333 |  | 31.8 | 32.7 | 33.1 | 33 | 32.5333
China |  | YANJI | YANJI, China | 42.87N | 129.50E | 178 | 8.00 (CHN) | 82-06 | 542920 | -25.2 |  | -31.4 | 37.7 | 31.9 | 33.5 | 32.6 | 33 | 32.6667 |  | 29.5 | 31.2 | 30.7 | 30 | 30.4667
China |  | YANZHOU | YANZHOU, China | 35.57N | 116.85E | 53 | 8.00 (CHN) | 82-06 | 549160 | -12.1 |  | -16 | 40.4 | 36.3 | 35.9 | 34.4 | 36 | 35.5333 |  | 34.5 | 34.4 | 32.7 | 34 | 33.8667
China |  | YAXIAN | YAXIAN, China | 18.23N | 109.52E | 7 | 8.00 (CHN) | 82-06 | 599480 | 13.4 |  | 8.5 | 38.1 | 33.7 | 33 | 32.8 | 33 | 33.1667 |  | 32.9 | 32.4 | 32.1 | 32 | 32.4667
China |  | YIBIN | YIBIN, China | 28.80N | 104.60E | 342 | 8.00 (CHN) | 82-06 | 564920 | 1.4 |  | -1.9 | 40.4 | 34.1 | 35.7 | 36.7 | 36 | 35.5 |  | 32.4 | 34.3 | 34.8 | 34 | 33.8333
China |  | YICHANG | YICHANG, China | 30.70N | 111.30E | 134 | 8.00 (CHN) | 82-06 | 574610 | -2.3 |  | -4.9 | 40.6 | 35.2 | 37.5 | 36.6 | 36 | 36.4333 |  | 33.5 | 36 | 35.1 | 35 | 34.8667
China |  | YICHUN | YICHUN, China | 47.72N | 128.90E | 232 | 8.00 (CHN) | 82-06 | 507740 | -36 |  | -41.5 | 37.3 | 31.7 | 32.4 | 31.2 | 32 | 31.7667 |  | 29.4 | 30.1 | 28.7 | 29 | 29.4
China |  | YICHUN | YICHUN, China | 27.80N | 114.38E | 129 | 8.00 (CHN) | 82-06 | 577930 | -3.1 |  | -7 | 40.1 | 34.7 | 37.2 | 36.8 | 36 | 36.2333 |  | 33.5 | 35.9 | 35.3 | 35 | 34.9
China |  | YINCHUAN | YINCHUAN, China | 38.47N | 106.20E | 1112 | 8.00 (CHN) | 82-06 | 536140 | -19.5 |  | -26.4 | 38.5 | 33.2 | 34.1 | 32.5 | 33 | 33.2667 |  | 31.2 | 32.5 | 31 | 32 | 31.5667
China |  | YINGKOU | YINGKOU, China | 40.67N | 122.20E | 4 | 8.00 (CHN) | 82-06 | 544710 | -19.7 |  | -28.5 | 35.5 | 30.4 | 32.3 | 31.5 | 31 | 31.4 |  | 28.7 | 30.9 | 30.4 | 30 | 30
China |  | YINING | YINING, China | 43.95N | 81.33E | 664 | 8.00 (CHN) | 82-06 | 514310 | -24.7 |  | -32.5 | 39.6 | 33.5 | 35.6 | 35 | 35 | 34.7 |  | 31.7 | 33.7 | 33.1 | 33 | 32.8333
China |  | YIWU | YIWU, China | 43.27N | 94.70E | 1729 | 8.00 (CHN) | 82-02 | 521180 | -23.8 |  | -31.5 | 32.3 | 28 | 28.7 | 28.2 | 28 | 28.3 |  | 25.8 | 27.2 | 26.8 | 27 | 26.6
China |  | YIYUAN | YIYUAN, China | 36.18N | 118.15E | 302 | 8.00 (CHN) | 82-06 | 548360 | -13.5 |  | -17.8 | 39.4 | 34.3 | 34.8 | 33.6 | 34 | 34.2333 |  | 32.6 | 33.3 | 31.7 | 33 | 32.5333
China |  | YONGAN | YONGAN, China | 25.97N | 117.35E | 204 | 8.00 (CHN) | 82-06 | 589210 | -1.4 |  | -5.3 | 40.3 | 35.6 | 37.6 | 37 | 37 | 36.7333 |  | 34.3 | 36.3 | 35.6 | 35 | 35.4
China |  | YOUYANG | YOUYANG, China | 28.83N | 108.77E | 665 | 8.00 (CHN) | 82-06 | 576330 | -3.7 |  | -8.9 | 37.4 | 32 | 34 | 34.2 | 33 | 33.4 |  | 30.5 | 32.5 | 32.8 | 32 | 31.9333 |  |  | Yukon
China |  | YU XIAN | YU XIAN, China | 39.83N | 114.57E | 910 | 8.00 (CHN) | 82-06 | 535930 | -25.1 |  | -30.6 | 39 | 33.2 | 34.1 | 31.8 | 33 | 33.0333 |  | 31.3 | 31.8 | 29.8 | 31 | 30.9667
China |  | YUANJIANG | YUANJIANG, China | 23.60N | 101.98E | 398 | 8.00 (CHN) | 82-06 | 569660 | 6.3 |  | -0.4 | 42.4 | 38.5 | 37.9 | 37.2 | 38 | 37.8667 |  | 36.9 | 36.1 | 35.5 | 36 | 36.1667
China |  | YUANLING | YUANLING, China | 28.47N | 110.40E | 143 | 8.00 (CHN) | 82-06 | 576550 | -2.3 |  | -5.2 | 40.8 | 34.5 | 36.8 | 37 | 36 | 36.1 |  | 33 | 35.4 | 35.6 | 35 | 34.6667 |  |  | Yukon
China |  | YUANMOU | YUANMOU, China | 25.73N | 101.87E | 1120 | 8.00 (CHN) | 83-06 | 567630 | 2.5 |  | -1.6 | 39.7 | 36.9 | 34.4 | 34 | 35 | 35.1 |  | 34.7 | 32.7 | 32.7 | 33 | 33.3667
China |  | YUANPING | YUANPING, China | 38.75N | 112.70E | 838 | 8.00 (CHN) | 82-06 | 536730 | -19.6 |  | -26 | 39.4 | 34.3 | 34.5 | 32.4 | 34 | 33.7333 |  | 32.2 | 32.5 | 30.6 | 32 | 31.7667
China |  | YUEYANG | YUEYANG, China | 29.38N | 113.08E | 52 | 8.00 (CHN) | 82-06 | 575840 | -2.3 |  | -6 | 39 | 33.7 | 35.5 | 35.3 | 35 | 34.8333 |  | 32.6 | 34.6 | 34.3 | 34 | 33.8333 |  |  | Yukon
China |  | YULIN | YULIN, China | 38.23N | 109.70E | 1058 | 8.00 (CHN) | 82-06 | 536460 | -23.7 |  | -31 | 40.8 | 33.9 | 35.1 | 33.1 | 34 | 34.0333 |  | 31.8 | 33.3 | 31.1 | 32 | 32.0667
China |  | YUMENZHEN | YUMENZHEN, China | 40.27N | 97.03E | 1527 | 8.00 (CHN) | 82-06 | 524360 | -24.4 |  | -33 | 37.1 | 31.7 | 33.4 | 33 | 33 | 32.7 |  | 30.1 | 31.9 | 31.2 | 31 | 31.0667
China |  | YUNCHENG | YUNCHENG, China | 35.05N | 111.05E | 365 | 8.00 (CHN) | 82-06 | 539590 | -11.5 |  | -15.9 | 42.9 | 37.8 | 38.2 | 37 | 38 | 37.6667 |  | 36 | 36.4 | 34.8 | 36 | 35.7333
China |  | YUSHE | YUSHE, China | 37.07N | 112.98E | 1042 | 8.00 (CHN) | 82-06 | 537870 | -19.6 |  | -25.1 | 39.4 | 32.8 | 33.1 | 31.3 | 32 | 32.4 |  | 30.7 | 31.3 | 29.5 | 31 | 30.5
China |  | YUSHU | YUSHU, China | 33.02N | 97.02E | 3682 | 8.00 (CHN) | 82-06 | 560290 | -21.5 |  | -27.8 | 29.1 | 23.7 | 25.1 | 24.6 | 24 | 24.4667 |  | 21.5 | 22.9 | 22.8 | 22 | 22.4
China |  | YUTIAN/KERIYA | YUTIAN/KERIYA, China | 36.87N | 81.70E | 1554 | 8.00 (CHN) | 82-98 | 519310 | -16 |  | -23.9 | 40.4 | 36 | 36.6 | 36.4 | 36 | 36.3333 |  | 33.8 | 34.9 | 34.4 | 34 | 34.3667
China |  | ZADOI | ZADOI, China | 32.90N | 95.30E | 4068 | 8.00 (CHN) | 82-06 | 560180 | -25.7 |  | -33.1 | 26.6 | 20.9 | 22.1 | 21.8 | 22 | 21.6 |  | 18.3 | 19.9 | 19.8 | 19 | 19.3333
China |  | ZAOYANG | ZAOYANG, China | 32.15N | 112.67E | 127 | 8.00 (CHN) | 82-06 | 572790 | -6.5 |  | -10.3 | 40.2 | 35.6 | 36.8 | 36.1 | 36 | 36.1667 |  | 33.9 | 35.3 | 34.2 | 34 | 34.4667
China |  | ZHANG PING | ZHANG PING, China | 25.30N | 117.40E | 203 | 8.00 (CHN) | 94-06 | 589260 | -1 |  | -5.6 | 40.2 | 36.1 | 37.5 | 37.2 | 37 | 36.9333 |  | 34.4 | 36.1 | 35.7 | 35 | 35.4
China |  | ZHANGJIAKOU | ZHANGJIAKOU, China | 40.78N | 114.88E | 726 | 8.00 (CHN) | 82-06 | 544010 | -19.2 |  | -24.5 | 38.9 | 34.7 | 35 | 32.3 | 34 | 34 |  | 32.4 | 32.7 | 30.5 | 32 | 31.8667
China |  | ZHANGWU | ZHANGWU, China | 42.42N | 122.53E | 84 | 8.00 (CHN) | 82-06 | 542360 | -24.5 |  | -33.4 | 38.2 | 33.7 | 33.2 | 32.3 | 33 | 33.0667 |  | 31.3 | 31.5 | 30.6 | 31 | 31.1333
China |  | ZHANGYE | ZHANGYE, China | 38.93N | 100.43E | 1483 | 8.00 (CHN) | 82-06 | 526520 | -22.1 |  | -28.2 | 39.5 | 33.1 | 35.2 | 34 | 34 | 34.1 |  | 30.8 | 33.2 | 31.8 | 32 | 31.9333
China |  | ZHANJIANG | ZHANJIANG, China | 21.22N | 110.40E | 28 | 8.00 (CHN) | 82-06 | 596580 | 6.3 |  | 1.4 | 37.5 | 34.5 | 34.8 | 34.5 | 35 | 34.6 |  | 33.4 | 33.7 | 33.4 | 34 | 33.5
China |  | ZHANYI | ZHANYI, China | 25.58N | 103.83E | 1900 | 8.00 (CHN) | 82-06 | 567860 | -3.5 |  | -8.4 | 32.5 | 28.2 | 27.6 | 27.5 | 28 | 27.7667 |  | 26.9 | 26.1 | 26 | 26 | 26.3333
China |  | ZHAOTONG | ZHAOTONG, China | 27.33N | 103.75E | 1950 | 8.00 (CHN) | 83-06 | 565860 | -6.2 |  | -11.3 | 33.1 | 29.3 | 28.8 | 28.8 | 29 | 28.9667 |  | 27.5 | 27.2 | 27.3 | 27 | 27.3333
China |  | ZHENGZHOU | ZHENGZHOU, China | 34.72N | 113.65E | 111 | 8.00 (CHN) | 82-06 | 570830 | -9.5 |  | -14.8 | 41.4 | 37.2 | 36.3 | 34.9 | 36 | 36.1333 |  | 35.4 | 34.7 | 33.2 | 34 | 34.4333
China |  | ZHIJIANG | ZHIJIANG, China | 27.45N | 109.68E | 273 | 8.00 (CHN) | 82-06 | 577450 | -3.7 |  | -9.8 | 39 | 33.5 | 35.5 | 36.2 | 35 | 35.0667 |  | 32.1 | 34.2 | 34.7 | 34 | 33.6667 |  |  | Yukon
China |  | ZHONGNING | ZHONGNING, China | 37.48N | 105.68E | 1193 | 8.00 (CHN) | 82-06 | 537050 | -19.1 |  | -26.6 | 39 | 33.5 | 35.2 | 33.8 | 34 | 34.1667 |  | 31.8 | 33.2 | 31.9 | 32 | 32.3
China |  | ZHONGXIANG | ZHONGXIANG, China | 31.17N | 112.57E | 66 | 8.00 (CHN) | 82-06 | 573780 | -4.2 |  | -7.6 | 39.4 | 34.5 | 36 | 35.9 | 35 | 35.4667 |  | 33 | 34.7 | 34.4 | 34 | 34.0333
China |  | ZHUMADIAN | ZHUMADIAN, China | 33.00N | 114.02E | 83 | 8.00 (CHN) | 82-06 | 572900 | -9.8 |  | -16.8 | 40.8 | 36.6 | 37.2 | 35.6 | 36 | 36.4667 |  | 34.7 | 35.4 | 33.7 | 35 | 34.6
China |  | ZUNYI | ZUNYI, China | 27.70N | 106.88E | 845 | 8.00 (CHN) | 82-06 | 577130 | -2.3 |  | -5 | 38.9 | 32 | 33.6 | 34.2 | 33 | 33.2667 |  | 30.7 | 32.3 | 32.7 | 32 | 31.9 |  |  | Yukon
Christmas Island |  | CHRISTMAS ISLAND AE | CHRISTMAS ISLAND AE, Christmas Island | 10.45S | 105.68E | 262 | 7.00 (SEA) | 97-06 | 969950 | 19.1 |  | 17.4 | 34.4 | 27.9 | 27 | 26.2 | 27 | 27.0333 |  | 27.2 | 26.2 | 26 | 26 | 26.4667
Cocos (Keeling) Islands |  | COCOS ISLAND AERO | COCOS ISLAND AERO, Cocos (Keeling) Islands | 12.18S | 96.83E | 4 | 7.00 (SEA) | 89-06 | 969960 | 22.1 |  | 20.9 | 36.1 | 29.8 | 29.1 | 29 | 29 | 29.3 |  | 29.2 | 28.6 | 28.2 | 29 | 28.6667
Colombia |  | BARRANQUILLA/ERNEST | BARRANQUILLA/ERNEST, Colombia | 10.88N | 74.78W | 30 | -5.00 (SAP) | 82-06 | 800280 | 20.4 |  | 16.8 | 39.6 | 34.9 | 34.2 | 34.6 | 35 | 34.5667 |  | 33.2 | 33 | 33.2 | 33 | 33.1333
Colombia |  | BOGOTA/ELDORADO | BOGOTA/ELDORADO, Colombia | 4.70N | 74.13W | 2546 | -5.00 (SAP) | 82-06 | 802220 | -0.5 |  | -5.6 | 30.5 | 20.4 | 20 | 20.2 | 20 | 20.2 |  | 19.2 | 18.9 | 19.1 | 19 | 19.0667
Colombia |  | CALI/ALFONSO BONILL | CALI/ALFONSO BONILL, Colombia | 3.55N | 76.38W | 969 | -5.00 (SAP) | 82-06 | 802590 | 13.4 |  | 6.4 | 38.4 | 31.8 | 32 | 33.1 | 32 | 32.3 |  | 30.2 | 30.8 | 31.8 | 31 | 30.9333
Colombia |  | CARTAGENA/RAFAEL NU | CARTAGENA/RAFAEL NU, Colombia | 10.45N | 75.52W | 12 | -5.00 (SAP) | 82-06 | 800220 | 19.2 |  | 11.6 | 40 | 33 | 33 | 33 | 33 | 33 |  | 32.1 | 32.1 | 32.1 | 32 | 32.1
Colombia |  | RIONEGRO/J.M.CORDOV | RIONEGRO/J.M.CORDOV, Colombia | 6.13N | 75.43W | 2142 | -5.00 (SAP) | 87-06 | 801120 | 6.8 |  | -2 | 32.2 | 23.9 | 23.5 | 23.8 | 24 | 23.7333 |  | 23.1 | 23 | 23.1 | 23 | 23.0667
Congo |  | BRAZZAVILLE/MAYA-M | BRAZZAVILLE/MAYA-M, Congo | 4.25S | 15.25E | 316 | 1.00 (AFW) | 82-06 | 644500 | 16.7 |  | 13.4 | 37 | 32.1 | 31 | 32.8 | 32 | 31.9667 |  | 30.4 | 29.5 | 31.1 | 30 | 30.3333
Cook Islands |  | AMURI/AITUTAKI ISL | AMURI/AITUTAKI ISL, Cook Islands | 18.83S | 159.77W | 4 | -10.00 (PCH) | 82-96 | 918300 | 18.6 |  | 15.2 | 36.9 | 28.5 | 28.2 | 28.1 | 28 | 28.2667 |  | 27.8 | 27.6 | 27.4 | 28 | 27.6
Cook Islands |  | MANGAIA ISLAND | MANGAIA ISLAND, Cook Islands | 21.92S | 157.95W | 9 | -10.00 (PCH) | 85-96 | 918470 | N/A |  | N/A | N/A | 27.6 | 27.2 | 26.9 | 27 | 27.2333 |  | 26.3 | 26.2 | 25.7 | 26 | 26.0667
Cook Islands |  | MAUKE ISLAND | MAUKE ISLAND, Cook Islands | 20.13S | 157.35W | 9 | -10.00 (PCH) | 82-96 | 918400 | N/A |  | N/A | N/A | 28.5 | 28.5 | 28.2 | 28 | 28.4 |  | 27.7 | 27.6 | 27.4 | 28 | 27.5667
Cook Islands |  | PENRHYN ISLAND | PENRHYN ISLAND, Cook Islands | 9.02S | 158.07W | 2 | -10.00 (PCH) | 82-95 | 918000 | 20.6 |  | 13.7 | 38.9 | 31.3 | 30.7 | 30.1 | 31 | 30.7 |  | 30.5 | 29.8 | 29.6 | 30 | 29.9667
Cook Islands |  | PUKAPUKA | PUKAPUKA, Cook Islands | 10.88S | 165.82W | 3 | -10.00 (PCH) | 82-98 | 918110 | 16.9 |  | 10.2 | 40.4 | 32 | 31.7 | 31.7 | 32 | 31.8 |  | 31.3 | 31 | 31 | 31 | 31.1
Cook Islands |  | RAROTONGA | RAROTONGA, Cook Islands | 21.20S | 159.82W | 7 | -10.00 (PCH) | 82-06 | 918430 | 14.8 |  | 11.8 | 34.8 | 28.2 | 28 | 27.2 | 28 | 27.8 |  | 27.1 | 26.4 | 26.2 | 27 | 26.5667
Costa Rica |  | JUAN SANTAMARIA INT | JUAN SANTAMARIA INT, Costa Rica | 9.98N | 84.22W | 934 | -6.00 (CAM) | 82-06 | 787620 | 13.8 |  | 8.1 | 38 | 30 | 30 | 30.1 | 30 | 30.0333 |  | 28.9 | 29 | 28.9 | 29 | 28.9333
Côte d'Ivoire |  | ABIDJAN | ABIDJAN, Côte d'Ivoire | 5.25N | 3.93W | 8 | 0.00 (GRW) | 82-06 | 655780 | 17.8 |  | 10.7 | 41.4 | 31.1 | 29.5 | 28.6 | 30 | 29.7333 |  | 30.1 | 28.9 | 28 | 29 | 29
Croatia |  | DARUVAR | DARUVAR, Croatia | 45.60N | 17.23E | 161 | 1.00 (EUW) | 82-06 | 142580 | -15.7 |  | -25.2 | 38.9 | 33 | 34.1 | 34.7 | 34 | 33.9333 |  | 31 | 31.9 | 32.2 | 32 | 31.7
Croatia |  | DUBROVNIK-CILIPI | DUBROVNIK-CILIPI, Croatia | 42.57N | 18.27E | 161 | 1.00 (EUW) | 82-95 | 134520 | -2.6 |  | -7.2 | 37.7 | 31 | 33.3 | 32.2 | 32 | 32.1667 |  | 28.8 | 31.8 | 31.1 | 31 | 30.5667
Croatia |  | GOSPIC | GOSPIC, Croatia | 44.55N | 15.37E | 565 | 1.00 (EUW) | 82-06 | 143300 | -19.8 |  | -29 | 38.3 | 31.2 | 32.8 | 33.5 | 33 | 32.5 |  | 29.1 | 30.3 | 31.3 | 30 | 30.2333
Croatia |  | PULA AERODROME | PULA AERODROME, Croatia | 44.90N | 13.92E | 63 | 1.00 (EUW) | 82-06 | 143070 | -6.6 |  | -11.6 | 37.3 | 32.2 | 33.8 | 34.2 | 33 | 33.4 |  | 30.1 | 32.1 | 32.8 | 32 | 31.6667
Croatia |  | SPLIT/MARJAN | SPLIT/MARJAN, Croatia | 43.52N | 16.43E | 128 | 1.00 (EUW) | 96-06 | 144450 | -2.6 |  | -8.1 | 40.1 | 34.7 | 35 | 35.3 | 35 | 35 |  | 32.7 | 33.7 | 34 | 33 | 33.4667
Croatia |  | SPLIT/RESNIK | SPLIT/RESNIK, Croatia | 43.53N | 16.30E | 21 | 1.00 (EUW) | 82-06 | 144440 | -3.3 |  | -7.3 | 40.3 | 34 | 35.2 | 35.9 | 35 | 35.0333 |  | 31.6 | 33.6 | 33.9 | 33 | 33.0333
Croatia |  | ZADAR/ZEMUNIK | ZADAR/ZEMUNIK, Croatia | 44.10N | 15.35E | 80 | 1.00 (EUW) | 82-06 | 144310 | -7.4 |  | -12 | 40.3 | 34.9 | 35.8 | 36.2 | 36 | 35.6333 |  | 32.4 | 34.1 | 34.5 | 34 | 33.6667
Croatia |  | ZAGREB/MAKSIMIR | ZAGREB/MAKSIMIR, Croatia | 45.82N | 16.03E | 128 | 1.00 (EUW) | 82-06 | 142400 | -14 |  | -23.1 | 39.6 | 33.1 | 33.1 | 34.3 | 34 | 33.5 |  | 30.7 | 31.1 | 31.8 | 31 | 31.2
Croatia |  | ZAGREB/PLESO | ZAGREB/PLESO, Croatia | 45.73N | 16.07E | 107 | 1.00 (EUW) | 82-06 | 142410 | -16.3 |  | -26.7 | 39.1 | 33 | 33.8 | 34.1 | 34 | 33.6333 |  | 30.9 | 31.8 | 31.8 | 32 | 31.5
Cuba |  | AEROPUERTO JOSE MAR | AEROPUERTO JOSE MAR, Cuba | 22.98N | 82.40W | 75 | -5.00 (NAE) | 82-06 | 782240 | 7.8 |  | 3.7 | 35.7 | 33.4 | 33.2 | 33.8 | 33 | 33.4667 |  | 32.6 | 32.8 | 33 | 33 | 32.8
Cuba |  | CAMAGUEY AEROPUERTO | CAMAGUEY AEROPUERTO, Cuba | 21.42N | 77.85W | 118 | -5.00 (NAE) | 82-06 | 782550 | 12.6 |  | 8.7 | 36.9 | 33.9 | 34 | 34.1 | 34 | 34 |  | 32.9 | 33 | 33.2 | 33 | 33.0333
Cuba |  | GUANTANAMO BAY NAS | GUANTANAMO BAY NAS, Cuba | 19.90N | 75.22W | 17 | -5.00 (NAE) | 82-06 | 783670 | 17.1 |  | 13.6 | 39.4 | 34.2 | 34.9 | 35.1 | 35 | 34.7333 |  | 33.2 | 34 | 34.1 | 34 | 33.7667
Cuba |  | SANTIAGO DE CUBA | SANTIAGO DE CUBA, Cuba | 19.97N | 75.85W | 55 | -5.00 (NAE) | 82-06 | 782640 | N/A |  | N/A | N/A | 31.2 | 32.1 | 32.2 | 32 | 31.8333 |  | 31 | 31.2 | 31.8 | 31 | 31.3333
Cuba |  | VARADERO/MT | VARADERO/MT, Cuba | 23.02N | 81.43W | 65 | -5.00 (NAE) | 82-06 | 782290 | 7.6 |  | -3.3 | 40.7 | 32.9 | 33 | 33.8 | 33 | 33.2333 |  | 31.9 | 32.1 | 32.2 | 32 | 32.0667
Cyprus |  | AKROTIRI | AKROTIRI, Cyprus | 34.58N | 32.98E | 23 | 2.00 (EUE) | 82-06 | 176010 | 2.5 |  | -2.7 | 40.4 | 33.3 | 34.9 | 34.2 | 34 | 34.1333 |  | 30.9 | 32.8 | 32.5 | 32 | 32.0667
Cyprus |  | LARNACA AIRPORT | LARNACA AIRPORT, Cyprus | 34.88N | 33.63E | 2 | 2.00 (EUE) | 82-06 | 176090 | 1.5 |  | -2.8 | 41.4 | 34.8 | 35.9 | 36 | 36 | 35.5667 |  | 32.3 | 34.1 | 34 | 33 | 33.4667
Cyprus |  | PAPHOS AIRPORT | PAPHOS AIRPORT, Cyprus | 34.72N | 32.48E | 8 | 2.00 (EUE) | 82-06 | 176000 | 2.1 |  | -2.6 | 39.1 | 30.9 | 32.8 | 32.2 | 32 | 31.9667 |  | 29 | 31 | 31.1 | 30 | 30.3667
Czech Republic |  | BRNO/TURANY | BRNO/TURANY, Czech Republic | 49.15N | 16.70E | 246 | 1.00 (EUW) | 82-06 | 117230 | -15.9 |  | -24.9 | 37.5 | 30.8 | 32.4 | 32.7 | 32 | 31.9667 |  | 28 | 30.1 | 30.1 | 29 | 29.4
Czech Republic |  | CASLAV | CASLAV, Czech Republic | 49.93N | 15.38E | 239 | 1.00 (EUW) | 97-06 | 116240 | -16.9 |  | -22.9 | 38 | 31.8 | 33.1 | 32.1 | 32 | 32.3333 |  | 29.2 | 30.4 | 29.7 | 30 | 29.7667
Czech Republic |  | CERVENA | CERVENA, Czech Republic | 49.77N | 17.55E | 753 | 1.00 (EUW) | 86-06 | 117660 | -17.5 |  | -28.3 | 33.6 | 27.4 | 29.2 | 29 | 29 | 28.5333 |  | 24.7 | 26.6 | 26 | 26 | 25.7667
Czech Republic |  | CESKE BUDEJOVICE | CESKE BUDEJOVICE, Czech Republic | 48.95N | 14.43E | 436 | 1.00 (EUW) | 82-05 | 115410 | -18.6 |  | -27.4 | 39.1 | 30.1 | 32.6 | 32.6 | 32 | 31.7667 |  | 27.2 | 29.5 | 30 | 29 | 28.9
Czech Republic |  | CHEB | CHEB, Czech Republic | 50.08N | 12.40E | 490 | 1.00 (EUW) | 82-06 | 114060 | -17 |  | -25.5 | 37.6 | 30.5 | 31.9 | 31.6 | 31 | 31.3333 |  | 27.8 | 29.3 | 28.5 | 29 | 28.5333
Czech Republic |  | CHURANOV | CHURANOV, Czech Republic | 49.07N | 13.62E | 1122 | 1.00 (EUW) | 82-06 | 114570 | -17.9 |  | -24.8 | 33.7 | 25.9 | 27.6 | 27 | 27 | 26.8333 |  | 23.3 | 24.6 | 24.3 | 24 | 24.0667
Czech Republic |  | DOKSANY | DOKSANY, Czech Republic | 50.47N | 14.17E | 159 | 1.00 (EUW) | 95-06 | 115090 | -18.4 |  | -27.4 | 40 | 32.1 | 34.3 | 33.2 | 33 | 33.2 |  | 29.5 | 31.4 | 30.5 | 30 | 30.4667
Czech Republic |  | DUKOVANY | DUKOVANY, Czech Republic | 49.10N | 16.13E | 405 | 1.00 (EUW) | 89-06 | 116930 | -15.4 |  | -22 | 38.1 | 30.8 | 32.7 | 32.6 | 32 | 32.0333 |  | 28.2 | 30.1 | 30 | 29 | 29.4333
Czech Republic |  | HOLESOV | HOLESOV, Czech Republic | 49.32N | 17.57E | 224 | 1.00 (EUW) | 82-06 | 117740 | -18.7 |  | -29.7 | 37.3 | 30.5 | 33.2 | 32.8 | 32 | 32.1667 |  | 28.2 | 30.5 | 30 | 30 | 29.5667
Czech Republic |  | HRADEC KRALOVE | HRADEC KRALOVE, Czech Republic | 50.25N | 15.85E | 244 | 1.00 (EUW) | 82-93 | 116480 | -17.5 |  | -30.6 | 38.8 | 29 | 32.1 | 33.1 | 31 | 31.4 |  | 26.8 | 29.2 | 30 | 29 | 28.6667
Czech Republic |  | KARLOVY VARY | KARLOVY VARY, Czech Republic | 50.20N | 12.92E | 607 | 1.00 (EUW) | 88-06 | 114140 | -16.3 |  | -21.9 | 35.7 | 29.5 | 30.9 | 30.7 | 30 | 30.3667 |  | 26.6 | 28 | 27.6 | 27 | 27.4
Czech Republic |  | KOCELOVICE | KOCELOVICE, Czech Republic | 49.47N | 13.83E | 522 | 1.00 (EUW) | 88-06 | 114870 | -17 |  | -23.4 | 37.3 | 30.5 | 31.9 | 32 | 31 | 31.4667 |  | 27.8 | 29 | 29 | 29 | 28.6
Czech Republic |  | KOSTELNI MYSLOVA | KOSTELNI MYSLOVA, Czech Republic | 49.18N | 15.47E | 573 | 1.00 (EUW) | 82-06 | 116360 | -16.8 |  | -23.9 | 37.1 | 29.1 | 31 | 31.1 | 30 | 30.4 |  | 26.1 | 28.2 | 28.2 | 28 | 27.5
Czech Republic |  | KRESIN-KRAMOLIN | KRESIN-KRAMOLIN, Czech Republic | 49.58N | 15.08E | 533 | 1.00 (EUW) | 89-06 | 116280 | -18.1 |  | -23.9 | 36.4 | 29.7 | 31.1 | 31.6 | 31 | 30.8 |  | 26.9 | 28.3 | 28.9 | 28 | 28.0333
Czech Republic |  | KUCHAROVICE | KUCHAROVICE, Czech Republic | 48.88N | 16.08E | 339 | 1.00 (EUW) | 88-06 | 116980 | -15 |  | -21.5 | 38.6 | 31.2 | 33.2 | 33.1 | 33 | 32.5 |  | 28.4 | 30.7 | 30.5 | 30 | 29.8667
Czech Republic |  | LIBEREC | LIBEREC, Czech Republic | 50.77N | 15.02E | 401 | 1.00 (EUW) | 82-06 | 116030 | -17.4 |  | -27.8 | 36.8 | 29.5 | 31.9 | 30.8 | 31 | 30.7333 |  | 26.8 | 28.9 | 28 | 28 | 27.9
Czech Republic |  | LUKA | LUKA, Czech Republic | 49.65N | 16.95E | 518 | 1.00 (EUW) | 88-06 | 117100 | -16 |  | -22.4 | 36.1 | 28.7 | 31.4 | 30.8 | 30 | 30.3 |  | 26.1 | 28.6 | 28.1 | 28 | 27.6
Czech Republic |  | LYSA HORA | LYSA HORA, Czech Republic | 49.55N | 18.45E | 1327 | 1.00 (EUW) | 82-06 | 117870 | -19.5 |  | -29.7 | 29.6 | 23.8 | 25 | 25.1 | 25 | 24.6333 |  | 21 | 22.5 | 22.5 | 22 | 22
Czech Republic |  | MARIANSKE LAZNE | MARIANSKE LAZNE, Czech Republic | 49.92N | 12.72E | 541 | 1.00 (EUW) | 89-99 | 114180 | -18.3 |  | -26 | 35.5 | 28.6 | 30.8 | 30.7 | 30 | 30.0333 |  | 25.7 | 28.1 | 28 | 27 | 27.2667
Czech Republic |  | MILESOVKA | MILESOVKA, Czech Republic | 50.55N | 13.93E | 836 | 1.00 (EUW) | 82-06 | 114640 | -15.7 |  | -25.4 | 36.2 | 28.4 | 30 | 29.2 | 29 | 29.2 |  | 25 | 27 | 26.4 | 26 | 26.1333
Czech Republic |  | NAMEST NAD OSLAV | NAMEST NAD OSLAV, Czech Republic | 49.17N | 16.12E | 479 | 1.00 (EUW) | 96-06 | 116920 | -15.6 |  | -22 | 36.7 | 29.8 | 31 | 30.6 | 30 | 30.4667 |  | 27 | 28.9 | 28.5 | 28 | 28.1333
Czech Republic |  | OSTRAVA/MOSNOV | OSTRAVA/MOSNOV, Czech Republic | 49.68N | 18.12E | 260 | 1.00 (EUW) | 82-06 | 117820 | -19.8 |  | -31.5 | 37.1 | 30.6 | 32.6 | 32.9 | 32 | 32.0333 |  | 28 | 30.1 | 29.8 | 29 | 29.3
Czech Republic |  | PARDUBICE | PARDUBICE, Czech Republic | 50.02N | 15.73E | 230 | 1.00 (EUW) | 96-06 | 116520 | -18.1 |  | -25.9 | 37.7 | 32.3 | 33.1 | 31.9 | 32 | 32.4333 |  | 29.4 | 30.3 | 29.7 | 30 | 29.8
Czech Republic |  | PEC POD SNEZKOU | PEC POD SNEZKOU, Czech Republic | 50.67N | 15.75E | 820 | 1.00 (EUW) | 89-06 | 116430 | -18.7 |  | -25.3 | 33 | 26.5 | 28.7 | 27.2 | 27 | 27.4667 |  | 24 | 25.7 | 24.6 | 25 | 24.7667
Czech Republic |  | PLZEN LINE | PLZEN LINE, Czech Republic | 49.68N | 13.27E | 362 | 1.00 (EUW) | 82-06 | 114480 | -18.2 |  | -31.4 | 39 | 30 | 32.9 | 32.2 | 32 | 31.7 |  | 27.3 | 30 | 29.1 | 29 | 28.8
Czech Republic |  | PRADED MOUNTAIN | PRADED MOUNTAIN, Czech Republic | 50.07N | 17.23E | 1492 | 1.00 (EUW) | 82-97 | 117350 | -20.3 |  | -30.8 | 25.4 | 19.5 | 21.8 | 21.5 | 21 | 20.9333 |  | 16.9 | 19.1 | 19 | 18 | 18.3333
Czech Republic |  | PRAHA/RUZYNE | PRAHA/RUZYNE, Czech Republic | 50.10N | 14.25E | 365 | 1.00 (EUW) | 82-06 | 115180 | -17.1 |  | -27.2 | 38.2 | 30.5 | 32.3 | 31.9 | 32 | 31.5667 |  | 27.3 | 29.4 | 28.9 | 29 | 28.5333
Czech Republic |  | PRAHA-KBELY | PRAHA-KBELY, Czech Republic | 50.12N | 14.53E | 287 | 1.00 (EUW) | 96-06 | 115670 | -15.8 |  | -22.5 | 37.4 | 31.4 | 32.6 | 32 | 32 | 32 |  | 28.4 | 29.5 | 29.2 | 29 | 29.0333
Czech Republic |  | PRAHA-LIBUS | PRAHA-LIBUS, Czech Republic | 50.02N | 14.45E | 303 | 1.00 (EUW) | 82-06 | 115200 | -16.1 |  | -26.2 | 38.7 | 31.3 | 33.4 | 32.6 | 32 | 32.4333 |  | 28.2 | 30.3 | 29.6 | 29 | 29.3667
Czech Republic |  | PREROV | PREROV, Czech Republic | 49.42N | 17.40E | 209 | 1.00 (EUW) | 96-06 | 117480 | -19 |  | -27.9 | 35.7 | 30.8 | 32.4 | 31.5 | 32 | 31.5667 |  | 28.7 | 30.3 | 28.9 | 29 | 29.3
Czech Republic |  | PRIBYSLAV | PRIBYSLAV, Czech Republic | 49.58N | 15.77E | 536 | 1.00 (EUW) | 82-06 | 116590 | -19.2 |  | -28.2 | 36.9 | 28.6 | 30.5 | 31.1 | 30 | 30.0667 |  | 25.9 | 28.1 | 28.1 | 27 | 27.3667
Czech Republic |  | PRIMDA | PRIMDA, Czech Republic | 49.67N | 12.67E | 748 | 1.00 (EUW) | 88-06 | 114230 | -15.4 |  | -21.4 | 36 | 28.4 | 30.2 | 30.6 | 30 | 29.7333 |  | 25.9 | 27 | 26.7 | 27 | 26.5333
Czech Republic |  | SVRATOUCH | SVRATOUCH, Czech Republic | 49.73N | 16.03E | 740 | 1.00 (EUW) | 88-06 | 116830 | -16.3 |  | -23.2 | 34.8 | 27.7 | 29.8 | 29.8 | 29 | 29.1 |  | 25.2 | 27.1 | 27.1 | 26 | 26.4667
Czech Republic |  | TEMELIN | TEMELIN, Czech Republic | 49.20N | 14.33E | 507 | 1.00 (EUW) | 89-06 | 115380 | -17.7 |  | -24.5 | 38.1 | 30.8 | 32.4 | 32.7 | 32 | 31.9667 |  | 28 | 29.4 | 29.8 | 29 | 29.0667
Czech Republic |  | TUSIMICE | TUSIMICE, Czech Republic | 50.38N | 13.33E | 328 | 1.00 (EUW) | 88-06 | 114380 | -14.8 |  | -22.5 | 39.3 | 30.9 | 32.7 | 32.6 | 32 | 32.0667 |  | 28 | 29.9 | 29.5 | 29 | 29.1333
Czech Republic |  | USTI NAD LABEM | USTI NAD LABEM, Czech Republic | 50.68N | 14.03E | 379 | 1.00 (EUW) | 88-06 | 115020 | -13.9 |  | -20.2 | 38 | 30.3 | 32.1 | 31.2 | 31 | 31.2 |  | 27.3 | 29.3 | 28.5 | 28 | 28.3667
Czech Republic |  | USTI NAD ORLICI | USTI NAD ORLICI, Czech Republic | 49.98N | 16.43E | 406 | 1.00 (EUW) | 82-06 | 116790 | -18.8 |  | -29 | 36.6 | 30.2 | 32.2 | 31.4 | 31 | 31.2667 |  | 27.4 | 29.1 | 28.8 | 28 | 28.4333
Denmark |  | AALBORG | AALBORG, Denmark | 57.10N | 9.85E | 13 | 1.00 (EUW) | 82-06 | 60300 | -13.6 |  | -26.5 | 32.8 | 26.2 | 28 | 27.8 | 27 | 27.3333 |  | 23.3 | 25.9 | 25.6 | 25 | 24.9333
Denmark |  | BILLUND | BILLUND, Denmark | 55.73N | 9.17E | 80 | 1.00 (EUW) | 82-06 | 61040 | -14 |  | -23.8 | 33.8 | 27.2 | 29 | 28.9 | 28 | 28.3667 |  | 24.8 | 26.6 | 26.7 | 26 | 26.0333
Denmark |  | BLAAVANDSHUK | BLAAVANDSHUK, Denmark | 55.55N | 8.08E | 18 | 1.00 (EUW) | 83-06 | 60810 | -9.6 |  | -14.2 | 32 | 23.1 | 26.6 | 26.5 | 25 | 25.4 |  | 20.2 | 24.3 | 24 | 23 | 22.8333
Denmark |  | CHRISTIANSO (LGT-H) | CHRISTIANSO (LGT-H), Denmark | 55.32N | 15.18E | 15 | 1.00 (EUW) | 82-98 | 61910 | -5.1 |  | -13.4 | 30.7 | 21.5 | 24.6 | 24.8 | 24 | 23.6333 |  | 19.5 | 22.8 | 23.3 | 22 | 21.8667
Denmark |  | DROGDEN | DROGDEN, Denmark | 55.53N | 12.72E | 0 | 1.00 (EUW) | 83-06 | 61830 | N/A |  | N/A | N/A | 21 | 23.8 | 23.5 | 23 | 22.7667 |  | 19.3 | 22.3 | 22.1 | 21 | 21.2333
Denmark |  | ESBJERG | ESBJERG, Denmark | 55.53N | 8.57E | 29 | 1.00 (EUW) | 82-04 | 60800 | -12.3 |  | -23.5 | 33.8 | 26.9 | 28.9 | 29.1 | 28 | 28.3 |  | 24.1 | 26.1 | 27.1 | 26 | 25.7667
Denmark |  | FORNAES (CAPE) | FORNAES (CAPE), Denmark | 56.45N | 10.97E | 8 | 1.00 (EUW) | 82-99 | 60710 | -8.4 |  | -20.4 | 28.2 | 23 | 24.7 | 24.1 | 24 | 23.9333 |  | 21.4 | 23.1 | 22.9 | 22 | 22.4667
Denmark |  | FREDERIKSHAVN | FREDERIKSHAVN, Denmark | 57.40N | 10.52E | 80 | 1.00 (EUW) | 91-03 | 60430 | N/A |  | N/A | N/A | 21.6 | 23.7 | 24.4 | 23 | 23.2333 |  | 20.1 | 22.3 | 22.7 | 22 | 21.7
Denmark |  | GNIBEN | GNIBEN, Denmark | 56.02N | 11.28E | 12 | 1.00 (EUW) | 83-06 | 61690 | -5.2 |  | -10.4 | 29.1 | 22.8 | 25.6 | 25.3 | 25 | 24.5667 |  | 20.3 | 23.3 | 23.7 | 22 | 22.4333
Denmark |  | HAMMER ODDE | HAMMER ODDE, Denmark | 55.30N | 14.78E | 11 | 1.00 (EUW) | 82-06 | 61930 | -6 |  | -12.3 | 32.5 | 23.6 | 25.2 | 26.3 | 25 | 25.0333 |  | 20.7 | 23.3 | 23.4 | 22 | 22.4667
Denmark |  | HOLBAEK | HOLBAEK, Denmark | 55.73N | 11.60E | 13 | 1.00 (EUW) | 83-06 | 61560 | -11 |  | -26.6 | 34.4 | 26.2 | 29.8 | 28.4 | 28 | 28.1333 |  | 24.2 | 27.3 | 26.1 | 26 | 25.8667
Denmark |  | HVIDE SANDE | HVIDE SANDE, Denmark | 56.00N | 8.13E | 5 | 1.00 (EUW) | 93-06 | 60580 | -8.7 |  | -17.2 | 33.8 | 23.8 | 28.1 | 27.2 | 26 | 26.3667 |  | 21.1 | 25.7 | 25.2 | 24 | 24
Denmark |  | KARUP | KARUP, Denmark | 56.30N | 9.12E | 53 | 1.00 (EUW) | 82-06 | 60600 | -14.4 |  | -25.9 | 33.7 | 27.8 | 29.9 | 29.4 | 29 | 29.0333 |  | 24.8 | 27 | 27.2 | 26 | 26.3333
Denmark |  | KEGNAES | KEGNAES, Denmark | 54.85N | 9.98E | 17 | 1.00 (EUW) | 82-06 | 61190 | -6.3 |  | -14 | 30.4 | 23.4 | 25.4 | 24.7 | 25 | 24.5 |  | 21 | 23.4 | 23.1 | 23 | 22.5
Denmark |  | KOEBENHAVN/KASTRUP | KOEBENHAVN/KASTRUP, Denmark | 55.62N | 12.65E | 5 | 1.00 (EUW) | 82-06 | 61800 | -11 |  | -20.2 | 32.2 | 25.2 | 28 | 27.2 | 27 | 26.8 |  | 23.1 | 26 | 25.2 | 25 | 24.7667
Denmark |  | LANGOE | LANGOE, Denmark | 54.82N | 11.00E | 4 | 1.00 (EUW) | 91-06 | 61380 | N/A |  | N/A | N/A | 25.7 | 28.7 | 27.2 | 27 | 27.2 |  | 22.2 | 26.1 | 25.4 | 25 | 24.5667
Denmark |  | MARIBO | MARIBO, Denmark | 54.70N | 11.45E | 4 | 1.00 (EUW) | 86-98 | 61430 | N/A |  | N/A | N/A | 26 | 29.5 | 29.2 | 28 | 28.2333 |  | 23.2 | 26.8 | 27 | 26 | 25.6667
Denmark |  | MOEN | MOEN, Denmark | 54.95N | 12.53E | 17 | 1.00 (EUW) | 82-06 | 61790 | -7.4 |  | -16.6 | 31 | 23.8 | 25.6 | 26.1 | 25 | 25.1667 |  | 21.1 | 23.6 | 24 | 23 | 22.9
Denmark |  | NAKKEHOVED | NAKKEHOVED, Denmark | 56.12N | 12.35E | 43 | 1.00 (EUW) | 93-06 | 61680 | -9.6 |  | -13.9 | 34.1 | 26.3 | 29.2 | 27.8 | 28 | 27.7667 |  | 23.4 | 26 | 25.8 | 25 | 25.0667
Denmark |  | ODENSE/BELDRINGE | ODENSE/BELDRINGE, Denmark | 55.48N | 10.33E | 21 | 1.00 (EUW) | 82-06 | 61200 | -12.4 |  | -23.7 | 35.7 | 27.9 | 29.3 | 29 | 29 | 28.7333 |  | 24.9 | 26.9 | 26.9 | 26 | 26.2333
Denmark |  | OMOE | OMOE, Denmark | 55.17N | 11.13E | 3 | 1.00 (EUW) | 82-06 | 61510 | N/A |  | N/A | N/A | 22.3 | 25.6 | 25 | 24 | 24.3 |  | 20.6 | 23.7 | 23.3 | 23 | 22.5333
Denmark |  | ROEMOE/JUVRE | ROEMOE/JUVRE, Denmark | 55.18N | 8.57E | 9 | 1.00 (EUW) | 87-06 | 60960 | -8.4 |  | -14.1 | 32.8 | 25.7 | 28.5 | 28.3 | 28 | 27.5 |  | 23 | 25.5 | 25.7 | 25 | 24.7333
Denmark |  | ROENNE | ROENNE, Denmark | 55.07N | 14.75E | 17 | 1.00 (EUW) | 88-06 | 61900 | -9.5 |  | -16.7 | 33.9 | 25 | 28.6 | 27 | 27 | 26.8667 |  | 22.2 | 25.9 | 25.1 | 24 | 24.4
Denmark |  | ROESNAES | ROESNAES, Denmark | 55.75N | 10.87E | 15 | 1.00 (EUW) | 83-06 | 61590 | -5.7 |  | -11.3 | 30.8 | 23.3 | 25.7 | 25.8 | 25 | 24.9333 |  | 20.8 | 23.7 | 23.6 | 23 | 22.7
Denmark |  | ROSKILDE/TUNE | ROSKILDE/TUNE, Denmark | 55.58N | 12.13E | 43 | 1.00 (EUW) | 82-06 | 61700 | -13.7 |  | -24.1 | 34 | 26.1 | 28.1 | 28.1 | 27 | 27.4333 |  | 23.5 | 26 | 25.8 | 25 | 25.1
Denmark |  | SAEDENSTRAND | SAEDENSTRAND, Denmark | 55.50N | 8.40E | 11 | 1.00 (EUW) | 82-92 | 60890 | -10.2 |  | -22.4 | 34.7 | 27.2 | 29 | 28.2 | 28 | 28.1333 |  | 23.1 | 25.7 | 24.1 | 24 | 24.3
Denmark |  | SKAGEN | SKAGEN, Denmark | 57.73N | 10.63E | 5 | 1.00 (EUW) | 82-06 | 60410 | -9 |  | -18.1 | 29.7 | 22.9 | 24.9 | 24.6 | 24 | 24.1333 |  | 20.9 | 22.7 | 23 | 22 | 22.2
Denmark |  | SKRYDSTRUP | SKRYDSTRUP, Denmark | 55.23N | 9.27E | 47 | 1.00 (EUW) | 82-06 | 61100 | -14 |  | -24.5 | 32.9 | 27 | 28.8 | 28.7 | 28 | 28.1667 |  | 24 | 26.2 | 26.2 | 25 | 25.4667
Denmark |  | THYBOROEN | THYBOROEN, Denmark | 56.70N | 8.22E | 4 | 1.00 (EUW) | 82-06 | 60520 | -7.1 |  | -16.4 | 33.1 | 23.9 | 26.5 | 26.8 | 26 | 25.7333 |  | 21.6 | 23.7 | 23.9 | 23 | 23.0667
Denmark |  | TIRSTRUP | TIRSTRUP, Denmark | 56.32N | 10.63E | 23 | 1.00 (EUW) | 82-06 | 60700 | -14.2 |  | -26 | 32.5 | 26.8 | 27.8 | 27.7 | 27 | 27.4333 |  | 23.9 | 25.9 | 25.8 | 25 | 25.2
Denmark |  | VAERLOESE | VAERLOESE, Denmark | 55.77N | 12.33E | 31 | 1.00 (EUW) | 82-06 | 61600 | -15.2 |  | -27.8 | 33.7 | 26.7 | 29.2 | 28.5 | 28 | 28.1333 |  | 23.9 | 26.7 | 26.2 | 26 | 25.6
Dominican Republic |  | LAS AMERICAS | LAS AMERICAS, Dominican Republic | 18.43N | 69.67W | 18 | -4.00 (SAZ) | 82-06 | 784850 | 16.8 |  | 14.5 | 37.8 | 32.7 | 33.1 | 33.2 | 33 | 33 |  | 32 | 32.2 | 32.2 | 32 | 32.1333
Dominican Republic |  | SANTO DOMINGO | SANTO DOMINGO, Dominican Republic | 18.43N | 69.88W | 14 | -4.00 (SAZ) | 83-06 | 784860 | 18.4 |  | 15.3 | 40.8 | 32.5 | 32.9 | 33.1 | 33 | 32.8333 |  | 31.8 | 32.1 | 32.2 | 32 | 32.0333
Ecuador |  | GUAYAQUIL AEROPUERT | GUAYAQUIL AEROPUERT, Ecuador | 2.15S | 79.88W | 9 | -5.00 (SAP) | 82-06 | 842030 | 17.2 |  | 5.6 | 37.8 | 32.2 | 32 | 31.9 | 32 | 32.0333 |  | 31 | 30.2 | 30.7 | 31 | 30.6333
Ecuador |  | MANTA | MANTA, Ecuador | 0.95S | 80.68W | 14 | -5.00 (SAP) | 95-06 | 841170 | N/A |  | N/A | N/A | 29.8 | 30.2 | 30.8 | 30 | 30.2667 |  | 28.2 | 29.1 | 29.2 | 29 | 28.8333
Ecuador |  | QUITO AEROPUERTO | QUITO AEROPUERTO, Ecuador | 0.13S | 78.48W | 2812 | -5.00 (SAP) | 82-06 | 840710 | 4.2 |  | -0.2 | 32.2 | 21.9 | 21.2 | 22 | 22 | 21.7 |  | 20.8 | 20.2 | 21 | 21 | 20.6667
Egypt |  | ALEXANDRIA/NOUZHA | ALEXANDRIA/NOUZHA, Egypt | 31.20N | 29.95E | 7 | 2.00 (EGP) | 82-06 | 623180 | 4.1 |  | -0.2 | 44.7 | 35.1 | 34.2 | 33 | 34 | 34.1 |  | 31.2 | 31.2 | 31.2 | 31 | 31.2
Egypt |  | ASSWAN | ASSWAN, Egypt | 23.97N | 32.78E | 194 | 2.00 (EGP) | 82-06 | 624140 | 4.3 |  | -0.5 | 48.4 | 45 | 44.9 | 44.2 | 45 | 44.7 |  | 43.4 | 43.2 | 42.9 | 43 | 43.1667
Egypt |  | ASYUT | ASYUT, Egypt | 27.05N | 31.02E | 70 | 2.00 (EGP) | 82-06 | 623930 | 2.7 |  | 1 | 49.6 | 42.5 | 41.5 | 40.8 | 42 | 41.6 |  | 40 | 39.6 | 39.1 | 40 | 39.5667
Egypt |  | BALTIM | BALTIM, Egypt | 31.55N | 31.10E | 2 | 2.00 (EGP) | 94-06 | 623250 | 5.4 |  | 0 | 41.8 | 32.9 | 33.9 | 33 | 33 | 33.2667 |  | 30.5 | 31.3 | 31.7 | 31 | 31.1667
Egypt |  | CAIRO AIRPORT | CAIRO AIRPORT, Egypt | 30.13N | 31.40E | 74 | 2.00 (EGP) | 82-06 | 623660 | 5.1 |  | -0.4 | 45.6 | 40.1 | 39.5 | 37.5 | 39 | 39.0333 |  | 37.6 | 36.9 | 36 | 37 | 36.8333
Egypt |  | DAKHLA | DAKHLA, Egypt | 25.48N | 29.00E | 117 | 2.00 (EGP) | 88-06 | 624320 | 1.7 |  | -1.6 | 48.5 | 44.4 | 43.9 | 43.9 | 44 | 44.0667 |  | 42.5 | 42.2 | 42.4 | 42 | 42.3667
Egypt |  | EL ARISH | EL ARISH, Egypt | 31.08N | 33.82E | 32 | 2.00 (EGP) | 85-06 | 623370 | 2.9 |  | 0.6 | 44.9 | 35.5 | 35.4 | 34.3 | 35 | 35.0667 |  | 32.4 | 33.3 | 32.9 | 33 | 32.8667
Egypt |  | EL TOR | EL TOR, Egypt | 28.23N | 33.62E | 14 | 2.00 (EGP) | 94-06 | 624590 | 6.7 |  | 3.1 | 45.3 | 37.5 | 38.7 | 37.8 | 38 | 38 |  | 34.6 | 35.5 | 35.1 | 35 | 35.0667
Egypt |  | HURGUADA | HURGUADA, Egypt | 27.15N | 33.72E | 14 | 2.00 (EGP) | 90-06 | 624630 | 7.8 |  | 5.3 | 44.3 | 39.2 | 40 | 39.6 | 40 | 39.6 |  | 37.6 | 38.2 | 38.2 | 38 | 38
Egypt |  | ISMAILIA | ISMAILIA, Egypt | 30.60N | 32.25E | 13 | 2.00 (EGP) | 87-06 | 624400 | 4.5 |  | 0 | 45.3 | 38.6 | 38.9 | 37.7 | 38 | 38.4 |  | 36.4 | 37 | 36.4 | 37 | 36.6
Egypt |  | KHARGA | KHARGA, Egypt | 25.45N | 30.53E | 73 | 2.00 (EGP) | 87-06 | 624350 | 2.2 |  | -1.2 | 51.6 | 45.9 | 45.2 | 44.3 | 45 | 45.1333 |  | 43.7 | 43.1 | 42.5 | 43 | 43.1
Egypt |  | KOSSEIR | KOSSEIR, Egypt | 26.13N | 34.15E | 11 | 2.00 (EGP) | 83-06 | 624650 | 9.5 |  | 6 | 43.3 | 35.6 | 36 | 36 | 36 | 35.8667 |  | 34 | 34.3 | 34.3 | 34 | 34.2
Egypt |  | LUXOR | LUXOR, Egypt | 25.67N | 32.70E | 99 | 2.00 (EGP) | 82-06 | 624050 | 1.8 |  | -1.5 | 49.8 | 44.8 | 44.2 | 43.5 | 44 | 44.1667 |  | 43 | 42.8 | 42 | 43 | 42.6
Egypt |  | MERSA MATRUH | MERSA MATRUH, Egypt | 31.33N | 27.22E | 30 | 2.00 (EGP) | 82-06 | 623060 | 5.3 |  | 2.7 | 46.1 | 36.1 | 33.6 | 32.8 | 34 | 34.1667 |  | 31.5 | 31 | 31 | 31 | 31.1667
Egypt |  | MINYA | MINYA, Egypt | 28.08N | 30.73E | 40 | 2.00 (EGP) | 86-06 | 623870 | 1.5 |  | -0.6 | 49.2 | 42.8 | 40.6 | 39.6 | 41 | 41 |  | 39.8 | 38.5 | 38 | 39 | 38.7667
Egypt |  | PORT SAID | PORT SAID, Egypt | 31.27N | 32.30E | 6 | 2.00 (EGP) | 86-06 | 623330 | N/A |  | N/A | N/A | 31 | 33.2 | 33.2 | 32 | 32.4667 |  | 29.8 | 32 | 32 | 31 | 31.2667
Egypt |  | PORT SAID/EL GAMIL | PORT SAID/EL GAMIL, Egypt | 31.28N | 32.23E | 6 | 2.00 (EGP) | 88-06 | 623320 | 7 |  | 1.5 | 42.2 | 31.5 | 32.9 | 32.6 | 32 | 32.3333 |  | 29.7 | 31.3 | 31.5 | 31 | 30.8333
Egypt |  | SIWA | SIWA, Egypt | 29.20N | 25.32E | -13 | 2.00 (EGP) | 82-06 | 624170 | N/A |  | N/A | N/A | 43.3 | 43.3 | 42 | 43 | 42.8667 |  | 40.4 | 41 | 40.1 | 41 | 40.5
Estonia |  | KUNDA | KUNDA, Estonia | 59.52N | 26.53E | 3 | 2.00 (EUE) | 93-06 | 260450 | -23.1 |  | -38.6 | 34 | 27.2 | 29.2 | 27 | 28 | 27.8 |  | 24 | 26.1 | 24.3 | 25 | 24.8
Estonia |  | KURESSAARE | KURESSAARE, Estonia | 58.23N | 22.50E | 4 | 2.00 (EUE) | 90-00 | 262150 | -15.9 |  | -27.7 | 31.1 | 24.6 | 27 | 26.4 | 26 | 26 |  | 22.5 | 25.3 | 24.6 | 24 | 24.1333
Estonia |  | NARVA | NARVA, Estonia | 59.37N | 28.12E | 30 | 2.00 (EUE) | 94-06 | 260580 | -25 |  | -35.2 | 35.2 | 28.6 | 30.5 | 28.1 | 29 | 29.0667 |  | 26.3 | 27.7 | 26 | 27 | 26.6667
Estonia |  | PJARNU | PJARNU, Estonia | 58.37N | 24.50E | 8 | 2.00 (EUE) | 82-06 | 262310 | -20.7 |  | -33 | 34 | 27.7 | 29.7 | 27.7 | 28 | 28.3667 |  | 25 | 27.3 | 25.5 | 26 | 25.9333
Estonia |  | RISTNA | RISTNA, Estonia | 58.92N | 22.07E | 9 | 2.00 (EUE) | 82-06 | 261150 | -14.6 |  | -29 | 32 | 24.7 | 27.2 | 25.8 | 26 | 25.9 |  | 21.3 | 25 | 23.5 | 23 | 23.2667
Estonia |  | TALLINN | TALLINN, Estonia | 59.47N | 24.82E | 34 | 2.00 (EUE) | 82-06 | 260380 | -21.7 |  | -33.6 | 34.6 | 26.8 | 29.2 | 27.2 | 28 | 27.7333 |  | 24.2 | 26.3 | 25 | 25 | 25.1667
Estonia |  | TARTU | TARTU, Estonia | 58.30N | 26.73E | 68 | 2.00 (EUE) | 82-06 | 262420 | -24.8 |  | -38 | 35.5 | 28 | 29.9 | 27.8 | 29 | 28.5667 |  | 25.6 | 27.5 | 26 | 26 | 26.3667
Estonia |  | TURI | TURI, Estonia | 58.82N | 25.42E | 65 | 2.00 (EUE) | 93-06 | 261350 | -25.4 |  | -34.7 | 34.7 | 27.8 | 30.5 | 27.7 | 29 | 28.6667 |  | 25.8 | 28.5 | 25.9 | 27 | 26.7333
Estonia |  | VALKE-MAARJA | VALKE-MAARJA, Estonia | 59.13N | 26.23E | 123 | 2.00 (EUE) | 94-06 | 261410 | -24.8 |  | -35.4 | 32.2 | 27 | 29.9 | 27.5 | 28 | 28.1333 |  | 25.3 | 27.6 | 25.7 | 26 | 26.2
Falkland Islands (Malvinas) |  | MOUNT PLEASANT AIRP | MOUNT PLEASANT AIRP, Falkland Islands (Malvinas) | 51.82S | 58.45W | 74 | -4.00 (FLK) | 86-06 | 888890 | -6.2 |  | -10.4 | 27.1 | 9.2 | 9.7 | 10.1 | 10 | 9.6667 |  | 7.9 | 7.9 | 8.3 | 8 | 8.0333
Faroe Islands |  | AKRABERG | AKRABERG, Faroe Islands | 61.40N | 6.67W | 102 | 0.00 (GMT) | 82-06 | 60090 | -4.6 |  | -7 | 22.1 | 12.6 | 14.4 | 14.8 | 14 | 13.9333 |  | 11.1 | 12.8 | 12.6 | 12 | 12.1667
Faroe Islands |  | TORSHAVN | TORSHAVN, Faroe Islands | 62.02N | 6.77W | 61 | 0.00 (GMT) | 82-06 | 60110 | -5.7 |  | -9.5 | 21.9 | 14.8 | 15.5 | 15.6 | 15 | 15.3 |  | 12.8 | 14.1 | 14.3 | 14 | 13.7333
Fiji |  | LAKEBA AWS | LAKEBA AWS, Fiji | 18.23S | 178.80W | 3 | 12.00 (FJI) | 82-06 | 916910 | 16.4 |  | 13.4 | 33.4 | 28.9 | 28.2 | 28 | 28 | 28.3667 |  | 27.8 | 27.2 | 27.1 | 27 | 27.3667
Fiji |  | MATUKU AWS | MATUKU AWS, Fiji | 19.13S | 179.75E | 5 | 12.00 (FJI) | 82-06 | 916970 | 16.9 |  | 12.4 | 33.9 | 28.3 | 28.2 | 27.3 | 28 | 27.9333 |  | 27.5 | 26.9 | 26.4 | 27 | 26.9333
Fiji |  | NADI AIRPORT | NADI AIRPORT, Fiji | 17.75S | 177.45E | 18 | 12.00 (FJI) | 82-06 | 916800 | 14.3 |  | 11.6 | 39.1 | 31 | 30.2 | 30.2 | 30 | 30.4667 |  | 29.8 | 29.1 | 29.2 | 29 | 29.3667
Fiji |  | NAUSORI | NAUSORI, Fiji | 18.05S | 178.57E | 7 | 12.00 (FJI) | 82-06 | 916830 | 15 |  | 12.5 | 35.1 | 29.2 | 28.7 | 28.8 | 29 | 28.9 |  | 28.2 | 27.6 | 27.4 | 28 | 27.7333
Fiji |  | ONO-I-LAU AWS | ONO-I-LAU AWS, Fiji | 20.67S | 178.72W | 28 | 12.00 (FJI) | 82-06 | 916990 | 17.4 |  | 12.3 | 32.8 | 27.4 | 27.1 | 26.7 | 27 | 27.0667 |  | 26.6 | 26 | 25.9 | 26 | 26.1667
Fiji |  | ROTUMA | ROTUMA, Fiji | 12.50S | 177.05E | 26 | 12.00 (FJI) | 82-06 | 916500 | 20.3 |  | 15.6 | 36.9 | 30.6 | 30.6 | 30.4 | 31 | 30.5333 |  | 30 | 29.9 | 29.7 | 30 | 29.8667
Fiji |  | UDU POINT AWS | UDU POINT AWS, Fiji | 16.13S | 179.98W | 63 | 12.00 (FJI) | 82-06 | 916520 | N/A |  | N/A | N/A | 29.8 | 29 | 29.5 | 29 | 29.4333 |  | 29 | 28.2 | 28.7 | 29 | 28.6333
Fiji |  | VIWA AWS | VIWA AWS, Fiji | 17.15S | 176.90E | 5 | 12.00 (FJI) | 82-06 | 916700 | N/A |  | N/A | N/A | 29.7 | 28.7 | 29.2 | 29 | 29.2 |  | 28.8 | 27.8 | 28.3 | 28 | 28.3
Fiji |  | VUNISEA | VUNISEA, Fiji | 19.05S | 178.17E | 33 | 12.00 (FJI) | 82-06 | 916930 | N/A |  | N/A | N/A | 28.7 | 28.1 | 27.9 | 28 | 28.2333 |  | 27.6 | 26.9 | 26.8 | 27 | 27.1
Fiji |  | YASAWA-I-RARA AWS | YASAWA-I-RARA AWS, Fiji | 16.70S | 177.58E | 50 | 12.00 (FJI) | 82-06 | 916600 | N/A |  | N/A | N/A | 30.5 | 29.9 | 30 | 30 | 30.1333 |  | 29.5 | 28.7 | 28.7 | 29 | 28.9667
Finland |  | AHTARI | AHTARI, Finland | 62.53N | 24.02E | 161 | 2.00 (EUE) | 82-06 | 29240 | -31.8 |  | -41.6 | 31.5 | 27.4 | 27.6 | 25.7 | 27 | 26.9 |  | 24.6 | 25.5 | 24 | 25 | 24.7
Finland |  | BAGASKAR | BAGASKAR, Finland | 59.93N | 24.02E | 21 | 2.00 (EUE) | 82-06 | 29840 | -19.8 |  | -33.8 | 29.6 | 23.9 | 25.9 | 24.7 | 25 | 24.8333 |  | 21.2 | 24 | 23.1 | 23 | 22.7667
Finland |  | HALLI | HALLI, Finland | 61.85N | 24.80E | 145 | 2.00 (EUE) | 82-06 | 29450 | -29.5 |  | -41 | 32.7 | 27.5 | 29 | 26.6 | 28 | 27.7 |  | 25.1 | 26.5 | 24.7 | 25 | 25.4333
Finland |  | HELSINKI-VANTAA | HELSINKI-VANTAA, Finland | 60.32N | 24.97E | 56 | 2.00 (EUE) | 82-06 | 29740 | -25.1 |  | -36.5 | 33.1 | 27.2 | 29.2 | 27.3 | 28 | 27.9 |  | 25.1 | 27.2 | 25.5 | 26 | 25.9333
Finland |  | ILOMANTSI | ILOMANTSI, Finland | 62.68N | 30.95E | 165 | 2.00 (EUE) | 82-00 | 29190 | -31.4 |  | -42.2 | 32.8 | 28.2 | 27.7 | 26 | 27 | 27.3 |  | 25.1 | 25.7 | 23.8 | 25 | 24.8667
Finland |  | ISOSAARI | ISOSAARI, Finland | 60.10N | 25.07E | 5 | 2.00 (EUE) | 84-06 | 29880 | -19.6 |  | -33 | 28.8 | 23.1 | 25 | 24 | 24 | 24.0333 |  | 20.6 | 23.3 | 22.3 | 22 | 22.0667
Finland |  | IVALO | IVALO, Finland | 68.62N | 27.42E | 148 | 2.00 (EUE) | 82-06 | 28070 | -35.7 |  | -47.3 | 32.4 | 26.6 | 27.1 | 25.3 | 26 | 26.3333 |  | 23.1 | 24.6 | 22.6 | 23 | 23.4333
Finland |  | JOENSUU | JOENSUU, Finland | 62.67N | 29.63E | 117 | 2.00 (EUE) | 82-06 | 29290 | -30.6 |  | -41.7 | 32.8 | 28 | 28.6 | 26.2 | 28 | 27.6 |  | 25.1 | 26.5 | 24 | 25 | 25.2
Finland |  | JOKIOINEN | JOKIOINEN, Finland | 60.82N | 23.50E | 103 | 2.00 (EUE) | 82-06 | 29630 | -26.7 |  | -36.7 | 34.7 | 26.7 | 28.8 | 27.1 | 28 | 27.5333 |  | 24.8 | 26.7 | 25 | 26 | 25.5
Finland |  | JOMALA | JOMALA, Finland | 60.15N | 19.87E | 10 | 2.00 (EUE) | 97-06 | 29710 | -21.4 |  | -31.3 | 33.8 | 23.9 | 27.9 | 27.3 | 26 | 26.3667 |  | 22.1 | 25.5 | 24.9 | 24 | 24.1667
Finland |  | JYVASKYLA | JYVASKYLA, Finland | 62.40N | 25.68E | 145 | 2.00 (EUE) | 82-06 | 29350 | -30.8 |  | -41 | 32.9 | 27.5 | 28.3 | 26.2 | 27 | 27.3333 |  | 25.1 | 26.3 | 24.4 | 25 | 25.2667
Finland |  | KAJAANI | KAJAANI, Finland | 64.28N | 27.68E | 136 | 2.00 (EUE) | 82-06 | 28970 | -33.6 |  | -42.3 | 31.8 | 26.9 | 27.4 | 25.4 | 27 | 26.5667 |  | 24.1 | 25.2 | 23 | 24 | 24.1
Finland |  | KAUHAVA | KAUHAVA, Finland | 63.10N | 23.03E | 44 | 2.00 (EUE) | 82-06 | 29130 | -29.8 |  | -41.8 | 32.5 | 27.5 | 28.5 | 26.7 | 28 | 27.5667 |  | 24.7 | 26 | 24.8 | 25 | 25.1667
Finland |  | KEMI | KEMI, Finland | 65.78N | 24.58E | 15 | 2.00 (EUE) | 82-06 | 28640 | -30.5 |  | -40.6 | 30.5 | 25.9 | 26 | 24.9 | 26 | 25.6 |  | 23.2 | 23.2 | 22.5 | 23 | 22.9667
Finland |  | KEVO | KEVO, Finland | 69.75N | 27.03E | 101 | 2.00 (EUE) | 82-06 | 28050 | -37 |  | -46.3 | 33.2 | 26.1 | 27.7 | 25.7 | 27 | 26.5 |  | 22.5 | 24.6 | 22 | 23 | 23.0333
Finland |  | KRUUNUPYY | KRUUNUPYY, Finland | 63.72N | 23.15E | 25 | 2.00 (EUE) | 82-95 | 29030 | -29.5 |  | -41.8 | 32.8 | 27.2 | 28.9 | 25.9 | 27 | 27.3333 |  | 24.8 | 25.4 | 23.4 | 25 | 24.5333
Finland |  | KUMLINGE ISLAND | KUMLINGE ISLAND, Finland | 60.30N | 20.75E | 5 | 2.00 (EUE) | 84-00 | 29900 | -16.1 |  | -37.9 | 29.4 | 23.5 | 25.6 | 24.4 | 25 | 24.5 |  | 21.2 | 23 | 22.1 | 22 | 22.1
Finland |  | KUOPIO | KUOPIO, Finland | 63.02N | 27.80E | 102 | 2.00 (EUE) | 82-06 | 29170 | -29.7 |  | -39.9 | 32.3 | 27.7 | 28.2 | 26.1 | 27 | 27.3333 |  | 25.1 | 26.3 | 24.2 | 25 | 25.2
Finland |  | KUUSAMO | KUUSAMO, Finland | 65.97N | 29.18E | 263 | 2.00 (EUE) | 82-06 | 28690 | -34.9 |  | -46.1 | 31.4 | 26.4 | 26 | 24.2 | 26 | 25.5333 |  | 23.2 | 23.9 | 21.5 | 23 | 22.8667
Finland |  | KUUSKAJASKARI | KUUSKAJASKARI, Finland | 61.13N | 21.37E | 10 | 2.00 (EUE) | 82-99 | 29610 | -20.1 |  | -34.7 | 29.4 | 23.4 | 25.2 | 24.6 | 24 | 24.4 |  | 20.9 | 22.6 | 22.6 | 22 | 22.0333
Finland |  | LAHTI | LAHTI, Finland | 60.97N | 25.63E | 84 | 2.00 (EUE) | 82-06 | 29650 | -28.2 |  | -39.1 | 32.9 | 28.1 | 29.4 | 27.1 | 28 | 28.2 |  | 25.7 | 27.2 | 25.4 | 26 | 26.1
Finland |  | LAPPEENRANTA | LAPPEENRANTA, Finland | 61.05N | 28.20E | 115 | 2.00 (EUE) | 82-06 | 29580 | -26.2 |  | -37.4 | 34 | 28.1 | 29.4 | 26.7 | 28 | 28.0667 |  | 25.8 | 27.1 | 25 | 26 | 25.9667
Finland |  | MARIEHAMN/ALAND ISL | MARIEHAMN/ALAND ISL, Finland | 60.12N | 19.90E | 6 | 2.00 (EUE) | 82-06 | 29700 | -20.2 |  | -35.5 | 31 | 24.6 | 26 | 25.1 | 25 | 25.2333 |  | 21.9 | 23.7 | 22.9 | 23 | 22.8333
Finland |  | MASSKAR | MASSKAR, Finland | 63.73N | 22.58E | 13 | 2.00 (EUE) | 82-91 | 29010 | -25.6 |  | -37.2 | 32.1 | 22.9 | 25.9 | 23.5 | 24 | 24.1 |  | 20.3 | 22.1 | 21.3 | 21 | 21.2333
Finland |  | MIKKELI | MIKKELI, Finland | 61.73N | 27.30E | 138 | 2.00 (EUE) | 95-06 | 29470 | -29.9 |  | -40.8 | 31.8 | 27.1 | 28.6 | 26.6 | 27 | 27.4333 |  | 25.2 | 27 | 25.1 | 26 | 25.7667
Finland |  | MOIKIPAA | MOIKIPAA, Finland | 62.88N | 21.10E | 13 | 2.00 (EUE) | 82-91 | 29210 | -24.1 |  | -35 | 29.8 | 21.8 | 24.2 | 21.4 | 22 | 22.4667 |  | 19.6 | 21.3 | 19.7 | 20 | 20.2
Finland |  | MUONIO | MUONIO, Finland | 67.97N | 23.68E | 253 | 2.00 (EUE) | 82-06 | 28230 | -35.9 |  | -46.8 | 29.3 | 25.2 | 26.1 | 23.8 | 25 | 25.0333 |  | 22.8 | 23.8 | 21.2 | 23 | 22.6
Finland |  | NIINISALO | NIINISALO, Finland | 61.85N | 22.47E | 136 | 2.00 (EUE) | 82-06 | 29420 | -25.6 |  | -35.1 | 32.9 | 27.2 | 28.8 | 27 | 28 | 27.6667 |  | 25 | 26.4 | 24.9 | 25 | 25.4333
Finland |  | NIVALA | NIVALA, Finland | 63.92N | 24.97E | 81 | 2.00 (EUE) | 82-00 | 29050 | -30.8 |  | -40.9 | 32.5 | 27.6 | 28.6 | 25.6 | 27 | 27.2667 |  | 25.2 | 25.6 | 23.6 | 25 | 24.8
Finland |  | NYHAMN | NYHAMN, Finland | 59.97N | 19.97E | 10 | 2.00 (EUE) | 82-06 | 29800 | -12.6 |  | -29.8 | 27.7 | 20.5 | 23.3 | 23.5 | 22 | 22.4333 |  | 18 | 21.9 | 21.7 | 21 | 20.5333
Finland |  | OULU | OULU, Finland | 64.93N | 25.37E | 15 | 2.00 (EUE) | 82-06 | 28750 | -29.9 |  | -41 | 33.3 | 27.1 | 28 | 25.7 | 27 | 26.9333 |  | 24.2 | 25 | 23.7 | 24 | 24.3
Finland |  | PELLO | PELLO, Finland | 66.80N | 24.00E | 84 | 2.00 (EUE) | 82-06 | 28440 | -34.5 |  | -41.5 | 31 | 26.6 | 27.1 | 25.2 | 26 | 26.3 |  | 23.9 | 25.1 | 23 | 24 | 24
Finland |  | PORI | PORI, Finland | 61.47N | 21.80E | 17 | 2.00 (EUE) | 82-06 | 29520 | -24.4 |  | -34.4 | 33.3 | 27 | 29.1 | 27.1 | 28 | 27.7333 |  | 24.2 | 26.1 | 25.2 | 25 | 25.1667
Finland |  | PUDASJARVI | PUDASJARVI, Finland | 65.37N | 27.02E | 117 | 2.00 (EUE) | 82-99 | 28670 | -31.7 |  | -40.5 | 31.7 | 27.1 | 27.4 | 24.9 | 26 | 26.4667 |  | 24.8 | 24.5 | 22.7 | 24 | 24
Finland |  | RANKKI | RANKKI, Finland | 60.37N | 26.97E | 12 | 2.00 (EUE) | 82-06 | 29760 | -22.2 |  | -34 | 31.4 | 25 | 26.9 | 25.1 | 26 | 25.6667 |  | 22.1 | 24.6 | 23.4 | 23 | 23.3667
Finland |  | ROVANIEMI | ROVANIEMI, Finland | 66.57N | 25.83E | 201 | 2.00 (EUE) | 82-06 | 28450 | -28.3 |  | -38.9 | 30.9 | 25.8 | 26.9 | 24.6 | 26 | 25.7667 |  | 23.2 | 24.4 | 22.2 | 23 | 23.2667
Finland |  | RUSSARO | RUSSARO, Finland | 59.77N | 22.95E | 11 | 2.00 (EUE) | 82-06 | 29820 | -17.2 |  | -31.7 | 30 | 22.9 | 25.3 | 24.2 | 24 | 24.1333 |  | 20.4 | 23.4 | 22.6 | 22 | 22.1333
Finland |  | SALLA KK | SALLA KK, Finland | 66.83N | 28.68E | 222 | 2.00 (EUE) | 82-06 | 28490 | -35.2 |  | -45.7 | 30.9 | 26.2 | 26 | 24.2 | 25 | 25.4667 |  | 23.2 | 23.8 | 22 | 23 | 23
Finland |  | SAVONLINNA | SAVONLINNA, Finland | 61.95N | 28.95E | 95 | 2.00 (EUE) | 86-06 | 29480 | -30.4 |  | -42.8 | 32.1 | 27.9 | 28.2 | 26.3 | 27 | 27.4667 |  | 25.8 | 26.2 | 24.4 | 25 | 25.4667
Finland |  | SODANKYLA | SODANKYLA, Finland | 67.37N | 26.65E | 179 | 2.00 (EUE) | 82-06 | 28360 | -37.5 |  | -47.3 | 31.7 | 26.6 | 26.8 | 25.3 | 26 | 26.2333 |  | 23.7 | 24.5 | 22.5 | 24 | 23.5667
Finland |  | SUOMUSSALMI | SUOMUSSALMI, Finland | 64.90N | 29.02E | 224 | 2.00 (EUE) | 82-00 | 28790 | -32.4 |  | -41.5 | 30.6 | 27.2 | 26.6 | 24.9 | 26 | 26.2333 |  | 24.5 | 24.2 | 22.4 | 24 | 23.7
Finland |  | TAMPERE/PIRKKALA | TAMPERE/PIRKKALA, Finland | 61.42N | 23.58E | 112 | 2.00 (EUE) | 82-06 | 29440 | -27.2 |  | -37.9 | 32.7 | 27.9 | 29.6 | 27.2 | 28 | 28.2333 |  | 25.2 | 27.1 | 25.2 | 26 | 25.8333
Finland |  | TURKU | TURKU, Finland | 60.52N | 22.27E | 59 | 2.00 (EUE) | 82-06 | 29720 | -24.1 |  | -34.9 | 32.4 | 27.7 | 29.8 | 27.6 | 28 | 28.3667 |  | 25 | 27 | 25.8 | 26 | 25.9333
Finland |  | UTO | UTO, Finland | 59.78N | 21.38E | 7 | 2.00 (EUE) | 82-06 | 29810 | -14 |  | -29.8 | 28.4 | 20.6 | 24 | 23.8 | 23 | 22.8 |  | 18.4 | 22.5 | 22.2 | 21 | 21.0333
Finland |  | UTTI | UTTI, Finland | 60.90N | 26.93E | 100 | 2.00 (EUE) | 82-06 | 29660 | -27.3 |  | -37.6 | 33.2 | 28.1 | 29.6 | 27 | 28 | 28.2333 |  | 25.8 | 27.3 | 25.2 | 26 | 26.1
Finland |  | VAASA AIRPORT | VAASA AIRPORT, Finland | 63.05N | 21.77E | 8 | 2.00 (EUE) | 82-06 | 29110 | -27.2 |  | -41 | 32 | 25.9 | 28 | 26.4 | 27 | 26.7667 |  | 23.8 | 25.4 | 24.2 | 24 | 24.4667
Finland |  | VALASSAARET | VALASSAARET, Finland | 63.43N | 21.07E | 8 | 2.00 (EUE) | 82-06 | 29100 | -19 |  | -31.5 | 28.4 | 20 | 23.5 | 23.1 | 22 | 22.2 |  | 17.8 | 21.8 | 21.2 | 20 | 20.2667
Finland |  | VIITASAARI | VIITASAARI, Finland | 63.08N | 25.87E | 132 | 2.00 (EUE) | 82-06 | 29150 | -27.7 |  | -37.8 | 32.1 | 27.8 | 28.2 | 26 | 27 | 27.3333 |  | 25.1 | 26.1 | 24.1 | 25 | 25.1
France |  | ABBEVILLE | ABBEVILLE, France | 50.13N | 1.83E | 77 | 1.00 (EUW) | 82-06 | 70050 | -8.1 |  | -17.7 | 37.3 | 29.1 | 30.7 | 31.4 | 30 | 30.4 |  | 25.7 | 27.7 | 27.9 | 27 | 27.1
France |  | AGEN | AGEN, France | 44.18N | 0.60E | 60 | 1.00 (EUW) | 82-06 | 75240 | -7.2 |  | -16.3 | 41 | 33.6 | 35.6 | 36.2 | 35 | 35.1333 |  | 30.8 | 32.9 | 32.6 | 32 | 32.1
France |  | AJACCIO | AJACCIO, France | 41.92N | 8.80E | 9 | 1.00 (EUW) | 82-06 | 77610 | -2.7 |  | -7 | 41.1 | 30.6 | 33.5 | 33.5 | 33 | 32.5333 |  | 28.4 | 30.9 | 30.8 | 30 | 30.0333
France |  | ALBI | ALBI, France | 43.92N | 2.12E | 176 | 1.00 (EUW) | 89-06 | 76320 | -6.7 |  | -11.8 | 42.3 | 35.1 | 36.2 | 38 | 36 | 36.4333 |  | 31.7 | 33.9 | 34.2 | 33 | 33.2667
France |  | ALENCON | ALENCON, France | 48.43N | 0.10E | 144 | 1.00 (EUW) | 82-06 | 71390 | -8 |  | -16.8 | 38.7 | 30.8 | 32 | 34 | 32 | 32.2667 |  | 27.2 | 29.6 | 29.7 | 29 | 28.8333
France |  | AMBERIEU | AMBERIEU, France | 45.98N | 5.33E | 253 | 1.00 (EUW) | 87-06 | 74820 | -10.3 |  | -17.1 | 39.8 | 33.4 | 34.1 | 36.1 | 35 | 34.5333 |  | 30.3 | 31.8 | 32.3 | 31 | 31.4667
France |  | AUCH | AUCH, France | 43.68N | 0.60E | 128 | 1.00 (EUW) | 85-06 | 76220 | -8 |  | -13.8 | 42.4 | 34 | 35.7 | 37.3 | 36 | 35.6667 |  | 30.6 | 32.9 | 33.2 | 32 | 32.2333
France |  | AURILLAC | AURILLAC, France | 44.88N | 2.42E | 640 | 1.00 (EUW) | 82-06 | 75490 | -11.3 |  | -18.4 | 37.3 | 30.9 | 32.2 | 34.6 | 33 | 32.5667 |  | 27.9 | 30 | 30 | 29 | 29.3
France |  | AUXERRE | AUXERRE, France | 47.80N | 3.55E | 212 | 1.00 (EUW) | 82-06 | 72650 | -9.5 |  | -19.4 | 41.7 | 32.4 | 34.7 | 37.3 | 35 | 34.8 |  | 29.8 | 31.8 | 31.9 | 31 | 31.1667
France |  | BALE-MULHOUSE | BALE-MULHOUSE, France | 47.60N | 7.52E | 271 | 1.00 (EUW) | 82-06 | 72990 | -13.1 |  | -24.6 | 39.9 | 32 | 34.1 | 35.2 | 34 | 33.7667 |  | 29.8 | 31.3 | 31.1 | 31 | 30.7333
France |  | BASTIA | BASTIA, France | 42.55N | 9.48E | 12 | 1.00 (EUW) | 82-06 | 77900 | -0.6 |  | -4.5 | 37.8 | 30.5 | 32.6 | 33 | 32 | 32.0333 |  | 29.1 | 31.1 | 31.2 | 30 | 30.4667
France |  | BEAUCOUZE | BEAUCOUZE, France | 47.48N | 0.60W | 50 | 1.00 (EUW) | 82-06 | 72300 | -6.7 |  | -15.2 | 39.4 | 32.2 | 33.5 | 34.6 | 33 | 33.4333 |  | 29.1 | 30.8 | 31.1 | 30 | 30.3333
France |  | BEAUVAIS | BEAUVAIS, France | 49.47N | 2.12E | 111 | 1.00 (EUW) | 86-06 | 70550 | -9 |  | -16.4 | 39.5 | 30.4 | 32.5 | 34.2 | 32 | 32.3667 |  | 27.3 | 29.8 | 30.5 | 29 | 29.2
France |  | BELFORT | BELFORT, France | 47.63N | 6.88E | 422 | 1.00 (EUW) | 82-06 | 72950 | -13.1 |  | -25 | 37.5 | 29.9 | 32.9 | 34.6 | 32 | 32.4667 |  | 27.8 | 30.1 | 29.5 | 29 | 29.1333
France |  | BELLE IIE LE TALUT | BELLE IIE LE TALUT, France | 47.30N | 3.17W | 43 | 1.00 (EUW) | 82-06 | 72070 | -2.5 |  | -9.6 | 34.4 | 26.3 | 28.7 | 28.2 | 28 | 27.7333 |  | 23.5 | 26 | 25 | 25 | 24.8333
France |  | BERGERAC | BERGERAC, France | 44.82N | 0.52E | 51 | 1.00 (EUW) | 89-06 | 75300 | -8.4 |  | -13.7 | 41.5 | 34.1 | 35.4 | 37.4 | 36 | 35.6333 |  | 31.1 | 32.7 | 33.4 | 32 | 32.4
France |  | BESANCON | BESANCON, France | 47.25N | 5.98E | 310 | 1.00 (EUW) | 82-06 | 72880 | -10.9 |  | -18.7 | 38.6 | 31.5 | 32.8 | 34.7 | 33 | 33 |  | 29.1 | 30.2 | 30.4 | 30 | 29.9
France |  | BIARRITZ | BIARRITZ, France | 43.47N | 1.53W | 71 | 1.00 (EUW) | 82-06 | 76020 | -4.5 |  | -10.9 | 40.2 | 32.9 | 33.5 | 33.1 | 33 | 33.1667 |  | 29.1 | 29.9 | 29.5 | 30 | 29.5
France |  | BISCAROSSE | BISCAROSSE, France | 44.43N | 1.25W | 39 | 1.00 (EUW) | 82-06 | 75030 | -3.2 |  | -8.8 | 39.6 | 33.2 | 33.7 | 34.1 | 34 | 33.6667 |  | 29.4 | 30.4 | 30.2 | 30 | 30
France |  | BORDEAUX MERIGNAC | BORDEAUX MERIGNAC, France | 44.83N | 0.68W | 61 | 1.00 (EUW) | 82-06 | 75100 | -6.7 |  | -15.1 | 40 | 33.4 | 35.1 | 36 | 35 | 34.8333 |  | 30.8 | 32.6 | 32.8 | 32 | 32.0667
France |  | BOULOGNE | BOULOGNE, France | 50.73N | 1.60E | 74 | 1.00 (EUW) | 94-06 | 70020 | -5.4 |  | -12.9 | 36.2 | 27.7 | 28.5 | 30.3 | 29 | 28.8333 |  | 24.4 | 25.7 | 27.2 | 26 | 25.7667
France |  | BOURG ST-MAURICE | BOURG ST-MAURICE, France | 45.62N | 6.77E | 868 | 1.00 (EUW) | 82-06 | 74970 | -13.6 |  | -23.3 | 38.4 | 32.3 | 33.3 | 33 | 33 | 32.8667 |  | 29.4 | 30.9 | 30.2 | 30 | 30.1667
France |  | BOURGES | BOURGES, France | 47.07N | 2.37E | 166 | 1.00 (EUW) | 85-06 | 72550 | -8.8 |  | -15.5 | 39.9 | 32.6 | 34.3 | 37 | 35 | 34.6333 |  | 29.9 | 31.7 | 32.1 | 31 | 31.2333
France |  | BREHAT ISLAND | BREHAT ISLAND, France | 48.85N | 3.00W | 36 | 1.00 (EUW) | 82-97 | 71210 | -2.7 |  | -8.6 | 31.7 | 21.8 | 24 | 24.5 | 23 | 23.4333 |  | 19.5 | 21.9 | 22.2 | 21 | 21.2
France |  | BREST | BREST, France | 48.45N | 4.42W | 99 | 1.00 (EUW) | 82-06 | 71100 | -4.1 |  | -9.4 | 35.4 | 27.5 | 29 | 28.4 | 28 | 28.3 |  | 23.6 | 26 | 24.8 | 25 | 24.8
France |  | BRIGNOGAN | BRIGNOGAN, France | 48.68N | 4.33W | 18 | 1.00 (EUW) | 84-06 | 71070 | -2 |  | -8.1 | 33 | 21.8 | 22.8 | 23.8 | 23 | 22.8 |  | 19.3 | 20.7 | 21.1 | 20 | 20.3667
France |  | BRIVE | BRIVE, France | 45.15N | 1.47E | 117 | 1.00 (EUW) | 88-06 | 74380 | -9.8 |  | -15.4 | 41 | 34.8 | 35.3 | 38.6 | 36 | 36.2333 |  | 32 | 33.3 | 33.8 | 33 | 33.0333
France |  | CAEN CARPIQUET | CAEN CARPIQUET, France | 49.18N | 0.45W | 67 | 1.00 (EUW) | 82-06 | 70270 | -7.5 |  | -17.2 | 38.7 | 30 | 30.5 | 32 | 31 | 30.8333 |  | 25.5 | 27.3 | 27.9 | 27 | 26.9
France |  | CALVI | CALVI, France | 42.53N | 8.80E | 58 | 1.00 (EUW) | 82-06 | 77540 | -1.8 |  | -5.2 | 41.8 | 32.5 | 34.4 | 35.2 | 34 | 34.0333 |  | 30.2 | 32.7 | 32.9 | 32 | 31.9333
France |  | CAP BEAR | CAP BEAR, France | 42.52N | 3.13E | 86 | 1.00 (EUW) | 82-06 | 77490 | -0.5 |  | -7 | 35.6 | 29.4 | 31.1 | 31.1 | 31 | 30.5333 |  | 27.4 | 29.4 | 29.1 | 29 | 28.6333
France |  | CAP CEPET | CAP CEPET, France | 43.08N | 5.93E | 136 | 1.00 (EUW) | 86-06 | 76610 | 0.4 |  | -6.1 | 35.2 | 29.4 | 31.4 | 32 | 31 | 30.9333 |  | 27.5 | 29.8 | 30.1 | 29 | 29.1333
France |  | CAP CORSE | CAP CORSE, France | 43.00N | 9.35E | 106 | 1.00 (EUW) | 82-06 | 77850 | 1.9 |  | -3.5 | 39.5 | 31.2 | 33.4 | 32.2 | 32 | 32.2667 |  | 28.4 | 31.4 | 30.5 | 30 | 30.1
France |  | CAP COURONNE | CAP COURONNE, France | 43.33N | 5.05E | 27 | 1.00 (EUW) | 82-06 | 76530 | -3.7 |  | -13.4 | 38 | 30.2 | 33.9 | 33 | 32 | 32.3667 |  | 28.4 | 31.2 | 30.5 | 30 | 30.0333
France |  | CAP DE LA HEVE | CAP DE LA HEVE, France | 49.50N | 0.07E | 103 | 1.00 (EUW) | 89-06 | 70280 | -4.8 |  | -11.6 | 37.3 | 29 | 29.6 | 31.5 | 30 | 30.0333 |  | 25.8 | 26.6 | 27.4 | 27 | 26.6
France |  | CAP FERRET | CAP FERRET, France | 44.63N | 1.25W | 10 | 1.00 (EUW) | 82-06 | 75000 | N/A |  | N/A | N/A | 32.6 | 33.2 | 33.7 | 33 | 33.1667 |  | 28.6 | 30.1 | 29.3 | 29 | 29.3333
France |  | CAP PERTUSATO | CAP PERTUSATO, France | 41.37N | 9.17E | 116 | 1.00 (EUW) | 82-06 | 77700 | 1.9 |  | -2.7 | 36.8 | 29.1 | 31.9 | 31.8 | 31 | 30.9333 |  | 26.6 | 29.8 | 29.6 | 29 | 28.6667
France |  | CAP POMEGUES | CAP POMEGUES, France | 43.27N | 5.30E | 70 | 1.00 (EUW) | 82-91 | 76520 | -2.5 |  | -14.1 | 36.4 | 27.4 | 31.9 | 29.5 | 30 | 29.6 |  | 25.7 | 29.7 | 28.2 | 28 | 27.8667
France |  | CAPE FERRAT | CAPE FERRAT, France | 43.68N | 7.33E | 144 | 1.00 (EUW) | 82-06 | 76950 | 1.6 |  | -6.2 | 35.8 | 28.7 | 30.2 | 31.2 | 30 | 30.0333 |  | 27.2 | 29.1 | 29.2 | 29 | 28.5
France |  | CAPE SAGRO | CAPE SAGRO, France | 42.80N | 9.48E | 120 | 1.00 (EUW) | 82-06 | 77910 | 1 |  | -5.3 | 34.9 | 27.3 | 31.3 | 30.4 | 30 | 29.6667 |  | 25.8 | 29.6 | 29.1 | 28 | 28.1667
France |  | CARCASSONNE | CARCASSONNE, France | 43.22N | 2.32E | 130 | 1.00 (EUW) | 82-06 | 76350 | -5.7 |  | -11.8 | 41 | 32.7 | 35.5 | 36.1 | 35 | 34.7667 |  | 30.1 | 32.9 | 32.5 | 32 | 31.8333
France |  | CARPENTRAS | CARPENTRAS, France | 44.08N | 5.05E | 105 | 1.00 (EUW) | 86-06 | 75860 | -8 |  | -12.8 | 41.7 | 36.3 | 37.3 | 38 | 37 | 37.2 |  | 34.1 | 35.4 | 35.1 | 35 | 34.8667
France |  | CAZAUX | CAZAUX, France | 44.53N | 1.13W | 24 | 1.00 (EUW) | 82-06 | 75020 | -6.8 |  | -13.7 | 39.8 | 33 | 35.1 | 35.3 | 34 | 34.4667 |  | 29.9 | 32.4 | 31.9 | 31 | 31.4
France |  | CHAMBERY/AIX-LES-BA | CHAMBERY/AIX-LES-BA, France | 45.63N | 5.87E | 235 | 1.00 (EUW) | 82-06 | 74910 | -8.4 |  | -12.5 | 38.5 | 32.7 | 33.4 | 34.3 | 33 | 33.4667 |  | 30.1 | 31.3 | 31.2 | 31 | 30.8667
France |  | CHARLEVILLE | CHARLEVILLE, France | 49.78N | 4.63E | 148 | 1.00 (EUW) | 90-06 | 70750 | -12.5 |  | -19.2 | 37.5 | 30.2 | 31.6 | 32.7 | 32 | 31.5 |  | 27.6 | 28.9 | 29.2 | 29 | 28.5667
France |  | CHARTRES | CHARTRES, France | 48.47N | 1.50E | 156 | 1.00 (EUW) | 82-06 | 71430 | -9.2 |  | -18.5 | 39.5 | 30.6 | 33.2 | 35.7 | 33 | 33.1667 |  | 27.7 | 30.5 | 30.7 | 30 | 29.6333
France |  | CHASSIRON | CHASSIRON, France | 46.05N | 1.42W | 22 | 1.00 (EUW) | 82-06 | 73140 | -2.9 |  | -10.3 | 37 | 27.7 | 29.1 | 28.6 | 28 | 28.4667 |  | 24.7 | 26.1 | 26.1 | 26 | 25.6333
France |  | CHATEAUROUX/DEOLS | CHATEAUROUX/DEOLS, France | 46.85N | 1.72E | 164 | 1.00 (EUW) | 82-06 | 73540 | -8 |  | -15.3 | 40 | 32.2 | 34.2 | 36.8 | 34 | 34.4 |  | 29.3 | 31.6 | 31.8 | 31 | 30.9
France |  | CLERMONT-FERRAND | CLERMONT-FERRAND, France | 45.78N | 3.17E | 330 | 1.00 (EUW) | 82-06 | 74600 | -11.4 |  | -19.2 | 40.3 | 32.9 | 34.9 | 35.8 | 35 | 34.5333 |  | 29.9 | 32 | 32.1 | 31 | 31.3333
France |  | COGNAC | COGNAC, France | 45.67N | 0.32W | 31 | 1.00 (EUW) | 82-06 | 74120 | -7.5 |  | -16.3 | 39.6 | 32.9 | 35.2 | 35.6 | 35 | 34.5667 |  | 30.5 | 32.4 | 32.7 | 32 | 31.8667
France |  | DIEPPE | DIEPPE, France | 49.93N | 1.10E | 38 | 1.00 (EUW) | 89-06 | 70400 | -6.2 |  | -12.5 | 36.8 | 29.5 | 27.7 | 30.1 | 29 | 29.1 |  | 24.5 | 23.3 | 24.7 | 24 | 24.1667
France |  | DIJON | DIJON, France | 47.27N | 5.08E | 227 | 1.00 (EUW) | 82-06 | 72800 | -11.3 |  | -19.9 | 39.4 | 31.6 | 33.7 | 35.8 | 34 | 33.7 |  | 29.1 | 31.5 | 31.1 | 31 | 30.5667
France |  | DINARD | DINARD, France | 48.58N | 2.07W | 59 | 1.00 (EUW) | 90-06 | 71250 | N/A |  | N/A | N/A | 29.5 | 30 | 31.2 | 30 | 30.2333 |  | 25.8 | 26.9 | 27.1 | 27 | 26.6
France |  | DUNKERQUE | DUNKERQUE, France | 51.05N | 2.33E | 17 | 1.00 (EUW) | 85-06 | 70100 | -5.4 |  | -13 | 36.7 | 27.3 | 26.9 | 28.2 | 27 | 27.4667 |  | 22.8 | 24 | 24.6 | 24 | 23.8
France |  | EMBRUN | EMBRUN, France | 44.57N | 6.50E | 876 | 1.00 (EUW) | 82-06 | 75910 | -11.1 |  | -17.5 | 36.6 | 31.4 | 33.1 | 32.7 | 32 | 32.4 |  | 29.1 | 31.2 | 30.5 | 30 | 30.2667
France |  | EVREUX/FAUVILLE FAF | EVREUX/FAUVILLE FAF, France | 49.02N | 1.22E | 141 | 1.00 (EUW) | 82-06 | 70380 | -9 |  | -17.9 | 38.5 | 30.2 | 31.9 | 34.1 | 32 | 32.0667 |  | 27 | 29.5 | 29.8 | 29 | 28.7667
France |  | FIGARI | FIGARI, France | 41.50N | 9.10E | 23 | 1.00 (EUW) | 88-06 | 77800 | -4.6 |  | -7.2 | 41.8 | 34.9 | 36.2 | 37.1 | 36 | 36.0667 |  | 32.3 | 33.9 | 34.2 | 33 | 33.4667
France |  | GOURDON | GOURDON, France | 44.75N | 1.40E | 261 | 1.00 (EUW) | 82-06 | 75350 | -8 |  | -13 | 41.6 | 33.8 | 35.7 | 35 | 35 | 34.8333 |  | 30.5 | 32.8 | 32.1 | 32 | 31.8
France |  | GRENOBLE-ST-GEOIRS | GRENOBLE-ST-GEOIRS, France | 45.37N | 5.33E | 386 | 1.00 (EUW) | 82-06 | 74860 | -10.2 |  | -18 | 39 | 32.5 | 33.8 | 36.1 | 34 | 34.1333 |  | 29.9 | 31.7 | 32.1 | 31 | 31.2333
France |  | GROUIN DE CANCALE | GROUIN DE CANCALE, France | 48.72N | 1.85W | 41 | 1.00 (EUW) | 82-98 | 71270 | -4.6 |  | -13 | 34 | 24.7 | 26 | 26.3 | 26 | 25.6667 |  | 21.9 | 23.5 | 23.7 | 23 | 23.0333
France |  | HYERES | HYERES, France | 43.10N | 6.15E | 4 | 1.00 (EUW) | 89-06 | 76670 | -1.8 |  | -5.2 | 37.8 | 30.2 | 32.6 | 33 | 32 | 31.9333 |  | 28.7 | 30.7 | 31 | 30 | 30.1333
France |  | ILE ROUSSE | ILE ROUSSE, France | 42.63N | 8.92E | 153 | 1.00 (EUW) | 88-06 | 77530 | N/A |  | N/A | N/A | 30.3 | 31.6 | 32.9 | 32 | 31.6 |  | 28.3 | 29.8 | 30 | 29 | 29.3667
France |  | ISTRES | ISTRES, France | 43.52N | 4.92E | 24 | 1.00 (EUW) | 82-06 | 76470 | -4.9 |  | -10.6 | 39.3 | 34.2 | 35 | 33.7 | 34 | 34.3 |  | 32 | 33 | 31.9 | 32 | 32.3
France |  | L IIE D YEU | L IIE D YEU, France | 46.70N | 2.33W | 32 | 1.00 (EUW) | 82-06 | 73000 | -3.6 |  | -11.8 | 35.3 | 27.8 | 30.6 | 29.9 | 29 | 29.4333 |  | 25 | 27.6 | 26.6 | 26 | 26.4
France |  | LA CHIAPPA | LA CHIAPPA, France | 41.60N | 9.37E | 68 | 1.00 (EUW) | 82-91 | 77680 | N/A |  | N/A | N/A | 29.5 | 32.7 | 32.3 | 32 | 31.5 |  | 27.7 | 30.6 | 30.4 | 30 | 29.5667
France |  | LA ROCHELLE | LA ROCHELLE, France | 46.15N | 1.15W | 10 | 1.00 (EUW) | 84-06 | 73150 | -5.4 |  | -12.4 | 39.1 | 31.9 | 33.2 | 32.7 | 33 | 32.6 |  | 28.1 | 30.3 | 29.6 | 29 | 29.3333
France |  | LA ROCHE-SUR-YON | LA ROCHE-SUR-YON, France | 46.70N | 1.38W | 90 | 1.00 (EUW) | 84-06 | 73060 | -7.6 |  | -17.1 | 38.5 | 31.5 | 33.4 | 34.2 | 33 | 33.0333 |  | 28.6 | 30.2 | 30.2 | 30 | 29.6667
France |  | LANGRES | LANGRES, France | 47.85N | 5.33E | 467 | 1.00 (EUW) | 82-06 | 72830 | -11 |  | -20.6 | 36.5 | 30.1 | 31.6 | 30.3 | 31 | 30.6667 |  | 27.7 | 29.5 | 27.6 | 28 | 28.2667
France |  | LE BOURGET | LE BOURGET, France | 48.97N | 2.43E | 52 | 1.00 (EUW) | 82-06 | 71500 | -7.1 |  | -13.8 | 41.3 | 31.8 | 33.8 | 36.2 | 34 | 33.9333 |  | 28.7 | 31.1 | 31.1 | 30 | 30.3
France |  | LE LUC | LE LUC, France | 43.38N | 6.38E | 82 | 1.00 (EUW) | 90-06 | 76750 | -7.1 |  | -10.5 | 40.6 | 34.7 | 36.2 | 35.8 | 36 | 35.5667 |  | 32.5 | 34.4 | 34.1 | 34 | 33.6667
France |  | LE MANS | LE MANS, France | 47.93N | 0.20E | 52 | 1.00 (EUW) | 82-06 | 72350 | -8.4 |  | -17.8 | 40 | 32.6 | 33.8 | 35.6 | 34 | 34 |  | 29.5 | 31.2 | 31.4 | 31 | 30.7
France |  | LE PUY | LE PUY, France | 45.08N | 3.77E | 833 | 1.00 (EUW) | 85-06 | 74710 | -14.2 |  | -20.5 | 36.4 | 30.8 | 31.2 | 32.1 | 31 | 31.3667 |  | 27.9 | 29 | 29.2 | 29 | 28.7
France |  | LE RAIZET/GUADELOUP | LE RAIZET/GUADELOUP, France | 16.27N | 61.60W | 8 | -4.00 (SAZ) | 82-06 | 788970 | 16.9 |  | 15.3 | 35.2 | 32.5 | 32.9 | 33.2 | 33 | 32.8667 |  | 32 | 32.2 | 32.5 | 32 | 32.2333
France |  | LILLE LESQUI | LILLE LESQUI, France | 50.57N | 3.10E | 52 | 1.00 (EUW) | 82-06 | 70150 | -9 |  | -19.1 | 37.7 | 30.3 | 31.6 | 32.2 | 31 | 31.3667 |  | 27.1 | 29 | 29.2 | 28 | 28.4333
France |  | LIMOGES | LIMOGES, France | 45.87N | 1.18E | 402 | 1.00 (EUW) | 82-06 | 74340 | -7.6 |  | -14.5 | 37.8 | 30.7 | 32.5 | 34.2 | 32 | 32.4667 |  | 28.1 | 29.9 | 30.1 | 29 | 29.3667
France |  | LONS-LE-SAUNIER | LONS-LE-SAUNIER, France | 46.68N | 5.52E | 279 | 1.00 (EUW) | 87-06 | 73900 | N/A |  | N/A | N/A | 33.3 | 33.9 | 37.7 | 35 | 34.9667 |  | 30.2 | 30.7 | 31.7 | 31 | 30.8667
France |  | LORIENT LAN BIHOUE | LORIENT LAN BIHOUE, France | 47.77N | 3.45W | 42 | 1.00 (EUW) | 82-06 | 72050 | -5.4 |  | -12.3 | 37.2 | 28.9 | 31.3 | 31 | 30 | 30.4 |  | 26 | 28.2 | 27.4 | 27 | 27.2
France |  | LUXEUIL | LUXEUIL, France | 47.80N | 6.38E | 273 | 1.00 (EUW) | 82-06 | 72920 | -14.9 |  | -27 | 38.6 | 31.5 | 33.1 | 32.9 | 33 | 32.5 |  | 29.3 | 30.9 | 30.4 | 30 | 30.2
France |  | LYON-BRON | LYON-BRON, France | 45.72N | 4.93E | 202 | 1.00 (EUW) | 89-06 | 74800 | -8.3 |  | -13.9 | 41.5 | 34.9 | 35.7 | 38.1 | 36 | 36.2333 |  | 32.1 | 33.5 | 33.6 | 33 | 33.0667
France |  | LYON-SATOLAS | LYON-SATOLAS, France | 45.73N | 5.08E | 240 | 1.00 (EUW) | 82-06 | 74810 | -9.1 |  | -17.4 | 39.3 | 33.1 | 35 | 35.4 | 35 | 34.5 |  | 30.3 | 32.6 | 32.4 | 32 | 31.7667
France |  | MACON | MACON, France | 46.30N | 4.80E | 217 | 1.00 (EUW) | 82-06 | 73850 | -9.4 |  | -16.2 | 39.5 | 33.2 | 34.1 | 36.2 | 35 | 34.5 |  | 30.2 | 31.7 | 31.8 | 31 | 31.2333
France |  | MARIGNANE | MARIGNANE, France | 43.45N | 5.23E | 32 | 1.00 (EUW) | 82-06 | 76500 | -5 |  | -11.5 | 39.4 | 33.3 | 35.1 | 34.4 | 34 | 34.2667 |  | 30.9 | 33 | 32.3 | 32 | 32.0667
France |  | MARTIN DE VIVIES (ILE AMST.) | MARTIN DE VIVIES (ILE AMST.), France | 37.80S | 77.50E | 29 | 5.00 (ASW) | 83-06 | 619960 | N/A |  | N/A | N/A | 16.7 | 15.6 | 15 | 16 | 15.7667 |  | 16.1 | 14.7 | 14.3 | 15 | 15.0333
France |  | MAUPERTUS | MAUPERTUS, France | 49.65N | 1.48W | 138 | 1.00 (EUW) | 82-06 | 70240 | -4.6 |  | -14.2 | 33.9 | 25.1 | 28 | 27.1 | 27 | 26.7333 |  | 22.7 | 24.5 | 23.4 | 24 | 23.5333
France |  | MELUN | MELUN, France | 48.62N | 2.68E | 92 | 1.00 (EUW) | 92-06 | 71530 | -8.2 |  | -14.2 | 39.8 | 31.3 | 33.5 | 36 | 34 | 33.6 |  | 28.6 | 30.8 | 31.5 | 30 | 30.3
France |  | METZ/FRESCATY | METZ/FRESCATY, France | 49.08N | 6.13E | 192 | 1.00 (EUW) | 90-06 | 70900 | -10.6 |  | -17.3 | 40.9 | 31.9 | 33.2 | 36.4 | 34 | 33.8333 |  | 29.4 | 30.7 | 31.9 | 31 | 30.6667
France |  | MEYENHEIM-COLMAR | MEYENHEIM-COLMAR, France | 47.92N | 7.40E | 220 | 1.00 (EUW) | 89-06 | 71970 | -12.3 |  | -18.3 | 40.3 | 32.9 | 34.4 | 35.5 | 34 | 34.2667 |  | 30.3 | 31.5 | 32.2 | 31 | 31.3333
France |  | MILLAU | MILLAU, France | 44.12N | 3.02E | 720 | 1.00 (EUW) | 82-06 | 75580 | -8.3 |  | -16.4 | 38.2 | 31 | 32.7 | 33.7 | 32 | 32.4667 |  | 28 | 30.2 | 30.3 | 30 | 29.5
France |  | MONT AIGOUAL | MONT AIGOUAL, France | 44.12N | 3.58E | 1565 | 1.00 (EUW) | 82-06 | 75600 | -12.8 |  | -20 | 27.5 | 22.4 | 24.3 | 25.5 | 24 | 24.0667 |  | 20.3 | 22.1 | 22.7 | 22 | 21.7
France |  | MONT-DE-MARSAN | MONT-DE-MARSAN, France | 43.92N | 0.50W | 60 | 1.00 (EUW) | 82-06 | 76070 | -8.9 |  | -17.5 | 41.2 | 34.3 | 35.5 | 36.6 | 35 | 35.4667 |  | 31.1 | 33 | 32.7 | 32 | 32.2667
France |  | MONTELIMAR | MONTELIMAR, France | 44.58N | 4.73E | 74 | 1.00 (EUW) | 82-06 | 75770 | -5.7 |  | -12.3 | 40.6 | 34.4 | 35.3 | 37 | 36 | 35.5667 |  | 31.6 | 33.4 | 33.3 | 33 | 32.7667
France |  | MONTPELLIER | MONTPELLIER, France | 43.58N | 3.97E | 8 | 1.00 (EUW) | 82-06 | 76430 | -5.3 |  | -11.5 | 38.3 | 33 | 34.1 | 33.7 | 34 | 33.6 |  | 30.4 | 32.2 | 31.9 | 32 | 31.5
France |  | NANCY-ESSEY | NANCY-ESSEY, France | 48.68N | 6.22E | 212 | 1.00 (EUW) | 82-06 | 71800 | -12.2 |  | -20.4 | 40 | 31.4 | 33.1 | 35.2 | 33 | 33.2333 |  | 28.8 | 30.7 | 30.5 | 30 | 30
France |  | NANCY-OCHEY | NANCY-OCHEY, France | 48.58N | 5.97E | 351 | 1.00 (EUW) | 91-06 | 71810 | N/A |  | N/A | N/A | 31.2 | 32.6 | 36 | 33 | 33.2667 |  | 28.7 | 29.7 | 31.4 | 30 | 29.9333
France |  | NANTES | NANTES, France | 47.15N | 1.60W | 27 | 1.00 (EUW) | 82-06 | 72220 | -6.1 |  | -14.3 | 39.2 | 31.7 | 33.9 | 34.2 | 33 | 33.2667 |  | 28.6 | 31 | 30.2 | 30 | 29.9333
France |  | NEVERS | NEVERS, France | 47.00N | 3.10E | 176 | 1.00 (EUW) | 86-06 | 72600 | -11.1 |  | -17.3 | 40 | 31.8 | 33.4 | 36.3 | 34 | 33.8333 |  | 29.4 | 30.6 | 31.2 | 30 | 30.4
France |  | NICE | NICE, France | 43.65N | 7.20E | 27 | 1.00 (EUW) | 82-06 | 76900 | 0 |  | -5.5 | 37.2 | 29 | 31.1 | 32 | 31 | 30.7 |  | 27.7 | 29.7 | 29.8 | 29 | 29.0667
France |  | NIMES/GARONS (NAVY) | NIMES/GARONS (NAVY), France | 43.75N | 4.42E | 96 | 1.00 (EUW) | 90-06 | 76460 | N/A |  | N/A | N/A | 34.8 | 35.2 | 35.9 | 35 | 35.3 |  | 32.5 | 33.8 | 33.6 | 33 | 33.3
France |  | NIMES-COURBESSAC | NIMES-COURBESSAC, France | 43.87N | 4.40E | 62 | 1.00 (EUW) | 82-06 | 76450 | -4.5 |  | -11.5 | 39.6 | 34.5 | 36 | 36.1 | 36 | 35.5333 |  | 32.1 | 34.1 | 33.6 | 33 | 33.2667
France |  | NIORT | NIORT, France | 46.32N | 0.40W | 61 | 1.00 (EUW) | 86-06 | 73300 | -6.7 |  | -12.3 | 40 | 32.9 | 34.3 | 36 | 34 | 34.4 |  | 29.9 | 31.4 | 31.8 | 31 | 31.0333
France |  | ORANGE | ORANGE, France | 44.13N | 4.83E | 55 | 1.00 (EUW) | 82-06 | 75790 | -6.4 |  | -11.8 | 41.9 | 34.8 | 36.4 | 36.4 | 36 | 35.8667 |  | 32.2 | 34.2 | 33.6 | 33 | 33.3333
France |  | ORLEANS | ORLEANS, France | 47.98N | 1.78E | 125 | 1.00 (EUW) | 82-06 | 72490 | -9 |  | -18.1 | 38.2 | 31.5 | 33.3 | 33.7 | 33 | 32.8333 |  | 28.7 | 31 | 30.5 | 30 | 30.0667
France |  | OUESSANT | OUESSANT, France | 48.48N | 5.05W | 68 | 1.00 (EUW) | 82-06 | 71000 | -0.4 |  | -6.9 | 30 | 21.2 | 22.9 | 22.9 | 22 | 22.3333 |  | 18.5 | 20.4 | 20.4 | 20 | 19.7667
France |  | PARIS-AEROPORT CHAR | PARIS-AEROPORT CHAR, France | 49.02N | 2.53E | 112 | 1.00 (EUW) | 82-06 | 71570 | -8 |  | -17.8 | 39.6 | 31.1 | 33 | 35 | 33 | 33.0333 |  | 28.3 | 30.5 | 30.9 | 30 | 29.9
France |  | PARIS-MONTSOURIS | PARIS-MONTSOURIS, France | 48.82N | 2.33E | 77 | 1.00 (EUW) | 89-06 | 71560 | -4.9 |  | -12.1 | 40.6 | 32.4 | 33.6 | 36.6 | 34 | 34.2 |  | 29.9 | 31.1 | 31.9 | 31 | 30.9667
France |  | PARIS-ORLY | PARIS-ORLY, France | 48.72N | 2.38E | 90 | 1.00 (EUW) | 82-06 | 71490 | -8 |  | -16.3 | 39.9 | 31.3 | 33.8 | 35.9 | 34 | 33.6667 |  | 28.8 | 30.8 | 31.1 | 30 | 30.2333
France |  | PAU | PAU, France | 43.38N | 0.42W | 183 | 1.00 (EUW) | 82-06 | 76100 | -6.3 |  | -13.4 | 40.7 | 33.3 | 34.2 | 35.3 | 34 | 34.2667 |  | 30.2 | 31.5 | 31.4 | 31 | 31.0333
France |  | PERPIGNAN | PERPIGNAN, France | 42.73N | 2.87E | 47 | 1.00 (EUW) | 82-06 | 77470 | -3.4 |  | -7.7 | 39.6 | 33.2 | 34.6 | 34.3 | 34 | 34.0333 |  | 30.3 | 32.8 | 32.1 | 32 | 31.7333
France |  | POINTE DU RAZ | POINTE DU RAZ, France | 48.03N | 4.73W | 89 | 1.00 (EUW) | 82-06 | 71030 | -2.5 |  | -10 | 32.8 | 23.1 | 26.4 | 25.8 | 25 | 25.1 |  | 20 | 23.8 | 22.6 | 22 | 22.1333
France |  | POITIERS | POITIERS, France | 46.58N | 0.30E | 120 | 1.00 (EUW) | 82-06 | 73350 | -9.1 |  | -17 | 39.1 | 31.9 | 34.1 | 36.2 | 34 | 34.0667 |  | 29.3 | 31.7 | 31.9 | 31 | 30.9667
France |  | PORQUEROLLES | PORQUEROLLES, France | 43.00N | 6.23E | 147 | 1.00 (EUW) | 82-06 | 76700 | N/A |  | N/A | N/A | 28.7 | 32.7 | 31.2 | 31 | 30.8667 |  | 26.7 | 30.9 | 29.5 | 29 | 29.0333
France |  | PORT EN BESSIN | PORT EN BESSIN, France | 49.35N | 0.77W | 73 | 1.00 (EUW) | 85-06 | 70290 | -6.2 |  | -18.3 | 35.4 | 25.1 | 25 | 27.6 | 26 | 25.9 |  | 21.6 | 22.6 | 23.7 | 23 | 22.6333
France |  | PTE DE LA HAGUE | PTE DE LA HAGUE, France | 49.72N | 1.93W | 12 | 1.00 (EUW) | 95-06 | 70200 | -1.1 |  | -4.7 | 29.8 | 23 | 22.8 | 23.9 | 23 | 23.2333 |  | 20.3 | 21.1 | 21.8 | 21 | 21.0667
France |  | PTE DE PENMARCH | PTE DE PENMARCH, France | 47.80N | 4.37W | 19 | 1.00 (EUW) | 82-06 | 72000 | -2.8 |  | -9.4 | 33.2 | 25 | 27.1 | 26.7 | 26 | 26.2667 |  | 22.4 | 24.2 | 23.3 | 23 | 23.3
France |  | QUIMPER | QUIMPER, France | 47.97N | 4.17W | 94 | 1.00 (EUW) | 89-06 | 72010 | -4.4 |  | -9.4 | 39.1 | 28.6 | 31.1 | 32.7 | 31 | 30.8 |  | 25.3 | 28.1 | 27.4 | 27 | 26.9333
France |  | REIMS | REIMS, France | 49.30N | 4.03E | 91 | 1.00 (EUW) | 82-06 | 70700 | -11.9 |  | -21.1 | 40 | 30.5 | 32.8 | 34.8 | 33 | 32.7 |  | 27.9 | 30.2 | 30.2 | 29 | 29.4333
France |  | RENNES | RENNES, France | 48.07N | 1.73W | 43 | 1.00 (EUW) | 82-06 | 71300 | -6.7 |  | -14.2 | 39.2 | 31.8 | 33 | 34.1 | 33 | 32.9667 |  | 28.1 | 30.3 | 29.9 | 29 | 29.4333
France |  | ROUEN | ROUEN, France | 49.38N | 1.18E | 156 | 1.00 (EUW) | 82-06 | 70370 | -8.5 |  | -16.8 | 38.1 | 29.4 | 31.2 | 32.9 | 31 | 31.1667 |  | 26.1 | 28.3 | 28.4 | 28 | 27.6
France |  | SAINT GIRONS | SAINT GIRONS, France | 43.00N | 1.10E | 412 | 1.00 (EUW) | 82-06 | 76270 | -7.9 |  | -13.7 | 39.5 | 31.9 | 33.4 | 35.2 | 34 | 33.5 |  | 29.1 | 31 | 31.6 | 31 | 30.5667
France |  | SAINT-DIZIER | SAINT-DIZIER, France | 48.63N | 4.90E | 140 | 1.00 (EUW) | 82-06 | 71690 | -11.1 |  | -18.8 | 41 | 32 | 33.8 | 36.5 | 34 | 34.1 |  | 29.5 | 31.2 | 31.4 | 31 | 30.7
France |  | SAINT-NAZAIRE-MONTO | SAINT-NAZAIRE-MONTO, France | 47.32N | 2.17W | 3 | 1.00 (EUW) | 89-06 | 72170 | N/A |  | N/A | N/A | 31.8 | 33.7 | 34.6 | 33 | 33.3667 |  | 28 | 30.9 | 30.8 | 30 | 29.9
France |  | SAINT-QUENTIN | SAINT-QUENTIN, France | 49.82N | 3.20E | 101 | 1.00 (EUW) | 82-06 | 70610 | -9 |  | -16.4 | 38.6 | 29.1 | 31.2 | 33 | 31 | 31.1 |  | 26.2 | 28.8 | 28.9 | 28 | 27.9667
France |  | SAINT-YAN | SAINT-YAN, France | 46.42N | 4.02E | 244 | 1.00 (EUW) | 89-06 | 73790 | -10.6 |  | -17.2 | 40.1 | 33.9 | 35 | 37.5 | 35 | 35.4667 |  | 30.5 | 31.8 | 32.6 | 32 | 31.6333
France |  | SERGE-FROLOW (ILE TROMELIN) | SERGE-FROLOW (ILE TROMELIN), France | 15.80S | 54.50E | 13 | 3.00 (AFE) | 82-06 | 619760 | 19.1 |  | 12.6 | 41 | 28.1 | 26.9 | 26.8 | 27 | 27.2667 |  | 27.5 | 26.4 | 26.3 | 27 | 26.7333
France |  | SETE | SETE, France | 43.40N | 3.68E | 85 | 1.00 (EUW) | 82-06 | 76410 | -2.8 |  | -11.9 | 37.9 | 31.8 | 33 | 32 | 32 | 32.2667 |  | 29.2 | 31.1 | 30.3 | 30 | 30.2
France |  | SOCOA | SOCOA, France | 43.40N | 1.68W | 25 | 1.00 (EUW) | 90-06 | 76000 | -2.4 |  | -7.4 | 40.3 | 32.2 | 31.6 | 31.1 | 32 | 31.6333 |  | 27.8 | 27.6 | 28.2 | 28 | 27.8667
France |  | SOLENZARA | SOLENZARA, France | 41.92N | 9.40E | 22 | 1.00 (EUW) | 82-06 | 77650 | 0 |  | -4.1 | 40.3 | 30.8 | 32.7 | 33.3 | 32 | 32.2667 |  | 29.4 | 31.1 | 31.2 | 31 | 30.5667
France |  | ST-AUBAN-SUR-DURANC | ST-AUBAN-SUR-DURANC, France | 44.07N | 6.00E | 461 | 1.00 (EUW) | 82-06 | 75880 | -6.7 |  | -11.3 | 38.3 | 33.6 | 35.3 | 34.7 | 35 | 34.5333 |  | 31.3 | 33.2 | 32.5 | 32 | 32.3333
France |  | ST-ETIENNE BOUTHEON | ST-ETIENNE BOUTHEON, France | 45.53N | 4.30E | 402 | 1.00 (EUW) | 86-06 | 74750 | -10.3 |  | -17.9 | 39.7 | 34.4 | 34.7 | 36.4 | 35 | 35.1667 |  | 31.3 | 32.2 | 32.9 | 32 | 32.1333
France |  | STRASBOURG-ENTZHEIM | STRASBOURG-ENTZHEIM, France | 48.55N | 7.63E | 153 | 1.00 (EUW) | 82-06 | 71900 | -12.2 |  | -21.7 | 38.6 | 32 | 33.2 | 34.7 | 33 | 33.3 |  | 29.4 | 31.1 | 30.9 | 30 | 30.4667
France |  | TARBES-OSSUN | TARBES-OSSUN, France | 43.18N | 0.00E | 364 | 1.00 (EUW) | 82-06 | 76210 | -7.9 |  | -15.4 | 40.1 | 32.7 | 34.1 | 34.9 | 34 | 33.9 |  | 29.4 | 31.2 | 31.1 | 31 | 30.5667
France |  | TOULON | TOULON, France | 43.10N | 5.93E | 25 | 1.00 (EUW) | 82-06 | 76600 | -1.1 |  | -9.3 | 39.6 | 32 | 34.1 | 33.8 | 33 | 33.3 |  | 29.7 | 32.2 | 31.8 | 31 | 31.2333
France |  | TOULOUSE BLAGNAC | TOULOUSE BLAGNAC, France | 43.63N | 1.37E | 154 | 1.00 (EUW) | 82-06 | 76300 | -6.5 |  | -15.4 | 41.9 | 33.3 | 35.8 | 37 | 35 | 35.3667 |  | 30.6 | 33.2 | 33.1 | 32 | 32.3
France |  | TOURS | TOURS, France | 47.45N | 0.73E | 112 | 1.00 (EUW) | 82-06 | 72400 | -7.6 |  | -17.6 | 39.6 | 31.9 | 33.5 | 35.8 | 34 | 33.7333 |  | 28.8 | 31.1 | 31.1 | 30 | 30.3333
France |  | TRAPPES | TRAPPES, France | 48.77N | 2.00E | 168 | 1.00 (EUW) | 87-06 | 71450 | -6.9 |  | -13.5 | 41 | 30.7 | 32.7 | 35.7 | 33 | 33.0333 |  | 28 | 30 | 30.9 | 30 | 29.6333
France |  | TREMUSON-ST-BRIEUC | TREMUSON-ST-BRIEUC, France | 48.53N | 2.85W | 138 | 1.00 (EUW) | 86-06 | 71200 | -5.3 |  | -12.4 | 36.7 | 27.9 | 27.3 | 29 | 28 | 28.0667 |  | 23.8 | 24.3 | 24.9 | 24 | 24.3333
France |  | TROYES BARBEREY | TROYES BARBEREY, France | 48.33N | 4.02E | 118 | 1.00 (EUW) | 82-06 | 71680 | -10.8 |  | -19.7 | 40.9 | 31.2 | 33.9 | 36.5 | 34 | 33.8667 |  | 28.8 | 31.2 | 31.2 | 30 | 30.4
France |  | VANNES/SENE | VANNES/SENE, France | 47.60N | 2.72W | 3 | 1.00 (EUW) | 87-06 | 72100 | N/A |  | N/A | N/A | 31.4 | 33.4 | 32.2 | 32 | 32.3333 |  | 26.9 | 29.9 | 28.4 | 28 | 28.4
France |  | VICHY | VICHY, France | 46.17N | 3.40E | 251 | 1.00 (EUW) | 88-06 | 73740 | -10.9 |  | -16.4 | 41.5 | 34.7 | 35.5 | 38 | 36 | 36.0667 |  | 31.4 | 32.5 | 32.8 | 32 | 32.2333
France |  | VILLACOUBLAY | VILLACOUBLAY, France | 48.77N | 2.20E | 179 | 1.00 (EUW) | 82-06 | 71470 | -7.6 |  | -16.1 | 38.4 | 30.5 | 32.1 | 34.3 | 32 | 32.3 |  | 27.7 | 29.6 | 30 | 29 | 29.1
French Guiana |  | ROCHAMBEAU | ROCHAMBEAU, French Guiana | 4.83N | 52.37W | 9 | -3.00 (SAE) | 82-06 | 814050 | 20 |  | 16.8 | 38.4 | 31.5 | 32 | 32.8 | 32 | 32.1 |  | 31 | 31.2 | 32 | 31 | 31.4
French Polynesia |  | ATUONA | ATUONA, French Polynesia | 9.80S | 139.03W | 53 | -9.50 (PCQ) | 83-06 | 919250 | 20.8 |  | 17.9 | 35.6 | 31 | 30.2 | 30.5 | 31 | 30.5667 |  | 30 | 29.3 | 29.4 | 30 | 29.5667
French Polynesia |  | BORA-BORA | BORA-BORA, French Polynesia | 16.43S | 151.75W | 3 | -10.00 (PCH) | 98-06 | 919290 | N/A |  | N/A | N/A | 31.1 | 30.8 | 31.7 | 31 | 31.2 |  | 30.3 | 29.9 | 30.4 | 30 | 30.2
French Polynesia |  | HAO | HAO, French Polynesia | 18.07S | 140.95W | 3 | -10.00 (PCH) | 82-06 | 919440 | 20.4 |  | 17.1 | 33 | 29 | 28.2 | 28.2 | 28 | 28.4667 |  | 28.4 | 27.8 | 27.6 | 28 | 27.9333
French Polynesia |  | MURUROA | MURUROA, French Polynesia | 21.82S | 138.80W | 3 | -10.00 (PCH) | 82-97 | 919520 | 18.2 |  | 16.5 | 37.5 | 28.3 | 27.2 | 27.2 | 28 | 27.5667 |  | 27.4 | 26.5 | 26.4 | 27 | 26.7667
French Polynesia |  | RAPA | RAPA, French Polynesia | 27.62S | 144.33W | 2 | -10.00 (PCH) | 82-06 | 919580 | 11.5 |  | 9.7 | 31.2 | 24.3 | 23 | 22.7 | 23 | 23.3333 |  | 23.1 | 22.3 | 22 | 22 | 22.4667
French Polynesia |  | RIKITEA | RIKITEA, French Polynesia | 23.13S | 134.97W | 89 | -9.00 (PCG) | 83-06 | 919480 | 16 |  | 12.1 | 30.5 | 26.1 | 25.3 | 25.5 | 26 | 25.6333 |  | 25.4 | 24.6 | 24.8 | 25 | 24.9333
French Polynesia |  | TAHITI-FAAA | TAHITI-FAAA, French Polynesia | 17.55S | 149.62W | 3 | -10.00 (PCH) | 82-06 | 919380 | 18.1 |  | 15.8 | 34 | 30.7 | 30.2 | 30 | 30 | 30.3 |  | 30 | 29.4 | 29.2 | 30 | 29.5333
French Polynesia |  | TAKAROA | TAKAROA, French Polynesia | 14.48S | 145.03W | 3 | -10.00 (PCH) | 83-06 | 919430 | 22.6 |  | 21.3 | 35.1 | 31 | 30 | 30.1 | 30 | 30.3667 |  | 30 | 29.4 | 29.3 | 30 | 29.5667
French Polynesia |  | TUBUAI | TUBUAI, French Polynesia | 23.35S | 149.48W | 3 | -10.00 (PCH) | 83-06 | 919540 | 12.6 |  | 10.4 | 31.4 | 26.7 | 26.2 | 26 | 26 | 26.3 |  | 25.7 | 25.2 | 25.1 | 25 | 25.3333
French Southern Territories |  | PORT-AUX-FRANCAIS | PORT-AUX-FRANCAIS, French Southern Territories | 49.30S | 70.20E | 30 | 5.00 (ASW) | 83-06 | 619980 | -5.2 |  | -8.4 | 23.3 | 10.2 | 11 | 10.5 | 11 | 10.5667 |  | 8.7 | 9.5 | 9.1 | 9 | 9.1
Gabon |  | LIBREVILLE | LIBREVILLE, Gabon | 0.45N | 9.42E | 15 | 1.00 (AFW) | 82-06 | 645000 | N/A |  | N/A | N/A | 30.1 | 29.1 | 28.8 | 29 | 29.3333 |  | 29.1 | 28.1 | 28 | 28 | 28.4
Gambia |  | BANJUL/YUNDUM | BANJUL/YUNDUM, Gambia | 13.20N | 16.63W | 33 | 0.00 (GRW) | 89-06 | 617010 | N/A |  | N/A | N/A | 35.1 | 33.2 | 32.3 | 34 | 33.5333 |  | 33.9 | 32.1 | 31.6 | 33 | 32.5333
Georgia |  | BATUMI | BATUMI, Georgia | 41.62N | 41.60E | 32 | 4.00 (GST) | 82-06 | 374840 | -2.7 |  | -8.1 | 38.3 | 28.2 | 28.6 | 29.3 | 29 | 28.7 |  | 25.8 | 27.3 | 28.4 | 27 | 27.1667
Georgia |  | KUTAISI | KUTAISI, Georgia | 42.27N | 42.63E | 116 | 4.00 (GST) | 82-06 | 373950 | -4.3 |  | -9.6 | 41.1 | 33.6 | 34.5 | 36.5 | 35 | 34.8667 |  | 31.2 | 31 | 32.9 | 32 | 31.7
Georgia |  | PASANAURI | PASANAURI, Georgia | 42.35N | 44.70E | 1064 | 4.00 (GST) | 82-06 | 374320 | -16 |  | -20.9 | 38.2 | 28.7 | 30.2 | 32.9 | 31 | 30.6 |  | 26.6 | 28.4 | 29.6 | 28 | 28.2
Georgia |  | SUHUMI | SUHUMI, Georgia | 42.87N | 41.13E | 13 | 4.00 (GST) | 82-91 | 372600 | -3.6 |  | -9.5 | 36.3 | 28.6 | 30 | 30.3 | 30 | 29.6333 |  | 26.7 | 28.2 | 28.9 | 28 | 27.9333
Georgia |  | TBILISI | TBILISI, Georgia | 41.68N | 44.95E | 448 | 4.00 (GST) | 82-06 | 375490 | -8.4 |  | -13.6 | 41.4 | 34.1 | 36.5 | 36.8 | 36 | 35.8 |  | 31.8 | 34.6 | 34.6 | 34 | 33.6667
Germany |  | AACHEN | AACHEN, Germany | 50.78N | 6.10E | 202 | 1.00 (EUW) | 82-03 | 105010 | -10.2 |  | -22.3 | 37.2 | 28.3 | 31.2 | 31.7 | 30 | 30.4 |  | 26.5 | 29 | 28.4 | 28 | 27.9667
Germany |  | AHLHORN(GAFB) | AHLHORN(GAFB), Germany | 52.88N | 8.23E | 56 | 1.00 (EUW) | 82-95 | 102180 | -12.7 |  | -25.9 | 38.2 | 29.9 | 32.2 | 32 | 31 | 31.3667 |  | 27 | 30 | 28.9 | 29 | 28.6333
Germany |  | ANGERMUENDE | ANGERMUENDE, Germany | 53.03N | 14.00E | 55 | 1.00 (EUW) | 82-03 | 102910 | -14.2 |  | -30.4 | 39.4 | 30.1 | 31.6 | 32.8 | 32 | 31.5 |  | 27.3 | 28.7 | 29.4 | 28 | 28.4667
Germany |  | ARKONA (CAPE) | ARKONA (CAPE), Germany | 54.68N | 13.43E | 42 | 1.00 (EUW) | 82-91 | 90910 | -8.9 |  | -22 | 32.2 | 22.6 | 24.6 | 25.9 | 24 | 24.3667 |  | 20.8 | 23.1 | 23.1 | 22 | 22.3333
Germany |  | ARTERN | ARTERN, Germany | 51.38N | 11.30E | 166 | 1.00 (EUW) | 82-03 | 104600 | -14.3 |  | -29.5 | 38.5 | 30 | 31.5 | 32.9 | 31 | 31.4667 |  | 27.2 | 29.3 | 29.5 | 29 | 28.6667
Germany |  | AUGSBERG/MULHAUSEN | AUGSBERG/MULHAUSEN, Germany | 48.43N | 10.93E | 477 | 1.00 (EUW) | 82-03 | 108520 | -17.6 |  | -32.2 | 38.2 | 29.3 | 32.2 | 31.9 | 31 | 31.1333 |  | 26.8 | 29.1 | 28.9 | 28 | 28.2667
Germany |  | BERGEN | BERGEN, Germany | 52.82N | 9.93E | 77 | 1.00 (EUW) | 97-06 | 102380 | N/A |  | N/A | N/A | 31.5 | 32.1 | 32.7 | 32 | 32.1 |  | 27.6 | 29.4 | 30 | 29 | 29
Germany |  | BERLIN/DAHLEM | BERLIN/DAHLEM, Germany | 52.47N | 13.30E | 51 | 1.00 (EUW) | 82-03 | 103810 | -12.4 |  | -24.6 | 38.4 | 30.8 | 31.8 | 32.1 | 32 | 31.5667 |  | 27.7 | 29.4 | 28.6 | 29 | 28.5667
Germany |  | BERLIN/SCHONEFELD | BERLIN/SCHONEFELD, Germany | 52.38N | 13.52E | 47 | 1.00 (EUW) | 82-91 | 93850 | -15.1 |  | -30.5 | 38.4 | 30.8 | 31.8 | 32.1 | 32 | 31.5667 |  | 27.2 | 29.9 | 29 | 29 | 28.7
Germany |  | BERLIN/TEGEL (FAFB) | BERLIN/TEGEL (FAFB), Germany | 52.57N | 13.32E | 37 | 1.00 (EUW) | 82-03 | 103820 | -13.5 |  | -26.7 | 41.1 | 31.2 | 32.2 | 33 | 32 | 32.1333 |  | 28.2 | 30.1 | 29.7 | 29 | 29.3333
Germany |  | BERLIN/TEMPELHOF | BERLIN/TEMPELHOF, Germany | 52.47N | 13.40E | 50 | 1.00 (EUW) | 82-03 | 103840 | -12.2 |  | -24.8 | 39.2 | 31.1 | 32.2 | 33.1 | 32 | 32.1333 |  | 28.1 | 30.1 | 29.7 | 29 | 29.3
Germany |  | BITBURG(US ARMY) | BITBURG(US ARMY), Germany | 49.95N | 6.57E | 374 | 1.00 (EUW) | 82-93 | 106100 | -11.3 |  | -21.3 | 37.6 | 27.9 | 31.2 | 31.8 | 30 | 30.3 |  | 25.9 | 29 | 28.2 | 28 | 27.7
Germany |  | BOIZENBURG (AUT) | BOIZENBURG (AUT), Germany | 53.40N | 10.68E | 46 | 1.00 (EUW) | 82-03 | 102490 | -13.1 |  | -27.5 | 38 | 30 | 30.9 | 30.1 | 30 | 30.3333 |  | 27.2 | 28.6 | 28 | 28 | 27.9333
Germany |  | BOLTENHAGEN | BOLTENHAGEN, Germany | 54.00N | 11.20E | 17 | 1.00 (EUW) | 82-03 | 101610 | -10.5 |  | -24.5 | 37.8 | 25.4 | 28.2 | 28.5 | 27 | 27.3667 |  | 22.5 | 25 | 25.2 | 24 | 24.2333
Germany |  | BRAUNSCHWEIG | BRAUNSCHWEIG, Germany | 52.30N | 10.45E | 81 | 1.00 (EUW) | 82-03 | 103480 | -14 |  | -29.1 | 38.6 | 30.2 | 30.1 | 31.1 | 30 | 30.4667 |  | 26.8 | 28.5 | 28.6 | 28 | 27.9667
Germany |  | BREMEN | BREMEN, Germany | 53.05N | 8.80E | 3 | 1.00 (EUW) | 82-03 | 102240 | -12.9 |  | -24.5 | 36.7 | 29.3 | 31 | 30.7 | 30 | 30.3333 |  | 26.4 | 28.6 | 28.4 | 28 | 27.8
Germany |  | BREMERHAVEN | BREMERHAVEN, Germany | 53.53N | 8.58E | 7 | 1.00 (EUW) | 82-03 | 101290 | -9.1 |  | -19.8 | 36.7 | 29.2 | 29.9 | 30 | 30 | 29.7 |  | 25.2 | 27.2 | 26.6 | 26 | 26.3333
Germany |  | BREMGARTEN(GAFB) | BREMGARTEN(GAFB), Germany | 47.90N | 7.62E | 217 | 1.00 (EUW) | 82-92 | 109000 | -13.6 |  | -27.1 | 40.3 | 31.8 | 35.9 | 34.2 | 34 | 33.9667 |  | 29 | 33 | 31.2 | 31 | 31.0667
Germany |  | BROCKEN (PEAK) | BROCKEN (PEAK), Germany | 51.80N | 10.62E | 1153 | 1.00 (EUW) | 82-03 | 104530 | -16.5 |  | -29.8 | 28.4 | 21.3 | 22.2 | 23.4 | 22 | 22.3 |  | 18.9 | 20.2 | 20.4 | 20 | 19.8333
Germany |  | BRUGGEN (RAF) | BRUGGEN (RAF), Germany | 51.20N | 6.13E | 76 | 1.00 (EUW) | 92-01 | 104010 | -10.9 |  | -19.2 | 38.9 | 31.1 | 32.8 | 32.9 | 32 | 32.2667 |  | 27.9 | 30.1 | 30.4 | 29 | 29.4667
Germany |  | BUECHEL | BUECHEL, Germany | 50.17N | 7.07E | 486 | 1.00 (EUW) | 82-06 | 106130 | -12.6 |  | -20.9 | 36.4 | 27.9 | 30 | 31.5 | 30 | 29.8 |  | 25.5 | 27.6 | 27.5 | 27 | 26.8667
Germany |  | BUECKEBURG | BUECKEBURG, Germany | 52.28N | 9.08E | 73 | 1.00 (EUW) | 82-06 | 103350 | -12.6 |  | -24.6 | 39 | 30.8 | 32.9 | 33.1 | 32 | 32.2667 |  | 27.9 | 30.1 | 30.2 | 29 | 29.4
Germany |  | CELLE | CELLE, Germany | 52.60N | 10.02E | 52 | 1.00 (EUW) | 82-06 | 103430 | -14 |  | -25.8 | 39.5 | 31.2 | 32.7 | 32.6 | 32 | 32.1667 |  | 28.1 | 30.2 | 30 | 29 | 29.4333
Germany |  | CHEMNITZ | CHEMNITZ, Germany | 50.80N | 12.87E | 420 | 1.00 (EUW) | 82-03 | 105770 | -15.3 |  | -27.5 | 36 | 28.4 | 30.2 | 31 | 30 | 29.8667 |  | 25.8 | 28.1 | 27.9 | 27 | 27.2667
Germany |  | COTTBUS (FLUGPLATZ) | COTTBUS (FLUGPLATZ), Germany | 51.77N | 14.30E | 67 | 1.00 (EUW) | 83-02 | 104920 | -16.6 |  | -30 | 40 | 32.6 | 33.6 | 32.7 | 33 | 32.9667 |  | 28.4 | 30.3 | 30.1 | 30 | 29.6
Germany |  | CUXHAVEN | CUXHAVEN, Germany | 53.87N | 8.70E | 4 | 1.00 (EUW) | 82-03 | 101310 | -8.2 |  | -19.6 | 37.1 | 26.3 | 27.5 | 28.2 | 27 | 27.3333 |  | 23.7 | 24.9 | 25 | 25 | 24.5333
Germany |  | DIEPHOLZ | DIEPHOLZ, Germany | 52.58N | 8.35E | 43 | 1.00 (EUW) | 94-06 | 103210 | -12.9 |  | -24.4 | 37.2 | 30.7 | 33 | 32.6 | 32 | 32.1 |  | 27.3 | 30.1 | 29.7 | 29 | 29.0333
Germany |  | DOBERLUG/KIRCHHAIN | DOBERLUG/KIRCHHAIN, Germany | 51.65N | 13.58E | 97 | 1.00 (EUW) | 82-91 | 94900 | -16.4 |  | -35.1 | 38.2 | 29.7 | 32 | 32.3 | 31 | 31.3333 |  | 26.8 | 29.4 | 29 | 28 | 28.4
Germany |  | DRESDEN/KLOTZSCHE | DRESDEN/KLOTZSCHE, Germany | 51.13N | 13.77E | 230 | 1.00 (EUW) | 82-91 | 94880 | -14.9 |  | -32 | 37.2 | 30.2 | 32.3 | 32.2 | 32 | 31.5667 |  | 26.9 | 29.9 | 28.9 | 29 | 28.5667
Germany |  | DUSSELDORF | DUSSELDORF, Germany | 51.28N | 6.78E | 45 | 1.00 (EUW) | 82-03 | 104000 | -10.8 |  | -23.4 | 37.3 | 29.7 | 32.4 | 32.5 | 32 | 31.5333 |  | 27.8 | 30 | 29.2 | 29 | 29
Germany |  | EGGEBEK | EGGEBEK, Germany | 54.63N | 9.35E | 19 | 1.00 (EUW) | 87-03 | 100340 | -12.4 |  | -20.7 | 36.2 | 28.8 | 30.1 | 30 | 30 | 29.6333 |  | 25.1 | 27.1 | 27.8 | 27 | 26.6667
Germany |  | EMDEN-FLUGPLATZ | EMDEN-FLUGPLATZ, Germany | 53.38N | 7.23E | 5 | 1.00 (EUW) | 97-06 | 102000 | -11.2 |  | -20.1 | 34.9 | 29.9 | 29.7 | 30.5 | 30 | 30.0333 |  | 26 | 27.8 | 27.7 | 27 | 27.1667
Germany |  | ERFURT/BINDERSLEBN | ERFURT/BINDERSLEBN, Germany | 50.98N | 10.97E | 315 | 1.00 (EUW) | 82-91 | 95540 | -16.5 |  | -34 | 36.1 | 29 | 30.8 | 31.2 | 30 | 30.3333 |  | 25.6 | 28.5 | 28.1 | 27 | 27.4
Germany |  | ESSEN/MULHEIM | ESSEN/MULHEIM, Germany | 51.40N | 6.97E | 154 | 1.00 (EUW) | 82-03 | 104100 | -9.8 |  | -23.8 | 35.7 | 28.3 | 31.3 | 30.6 | 30 | 30.0667 |  | 26.2 | 28.7 | 27.9 | 28 | 27.6
Germany |  | FASSBERG | FASSBERG, Germany | 52.92N | 10.18E | 88 | 1.00 (EUW) | 90-05 | 102460 | -15.9 |  | -27.9 | 38.3 | 32.6 | 31.3 | 32.8 | 32 | 32.2333 |  | 28.3 | 28.8 | 29.9 | 29 | 29
Germany |  | FICHTELBERG MTN | FICHTELBERG MTN, Germany | 50.43N | 12.95E | 1213 | 1.00 (EUW) | 82-91 | 95780 | -17.5 |  | -30.9 | 31 | 21.2 | 24.7 | 23.4 | 23 | 23.1 |  | 18.9 | 21.6 | 21 | 21 | 20.5
Germany |  | FRANKFURT MAIN ARPT | FRANKFURT MAIN ARPT, Germany | 50.05N | 8.60E | 112 | 1.00 (EUW) | 82-03 | 106370 | -12.4 |  | -22.4 | 38.6 | 30.9 | 33.5 | 33.7 | 33 | 32.7 |  | 28.8 | 31.1 | 30.6 | 30 | 30.1667
Germany |  | FREIBURG (CIV/FAFB) | FREIBURG (CIV/FAFB), Germany | 48.00N | 7.85E | 269 | 1.00 (EUW) | 82-03 | 108030 | -10.1 |  | -20.8 | 38.4 | 31.5 | 34 | 33.9 | 33 | 33.1333 |  | 29.1 | 31.2 | 31.1 | 30 | 30.4667
Germany |  | FRITZLAR | FRITZLAR, Germany | 51.12N | 9.28E | 181 | 1.00 (EUW) | 82-06 | 104390 | -14.4 |  | -25.8 | 38.4 | 30.2 | 32.4 | 33.7 | 32 | 32.1 |  | 27.6 | 29.9 | 30.1 | 29 | 29.2
Germany |  | FUERSTENFELDBRUCK | FUERSTENFELDBRUCK, Germany | 48.20N | 11.27E | 535 | 1.00 (EUW) | 82-98 | 108580 | -17.7 |  | -29.8 | 36.9 | 29.2 | 32.9 | 31.8 | 31 | 31.3 |  | 26.8 | 29.9 | 28.8 | 29 | 28.5
Germany |  | FUERSTENZELL | FUERSTENZELL, Germany | 48.55N | 13.35E | 480 | 1.00 (EUW) | 98-06 | 108950 | -16.3 |  | -19.1 | 36.3 | 30.3 | 31.7 | 31.6 | 31 | 31.2 |  | 28.3 | 29.1 | 28.6 | 29 | 28.6667
Germany |  | GARDELEGEN (AUT) | GARDELEGEN (AUT), Germany | 52.52N | 11.40E | 48 | 1.00 (EUW) | 82-03 | 103590 | -16.9 |  | -35 | 39 | 31.3 | 31.6 | 32.1 | 32 | 31.6667 |  | 28.2 | 29.8 | 29.5 | 29 | 29.1667
Germany |  | GEILENKIRCHEN | GEILENKIRCHEN, Germany | 50.97N | 6.05E | 98 | 1.00 (EUW) | 82-00 | 105000 | -12.6 |  | -24.5 | 39.9 | 30.7 | 33.2 | 33 | 32 | 32.3 |  | 27.9 | 30.3 | 30 | 29 | 29.4
Germany |  | GERA/LEUMNITZ | GERA/LEUMNITZ, Germany | 50.88N | 12.13E | 312 | 1.00 (EUW) | 82-03 | 105670 | -16.6 |  | -34.2 | 36.6 | 29.5 | 31.1 | 32.2 | 31 | 30.9333 |  | 26.6 | 28.9 | 28.7 | 28 | 28.0667
Germany |  | GIESSEN | GIESSEN, Germany | 50.58N | 8.70E | 186 | 1.00 (EUW) | 82-03 | 105320 | -12.6 |  | -24 | 36.3 | 29.8 | 31.8 | 32.5 | 31 | 31.3667 |  | 27.6 | 29.9 | 29.5 | 29 | 29
Germany |  | GLUECKSBURG/MEIERWI | GLUECKSBURG/MEIERWI, Germany | 54.83N | 9.50E | 33 | 1.00 (EUW) | 87-06 | 100330 | -8.3 |  | -15 | 35.4 | 27.1 | 28 | 28.2 | 28 | 27.7667 |  | 24 | 25.9 | 25.9 | 25 | 25.2667
Germany |  | GOERLITZ | GOERLITZ, Germany | 51.17N | 14.95E | 238 | 1.00 (EUW) | 82-03 | 104990 | -15.2 |  | -29.8 | 37 | 29.2 | 30.8 | 32.6 | 31 | 30.8667 |  | 26.7 | 28.7 | 29.1 | 28 | 28.1667
Germany |  | GRAFENWOEHR | GRAFENWOEHR, Germany | 49.70N | 11.95E | 415 | 1.00 (EUW) | 82-06 | 106870 | -20.5 |  | -32.7 | 38.9 | 31.1 | 32.9 | 32 | 32 | 32 |  | 28 | 30.1 | 29.1 | 29 | 29.0667
Germany |  | GREIFSWALD | GREIFSWALD, Germany | 54.10N | 13.38E | 2 | 1.00 (EUW) | 82-91 | 91840 | -13.6 |  | -31.2 | 37 | 27.4 | 29.3 | 29.7 | 29 | 28.8 |  | 24.5 | 27.2 | 26.5 | 26 | 26.0667
Germany |  | GUETERSLOH | GUETERSLOH, Germany | 51.93N | 8.32E | 72 | 1.00 (EUW) | 82-06 | 103200 | -11.5 |  | -21.8 | 39.3 | 30.7 | 32.2 | 33 | 32 | 31.9667 |  | 27.8 | 29.7 | 30 | 29 | 29.1667
Germany |  | HAHN | HAHN, Germany | 49.95N | 7.27E | 503 | 1.00 (EUW) | 82-06 | 106160 | -11.5 |  | -19.5 | 36.6 | 28 | 30.1 | 31.9 | 30 | 30 |  | 25.5 | 27.6 | 27.8 | 27 | 26.9667
Germany |  | HAMBURG/FUHLSBUTTEL | HAMBURG/FUHLSBUTTEL, Germany | 53.63N | 10.00E | 16 | 1.00 (EUW) | 82-03 | 101470 | -12.5 |  | -25.3 | 37.9 | 29.3 | 30.3 | 30 | 30 | 29.8667 |  | 26.4 | 28 | 27.2 | 27 | 27.2
Germany |  | HANNOVER | HANNOVER, Germany | 52.47N | 9.70E | 55 | 1.00 (EUW) | 82-03 | 103380 | -13.1 |  | -27.7 | 38.1 | 30 | 31 | 31.1 | 31 | 30.7 |  | 27.3 | 29.1 | 28.6 | 28 | 28.3333
Germany |  | HEIDELBERG (USA-AF) | HEIDELBERG (USA-AF), Germany | 49.40N | 8.65E | 109 | 1.00 (EUW) | 82-98 | 107340 | -10.9 |  | -22.8 | 39.7 | 31.1 | 34.8 | 34.9 | 34 | 33.6 |  | 29.1 | 32.8 | 31.8 | 31 | 31.2333
Germany |  | HOF | HOF, Germany | 50.32N | 11.88E | 567 | 1.00 (EUW) | 82-03 | 106850 | -18 |  | -28.2 | 34.9 | 27.8 | 29.4 | 30 | 29 | 29.0667 |  | 25.1 | 27 | 27.2 | 26 | 26.4333
Germany |  | HOHENPEISSENBERG | HOHENPEISSENBERG, Germany | 47.80N | 11.02E | 977 | 1.00 (EUW) | 82-03 | 109620 | -15 |  | -25.3 | 33.8 | 25.5 | 28.3 | 27.1 | 27 | 26.9667 |  | 23.3 | 25.9 | 25.3 | 25 | 24.8333
Germany |  | HOHN | HOHN, Germany | 54.32N | 9.53E | 22 | 1.00 (EUW) | 87-06 | 100380 | -13.2 |  | -22.7 | 40.7 | 29.9 | 31.7 | 31 | 31 | 30.8667 |  | 26 | 28.2 | 28.3 | 28 | 27.5
Germany |  | HOLZDORF | HOLZDORF, Germany | 51.77N | 13.17E | 82 | 1.00 (EUW) | 98-06 | 104760 | -17.4 |  | -22.7 | 39.3 | 33.4 | 34.3 | 33.7 | 34 | 33.8 |  | 30.5 | 32.2 | 30.5 | 31 | 31.0667
Germany |  | HOPSTEN | HOPSTEN, Germany | 52.33N | 7.53E | 52 | 1.00 (EUW) | 82-02 | 103140 | -12.8 |  | -25.6 | 37.4 | 31 | 32.4 | 32.1 | 32 | 31.8333 |  | 27.8 | 29.9 | 29.7 | 29 | 29.1333
Germany |  | IDAR-OBERSTEIN | IDAR-OBERSTEIN, Germany | 49.70N | 7.33E | 377 | 1.00 (EUW) | 94-06 | 106180 | -15.2 |  | -21.8 | 38.5 | 30.6 | 32.4 | 34.7 | 33 | 32.5667 |  | 28.2 | 30 | 30.6 | 30 | 29.6
Germany |  | ITZEHOE | ITZEHOE, Germany | 53.98N | 9.57E | 26 | 1.00 (EUW) | 86-06 | 101420 | -14.8 |  | -22.7 | 37.5 | 30.1 | 30.7 | 30.9 | 31 | 30.5667 |  | 26.1 | 27.7 | 28.9 | 28 | 27.5667
Germany |  | JEVER | JEVER, Germany | 53.53N | 7.90E | 21 | 1.00 (EUW) | 82-05 | 101220 | -11.5 |  | -21 | 39.8 | 29.9 | 30.2 | 30.7 | 30 | 30.2667 |  | 25.4 | 27.6 | 27.6 | 27 | 26.8667
Germany |  | KAHLER ASTEN(MOUNT) | KAHLER ASTEN(MOUNT), Germany | 51.18N | 8.48E | 835 | 1.00 (EUW) | 82-03 | 104270 | -14.8 |  | -27 | 31.2 | 24.1 | 25.8 | 26.6 | 26 | 25.5 |  | 21.9 | 24 | 23.3 | 23 | 23.0667
Germany |  | KALKAR | KALKAR, Germany | 51.73N | 6.27E | 43 | 1.00 (EUW) | 94-06 | 104040 | -10.1 |  | -18.5 | 38.5 | 32.1 | 33.4 | 33.8 | 33 | 33.1 |  | 28.8 | 30.6 | 30.7 | 30 | 30.0333
Germany |  | KARLSRUHE BADEN BAD | KARLSRUHE BADEN BAD, Germany | 48.77N | 8.07E | 128 | 1.00 (EUW) | 82-06 | 107275 | -12.6 |  | -24.8 | 39.5 | 32.2 | 34.1 | 35.8 | 34 | 34.0333 |  | 29.9 | 31.9 | 31.8 | 31 | 31.2
Germany |  | KASSEL | KASSEL, Germany | 51.30N | 9.45E | 158 | 1.00 (EUW) | 82-03 | 104380 | -12.9 |  | -24.5 | 36.6 | 29 | 30.7 | 31.6 | 30 | 30.4333 |  | 26.6 | 28.6 | 28.4 | 28 | 27.8667
Germany |  | KIEL HOLTENAU | KIEL HOLTENAU, Germany | 54.37N | 10.13E | 32 | 1.00 (EUW) | 95-06 | 100465 | -11.4 |  | -17.2 | 35.8 | 30.2 | 29.9 | 29.9 | 30 | 30 |  | 25.8 | 27 | 27.8 | 27 | 26.8667
Germany |  | KOLN/BONN (CIV/MIL) | KOLN/BONN (CIV/MIL), Germany | 50.87N | 7.17E | 91 | 1.00 (EUW) | 82-03 | 105130 | -13.5 |  | -26.4 | 38.1 | 30.1 | 32.7 | 32.5 | 32 | 31.7667 |  | 28 | 30.3 | 29.7 | 29 | 29.3333
Germany |  | KONSTANZ | KONSTANZ, Germany | 47.68N | 9.18E | 443 | 1.00 (EUW) | 82-03 | 109290 | -10.9 |  | -21.9 | 36.3 | 30.6 | 32.1 | 31.7 | 31 | 31.4667 |  | 28.2 | 30.1 | 29.1 | 29 | 29.1333
Germany |  | KUEMMERSBRUCK | KUEMMERSBRUCK, Germany | 49.43N | 11.90E | 418 | 1.00 (EUW) | 94-06 | 107710 | -17.8 |  | -24.8 | 37.8 | 32.5 | 33.2 | 35 | 34 | 33.5667 |  | 30.1 | 31.1 | 30.7 | 31 | 30.6333
Germany |  | LAAGE | LAAGE, Germany | 53.92N | 12.28E | 59 | 1.00 (EUW) | 95-06 | 101720 | -14.5 |  | -23.2 | 36.1 | 30.9 | 31.3 | 30.9 | 31 | 31.0333 |  | 26.7 | 28.8 | 29.1 | 28 | 28.2
Germany |  | LAHR | LAHR, Germany | 48.37N | 7.83E | 157 | 1.00 (EUW) | 82-06 | 108050 | -13 |  | -23.9 | 38.9 | 32 | 33.2 | 34.8 | 33 | 33.3333 |  | 29.2 | 30.9 | 30.7 | 30 | 30.2667
Germany |  | LANDSBERG | LANDSBERG, Germany | 48.07N | 10.90E | 628 | 1.00 (EUW) | 82-06 | 108570 | -18 |  | -26.9 | 36.3 | 30 | 32 | 31.7 | 31 | 31.2333 |  | 27.6 | 29.1 | 28.9 | 29 | 28.5333
Germany |  | LAUPHEIM | LAUPHEIM, Germany | 48.22N | 9.92E | 550 | 1.00 (EUW) | 85-06 | 108370 | -15.9 |  | -24.1 | 37.1 | 30.9 | 32.2 | 32.8 | 32 | 31.9667 |  | 28.2 | 29.4 | 29.3 | 29 | 28.9667
Germany |  | LECHFELD | LECHFELD, Germany | 48.18N | 10.85E | 562 | 1.00 (EUW) | 82-06 | 108560 | -18.7 |  | -27.7 | 38.3 | 31 | 32.6 | 33.1 | 32 | 32.2333 |  | 28.1 | 29.9 | 29.5 | 29 | 29.1667
Germany |  | LECK | LECK, Germany | 54.80N | 8.95E | 17 | 1.00 (EUW) | 87-06 | 100220 | -13 |  | -21.4 | 34.7 | 27.7 | 29.9 | 29.2 | 29 | 28.9333 |  | 24.8 | 27 | 27 | 26 | 26.2667
Germany |  | LEINEFELDE (AUT) | LEINEFELDE (AUT), Germany | 51.40N | 10.32E | 356 | 1.00 (EUW) | 82-03 | 104490 | -14.1 |  | -27.7 | 35.2 | 28.1 | 29.2 | 30.6 | 29 | 29.3 |  | 25.2 | 27.2 | 27.4 | 27 | 26.6
Germany |  | LEIPZIG | LEIPZIG, Germany | 51.32N | 12.42E | 151 | 1.00 (EUW) | 97-06 | 104710 | -12.9 |  | -19 | 39.3 | 31.9 | 33.4 | 33 | 33 | 32.7667 |  | 28.8 | 30.7 | 29.8 | 30 | 29.7667
Germany |  | LEIPZIG/SCHKEUDITZ | LEIPZIG/SCHKEUDITZ, Germany | 51.42N | 12.23E | 133 | 1.00 (EUW) | 82-03 | 104690 | -14.3 |  | -31.9 | 38.3 | 30.6 | 31.8 | 32.8 | 32 | 31.7333 |  | 27.8 | 29.9 | 29.7 | 29 | 29.1333
Germany |  | LINDENBERG | LINDENBERG, Germany | 52.22N | 14.12E | 98 | 1.00 (EUW) | 82-91 | 93930 | -13.9 |  | -28.2 | 37.9 | 29.8 | 31.9 | 32.6 | 31 | 31.4333 |  | 26.8 | 29.5 | 29 | 28 | 28.4333
Germany |  | LUEDENSCHEID | LUEDENSCHEID, Germany | 51.25N | 7.65E | 392 | 1.00 (EUW) | 94-06 | 104180 | -12.4 |  | -19.9 | 35.2 | 29 | 30.1 | 30.7 | 30 | 29.9333 |  | 26.3 | 27.4 | 28 | 27 | 27.2333
Germany |  | MAGDEBURG | MAGDEBURG, Germany | 52.10N | 11.58E | 79 | 1.00 (EUW) | 82-91 | 93610 | -14.1 |  | -30.9 | 36.2 | 31 | 31.5 | 32 | 32 | 31.5 |  | 27.1 | 29.7 | 29.1 | 29 | 28.6333
Germany |  | MARNITZ (AUT) | MARNITZ (AUT), Germany | 53.32N | 11.93E | 87 | 1.00 (EUW) | 82-03 | 102640 | -14 |  | -30.4 | 35 | 30.1 | 30.3 | 30.2 | 30 | 30.2 |  | 26.9 | 28.4 | 27.8 | 28 | 27.7
Germany |  | MEININGEN | MEININGEN, Germany | 50.57N | 10.38E | 453 | 1.00 (EUW) | 82-03 | 105480 | -15.5 |  | -25.4 | 34.6 | 27.9 | 29.4 | 30.3 | 29 | 29.2 |  | 25.2 | 27.2 | 27.1 | 27 | 26.5
Germany |  | MEMMINGEN (GER-AFB) | MEMMINGEN (GER-AFB), Germany | 47.98N | 10.23E | 644 | 1.00 (EUW) | 82-01 | 109470 | -17.7 |  | -27.4 | 37.5 | 29.3 | 31.9 | 31 | 31 | 30.7333 |  | 26.7 | 29.1 | 28.2 | 28 | 28
Germany |  | MENDIG | MENDIG, Germany | 50.37N | 7.32E | 190 | 1.00 (EUW) | 83-05 | 105140 | -13.3 |  | -21.6 | 39.8 | 31.3 | 33.1 | 34.8 | 33 | 33.0667 |  | 28.8 | 30.8 | 31.2 | 30 | 30.2667
Germany |  | MESSSTETTEN | MESSSTETTEN, Germany | 48.18N | 9.00E | 930 | 1.00 (EUW) | 93-06 | 108270 | -15.3 |  | -20.2 | 34.2 | 28 | 28.7 | 30.1 | 29 | 28.9333 |  | 25.6 | 26.5 | 26.9 | 26 | 26.3333
Germany |  | MUNICH | MUNICH, Germany | 48.13N | 11.55E | 520 | 1.00 (EUW) | 82-03 | 108650 | -13.4 |  | -24.5 | 38.4 | 29.9 | 32.9 | 31.9 | 32 | 31.5667 |  | 27.3 | 29.8 | 29.5 | 29 | 28.8667
Germany |  | MUNICH/RIEM | MUNICH/RIEM, Germany | 48.13N | 11.70E | 529 | 1.00 (EUW) | 82-06 | 108660 | -18.2 |  | -27.9 | 37.5 | 30.2 | 32.1 | 32.2 | 32 | 31.5 |  | 27.9 | 29.5 | 29.4 | 29 | 28.9333
Germany |  | NEUBURG/DONAU | NEUBURG/DONAU, Germany | 48.72N | 11.22E | 387 | 1.00 (EUW) | 82-06 | 108530 | -17.7 |  | -31 | 38.7 | 30.9 | 32.9 | 33.2 | 32 | 32.3333 |  | 28.6 | 30 | 29.9 | 30 | 29.5
Germany |  | NEUHAUSEN OB ECK | NEUHAUSEN OB ECK, Germany | 47.98N | 8.90E | 804 | 1.00 (EUW) | 84-93 | 109210 | -16.7 |  | -30.1 | 33 | 26.2 | 29.2 | 29.9 | 28 | 28.4333 |  | 24 | 26.9 | 27.2 | 26 | 26.0333
Germany |  | NEURUPPIN | NEURUPPIN, Germany | 52.90N | 12.82E | 39 | 1.00 (EUW) | 82-03 | 102700 | -15 |  | -29.1 | 37.1 | 29.6 | 30.6 | 31 | 30 | 30.4 |  | 27.1 | 28.6 | 27.8 | 28 | 27.8333
Germany |  | NIEDERSTETTEN | NIEDERSTETTEN, Germany | 49.38N | 9.97E | 473 | 1.00 (EUW) | 82-06 | 107430 | -14.2 |  | -21.6 | 37.7 | 31.1 | 32.1 | 33.9 | 32 | 32.3667 |  | 28 | 29.5 | 30 | 29 | 29.1667
Germany |  | NOERVENICH | NOERVENICH, Germany | 50.83N | 6.67E | 135 | 1.00 (EUW) | 82-06 | 105020 | -11.9 |  | -23.4 | 39.7 | 31.2 | 33 | 33.8 | 33 | 32.6667 |  | 28.1 | 30.2 | 30.2 | 30 | 29.5
Germany |  | NORDHOLZ | NORDHOLZ, Germany | 53.77N | 8.67E | 32 | 1.00 (EUW) | 82-06 | 101360 | -11.8 |  | -21.6 | 37.1 | 29.5 | 31 | 30.8 | 30 | 30.4333 |  | 26 | 28 | 28 | 27 | 27.3333
Germany |  | NUERBURG-BARWEILER | NUERBURG-BARWEILER, Germany | 50.37N | 6.87E | 488 | 1.00 (EUW) | 95-06 | 105060 | -13.1 |  | -19.7 | 37.2 | 28.7 | 29.9 | 31.8 | 30 | 30.1333 |  | 26.1 | 27.4 | 27.9 | 27 | 27.1333
Germany |  | NURNBERG | NURNBERG, Germany | 49.50N | 11.08E | 319 | 1.00 (EUW) | 82-03 | 107630 | -15.9 |  | -27.4 | 39.6 | 30.5 | 33.2 | 32.9 | 32 | 32.2 |  | 28.1 | 30.6 | 29.9 | 30 | 29.5333
Germany |  | OLDENBURG | OLDENBURG, Germany | 53.18N | 8.17E | 20 | 1.00 (EUW) | 82-06 | 102150 | -12.2 |  | -22.7 | 38.1 | 30.9 | 31.7 | 31.7 | 31 | 31.4333 |  | 27 | 29 | 28.8 | 28 | 28.2667
Germany |  | OSCHATZ | OSCHATZ, Germany | 51.30N | 13.10E | 152 | 1.00 (EUW) | 83-03 | 104800 | -14.7 |  | -33.7 | 39.2 | 30.1 | 32.1 | 33.8 | 32 | 32 |  | 27.7 | 30.1 | 30 | 29 | 29.2667
Germany |  | PASSAU | PASSAU, Germany | 48.58N | 13.47E | 409 | 1.00 (EUW) | 82-92 | 108930 | -16.3 |  | -28.7 | 37.8 | 28.6 | 32 | 32.4 | 31 | 31 |  | 26.8 | 29.6 | 29.1 | 29 | 28.5
Germany |  | PFERDSFELD (GER-AF) | PFERDSFELD (GER-AF), Germany | 49.85N | 7.60E | 396 | 1.00 (EUW) | 82-96 | 106260 | -12.3 |  | -20.4 | 37.8 | 27.9 | 31 | 31.1 | 30 | 30 |  | 26 | 28.9 | 27.9 | 28 | 27.6
Germany |  | PLAUEN (AUT) | PLAUEN (AUT), Germany | 50.48N | 12.13E | 389 | 1.00 (EUW) | 82-03 | 105690 | -18.8 |  | -32.2 | 37.1 | 29.4 | 31 | 31.6 | 31 | 30.6667 |  | 26.5 | 28.5 | 28.6 | 28 | 27.8667
Germany |  | POTSDAM | POTSDAM, Germany | 52.38N | 13.07E | 81 | 1.00 (EUW) | 82-91 | 93790 | -13.9 |  | -28.3 | 38.3 | 30.6 | 31.6 | 32 | 31 | 31.4 |  | 27.2 | 29.7 | 28.6 | 29 | 28.5
Germany |  | QUICKBORN | QUICKBORN, Germany | 53.73N | 9.88E | 17 | 1.00 (EUW) | 96-06 | 101460 | -14.3 |  | -25.4 | 37.3 | 30.3 | 31.4 | 30.2 | 31 | 30.6333 |  | 26.5 | 28.2 | 28.1 | 28 | 27.6
Germany |  | RAMSTEIN | RAMSTEIN, Germany | 49.43N | 7.60E | 238 | 1.00 (EUW) | 82-06 | 106140 | -14.6 |  | -24.2 | 39.6 | 31.1 | 33.8 | 35.1 | 33 | 33.3333 |  | 28.9 | 31.1 | 30.9 | 30 | 30.3
Germany |  | REGENSBURG/OBERHUB | REGENSBURG/OBERHUB, Germany | 49.05N | 12.10E | 376 | 1.00 (EUW) | 82-03 | 107760 | -15.8 |  | -27.5 | 39.2 | 30 | 32.6 | 32.2 | 32 | 31.6 |  | 27.5 | 29.7 | 29.8 | 29 | 29
Germany |  | RHEINE-BENTLAGE | RHEINE-BENTLAGE, Germany | 52.30N | 7.38E | 49 | 1.00 (EUW) | 82-06 | 103060 | -12 |  | -24.8 | 42.2 | 30.9 | 32.8 | 32.4 | 32 | 32.0333 |  | 27.9 | 30 | 29.8 | 29 | 29.2333
Germany |  | ROTH | ROTH, Germany | 49.22N | 11.10E | 395 | 1.00 (EUW) | 84-06 | 107650 | -17.6 |  | -26.4 | 39.8 | 32.3 | 33.2 | 34.8 | 33 | 33.4333 |  | 29.2 | 30.4 | 30.6 | 30 | 30.0667
Germany |  | SAARBRUCKEN/ENSHEIM | SAARBRUCKEN/ENSHEIM, Germany | 49.22N | 7.12E | 322 | 1.00 (EUW) | 82-03 | 107080 | -11.3 |  | -20.7 | 35.8 | 28.6 | 31 | 31.3 | 30 | 30.3 |  | 26.4 | 28.9 | 28.3 | 28 | 27.8667
Germany |  | SCHLESWIG-JAGEL | SCHLESWIG-JAGEL, Germany | 54.47N | 9.52E | 25 | 1.00 (EUW) | 87-06 | 100370 | -13.1 |  | -22.8 | 37.8 | 29.5 | 30.9 | 30.2 | 30 | 30.2 |  | 25.5 | 28 | 27.9 | 27 | 27.1333
Germany |  | SCHMUECKE (RIDGE) | SCHMUECKE (RIDGE), Germany | 50.65N | 10.77E | 942 | 1.00 (EUW) | 82-03 | 105520 | -15.9 |  | -28.9 | 30.9 | 24.6 | 26.4 | 26.3 | 26 | 25.7667 |  | 21.9 | 23.7 | 23.1 | 23 | 22.9
Germany |  | SCHWERIN | SCHWERIN, Germany | 53.63N | 11.42E | 59 | 1.00 (EUW) | 82-91 | 91620 | -12.4 |  | -27.9 | 35.3 | 28.8 | 30.2 | 29.2 | 29 | 29.4 |  | 25.2 | 27.7 | 27.3 | 27 | 26.7333
Germany |  | SEEHAUSEN/ALTMARK | SEEHAUSEN/ALTMARK, Germany | 52.90N | 11.73E | 0 | 1.00 (EUW) | 82-91 | 92610 | -15.3 |  | -33.2 | 36.2 | 31 | 31.6 | 31.6 | 31 | 31.4 |  | 27.2 | 29.7 | 28.9 | 29 | 28.6
Germany |  | SONNEBERG/NEUFANG | SONNEBERG/NEUFANG, Germany | 50.38N | 11.18E | 630 | 1.00 (EUW) | 82-03 | 105580 | -15 |  | -25.6 | 33.8 | 27.2 | 28.9 | 28.7 | 28 | 28.2667 |  | 24.2 | 26.5 | 26.1 | 26 | 25.6
Germany |  | SPANGDAHLEM | SPANGDAHLEM, Germany | 49.98N | 6.70E | 356 | 1.00 (EUW) | 82-06 | 106070 | -11.2 |  | -19.7 | 37.8 | 29.1 | 31.9 | 32.1 | 31 | 31.0333 |  | 27.1 | 29.1 | 28.9 | 28 | 28.3667
Germany |  | STRAUBING | STRAUBING, Germany | 48.83N | 12.57E | 360 | 1.00 (EUW) | 95-06 | 107880 | -18.5 |  | -25.8 | 37.3 | 30.4 | 31.7 | 32.9 | 32 | 31.6667 |  | 28.5 | 29.4 | 29.4 | 29 | 29.1
Germany |  | STUTTGART/ECHTERDI | STUTTGART/ECHTERDI, Germany | 48.68N | 9.22E | 396 | 1.00 (EUW) | 82-03 | 107380 | -16 |  | -30.4 | 38.9 | 29 | 32.7 | 32.2 | 31 | 31.3 |  | 27.1 | 29.6 | 29.4 | 29 | 28.7
Germany |  | STUTTGART/SCHNARREN | STUTTGART/SCHNARREN, Germany | 48.83N | 9.20E | 315 | 1.00 (EUW) | 84-03 | 107390 | -13.1 |  | -27 | 36.8 | 29.8 | 31.3 | 33.1 | 31 | 31.4 |  | 27.5 | 29.1 | 30.3 | 29 | 28.9667
Germany |  | TETEROW | TETEROW, Germany | 53.77N | 12.62E | 50 | 1.00 (EUW) | 82-03 | 101770 | -13.2 |  | -28.7 | 41.5 | 30.7 | 31.3 | 31.4 | 31 | 31.1333 |  | 27 | 28.6 | 28.3 | 28 | 27.9667
Germany |  | TRIER/PETRISBERG | TRIER/PETRISBERG, Germany | 49.75N | 6.67E | 265 | 1.00 (EUW) | 82-03 | 106090 | -11.2 |  | -20.3 | 38.2 | 29.6 | 32.4 | 32.7 | 32 | 31.5667 |  | 27.5 | 30.2 | 29.2 | 29 | 28.9667
Germany |  | TROLLENHAGEN | TROLLENHAGEN, Germany | 53.60N | 13.32E | 69 | 1.00 (EUW) | 82-06 | 102810 | -14.4 |  | -27.5 | 38.1 | 30 | 31.4 | 30.8 | 31 | 30.7333 |  | 26.4 | 28.8 | 28.6 | 28 | 27.9333
Germany |  | UECKERMUENDE (AUT) | UECKERMUENDE (AUT), Germany | 53.75N | 14.07E | 1 | 1.00 (EUW) | 82-91 | 91930 | -14.8 |  | -33.5 | 36.7 | 27.8 | 29.5 | 29.9 | 29 | 29.0667 |  | 24.7 | 26.8 | 26.8 | 26 | 26.1
Germany |  | WAREN | WAREN, Germany | 53.52N | 12.67E | 71 | 1.00 (EUW) | 94-06 | 102680 | -13.6 |  | -23.4 | 38 | 31.6 | 32 | 30.9 | 32 | 31.5 |  | 27.1 | 29.4 | 29.2 | 29 | 28.5667
Germany |  | WARNEMUENDE | WARNEMUENDE, Germany | 54.18N | 12.08E | 4 | 1.00 (EUW) | 82-91 | 91700 | -9.9 |  | -22.3 | 35.4 | 26.8 | 29.5 | 29.1 | 28 | 28.4667 |  | 22.8 | 25.8 | 26 | 25 | 24.8667
Germany |  | WASSERKUPPE (MOUNT) | WASSERKUPPE (MOUNT), Germany | 50.50N | 9.95E | 921 | 1.00 (EUW) | 82-03 | 105440 | -15.2 |  | -27.3 | 32.5 | 24.4 | 26.5 | 27.7 | 26 | 26.2 |  | 22.2 | 24.1 | 24.2 | 24 | 23.5
Germany |  | WEIMAR | WEIMAR, Germany | 50.98N | 11.32E | 268 | 1.00 (EUW) | 97-06 | 105550 | -14.9 |  | -22 | 38.1 | 30.7 | 32.6 | 33.1 | 32 | 32.1333 |  | 28.1 | 30 | 29.7 | 29 | 29.2667
Germany |  | WERNIGERODE (AUT) | WERNIGERODE (AUT), Germany | 51.85N | 10.77E | 240 | 1.00 (EUW) | 82-03 | 104540 | -16.3 |  | -30.9 | 35.8 | 29 | 30.1 | 31 | 30 | 30.0333 |  | 26.1 | 28 | 27.8 | 27 | 27.3
Germany |  | WESTERMARKELSDORF | WESTERMARKELSDORF, Germany | 54.53N | 11.07E | 9 | 1.00 (EUW) | 97-06 | 100550 | -6.9 |  | -10.6 | 34.2 | 26.6 | 26.5 | 26.8 | 27 | 26.6333 |  | 22.5 | 24.7 | 24.6 | 24 | 23.9333
Germany |  | WIESENBURG | WIESENBURG, Germany | 52.12N | 12.47E | 188 | 1.00 (EUW) | 92-06 | 103680 | -14.2 |  | -21.8 | 39.1 | 31.1 | 32.5 | 32.3 | 32 | 31.9667 |  | 27.8 | 30.2 | 29 | 29 | 29
Germany |  | WILDENRATH(GAFB) | WILDENRATH(GAFB), Germany | 51.12N | 6.22E | 89 | 1.00 (EUW) | 82-91 | 104020 | -11.4 |  | -25.5 | 37.8 | 29 | 31.8 | 31.8 | 31 | 30.8667 |  | 27.1 | 29.3 | 28.5 | 28 | 28.3
Germany |  | WITTENBERG | WITTENBERG, Germany | 51.88N | 12.65E | 106 | 1.00 (EUW) | 82-03 | 104740 | -14.1 |  | -26.8 | 39.2 | 31.4 | 32.1 | 33.1 | 32 | 32.2 |  | 28.1 | 30.2 | 29.4 | 29 | 29.2333
Germany |  | WITTMUNDHAVEN | WITTMUNDHAVEN, Germany | 53.55N | 7.67E | 12 | 1.00 (EUW) | 82-06 | 101260 | -11.3 |  | -21.5 | 36.8 | 30.2 | 31 | 31.5 | 31 | 30.9 |  | 26.2 | 28.2 | 28.2 | 28 | 27.5333
Germany |  | WUNSTORF | WUNSTORF, Germany | 52.47N | 9.43E | 51 | 1.00 (EUW) | 82-06 | 103340 | -12.5 |  | -25.4 | 39.8 | 31 | 33 | 33.1 | 32 | 32.3667 |  | 27.8 | 30.1 | 30.2 | 29 | 29.3667
Germany |  | ZINNWALD/GEORGENFE | ZINNWALD/GEORGENFE, Germany | 50.73N | 13.75E | 882 | 1.00 (EUW) | 82-03 | 105820 | -15.9 |  | -25.7 | 31.3 | 23.4 | 25.6 | 26.2 | 25 | 25.0667 |  | 21.1 | 23.2 | 23.5 | 23 | 22.6
Germany |  | ZUGSPITZE MOUNTAIN | ZUGSPITZE MOUNTAIN, Germany | 47.42N | 10.98E | 2960 | 1.00 (EUW) | 82-03 | 109610 | -25.8 |  | -35.1 | 17.6 | 10.6 | 13.7 | 13.2 | 13 | 12.5 |  | 8.3 | 11.3 | 10.9 | 10 | 10.1667
Gibraltar |  | GIBRALTAR | GIBRALTAR, Gibraltar | 36.15N | 5.35W | 5 | 1.00 (EUW) | 82-06 | 84950 | 5.2 |  | -0.4 | 41.2 | 31 | 34.4 | 33.1 | 33 | 32.8333 |  | 28.3 | 31.1 | 31 | 30 | 30.1333
Greece |  | AKTION (AIRPORT) | AKTION (AIRPORT), Greece | 38.95N | 20.77E | 4 | 2.00 (EUE) | 82-06 | 166430 | 0.4 |  | -3.3 | 40.9 | 32 | 33.9 | 34.8 | 34 | 33.5667 |  | 29.9 | 31.6 | 32 | 31 | 31.1667
Greece |  | ALEXANDROUPOLI (AIR) | ALEXANDROUPOLI (AIR), Greece | 40.85N | 25.92E | 3 | 2.00 (EUE) | 82-06 | 166270 | -8.4 |  | -14.3 | 40.3 | 33.4 | 35.2 | 36.2 | 35 | 34.9333 |  | 31.1 | 33.8 | 34 | 33 | 32.9667
Greece |  | ANDRAVIDA (AIRPORT) | ANDRAVIDA (AIRPORT), Greece | 37.92N | 21.28E | 14 | 2.00 (EUE) | 82-06 | 166820 | -2.6 |  | -6.3 | 39.7 | 33.2 | 34.7 | 35.2 | 34 | 34.3667 |  | 31.2 | 32.8 | 33.2 | 32 | 32.4
Greece |  | ARAXOS (AIRPORT) | ARAXOS (AIRPORT), Greece | 38.15N | 21.42E | 12 | 2.00 (EUE) | 83-06 | 166870 | -1.5 |  | -5.7 | 41.6 | 34.9 | 37.1 | 37.8 | 37 | 36.6 |  | 32.9 | 34.8 | 35 | 34 | 34.2333
Greece |  | ATHINAI (AIRPORT) | ATHINAI (AIRPORT), Greece | 37.90N | 23.73E | 15 | 2.00 (EUE) | 82-06 | 167160 | -0.4 |  | -4.9 | 42.8 | 35.1 | 37.2 | 37.1 | 36 | 36.4667 |  | 33 | 35.1 | 35.1 | 34 | 34.4
Greece |  | CHRYSOPOULI (AIRPORT) | CHRYSOPOULI (AIRPORT), Greece | 40.98N | 24.60E | 5 | 2.00 (EUE) | 92-06 | 166240 | -5.2 |  | -10.8 | 39.2 | 32 | 34.2 | 34.9 | 34 | 33.7 |  | 30 | 32.8 | 32.2 | 32 | 31.6667
Greece |  | ELEFSIS (AIRPORT) | ELEFSIS (AIRPORT), Greece | 38.07N | 23.55E | 31 | 2.00 (EUE) | 82-06 | 167180 | -1.3 |  | -5.7 | 46.4 | 36.2 | 40.1 | 38.2 | 38 | 38.1667 |  | 34.2 | 36.9 | 36.1 | 36 | 35.7333
Greece |  | HERAKLION (AIRPORT) | HERAKLION (AIRPORT), Greece | 35.33N | 25.18E | 39 | 2.00 (EUE) | 82-06 | 167540 | 3.2 |  | -1 | 43.6 | 33.5 | 34 | 33.6 | 34 | 33.7 |  | 30.2 | 31.2 | 30.9 | 31 | 30.7667
Greece |  | KALAMATA (AIRPORT) | KALAMATA (AIRPORT), Greece | 37.07N | 22.02E | 8 | 2.00 (EUE) | 90-06 | 167260 | -2.2 |  | -6.1 | 44.2 | 34.2 | 37.2 | 36.2 | 36 | 35.8667 |  | 32.1 | 34 | 34 | 33 | 33.3667
Greece |  | KERKYRA (AIRPORT) | KERKYRA (AIRPORT), Greece | 39.62N | 19.92E | 4 | 2.00 (EUE) | 82-06 | 166410 | -1.9 |  | -5.6 | 42.3 | 34.6 | 37.2 | 36.2 | 36 | 36 |  | 32.1 | 34.2 | 34.3 | 34 | 33.5333
Greece |  | KOS (AIRPORT) | KOS (AIRPORT), Greece | 36.78N | 27.07E | 129 | 2.00 (EUE) | 82-06 | 167420 | 1.7 |  | -2.8 | 41 | 33.2 | 36 | 35.2 | 35 | 34.8 |  | 31.1 | 33.2 | 33.1 | 32 | 32.4667
Greece |  | LARISSA (AIRPORT) | LARISSA (AIRPORT), Greece | 39.63N | 22.42E | 74 | 2.00 (EUE) | 82-06 | 166480 | -8.7 |  | -17.8 | 46.5 | 37.2 | 40.2 | 37.7 | 38 | 38.3667 |  | 34.9 | 36.8 | 35.2 | 36 | 35.6333
Greece |  | LIMNOS (AIRPORT) | LIMNOS (AIRPORT), Greece | 39.92N | 25.23E | 4 | 2.00 (EUE) | 82-06 | 166500 | -3.1 |  | -6.6 | 39.2 | 32.2 | 34.3 | 33.2 | 33 | 33.2333 |  | 30.2 | 32.2 | 31.6 | 31 | 31.3333
Greece |  | METHONI | METHONI, Greece | 36.83N | 21.70E | 34 | 2.00 (EUE) | 82-05 | 167340 | 1.3 |  | -2.6 | 40.9 | 30.1 | 33.1 | 31.9 | 32 | 31.7 |  | 27.7 | 30 | 30.2 | 29 | 29.3
Greece |  | MILOS | MILOS, Greece | 36.72N | 24.45E | 183 | 2.00 (EUE) | 82-06 | 167380 | 2.8 |  | -2 | 41.3 | 34.9 | 36.4 | 35.2 | 36 | 35.5 |  | 32.1 | 33.5 | 32.4 | 33 | 32.6667
Greece |  | MYTILINI (AIRPORT) | MYTILINI (AIRPORT), Greece | 39.07N | 26.60E | 5 | 2.00 (EUE) | 82-06 | 166670 | -0.5 |  | -3.4 | 42 | 34 | 35.9 | 35.7 | 35 | 35.2 |  | 32 | 34 | 33.5 | 33 | 33.1667
Greece |  | NAXOS | NAXOS, Greece | 37.10N | 25.38E | 9 | 2.00 (EUE) | 82-03 | 167320 | N/A |  | N/A | N/A | 31.4 | 31.4 | 30.5 | 31 | 31.1 |  | 29.2 | 29.8 | 28.7 | 29 | 29.2333
Greece |  | RHODES (AIRPORT) | RHODES (AIRPORT), Greece | 36.40N | 28.08E | 11 | 2.00 (EUE) | 82-06 | 167490 | 3.7 |  | -1.4 | 40.6 | 31.8 | 34.9 | 33.9 | 34 | 33.5333 |  | 30.1 | 32.2 | 32 | 31 | 31.4333
Greece |  | SAMOS (AIRPORT) | SAMOS (AIRPORT), Greece | 37.70N | 26.92E | 7 | 2.00 (EUE) | 82-04 | 167230 | 0.3 |  | -3.5 | 43.5 | 35.2 | 38.7 | 37.5 | 37 | 37.1333 |  | 33.2 | 36 | 35.3 | 35 | 34.8333
Greece |  | SKYROS (AIRPORT) | SKYROS (AIRPORT), Greece | 38.97N | 24.48E | 28 | 2.00 (EUE) | 82-06 | 166840 | 0.5 |  | -3.4 | 42.4 | 32.1 | 34.2 | 32.9 | 33 | 33.0667 |  | 29.9 | 31.4 | 30.4 | 31 | 30.5667
Greece |  | SOUDA (AIRPORT) | SOUDA (AIRPORT), Greece | 35.48N | 24.12E | 151 | 2.00 (EUE) | 82-06 | 167460 | 2.3 |  | -2.1 | 43.6 | 35.9 | 37.9 | 36.6 | 37 | 36.8 |  | 32.9 | 34.9 | 34 | 34 | 33.9333
Greece |  | SOUDA BAY CRETE | SOUDA BAY CRETE, Greece | 35.53N | 24.15E | 146 | 2.00 (EUE) | 82-04 | 167464 | 1.6 |  | -0.9 | 43.6 | 36.9 | 38 | 37.1 | 37 | 37.3333 |  | 33.8 | 35 | 34 | 34 | 34.2667
Greece |  | THESSALONIKI (AIRPORT) | THESSALONIKI (AIRPORT), Greece | 40.52N | 22.97E | 4 | 2.00 (EUE) | 82-06 | 166220 | -6.3 |  | -11.7 | 43.8 | 34.8 | 37.1 | 36 | 36 | 35.9667 |  | 32.2 | 34.2 | 33.9 | 33 | 33.4333
Greece |  | TRIPOLIS (AIRPORT) | TRIPOLIS (AIRPORT), Greece | 37.53N | 22.40E | 652 | 2.00 (EUE) | 82-05 | 167100 | N/A |  | N/A | N/A | 35.2 | 36.2 | 36.5 | 36 | 35.9667 |  | 32.4 | 34.1 | 33.3 | 33 | 33.2667
Greenland |  | AASIAAT (EGEDESMINDE) | AASIAAT (EGEDESMINDE), Greenland | 68.70N | 52.85W | 41 | -3.00 (GRN) | 82-06 | 42200 | -29.8 |  | -41.3 | 20.3 | 11.9 | 13.2 | 12.5 | 13 | 12.5333 |  | 10.2 | 11.5 | 10.5 | 11 | 10.7333
Greenland |  | ANGISOQ | ANGISOQ, Greenland | 59.98N | 45.20W | 16 | -3.00 (GRN) | 82-06 | 42850 | N/A |  | N/A | N/A | 10.6 | 15.9 | 19.5 | 15 | 15.3333 |  | 8.7 | 10.2 | 12.7 | 11 | 10.5333
Greenland |  | APUTITEEQ | APUTITEEQ, Greenland | 67.78N | 32.30W | 12 | -3.00 (GRN) | 82-06 | 43510 | N/A |  | N/A | N/A | 7.8 | 10.4 | 9.9 | 9 | 9.3667 |  | 6.2 | 7.7 | 7.4 | 7 | 7.1
Greenland |  | DANEBORG | DANEBORG, Greenland | 74.30N | 20.22W | 44 | -1.00 (AZR) | 82-06 | 43300 | N/A |  | N/A | N/A | 11.1 | 14.1 | 14 | 13 | 13.0667 |  | 8.9 | 11.9 | 11.5 | 11 | 10.7667
Greenland |  | DANMARKSHAVN | DANMARKSHAVN, Greenland | 76.77N | 18.67W | 12 | -3.00 (GRN) | 82-06 | 43200 | -37.7 |  | -43.7 | 17.1 | 10.7 | 12.8 | 11.6 | 12 | 11.7 |  | 8.4 | 11.1 | 9.4 | 10 | 9.6333
Greenland |  | HALL LAND | HALL LAND, Greenland | 81.68N | 59.93W | 105 | -3.00 (GRN) | 83-00 | 42070 | N/A |  | N/A | N/A | 11.8 | 13.9 | 13.6 | 13 | 13.1 |  | 9.9 | 12.3 | 11 | 11 | 11.0667
Greenland |  | HENRIK KROEYER HOLM | HENRIK KROEYER HOLM, Greenland | 80.65N | 13.72W | 10 | -3.00 (GRN) | 84-06 | 43130 | N/A |  | N/A | N/A | 6.3 | 7.9 | 7.3 | 7 | 7.1667 |  | 4.5 | 6.5 | 5.1 | 5 | 5.3667
Greenland |  | IKERMIIT | IKERMIIT, Greenland | 64.78N | 40.30W | 80 | -3.00 (GRN) | 87-06 | 43730 | N/A |  | N/A | N/A | 18.7 | 16.2 | 18.6 | 18 | 17.8333 |  | 12.6 | 13.3 | 13.5 | 13 | 13.1333
Greenland |  | IKERMIUARSUK | IKERMIUARSUK, Greenland | 61.93N | 42.07W | 39 | -3.00 (GRN) | 87-06 | 43820 | N/A |  | N/A | N/A | 10.5 | 17.5 | 21 | 16 | 16.3333 |  | 8.9 | 13.5 | 18.4 | 14 | 13.6
Greenland |  | ILULISSAT (JAKOBSHAVN) | ILULISSAT (JAKOBSHAVN), Greenland | 69.23N | 51.07W | 31 | -3.00 (GRN) | 91-05 | 42210 | -33.3 |  | -45.5 | 21.9 | 17.2 | 16.8 | 16.1 | 17 | 16.7 |  | 14.9 | 14.2 | 13.2 | 14 | 14.1
Greenland |  | ITTOQQORTOORMIIT | ITTOQQORTOORMIIT, Greenland | 70.48N | 21.95W | 69 | -1.00 (AZR) | 93-06 | 43390 | -28.9 |  | -39.2 | 19.8 | 13.1 | 14.8 | 14.6 | 14 | 14.1667 |  | 9.9 | 12.5 | 12 | 11 | 11.4667
Greenland |  | KANGERLUSSUAQ (SDR.) | KANGERLUSSUAQ (SDR.), Greenland | 67.02N | 50.70W | 53 | -3.00 (GRN) | 82-06 | 42310 | -39.7 |  | -49.8 | 24 | 20 | 20.1 | 18.3 | 19 | 19.4667 |  | 18.5 | 18.9 | 16.9 | 18 | 18.1
Greenland |  | KAP MORRIS JESUP | KAP MORRIS JESUP, Greenland | 83.65N | 33.37W | 4 | -3.00 (GRN) | 82-05 | 43010 | N/A |  | N/A | N/A | 8.8 | 9.9 | 9.8 | 10 | 9.5 |  | 5.5 | 7.5 | 6.5 | 7 | 6.5
Greenland |  | KITSISSORSUIT | KITSISSORSUIT, Greenland | 74.03N | 57.82W | 40 | -3.00 (GRN) | 89-06 | 42080 | N/A |  | N/A | N/A | 10.1 | 10.2 | 10.8 | 10 | 10.3667 |  | 6.8 | 9 | 8.9 | 8 | 8.2333
Greenland |  | KITSISSUT (ATTU) | KITSISSUT (ATTU), Greenland | 67.78N | 53.97W | 12 | -3.00 (GRN) | 85-06 | 42280 | N/A |  | N/A | N/A | 14.8 | 9.9 | 10.2 | 12 | 11.6333 |  | 8.6 | 8.1 | 8.4 | 8 | 8.3667
Greenland |  | KITSISSUT (CAREY OEER) | KITSISSUT (CAREY OEER), Greenland | 76.63N | 73.00W | 11 | -4.00 (NAA) | 82-04 | 42030 | N/A |  | N/A | N/A | 10.5 | 10.6 | 9 | 10 | 10.0333 |  | 6.6 | 8.7 | 7.3 | 8 | 7.5333
Greenland |  | NARSARSUAQ | NARSARSUAQ, Greenland | 61.13N | 45.43W | 5 | -3.00 (GRN) | 82-06 | 42700 | -25.5 |  | -37.9 | 24.1 | 19.3 | 19.9 | 19.6 | 20 | 19.6 |  | 17.2 | 18.1 | 17.1 | 17 | 17.4667
Greenland |  | NUNARSUIT | NUNARSUIT, Greenland | 60.77N | 48.42W | 33 | -3.00 (GRN) | 89-06 | 42660 | N/A |  | N/A | N/A | 10.2 | 11.4 | 11 | 11 | 10.8667 |  | 7.9 | 9.3 | 9.3 | 9 | 8.8333
Greenland |  | NUUK (GODTHAAB) | NUUK (GODTHAAB), Greenland | 64.17N | 51.75W | 84 | -3.00 (GRN) | 82-06 | 42500 | -21.3 |  | -30.5 | 22.6 | 15.9 | 16.8 | 16.2 | 16 | 16.3 |  | 13 | 14.2 | 13.1 | 13 | 13.4333
Greenland |  | NUUSSUAATAA | NUUSSUAATAA, Greenland | 70.68N | 54.62W | 27 | -3.00 (GRN) | 83-06 | 42140 | -29.7 |  | -39.2 | 19.8 | 12.4 | 13 | 12.6 | 13 | 12.6667 |  | 9.7 | 11.2 | 10.7 | 11 | 10.5333
Greenland |  | PAAMIUT (FREDERIKSHAAB) | PAAMIUT (FREDERIKSHAAB), Greenland | 62.00N | 49.67W | 15 | -3.00 (GRN) | 82-06 | 42600 | -22.3 |  | -31.3 | 21.3 | 13.6 | 14.7 | 15.2 | 15 | 14.5 |  | 11.3 | 12.1 | 12.4 | 12 | 11.9333
Greenland |  | PITUFFIK (THULE A.B.) | PITUFFIK (THULE A.B.), Greenland | 76.53N | 68.75W | 59 | -4.00 (NAA) | 82-06 | 42020 | -37.8 |  | -43.7 | 20.8 | 13.5 | 15 | 12.9 | 14 | 13.8 |  | 10.2 | 12.2 | 10.6 | 11 | 11
Greenland |  | PRINS CHRISTIAN SUN | PRINS CHRISTIAN SUN, Greenland | 60.05N | 43.17W | 75 | -3.00 (GRN) | 82-06 | 43900 | -12.7 |  | -20 | 22.7 | 14.2 | 17.1 | 16.4 | 16 | 15.9 |  | 11.7 | 13.9 | 13.6 | 13 | 13.0667
Greenland |  | QAQORTOQ (JULIANEHAAB) | QAQORTOQ (JULIANEHAAB), Greenland | 60.72N | 46.05W | 34 | -3.00 (GRN) | 82-06 | 42720 | -19.5 |  | -28.9 | 21.1 | 16 | 17.1 | 17.1 | 17 | 16.7333 |  | 13.8 | 15 | 14.5 | 14 | 14.4333
Greenland |  | SIORALIK | SIORALIK, Greenland | 65.02N | 52.55W | 14 | -3.00 (GRN) | 86-06 | 42420 | N/A |  | N/A | N/A | 12.6 | 19.7 | 19.7 | 17 | 17.3333 |  | 9.8 | 17.9 | 18.1 | 15 | 15.2667
Greenland |  | SISIMIUT (HOLSTEINS) | SISIMIUT (HOLSTEINS), Greenland | 66.92N | 53.67W | 9 | -3.00 (GRN) | 82-01 | 42300 | -30.1 |  | -40.9 | 20.7 | 14.7 | 16.7 | 14.4 | 15 | 15.2667 |  | 11.9 | 13.8 | 11.6 | 12 | 12.4333
Greenland |  | STATION NORD AWS | STATION NORD AWS, Greenland | 81.60N | 16.68W | 36 | -3.00 (GRN) | 85-06 | 43120 | N/A |  | N/A | N/A | 10.6 | 14.6 | 12.8 | 13 | 12.6667 |  | 8 | 12.8 | 11.1 | 11 | 10.6333
Greenland |  | TASIILAQ (AMMASSALIK) | TASIILAQ (AMMASSALIK), Greenland | 65.60N | 37.63W | 52 | -3.00 (GRN) | 82-06 | 43600 | -20 |  | -26.3 | 24.2 | 14.3 | 17.4 | 14.7 | 15 | 15.4667 |  | 11.1 | 13.2 | 12.3 | 12 | 12.2
Greenland |  | UKIIVIK (FREDERIKSHAAB) | UKIIVIK (FREDERIKSHAAB), Greenland | 62.57N | 50.42W | 22 | -3.00 (GRN) | 89-06 | 42530 | N/A |  | N/A | N/A | 11.8 | 12.3 | 11.8 | 12 | 11.9667 |  | 9.5 | 10.1 | 9.7 | 10 | 9.7667
Grenada |  | POINT SALINES AIRPO | POINT SALINES AIRPO, Grenada | 12.00N | 61.78W | 7 | -4.00 (SAZ) | 88-06 | 789580 | 20.4 |  | 14.7 | 38 | 31.2 | 31.2 | 31.8 | 31 | 31.4 |  | 30.8 | 30.7 | 31.1 | 31 | 30.8667
Guatemala |  | GUATEMALA (AEROPUERTO) | GUATEMALA (AEROPUERTO), Guatemala | 14.58N | 90.52W | 1489 | -6.00 (CAM) | 82-06 | 786410 | 7.6 |  | 2.9 | 33.1 | 26.9 | 26.1 | 26.2 | 26 | 26.4 |  | 25.8 | 25.1 | 25.8 | 26 | 25.5667
Guernsey |  | GUERNSEY AIRPORT | GUERNSEY AIRPORT, Guernsey | 49.43N | 2.60W | 101 | 0.00 (GMT) | 82-06 | 38940 | -1.3 |  | -7.5 | 33.6 | 24.6 | 26.1 | 27.1 | 26 | 25.9333 |  | 21.8 | 23.5 | 23.6 | 23 | 22.9667
Guyana |  | TIMEHRI\CHEDDI JAG | TIMEHRI\CHEDDI JAG, Guyana | 6.50N | 58.25W | 29 | -4.00 (SAW) | 96-06 | 810020 | N/A |  | N/A | N/A | 32.2 | 32.2 | 33.2 | 33 | 32.5333 |  | 31.5 | 31.8 | 32.4 | 32 | 31.9
Honduras |  | LA MESA (SAN PEDRO SULA) | LA MESA (SAN PEDRO SULA), Honduras | 15.45N | 87.93W | 31 | -6.00 (CAM) | 82-06 | 787080 | N/A |  | N/A | N/A | 37.1 | 35.5 | 36 | 36 | 36.2 |  | 35.9 | 34.1 | 34.8 | 35 | 34.9333
Honduras |  | TEGUCIGALPA | TEGUCIGALPA, Honduras | 14.05N | 87.22W | 1007 | -6.00 (CAM) | 82-06 | 787200 | 7.5 |  | 3.1 | 37.3 | 31.1 | 29.9 | 30.8 | 31 | 30.6 |  | 29.9 | 28.8 | 29.8 | 30 | 29.5
Hungary |  | BAJA | BAJA, Hungary | 46.18N | 19.02E | 113 | 1.00 (EUW) | 82-06 | 129600 | -17.4 |  | -29.9 | 38.8 | 34.1 | 34.2 | 35.5 | 35 | 34.6 |  | 31.5 | 32.5 | 32.7 | 32 | 32.2333
Hungary |  | BEKESCSABA | BEKESCSABA, Hungary | 46.68N | 21.17E | 90 | 1.00 (EUW) | 82-06 | 129920 | -17.2 |  | -28.3 | 39.5 | 33.9 | 34.2 | 35.2 | 34 | 34.4333 |  | 31 | 32.5 | 32.6 | 32 | 32.0333
Hungary |  | BUDAORS | BUDAORS, Hungary | 47.45N | 18.97E | 132 | 1.00 (EUW) | 82-92 | 128380 | -16.3 |  | -29.4 | 37.1 | 30.3 | 33.2 | 32.4 | 32 | 31.9667 |  | 28.2 | 31.4 | 30.8 | 30 | 30.1333
Hungary |  | BUDAPEST/FERIHEGY I | BUDAPEST/FERIHEGY I, Hungary | 47.43N | 19.27E | 185 | 1.00 (EUW) | 82-06 | 128390 | -16 |  | -25.1 | 38.8 | 33.5 | 33.9 | 35.2 | 34 | 34.2 |  | 30.8 | 32 | 32.3 | 32 | 31.7
Hungary |  | BUDAPEST/PESTSZENTL | BUDAPEST/PESTSZENTL, Hungary | 47.43N | 19.18E | 139 | 1.00 (EUW) | 82-06 | 128430 | -13.7 |  | -21.5 | 38.8 | 33.5 | 34 | 34.9 | 34 | 34.1333 |  | 30.7 | 32.3 | 32.1 | 32 | 31.7
Hungary |  | DEBRECEN | DEBRECEN, Hungary | 47.48N | 21.60E | 109 | 1.00 (EUW) | 82-06 | 128820 | -16.5 |  | -25.2 | 37.5 | 32.7 | 33.2 | 34.3 | 33 | 33.4 |  | 29.9 | 31.6 | 31.6 | 31 | 31.0333
Hungary |  | GYOR | GYOR, Hungary | 47.72N | 17.68E | 117 | 1.00 (EUW) | 82-06 | 128220 | -15.3 |  | -24.3 | 38.7 | 32.8 | 33.9 | 34.6 | 34 | 33.7667 |  | 30 | 31.8 | 31.9 | 31 | 31.2333
Hungary |  | KECSKEMET | KECSKEMET, Hungary | 46.92N | 19.75E | 123 | 1.00 (EUW) | 82-06 | 129700 | -16.7 |  | -25.8 | 38.2 | 33.8 | 34.1 | 34.7 | 34 | 34.2 |  | 30.8 | 32.4 | 32.3 | 32 | 31.8333
Hungary |  | KEKESTETO | KEKESTETO, Hungary | 47.87N | 20.02E | 1015 | 1.00 (EUW) | 82-06 | 128510 | -15.6 |  | -22 | 30.5 | 25.5 | 26 | 26.7 | 26 | 26.0667 |  | 22.7 | 24.2 | 24.3 | 24 | 23.7333
Hungary |  | KESZTHELY | KESZTHELY, Hungary | 46.73N | 17.23E | 113 | 1.00 (EUW) | 82-00 | 129200 | -13.9 |  | -22.5 | 37.8 | 31.4 | 32.3 | 33.8 | 33 | 32.5 |  | 28.7 | 30.3 | 31.3 | 30 | 30.1
Hungary |  | MISKOLC | MISKOLC, Hungary | 48.10N | 20.77E | 236 | 1.00 (EUW) | 82-06 | 127720 | -15.4 |  | -25.4 | 37.3 | 31.7 | 33.1 | 33.3 | 33 | 32.7 |  | 29.2 | 31.2 | 30.7 | 30 | 30.3667
Hungary |  | MOSONMAGYAROVAR | MOSONMAGYAROVAR, Hungary | 47.88N | 17.28E | 122 | 1.00 (EUW) | 96-06 | 128150 | -14.3 |  | -20.2 | 39.7 | 33.3 | 34 | 34.2 | 34 | 33.8333 |  | 31.1 | 32.3 | 31.6 | 32 | 31.6667
Hungary |  | NAGYKANIZSA | NAGYKANIZSA, Hungary | 46.45N | 16.97E | 141 | 1.00 (EUW) | 82-06 | 129250 | -16.8 |  | -26.9 | 38 | 32.5 | 32.8 | 33.8 | 33 | 33.0333 |  | 30.1 | 30.9 | 31.6 | 31 | 30.8667
Hungary |  | NYIREGYHAZA/NAPKOR | NYIREGYHAZA/NAPKOR, Hungary | 47.97N | 21.88E | 142 | 1.00 (EUW) | 82-06 | 128920 | -16.3 |  | -24.9 | 38.3 | 32.3 | 33.4 | 33.8 | 33 | 33.1667 |  | 29.7 | 31.5 | 31.2 | 31 | 30.8
Hungary |  | PAKS | PAKS, Hungary | 46.58N | 18.85E | 98 | 1.00 (EUW) | 92-06 | 129500 | -18.2 |  | -25.7 | 38.2 | 34.5 | 34.4 | 35.5 | 35 | 34.8 |  | 32.4 | 33 | 33.1 | 33 | 32.8333
Hungary |  | PAPA | PAPA, Hungary | 47.20N | 17.50E | 146 | 1.00 (EUW) | 82-06 | 128250 | -14.9 |  | -25.3 | 37.8 | 32.5 | 33.2 | 34.1 | 33 | 33.2667 |  | 29.6 | 31.2 | 31.7 | 31 | 30.8333
Hungary |  | PECS/POGANY | PECS/POGANY, Hungary | 46.00N | 18.23E | 203 | 1.00 (EUW) | 82-06 | 129420 | -13.2 |  | -20.7 | 37.5 | 32.5 | 32.9 | 34.4 | 33 | 33.2667 |  | 30 | 31.3 | 32 | 31 | 31.1
Hungary |  | SIOFOK | SIOFOK, Hungary | 46.92N | 18.05E | 109 | 1.00 (EUW) | 82-06 | 129350 | -13.7 |  | -24.6 | 37.9 | 32 | 32.5 | 32.6 | 32 | 32.3667 |  | 29.3 | 30.2 | 30.6 | 30 | 30.0333
Hungary |  | SOPRON | SOPRON, Hungary | 47.68N | 16.60E | 239 | 1.00 (EUW) | 82-06 | 128050 | -13 |  | -20.9 | 39.7 | 32.4 | 33.3 | 34.2 | 33 | 33.3 |  | 29.2 | 31.1 | 31.6 | 31 | 30.6333
Hungary |  | SZEGED | SZEGED, Hungary | 46.25N | 20.10E | 83 | 1.00 (EUW) | 82-06 | 129820 | -16.2 |  | -27.6 | 39 | 34 | 34.5 | 35.5 | 35 | 34.6667 |  | 31.2 | 32.9 | 32.9 | 32 | 32.3333
Hungary |  | SZENTGOTTHARD/FARKA | SZENTGOTTHARD/FARKA, Hungary | 46.92N | 16.32E | 313 | 1.00 (EUW) | 82-06 | 129100 | -15 |  | -22.7 | 38.1 | 31.2 | 31.7 | 33.1 | 32 | 32 |  | 28.7 | 29.6 | 30.6 | 30 | 29.6333
Hungary |  | SZOLNOK | SZOLNOK, Hungary | 47.12N | 20.23E | 94 | 1.00 (EUW) | 82-06 | 128600 | -16 |  | -25.8 | 38.8 | 33.8 | 34.5 | 35.5 | 35 | 34.6 |  | 30.9 | 32.7 | 32.7 | 32 | 32.1
Hungary |  | SZOMBATHELY | SZOMBATHELY, Hungary | 47.27N | 16.63E | 221 | 1.00 (EUW) | 82-06 | 128120 | -15.1 |  | -24 | 38.9 | 32.3 | 32.7 | 34 | 33 | 33 |  | 29.3 | 30.7 | 31.5 | 31 | 30.5
Hungary |  | TASZAR | TASZAR, Hungary | 46.40N | 17.92E | 156 | 1.00 (EUW) | 96-05 | 129320 | -15.1 |  | -25.1 | 39.4 | 33.4 | 33.1 | 35 | 34 | 33.8333 |  | 31.4 | 31.4 | 32.4 | 32 | 31.7333
Hungary |  | VESZPREM/SZENTKIRAL | VESZPREM/SZENTKIRAL, Hungary | 47.07N | 17.83E | 281 | 1.00 (EUW) | 88-06 | 128300 | -13.6 |  | -20 | 37.5 | 31.9 | 31.9 | 33.6 | 32 | 32.4667 |  | 29.6 | 29.9 | 31.3 | 30 | 30.2667
Hungary |  | ZALAEGERSZEG/ANDRAS | ZALAEGERSZEG/ANDRAS, Hungary | 46.87N | 16.80E | 180 | 1.00 (EUW) | 82-06 | 129150 | -15.8 |  | -28.4 | 38.4 | 31.9 | 32.4 | 32.7 | 32 | 32.3333 |  | 29.3 | 30.4 | 30.7 | 30 | 30.1333
Iceland |  | AKUREYRI | AKUREYRI, Iceland | 65.68N | 18.08W | 27 | 0.00 (GMT) | 82-06 | 40630 | -17.3 |  | -23.7 | 25.9 | 20.7 | 21.2 | 20.2 | 21 | 20.7 |  | 17.9 | 19.2 | 18.1 | 18 | 18.4
Iceland |  | AKURNES | AKURNES, Iceland | 64.30N | 15.22W | 21 | 0.00 (GMT) | 82-06 | 40820 | -11 |  | -15.5 | 25.8 | 17.2 | 17.3 | 17.9 | 17 | 17.4667 |  | 14.4 | 15 | 15 | 15 | 14.8
Iceland |  | BERGSTADIR | BERGSTADIR, Iceland | 65.70N | 19.62W | 43 | 0.00 (GMT) | 82-06 | 40530 | N/A |  | N/A | N/A | 18.5 | 20.1 | 18.2 | 19 | 18.9333 |  | 16 | 17.7 | 16.2 | 17 | 16.6333
Iceland |  | BOLUNGAVIK | BOLUNGAVIK, Iceland | 66.15N | 23.25W | 24 | 0.00 (GMT) | 82-06 | 40050 | -12 |  | -15.8 | 22.5 | 16.5 | 17.1 | 17.1 | 17 | 16.9 |  | 14.2 | 15.2 | 15.1 | 15 | 14.8333
Iceland |  | DALATANGI | DALATANGI, Iceland | 65.27N | 13.58W | 11 | 0.00 (GMT) | 82-06 | 40970 | -10.6 |  | -15.9 | 25.3 | 15.4 | 17.3 | 15.9 | 16 | 16.2 |  | 12.5 | 14.1 | 13.6 | 13 | 13.4
Iceland |  | EGILSSTADIR | EGILSSTADIR, Iceland | 65.28N | 14.40W | 23 | 0.00 (GMT) | 82-06 | 40890 | -18.1 |  | -23.3 | 30.1 | 21.4 | 23.3 | 21.1 | 22 | 21.9333 |  | 18 | 20.1 | 18.4 | 19 | 18.8333
Iceland |  | GUFUSKALAR | GUFUSKALAR, Iceland | 64.90N | 23.93W | 7 | 0.00 (GMT) | 82-94 | 40040 | -10.8 |  | -13.9 | 20.1 | 13.6 | 15.7 | 14.8 | 15 | 14.7 |  | 12.4 | 14.2 | 13.5 | 13 | 13.3667
Iceland |  | HORNBJARGSVITI (LH) | HORNBJARGSVITI (LH), Iceland | 66.42N | 22.38W | 26 | 0.00 (GMT) | 82-95 | 40230 | -12.4 |  | -16.5 | 18.7 | 13.8 | 15 | 14.6 | 14 | 14.4667 |  | 12.3 | 13.3 | 13.1 | 13 | 12.9
Iceland |  | HVERAVELLIR | HVERAVELLIR, Iceland | 64.87N | 19.57W | 642 | 0.00 (GMT) | 84-04 | 40560 | -21.7 |  | -25.1 | 25 | 16.7 | 19.7 | 17.1 | 18 | 17.8333 |  | 13.7 | 16 | 14.1 | 15 | 14.6
Iceland |  | KEFLAVIK | KEFLAVIK, Iceland | 63.97N | 22.60W | 50 | 0.00 (GMT) | 82-06 | 40180 | -10.7 |  | -14.5 | 23.8 | 16.1 | 17.2 | 17.5 | 17 | 16.9333 |  | 14 | 15.3 | 15.1 | 15 | 14.8
Iceland |  | KIRKJUBAEJARKLAUSTU | KIRKJUBAEJARKLAUSTU, Iceland | 63.78N | 18.07W | 38 | 0.00 (GMT) | 82-06 | 40640 | -11.3 |  | -15.7 | 27.5 | 20.7 | 20.1 | 20.1 | 20 | 20.3 |  | 17.4 | 17.8 | 17.1 | 17 | 17.4333
Iceland |  | RAUFARHOFN | RAUFARHOFN, Iceland | 66.45N | 15.95W | 8 | 0.00 (GMT) | 82-06 | 40770 | -15.7 |  | -20.3 | 25.9 | 18.2 | 18.9 | 17.9 | 18 | 18.3333 |  | 14.3 | 16 | 15.1 | 15 | 15.1333
Iceland |  | REYKJAVIK | REYKJAVIK, Iceland | 64.13N | 21.90W | 61 | 0.00 (GMT) | 82-06 | 40300 | -12.2 |  | -15.5 | 24.3 | 17.1 | 18.1 | 17.2 | 17 | 17.4667 |  | 14.8 | 16.1 | 15.5 | 15 | 15.4667
Iceland |  | VESTMANNAEYJAR | VESTMANNAEYJAR, Iceland | 63.40N | 20.28W | 124 | 0.00 (GMT) | 82-06 | 40480 | -9.2 |  | -13.7 | 20.4 | 13.6 | 15 | 16.2 | 15 | 14.9333 |  | 12 | 13.7 | 13.6 | 13 | 13.1
India |  | AGARTALA | AGARTALA, India | 23.88N | 91.25E | 16 | 5.50 (IND) | 88-06 | 427240 | 7.5 |  | 4.1 | 38 | 34.4 | 33.7 | 34 | 34 | 34.0333 |  | 33.4 | 32.7 | 32.9 | 33 | 33
India |  | AHMADABAD | AHMADABAD, India | 23.07N | 72.63E | 55 | 5.50 (IND) | 82-06 | 426470 | 7.1 |  | 2.8 | 47.6 | 42.9 | 38.1 | 35.7 | 39 | 38.9 |  | 41.1 | 36.2 | 33.7 | 37 | 37
India |  | AKOLA | AKOLA, India | 20.70N | 77.07E | 309 | 5.50 (IND) | 82-01 | 429340 | N/A |  | N/A | N/A | 43.5 | 36.2 | 34 | 38 | 37.9 |  | 41.3 | 34.2 | 32.3 | 36 | 35.9333
India |  | AURANGABAD CHIKALTH | AURANGABAD CHIKALTH, India | 19.85N | 75.40E | 579 | 5.50 (IND) | 82-06 | 430140 | 8.1 |  | 5 | 47.8 | 40.2 | 33.6 | 32 | 35 | 35.2667 |  | 38.4 | 32.1 | 30.2 | 34 | 33.5667
India |  | BALASORE | BALASORE, India | 21.52N | 86.93E | 20 | 5.50 (IND) | 82-06 | 428950 | 10.9 |  | 7.6 | 47.3 | 38.7 | 35.5 | 34.1 | 36 | 36.1 |  | 36.4 | 33.8 | 32.8 | 34 | 34.3333
India |  | BANGALORE | BANGALORE, India | 12.97N | 77.58E | 921 | 5.50 (IND) | 82-06 | 432950 | 13.2 |  | 10 | 38.4 | 32.4 | 30.2 | 29.4 | 31 | 30.6667 |  | 30.5 | 29.1 | 28.3 | 29 | 29.3
India |  | BELGAUM/SAMBRA | BELGAUM/SAMBRA, India | 15.85N | 74.62E | 747 | 5.50 (IND) | 82-06 | 431980 | N/A |  | N/A | N/A | 33.5 | 28.6 | 28.8 | 30 | 30.3 |  | 30.8 | 27.3 | 27.2 | 28 | 28.4333
India |  | BHOPAL/BAIRAGARH | BHOPAL/BAIRAGARH, India | 23.28N | 77.35E | 523 | 5.50 (IND) | 82-06 | 426670 | 7.6 |  | 4.6 | 45.3 | 42.6 | 35.8 | 32.5 | 37 | 36.9667 |  | 40.8 | 34 | 30.9 | 35 | 35.2333
India |  | BHUBANESWAR | BHUBANESWAR, India | 20.25N | 85.83E | 46 | 5.50 (IND) | 82-06 | 429710 | 11.4 |  | 8.7 | 47.2 | 40.1 | 35.3 | 33.7 | 36 | 36.3667 |  | 37.5 | 33.8 | 32.7 | 35 | 34.6667
India |  | BHUJ-RUDRAMATA | BHUJ-RUDRAMATA, India | 23.25N | 69.67E | 80 | 5.50 (IND) | 82-06 | 426340 | 6.3 |  | -0.9 | 48.6 | 42.2 | 38 | 36.1 | 39 | 38.7667 |  | 39.9 | 36.3 | 34.7 | 37 | 36.9667
India |  | BIKANER | BIKANER, India | 28.00N | 73.30E | 224 | 5.50 (IND) | 82-06 | 421650 | 3.3 |  | -0.4 | 48.8 | 45.1 | 42.1 | 40.4 | 43 | 42.5333 |  | 43.5 | 40.9 | 38.7 | 41 | 41.0333
India |  | BOMBAY/SANTACRUZ | BOMBAY/SANTACRUZ, India | 19.12N | 72.85E | 14 | 5.50 (IND) | 82-06 | 430030 | 13.5 |  | 10 | 42.2 | 34.3 | 32.1 | 32.1 | 33 | 32.8333 |  | 33.4 | 31.2 | 31.1 | 32 | 31.9
India |  | CALCUTTA/DUM DUM | CALCUTTA/DUM DUM, India | 22.65N | 88.45E | 6 | 5.50 (IND) | 82-06 | 428090 | 9.6 |  | 7 | 43.9 | 38.1 | 35.5 | 34.7 | 36 | 36.1 |  | 36.2 | 34.1 | 33.4 | 35 | 34.5667
India |  | CHITRADURGA | CHITRADURGA, India | 14.23N | 76.43E | 733 | 5.50 (IND) | 82-06 | 432330 | N/A |  | N/A | N/A | 33.3 | 30.9 | 29.9 | 31 | 31.3667 |  | 31.5 | 29.8 | 28.5 | 30 | 29.9333
India |  | COIMBATORE/PEELAMED | COIMBATORE/PEELAMED, India | 11.03N | 77.05E | 399 | 5.50 (IND) | 82-06 | 433210 | 15.9 |  | 11 | 41.1 | 34.8 | 32.8 | 32.9 | 34 | 33.5 |  | 33.2 | 31.6 | 31.8 | 32 | 32.2
India |  | CUDDALORE | CUDDALORE, India | 11.77N | 79.77E | 12 | 5.50 (IND) | 82-06 | 433290 | 17.8 |  | 14.9 | 43.3 | 38.7 | 37.6 | 37 | 38 | 37.7667 |  | 37.4 | 36.2 | 35.7 | 36 | 36.4333
India |  | CWC VISHAKHAPATNAM | CWC VISHAKHAPATNAM, India | 17.70N | 83.30E | 66 | 5.50 (IND) | 83-06 | 431500 | 17.4 |  | 10.7 | 43.1 | 35.8 | 34.3 | 33.6 | 35 | 34.5667 |  | 33.7 | 32.5 | 32 | 33 | 32.7333
India |  | GADAG | GADAG, India | 15.42N | 75.63E | 650 | 5.50 (IND) | 82-06 | 432010 | N/A |  | N/A | N/A | 34.8 | 31 | 31.2 | 32 | 32.3333 |  | 32.5 | 29.7 | 29.5 | 31 | 30.5667
India |  | GAUHATI | GAUHATI, India | 26.10N | 91.58E | 54 | 5.50 (IND) | 82-06 | 424100 | 8.8 |  | 5.9 | 41.5 | 34.5 | 35 | 35 | 35 | 34.8333 |  | 33.3 | 33.6 | 33.7 | 34 | 33.5333
India |  | GOA/PANJIM | GOA/PANJIM, India | 15.48N | 73.82E | 60 | 5.50 (IND) | 82-06 | 431920 | 17.4 |  | 12.7 | 39.1 | 33.7 | 31 | 30.4 | 32 | 31.7 |  | 32.6 | 30.2 | 29.7 | 31 | 30.8333
India |  | GWALIOR | GWALIOR, India | 26.23N | 78.25E | 207 | 5.50 (IND) | 82-06 | 423610 | N/A |  | N/A | N/A | 45.4 | 41.2 | 35.9 | 41 | 40.8333 |  | 43.6 | 39.4 | 34.3 | 39 | 39.1
India |  | HISSAR | HISSAR, India | 29.17N | 75.73E | 221 | 5.50 (IND) | 82-06 | 421310 | 4.2 |  | 1.1 | 49.5 | 46.1 | 42.8 | 39.9 | 43 | 42.9333 |  | 44.7 | 41.2 | 38.5 | 41 | 41.4667
India |  | HYDERABAD AIRPORT | HYDERABAD AIRPORT, India | 17.45N | 78.47E | 545 | 5.50 (IND) | 82-06 | 431280 | 11.1 |  | 6.8 | 44.3 | 40.4 | 34 | 32 | 35 | 35.4667 |  | 38 | 32.8 | 30.9 | 34 | 33.9
India |  | INDORE | INDORE, India | 22.72N | 75.80E | 567 | 5.50 (IND) | 82-06 | 427540 | 6 |  | 3.3 | 44.9 | 41 | 35.2 | 32 | 36 | 36.0667 |  | 39.1 | 33.2 | 30.1 | 34 | 34.1333
India |  | JABALPUR | JABALPUR, India | 23.20N | 79.95E | 393 | 5.50 (IND) | 82-06 | 426750 | N/A |  | N/A | N/A | 43.3 | 36.9 | 32.5 | 38 | 37.5667 |  | 42.1 | 35.1 | 31.2 | 36 | 36.1333
India |  | JAGDALPUR | JAGDALPUR, India | 19.08N | 82.03E | 553 | 5.50 (IND) | 82-06 | 430410 | N/A |  | N/A | N/A | 40.7 | 33 | 30.9 | 35 | 34.8667 |  | 38.1 | 31.1 | 29.9 | 33 | 33.0333
India |  | JAIPUR/SANGANER | JAIPUR/SANGANER, India | 26.82N | 75.80E | 390 | 5.50 (IND) | 82-06 | 423480 | 4.2 |  | 0.1 | 48.5 | 43.7 | 39.4 | 36.8 | 40 | 39.9667 |  | 42 | 37.9 | 34.7 | 38 | 38.2
India |  | JAMSHEDPUR | JAMSHEDPUR, India | 22.82N | 86.18E | 142 | 5.50 (IND) | 84-06 | 427980 | N/A |  | N/A | N/A | 43.7 | 35.6 | 34.7 | 38 | 38 |  | 41.5 | 34.1 | 33.3 | 36 | 36.3
India |  | JODHPUR | JODHPUR, India | 26.30N | 73.02E | 224 | 5.50 (IND) | 82-06 | 423390 | N/A |  | N/A | N/A | 43.6 | 40 | 37.5 | 40 | 40.3667 |  | 41.9 | 38.3 | 35.9 | 39 | 38.7
India |  | KAKINADA | KAKINADA, India | 16.95N | 82.23E | 8 | 5.50 (IND) | 82-06 | 431890 | 17.3 |  | 15.4 | 47.8 | 41.3 | 37.7 | 35.1 | 38 | 38.0333 |  | 38.7 | 35.6 | 34 | 36 | 36.1
India |  | KOZHIKODE | KOZHIKODE, India | 11.25N | 75.78E | 5 | 5.50 (IND) | 82-06 | 433140 | N/A |  | N/A | N/A | 32.9 | 30.8 | 30.5 | 31 | 31.4 |  | 31.9 | 30 | 29.9 | 31 | 30.6
India |  | KURNOOL | KURNOOL, India | 15.80N | 78.07E | 281 | 5.50 (IND) | 82-06 | 432130 | 14.5 |  | 13.1 | 45.5 | 40.9 | 36.1 | 34.7 | 37 | 37.2333 |  | 38.7 | 35.1 | 33.8 | 36 | 35.8667
India |  | LUCKNOW/AMAUSI | LUCKNOW/AMAUSI, India | 26.75N | 80.88E | 128 | 5.50 (IND) | 82-06 | 423690 | 4.8 |  | 1.4 | 46.8 | 43.8 | 40.1 | 35.9 | 40 | 39.9333 |  | 42 | 37.4 | 34.8 | 38 | 38.0667
India |  | MACHILIPATNAM | MACHILIPATNAM, India | 16.20N | 81.15E | 3 | 5.50 (IND) | 82-06 | 431850 | 16.1 |  | 9.5 | 49.9 | 42 | 37.8 | 35.3 | 38 | 38.3667 |  | 39.5 | 36 | 34.2 | 37 | 36.5667
India |  | MADRAS/MINAMBAKKAM | MADRAS/MINAMBAKKAM, India | 13.00N | 80.18E | 16 | 5.50 (IND) | 82-06 | 432790 | 18.5 |  | 16.5 | 45.5 | 39.2 | 37.7 | 36.6 | 38 | 37.8333 |  | 38 | 36.2 | 35.4 | 37 | 36.5333
India |  | MANGALORE/BAJPE | MANGALORE/BAJPE, India | 12.92N | 74.88E | 102 | 5.50 (IND) | 82-06 | 432840 | N/A |  | N/A | N/A | 32.6 | 30.4 | 30.3 | 31 | 31.1 |  | 31.1 | 29.7 | 29.5 | 30 | 30.1
India |  | NAGPUR SONEGAON | NAGPUR SONEGAON, India | 21.10N | 79.05E | 310 | 5.50 (IND) | 82-06 | 428670 | 8.8 |  | 5.4 | 47.9 | 44.5 | 36.7 | 33.2 | 38 | 38.1333 |  | 42.8 | 34.2 | 31.9 | 36 | 36.3
India |  | NELLORE | NELLORE, India | 14.45N | 79.98E | 20 | 5.50 (IND) | 82-06 | 432450 | 18.7 |  | 15 | 46.2 | 41.3 | 38.5 | 37.3 | 39 | 39.0333 |  | 39.4 | 37.4 | 36.4 | 38 | 37.7333
India |  | NEW DELHI/PALAM | NEW DELHI/PALAM, India | 28.57N | 77.12E | 233 | 5.50 (IND) | 96-06 | 421810 | N/A |  | N/A | N/A | 45 | 40.2 | 38.1 | 41 | 41.1 |  | 43.1 | 38.8 | 37.1 | 40 | 39.6667
India |  | NEW DELHI/SAFDARJUN | NEW DELHI/SAFDARJUN, India | 28.58N | 77.20E | 216 | 5.50 (IND) | 82-06 | 421820 | 4.4 |  | 0.1 | 47.1 | 44 | 40.4 | 37.5 | 41 | 40.6333 |  | 42.1 | 38.7 | 36 | 39 | 38.9333
India |  | PATIALA | PATIALA, India | 30.33N | 76.47E | 251 | 5.50 (IND) | 82-06 | 421010 | N/A |  | N/A | N/A | 43.1 | 37.8 | 35.2 | 39 | 38.7 |  | 41.5 | 36.5 | 34.3 | 37 | 37.4333
India |  | PATNA | PATNA, India | 25.60N | 85.10E | 60 | 5.50 (IND) | 82-06 | 424920 | 5.7 |  | 2.4 | 47.9 | 42.9 | 37.3 | 35.3 | 39 | 38.5 |  | 40.5 | 35.3 | 34.3 | 37 | 36.7
India |  | PBO ANANTAPUR | PBO ANANTAPUR, India | 14.58N | 77.63E | 364 | 5.50 (IND) | 82-06 | 432370 | 13.6 |  | 8.6 | 43.9 | 39.6 | 35.9 | 35 | 37 | 36.8333 |  | 37.3 | 34.8 | 33.7 | 35 | 35.2667
India |  | POONA | POONA, India | 18.53N | 73.85E | 559 | 5.50 (IND) | 82-06 | 430630 | 7.3 |  | 3.6 | 42.6 | 36.7 | 30.8 | 29.6 | 32 | 32.3667 |  | 34.4 | 29.5 | 28.2 | 31 | 30.7
India |  | RAJKOT | RAJKOT, India | 22.30N | 70.78E | 138 | 5.50 (IND) | 82-06 | 427370 | 9.2 |  | 5.7 | 45.8 | 41.1 | 36.4 | 34.9 | 37 | 37.4667 |  | 39.5 | 34.7 | 33.5 | 36 | 35.9
India |  | RATNAGIRI | RATNAGIRI, India | 16.98N | 73.33E | 67 | 5.50 (IND) | 82-06 | 431100 | 15.7 |  | 12.7 | 43.1 | 33.1 | 30.2 | 29.7 | 31 | 31 |  | 32.1 | 29.5 | 28.9 | 30 | 30.1667
India |  | SHOLAPUR | SHOLAPUR, India | 17.67N | 75.90E | 479 | 5.50 (IND) | 82-06 | 431170 | 12.8 |  | 6.4 | 45.1 | 40.2 | 34.4 | 33.3 | 36 | 35.9667 |  | 38.1 | 33.2 | 32.2 | 35 | 34.5
India |  | SURAT | SURAT, India | 21.20N | 72.83E | 12 | 5.50 (IND) | 82-06 | 428400 | 11.9 |  | 6 | 44.7 | 37.1 | 33.3 | 31.7 | 34 | 34.0333 |  | 34.9 | 32 | 31 | 33 | 32.6333
India |  | THIRUVANANTHAPURAM | THIRUVANANTHAPURAM, India | 8.48N | 76.95E | 64 | 5.50 (IND) | 82-06 | 433710 | 19 |  | 12.3 | 41.1 | 33 | 31.5 | 31.6 | 32 | 32.0333 |  | 31.5 | 30.7 | 30.8 | 31 | 31
India |  | TIRUCHCHIRAPALLI | TIRUCHCHIRAPALLI, India | 10.77N | 78.72E | 88 | 5.50 (IND) | 82-06 | 433440 | 18.4 |  | 16.2 | 42.5 | 38.9 | 38.1 | 37.6 | 38 | 38.2 |  | 37.8 | 37.1 | 36.6 | 37 | 37.1667
India |  | VERAVAL | VERAVAL, India | 20.90N | 70.37E | 8 | 5.50 (IND) | 82-06 | 429090 | 12 |  | 8.4 | 41.7 | 34.3 | 32.5 | 31.3 | 33 | 32.7 |  | 33.4 | 31.8 | 30.6 | 32 | 31.9333
Indonesia |  | DENPASAR/NGURAH RAI | DENPASAR/NGURAH RAI, Indonesia | 8.75S | 115.17E | 1 | 7.00 (SEA) | 82-06 | 972300 | 19.6 |  | 17.7 | 38.1 | 32.1 | 31.2 | 31.1 | 31 | 31.4667 |  | 31 | 30.1 | 30.1 | 30 | 30.4
Indonesia |  | JAKARTA/SOEKARNO-HA | JAKARTA/SOEKARNO-HA, Indonesia | 6.12S | 106.65E | 8 | 7.00 (SEA) | 88-05 | 967490 | 17.8 |  | 6 | 39.5 | 33.1 | 32.9 | 33.1 | 33 | 33.0333 |  | 32.2 | 32.1 | 32.2 | 32 | 32.1667
Indonesia |  | MEDAN/POLONIA | MEDAN/POLONIA, Indonesia | 3.57N | 98.68E | 25 | 7.00 (SEA) | 82-06 | 960350 | 21.3 |  | 20.5 | 39.1 | 34.7 | 34.8 | 34.8 | 35 | 34.7667 |  | 33.4 | 33.5 | 33.2 | 33 | 33.3667
Indonesia |  | MENADO/ SAM RATULAN | MENADO/ SAM RATULAN, Indonesia | 1.53N | 124.92E | 80 | 8.00 (CHN) | 82-06 | 970140 | N/A |  | N/A | N/A | 32.7 | 32.7 | 33.2 | 33 | 32.8667 |  | 32.1 | 32.1 | 32.6 | 32 | 32.2667
Indonesia |  | PADANG/TABING | PADANG/TABING, Indonesia | 0.88S | 100.35E | 3 | 7.00 (SEA) | 82-05 | 961630 | N/A |  | N/A | N/A | 32.2 | 31.9 | 31.7 | 32 | 31.9333 |  | 31.7 | 31.2 | 31.2 | 31 | 31.3667
Indonesia |  | PEKAN BARU/SIMPANGT | PEKAN BARU/SIMPANGT, Indonesia | 0.47N | 101.45E | 31 | 7.00 (SEA) | 83-06 | 961090 | N/A |  | N/A | N/A | 35 | 34.2 | 34.2 | 34 | 34.4667 |  | 34.1 | 33.5 | 33.5 | 34 | 33.7
Indonesia |  | RENGAT/JAPURA | RENGAT/JAPURA, Indonesia | 0.33S | 102.32E | 46 | 7.00 (SEA) | 82-06 | 961710 | 19.5 |  | 12.5 | 35.6 | 33.7 | 33.2 | 33.4 | 33 | 33.4333 |  | 33 | 32.5 | 32.7 | 33 | 32.7333
Indonesia |  | SIBOLGA/PINANGSORI | SIBOLGA/PINANGSORI, Indonesia | 1.55N | 98.88E | 3 | 7.00 (SEA) | 92-06 | 960730 | 18.5 |  | 13.6 | 35.8 | 33.1 | 32.7 | 32.3 | 33 | 32.7 |  | 32.3 | 32 | 31.7 | 32 | 32
Indonesia |  | SURABAYA/JUANDA | SURABAYA/JUANDA, Indonesia | 7.37S | 112.77E | 3 | 7.00 (SEA) | 84-06 | 969350 | 19 |  | 15.3 | 37.8 | 32.2 | 32.1 | 32.4 | 32 | 32.2333 |  | 31.9 | 31.3 | 31.9 | 32 | 31.7
Indonesia |  | UJUNG PANDANG/HASAN | UJUNG PANDANG/HASAN, Indonesia | 5.07S | 119.55E | 14 | 8.00 (CHN) | 82-06 | 971800 | 18.2 |  | 15.3 | 39.4 | 33.6 | 33.5 | 34.4 | 34 | 33.8333 |  | 32.7 | 32.6 | 33.2 | 33 | 32.8333
Iran |  | ABADAN | ABADAN, Iran, Islamic Republic of | 30.37N | 48.25E | 6 | 3.50 (IRN) | 92-06 | 408310 | 2.5 |  | -2.8 | 52.7 | 47.7 | 48.7 | 49.1 | 49 | 48.5 |  | 46.4 | 47.3 | 47.9 | 47 | 47.2
Iran |  | AHWAZ | AHWAZ, Iran, Islamic Republic of | 31.33N | 48.67E | 22 | 3.50 (IRN) | 90-06 | 408110 | 2.9 |  | -0.9 | 51.5 | 47.9 | 49 | 48.5 | 48 | 48.4667 |  | 46.2 | 47.8 | 47.4 | 47 | 47.1333
Iran |  | ANZALI | ANZALI, Iran, Islamic Republic of | 37.47N | 49.47E | -26 | 3.50 (IRN) | 90-06 | 407180 | -0.4 |  | -5.6 | 35.2 | 30 | 31.1 | 31.3 | 31 | 30.8 |  | 28.8 | 30.1 | 30.5 | 30 | 29.8
Iran |  | ARAK | ARAK, Iran, Islamic Republic of | 34.10N | 49.77E | 1708 | 3.50 (IRN) | 90-06 | 407690 | -14.8 |  | -27.7 | 42.3 | 36.1 | 38.2 | 37.3 | 37 | 37.2 |  | 34.5 | 36.6 | 36 | 36 | 35.7
Iran |  | BABULSAR | BABULSAR, Iran, Islamic Republic of | 36.72N | 52.65E | -21 | 3.50 (IRN) | 91-06 | 407360 | 0.5 |  | -1.7 | 38 | 31.8 | 32.8 | 33.6 | 33 | 32.7333 |  | 30.5 | 31.8 | 32.9 | 32 | 31.7333
Iran |  | BANDARABBASS | BANDARABBASS, Iran, Islamic Republic of | 27.22N | 56.37E | 10 | 3.50 (IRN) | 91-06 | 408750 | 6.6 |  | 3 | 46.7 | 43.2 | 43.2 | 42.8 | 43 | 43.0667 |  | 41.7 | 41.2 | 39.9 | 41 | 40.9333
Iran |  | BIRJAND | BIRJAND, Iran, Islamic Republic of | 32.87N | 59.20E | 1491 | 3.50 (IRN) | 90-06 | 408090 | -12.9 |  | -20.5 | 43.7 | 39.5 | 40.2 | 38.6 | 39 | 39.4333 |  | 37.5 | 38.5 | 36.6 | 38 | 37.5333
Iran |  | ESFAHAN | ESFAHAN, Iran, Islamic Republic of | 32.47N | 51.67E | 1550 | 3.50 (IRN) | 90-06 | 408000 | N/A |  | N/A | N/A | 38.9 | 40.3 | 39.1 | 39 | 39.4333 |  | 37.2 | 39.8 | 38 | 38 | 38.3333
Iran |  | HAMEDAN | HAMEDAN, Iran, Islamic Republic of | 34.85N | 48.53E | 1749 | 3.50 (IRN) | 96-06 | 407680 | N/A |  | N/A | N/A | 34.3 | 37.2 | 37.1 | 36 | 36.2 |  | 32.9 | 35.7 | 35.7 | 35 | 34.7667
Iran |  | KASHAN | KASHAN, Iran, Islamic Republic of | 33.98N | 51.45E | 982 | 3.50 (IRN) | 92-06 | 407850 | N/A |  | N/A | N/A | 41.6 | 43.8 | 42.9 | 43 | 42.7667 |  | 40.3 | 42.1 | 41.5 | 41 | 41.3
Iran |  | KERMAN | KERMAN, Iran, Islamic Republic of | 30.25N | 56.97E | 1754 | 3.50 (IRN) | 90-06 | 408410 | -11.4 |  | -18.7 | 43.2 | 38.9 | 39.3 | 38.1 | 39 | 38.7667 |  | 37.3 | 38.3 | 36.2 | 37 | 37.2667
Iran |  | KERMANSHAH | KERMANSHAH, Iran, Islamic Republic of | 34.27N | 47.12E | 1322 | 3.50 (IRN) | 90-06 | 407660 | -10.6 |  | -18.2 | 47 | 38.8 | 41.3 | 40.6 | 40 | 40.2333 |  | 37.1 | 40 | 39.5 | 39 | 38.8667
Iran |  | KHOY | KHOY, Iran, Islamic Republic of | 38.55N | 44.97E | 1103 | 3.50 (IRN) | 92-06 | 407030 | -17 |  | -28.5 | 42.5 | 34.7 | 36.4 | 37.6 | 36 | 36.2333 |  | 32.7 | 34.5 | 35.2 | 34 | 34.1333
Iran |  | MASHHAD | MASHHAD, Iran, Islamic Republic of | 36.27N | 59.63E | 999 | 3.50 (IRN) | 90-06 | 407450 | -10.1 |  | -19.2 | 43.2 | 38.7 | 39 | 38.6 | 39 | 38.7667 |  | 36.2 | 37.1 | 36.8 | 37 | 36.7
Iran |  | ORUMIEH | ORUMIEH, Iran, Islamic Republic of | 37.53N | 45.08E | 1316 | 3.50 (IRN) | 91-06 | 407120 | -12.5 |  | -20 | 39.2 | 32.2 | 34.4 | 35.2 | 34 | 33.9333 |  | 30.6 | 32.6 | 33.2 | 32 | 32.1333
Iran |  | RAMSAR | RAMSAR, Iran, Islamic Republic of | 36.90N | 50.67E | -20 | 3.50 (IRN) | 90-06 | 407320 | -0.3 |  | -2.5 | 38.5 | 30 | 31.2 | 31.6 | 31 | 30.9333 |  | 28.8 | 30.2 | 30.8 | 30 | 29.9333
Iran |  | SABZEVAR | SABZEVAR, Iran, Islamic Republic of | 36.22N | 57.67E | 978 | 3.50 (IRN) | 90-06 | 407430 | -7.6 |  | -12.7 | 45.1 | 40.9 | 42 | 40.6 | 41 | 41.1667 |  | 39 | 40.1 | 39 | 39 | 39.3667
Iran |  | SHAHRUD | SHAHRUD, Iran, Islamic Republic of | 36.42N | 54.95E | 1345 | 3.50 (IRN) | 90-06 | 407390 | N/A |  | N/A | N/A | 36.1 | 37.8 | 36.9 | 37 | 36.9333 |  | 34.4 | 35.8 | 35.4 | 35 | 35.2
Iran |  | SHIRAZ | SHIRAZ, Iran, Islamic Republic of | 29.53N | 52.53E | 1481 | 3.50 (IRN) | 90-06 | 408480 | -3.5 |  | -8.3 | 43.9 | 38.8 | 40.8 | 40 | 40 | 39.8667 |  | 37.2 | 39.6 | 38.7 | 39 | 38.5
Iran |  | TABRIZ | TABRIZ, Iran, Islamic Republic of | 38.08N | 46.28E | 1361 | 3.50 (IRN) | 90-06 | 407060 | -13.1 |  | -22.5 | 41.1 | 34.2 | 36.8 | 37.5 | 36 | 36.1667 |  | 32.9 | 35.2 | 35.9 | 35 | 34.6667
Iran |  | TEHRAN-MEHRABAD | TEHRAN-MEHRABAD, Iran, Islamic Republic of | 35.68N | 51.32E | 1191 | 3.50 (IRN) | 90-06 | 407540 | -5.4 |  | -13.1 | 43.6 | 38.1 | 40.2 | 39.6 | 39 | 39.3 |  | 36.9 | 39.1 | 38.1 | 38 | 38.0333
Iran |  | TORBAT-HEYDARIEH | TORBAT-HEYDARIEH, Iran, Islamic Republic of | 35.27N | 59.22E | 1451 | 3.50 (IRN) | 90-06 | 407620 | -13 |  | -18.9 | 40.2 | 35.9 | 36.7 | 35.2 | 36 | 35.9333 |  | 33.9 | 35 | 33.9 | 34 | 34.2667
Iran |  | ZAHEDAN | ZAHEDAN, Iran, Islamic Republic of | 29.47N | 60.88E | 1370 | 3.50 (IRN) | 90-06 | 408560 | -8.8 |  | -14.6 | 48.1 | 40.9 | 40.9 | 39.1 | 40 | 40.3 |  | 39 | 39.2 | 37.3 | 39 | 38.5
Iran |  | ZANJAN | ZANJAN, Iran, Islamic Republic of | 36.68N | 48.48E | 1663 | 3.50 (IRN) | 93-06 | 407290 | -17.1 |  | -28.4 | 39.2 | 34.6 | 35.2 | 35.6 | 35 | 35.1333 |  | 32.1 | 33.6 | 34.2 | 33 | 33.3
Ireland |  | BELMULLET | BELMULLET, Ireland | 54.23N | 10.00W | 10 | 0.00 (GMT) | 82-06 | 39760 | -2.9 |  | -7.4 | 30.1 | 22.9 | 23.9 | 23.1 | 23 | 23.3 |  | 19.2 | 20.9 | 20.4 | 20 | 20.1667
Ireland |  | BIRR | BIRR, Ireland | 53.08N | 7.88W | 72 | 0.00 (GMT) | 82-06 | 39650 | -6.6 |  | -12.8 | 31.9 | 24 | 27 | 25.1 | 25 | 25.3667 |  | 21.7 | 24.7 | 22.4 | 23 | 22.9333
Ireland |  | CASEMENT AERODROME | CASEMENT AERODROME, Ireland | 53.30N | 6.43W | 93 | 0.00 (GMT) | 87-06 | 39670 | -5.8 |  | -9.6 | 31.2 | 23.5 | 25.7 | 25.1 | 25 | 24.7667 |  | 21.2 | 23.5 | 22.6 | 22 | 22.4333
Ireland |  | CLAREMORRIS | CLAREMORRIS, Ireland | 53.72N | 8.98W | 69 | 0.00 (GMT) | 82-06 | 39700 | -6.3 |  | -12.5 | 32.1 | 24.4 | 25.7 | 25.4 | 25 | 25.1667 |  | 21.3 | 23.1 | 22.1 | 22 | 22.1667
Ireland |  | CLONES | CLONES, Ireland | 54.18N | 7.23W | 89 | 0.00 (GMT) | 82-06 | 39740 | -6.3 |  | -12.2 | 31.4 | 23.8 | 26.6 | 24.1 | 25 | 24.8333 |  | 21.2 | 23.9 | 21.5 | 22 | 22.2
Ireland |  | CONNAUGHT AIRPORT | CONNAUGHT AIRPORT, Ireland | 53.90N | 8.82W | 209 | 0.00 (GMT) | 96-06 | 39730 | -3.9 |  | -6.7 | 29.5 | 22 | 24.1 | 23 | 23 | 23.0333 |  | 19.2 | 20.9 | 19.8 | 20 | 19.9667
Ireland |  | CORK AIRPORT | CORK AIRPORT, Ireland | 51.85N | 8.48W | 162 | 0.00 (GMT) | 82-06 | 39550 | -3.2 |  | -7.2 | 28.6 | 22.7 | 24.2 | 23.5 | 23 | 23.4667 |  | 20 | 21.8 | 21.1 | 21 | 20.9667
Ireland |  | DUBLIN AIRPORT | DUBLIN AIRPORT, Ireland | 53.43N | 6.25W | 85 | 0.00 (GMT) | 82-06 | 39690 | -4.5 |  | -9.2 | 29 | 22.6 | 24.2 | 23.8 | 24 | 23.5333 |  | 20.3 | 22.3 | 21.8 | 21 | 21.4667
Ireland |  | KILKENNY | KILKENNY, Ireland | 52.67N | 7.27W | 64 | 0.00 (GMT) | 82-06 | 39600 | -6.5 |  | -11.7 | 32.3 | 24.1 | 28 | 25.6 | 26 | 25.9 |  | 22 | 24.9 | 23.1 | 23 | 23.3333
Ireland |  | MALIN HEAD | MALIN HEAD, Ireland | 55.37N | 7.33W | 25 | 0.00 (GMT) | 82-06 | 39800 | -1.9 |  | -5.9 | 25.8 | 20.2 | 21.5 | 22 | 21 | 21.2333 |  | 17.8 | 19.4 | 19.7 | 19 | 18.9667
Ireland |  | MULLINGAR | MULLINGAR, Ireland | 53.53N | 7.37W | 104 | 0.00 (GMT) | 82-06 | 39710 | -6.3 |  | -11.1 | 31.2 | 23.1 | 26.4 | 24.4 | 25 | 24.6333 |  | 21 | 23.8 | 21.6 | 22 | 22.1333
Ireland |  | ROCHES POINT | ROCHES POINT, Ireland | 51.80N | 8.25W | 41 | 0.00 (GMT) | 82-06 | 39520 | -1.2 |  | -6.6 | 28.1 | 21.1 | 23 | 22.1 | 22 | 22.0667 |  | 19 | 21.2 | 20.5 | 20 | 20.2333
Ireland |  | ROSSLARE | ROSSLARE, Ireland | 52.25N | 6.33W | 25 | 0.00 (GMT) | 82-06 | 39570 | -0.9 |  | -4.2 | 26.9 | 20.5 | 21.8 | 22.1 | 21 | 21.4667 |  | 18.5 | 20 | 20.2 | 20 | 19.5667
Ireland |  | SHANNON AIRPORT | SHANNON AIRPORT, Ireland | 52.70N | 8.92W | 20 | 0.00 (GMT) | 82-06 | 39620 | -4.1 |  | -8.2 | 32.1 | 25.4 | 26.2 | 25.7 | 26 | 25.7667 |  | 21.8 | 23.9 | 22.8 | 23 | 22.8333
Ireland |  | VALENTIA OBSERVATOR | VALENTIA OBSERVATOR, Ireland | 51.93N | 10.25W | 9 | 0.00 (GMT) | 82-06 | 39530 | -2.9 |  | -6.6 | 29.8 | 22.8 | 23.9 | 23.7 | 23 | 23.4667 |  | 19.6 | 21.3 | 20.6 | 21 | 20.5
Isle of Man |  | ISLE OF MAN/RONALDS | ISLE OF MAN/RONALDS, Isle of Man | 54.08N | 4.63W | 16 | 0.00 (GMT) | 82-06 | 32040 | -3.1 |  | -7.5 | 29.6 | 22 | 23.9 | 23.1 | 23 | 23 |  | 19.2 | 21.4 | 20.5 | 20 | 20.3667
Isle of Man |  | POINT OF AYRE (LH) | POINT OF AYRE (LH), Isle of Man | 54.42N | 4.37W | 9 | 0.00 (GMT) | 82-02 | 32080 | -2.1 |  | -6.8 | 27.4 | 21.2 | 22 | 22 | 22 | 21.7333 |  | 19 | 20.4 | 20.3 | 20 | 19.9
Israel |  | BEER-SHEVA | BEER-SHEVA, Israel | 31.23N | 34.78E | 280 | 2.00 (IST) | 87-05 | 401910 | 2.5 |  | -2.1 | 44 | 37.5 | 36.5 | 35.1 | 36 | 36.3667 |  | 33.8 | 34.6 | 33.5 | 34 | 33.9667
Israel |  | BEN-GURION INT. AIR | BEN-GURION INT. AIR, Israel | 32.00N | 34.90E | 49 | 2.00 (IST) | 82-06 | 401800 | 3 |  | -1.3 | 45.1 | 36.2 | 34.9 | 34.1 | 35 | 35.0667 |  | 32.2 | 33 | 32.9 | 33 | 32.7
Israel |  | EILAT | EILAT, Israel | 29.55N | 34.95E | 12 | 2.00 (IST) | 82-06 | 401990 | 5.5 |  | 2.2 | 48.2 | 43.2 | 44 | 43.3 | 44 | 43.5 |  | 41.6 | 42.2 | 42 | 42 | 41.9333
Israel |  | HAIFA | HAIFA, Israel | 32.80N | 35.03E | 9 | 2.00 (IST) | 89-05 | 401550 | 4.6 |  | 0.3 | 43.5 | 32.9 | 33.8 | 33.1 | 33 | 33.2667 |  | 30.6 | 32.1 | 31.9 | 32 | 31.5333
Israel |  | OVDA | OVDA, Israel | 30.00N | 34.83E | 445 | 2.00 (IST) | 83-06 | 401980 | 0.4 |  | -3.2 | 43 | 39.1 | 39.2 | 38.9 | 39 | 39.0667 |  | 37.1 | 37.9 | 37.1 | 37 | 37.3667
Israel |  | SDE-DOV (TEL-AVIV) | SDE-DOV (TEL-AVIV), Israel | 32.10N | 34.78E | 4 | 2.00 (IST) | 82-06 | 401760 | 5.4 |  | 1.2 | 45.8 | 31 | 31.1 | 31.3 | 31 | 31.1333 |  | 28.8 | 30.1 | 30.6 | 30 | 29.8333
Italy |  | ALGHERO | ALGHERO, Italy | 40.63N | 8.28E | 40 | 1.00 (EUW) | 82-06 | 165200 | -2.1 |  | -4.9 | 42.2 | 34.9 | 37.2 | 37 | 36 | 36.3667 |  | 32 | 34.3 | 34.2 | 34 | 33.5
Italy |  | AMENDOLA | AMENDOLA, Italy | 41.53N | 15.72E | 60 | 1.00 (EUW) | 82-06 | 162610 | -3.9 |  | -8.3 | 45.1 | 36.2 | 38.2 | 38 | 37 | 37.4667 |  | 33.9 | 36 | 35.4 | 35 | 35.1
Italy |  | AVIANO (USAF) | AVIANO (USAF), Italy | 46.02N | 12.62E | 126 | 1.00 (EUW) | 82-95 | 160365 | -8.8 |  | -14.3 | 38.5 | 30.9 | 33.1 | 34 | 33 | 32.6667 |  | 29 | 32 | 32.2 | 31 | 31.0667
Italy |  | BARI/PALESE MACCHIE | BARI/PALESE MACCHIE, Italy | 41.13N | 16.78E | 49 | 1.00 (EUW) | 82-06 | 162700 | -1.6 |  | -5.5 | 45.6 | 35 | 36.8 | 36.2 | 36 | 36 |  | 32 | 33.4 | 33.2 | 33 | 32.8667
Italy |  | BERGAMO/ORIO AL SER | BERGAMO/ORIO AL SER, Italy | 45.67N | 9.70E | 237 | 1.00 (EUW) | 82-06 | 160760 | -6.8 |  | -11 | 38.7 | 33.4 | 33.7 | 34.6 | 34 | 33.9 |  | 31.2 | 32 | 32.2 | 32 | 31.8
Italy |  | BOLOGNA/BORGO PANIG | BOLOGNA/BORGO PANIG, Italy | 44.53N | 11.30E | 49 | 1.00 (EUW) | 82-06 | 161400 | -6.9 |  | -12.3 | 40.8 | 34.2 | 36 | 36.2 | 35 | 35.4667 |  | 32.2 | 34.1 | 34.2 | 34 | 33.5
Italy |  | BOLZANO | BOLZANO, Italy | 46.47N | 11.33E | 241 | 1.00 (EUW) | 82-06 | 160200 | -10.5 |  | -16.1 | 42.4 | 33.9 | 35.5 | 35.5 | 35 | 34.9667 |  | 31.8 | 33 | 31.9 | 32 | 32.2333
Italy |  | BRESCIA/GHEDI | BRESCIA/GHEDI, Italy | 45.42N | 10.28E | 97 | 1.00 (EUW) | 82-06 | 160880 | -8.7 |  | -14.7 | 39.1 | 33.7 | 34.1 | 35 | 34 | 34.2667 |  | 31.8 | 32.7 | 33 | 33 | 32.5
Italy |  | BRINDISI | BRINDISI, Italy | 40.65N | 17.95E | 10 | 1.00 (EUW) | 82-06 | 163200 | 0.3 |  | -3.5 | 44.6 | 33.4 | 36.1 | 34.2 | 35 | 34.5667 |  | 30.9 | 32.8 | 32.2 | 32 | 31.9667
Italy |  | CAGLIARI/ELMAS | CAGLIARI/ELMAS, Italy | 39.25N | 9.07E | 5 | 1.00 (EUW) | 82-06 | 165600 | -1.6 |  | -4.1 | 43 | 34.2 | 36.9 | 36.9 | 36 | 36 |  | 31.5 | 34.1 | 34.1 | 33 | 33.2333
Italy |  | CAMPOBASSO | CAMPOBASSO, Italy | 41.57N | 14.65E | 807 | 1.00 (EUW) | 82-06 | 162520 | -5.5 |  | -11.9 | 38.2 | 31.1 | 33.2 | 33.1 | 32 | 32.4667 |  | 28.9 | 31.2 | 30.6 | 30 | 30.2333
Italy |  | CAPO BELLAVISTA | CAPO BELLAVISTA, Italy | 39.93N | 9.72E | 150 | 1.00 (EUW) | 91-06 | 165500 | 1.9 |  | -3.6 | 38.7 | 31.1 | 33 | 34.2 | 33 | 32.7667 |  | 29.2 | 31.2 | 32.4 | 31 | 30.9333
Italy |  | CAPO CACCIA | CAPO CACCIA, Italy | 40.57N | 8.17E | 204 | 1.00 (EUW) | 90-06 | 165220 | 1.8 |  | -4.3 | 41.7 | 32.3 | 33.5 | 34.1 | 33 | 33.3 |  | 29.8 | 31 | 31.8 | 31 | 30.8667
Italy |  | CAPO FRASCA | CAPO FRASCA, Italy | 39.75N | 8.47E | 95 | 1.00 (EUW) | 82-05 | 165390 | N/A |  | N/A | N/A | 31.6 | 33.5 | 35.2 | 33 | 33.4333 |  | 28.4 | 31 | 32.9 | 31 | 30.7667
Italy |  | CAPO MELE | CAPO MELE, Italy | 43.95N | 8.17E | 221 | 1.00 (EUW) | 82-06 | 161530 | -0.5 |  | -7.5 | 36.8 | 29.7 | 31.8 | 32.2 | 31 | 31.2333 |  | 27.4 | 30 | 30.1 | 29 | 29.1667
Italy |  | CAPO PALINURO | CAPO PALINURO, Italy | 40.02N | 15.28E | 185 | 1.00 (EUW) | 82-06 | 163100 | 1.1 |  | -3 | 38.9 | 32.3 | 32.9 | 31.8 | 32 | 32.3333 |  | 29.4 | 31 | 30.5 | 30 | 30.3
Italy |  | CATANIA/FONTANAROSS | CATANIA/FONTANAROSS, Italy | 37.47N | 15.05E | 17 | 1.00 (EUW) | 82-06 | 164600 | -0.7 |  | -3.6 | 46.6 | 35.3 | 38.1 | 37.2 | 37 | 36.8667 |  | 32.1 | 34.9 | 34.8 | 34 | 33.9333
Italy |  | CATANIA/SIGONELLA | CATANIA/SIGONELLA, Italy | 37.40N | 14.92E | 22 | 1.00 (EUW) | 82-06 | 164590 | -0.5 |  | -3.6 | 47.5 | 37.2 | 39.9 | 39 | 39 | 38.7 |  | 33.8 | 36 | 36 | 35 | 35.2667
Italy |  | CERVIA | CERVIA, Italy | 44.22N | 12.30E | 10 | 1.00 (EUW) | 92-06 | 161480 | -6.9 |  | -8.9 | 40.9 | 33.2 | 34.1 | 35.2 | 34 | 34.1667 |  | 32 | 32.2 | 33.9 | 33 | 32.7
Italy |  | COZZO SPADARO | COZZO SPADARO, Italy | 36.68N | 15.13E | 51 | 1.00 (EUW) | 82-06 | 164800 | 2.9 |  | -2.9 | 42.2 | 33.4 | 35.4 | 35.5 | 35 | 34.7667 |  | 30.1 | 32.8 | 32.7 | 32 | 31.8667
Italy |  | CROTONE | CROTONE, Italy | 39.00N | 17.07E | 161 | 1.00 (EUW) | 82-96 | 163500 | -0.8 |  | -6.4 | 45.6 | 34 | 38.4 | 35.2 | 36 | 35.8667 |  | 30.4 | 34.4 | 33.9 | 33 | 32.9
Italy |  | DOBBIACO | DOBBIACO, Italy | 46.73N | 12.22E | 1226 | 1.00 (EUW) | 91-06 | 160330 | -18.8 |  | -25 | 31.6 | 27.2 | 27.6 | 28.1 | 28 | 27.6333 |  | 25.2 | 25.6 | 26 | 26 | 25.6
Italy |  | FALCONARA | FALCONARA, Italy | 43.62N | 13.37E | 10 | 1.00 (EUW) | 82-06 | 161910 | -5.2 |  | -12.9 | 41.3 | 32.7 | 34.2 | 34.7 | 34 | 33.8667 |  | 30.1 | 32.2 | 32.1 | 31 | 31.4667
Italy |  | FIRENZE/PERETOLA | FIRENZE/PERETOLA, Italy | 43.80N | 11.20E | 38 | 1.00 (EUW) | 95-06 | 161700 | -5.9 |  | -9.8 | 41.6 | 35.7 | 37 | 37.2 | 37 | 36.6333 |  | 34 | 35 | 35.1 | 35 | 34.7
Italy |  | FORLI | FORLI, Italy | 44.20N | 12.07E | 32 | 1.00 (EUW) | 82-06 | 161470 | -7.9 |  | -13.1 | 40.4 | 34 | 35.1 | 36 | 35 | 35.0333 |  | 31.4 | 33 | 33.2 | 33 | 32.5333
Italy |  | FUCINO | FUCINO, Italy | 41.88N | 13.58E | 655 | 1.00 (EUW) | 84-06 | 162270 | -10.5 |  | -18.2 | 38.7 | 31.9 | 33.7 | 33.5 | 33 | 33.0333 |  | 29.6 | 31.6 | 31.6 | 31 | 30.9333
Italy |  | GELA | GELA, Italy | 37.08N | 14.22E | 65 | 1.00 (EUW) | 82-99 | 164530 | 3.7 |  | -1 | 36.6 | 30 | 30.7 | 31.2 | 31 | 30.6333 |  | 27.1 | 29.1 | 29.8 | 29 | 28.6667
Italy |  | GENOVA/SESTRI | GENOVA/SESTRI, Italy | 44.42N | 8.85E | 3 | 1.00 (EUW) | 82-06 | 161200 | -0.8 |  | -6.2 | 36.4 | 29.2 | 31.9 | 31.8 | 31 | 30.9667 |  | 27.8 | 29.9 | 30 | 29 | 29.2333
Italy |  | GIOIA DEL COLLE | GIOIA DEL COLLE, Italy | 40.77N | 16.93E | 350 | 1.00 (EUW) | 82-06 | 163120 | -4.8 |  | -9.7 | 43.7 | 35 | 37.8 | 36.8 | 37 | 36.5333 |  | 32.1 | 34.2 | 34 | 33 | 33.4333
Italy |  | GRAZZANISE | GRAZZANISE, Italy | 41.05N | 14.07E | 10 | 1.00 (EUW) | 82-06 | 162530 | -3.4 |  | -6.2 | 38.8 | 32.2 | 34.1 | 34.1 | 33 | 33.4667 |  | 30.8 | 32.1 | 32.2 | 32 | 31.7
Italy |  | GROSSETO | GROSSETO, Italy | 42.75N | 11.07E | 7 | 1.00 (EUW) | 82-06 | 162060 | -5.3 |  | -11.6 | 40.8 | 34.8 | 35.2 | 36.1 | 35 | 35.3667 |  | 31.7 | 33.3 | 33.9 | 33 | 32.9667
Italy |  | ISOLA DI CARLOFORTE | ISOLA DI CARLOFORTE, Italy | 39.13N | 8.32E | 12 | 1.00 (EUW) | 85-06 | 165490 | 4.2 |  | 0.3 | 37.8 | 31 | 34.1 | 33.5 | 33 | 32.8667 |  | 29.4 | 32.1 | 32.1 | 31 | 31.2
Italy |  | LAMEZIA TERME | LAMEZIA TERME, Italy | 38.90N | 16.25E | 15 | 1.00 (EUW) | 82-06 | 163620 | -2 |  | -5.2 | 40.8 | 32.2 | 34 | 33.2 | 33 | 33.1333 |  | 29.4 | 31.2 | 30.9 | 31 | 30.5
Italy |  | LAMPEDUSA | LAMPEDUSA, Italy | 35.50N | 12.60E | 20 | 1.00 (EUW) | 82-06 | 164900 | 8.2 |  | 4.6 | 39.4 | 33 | 33.5 | 33.9 | 33 | 33.4667 |  | 30 | 32 | 31.9 | 31 | 31.3
Italy |  | LATINA | LATINA, Italy | 41.55N | 12.90E | 26 | 1.00 (EUW) | 82-02 | 162430 | -2.5 |  | -5.6 | 41 | 31.2 | 34.1 | 34.9 | 33 | 33.4 |  | 29.2 | 32.2 | 33.1 | 32 | 31.5
Italy |  | LECCE | LECCE, Italy | 40.23N | 18.15E | 61 | 1.00 (EUW) | 82-94 | 163320 | N/A |  | N/A | N/A | 36.2 | 39.2 | 36.3 | 37 | 37.2333 |  | 32.8 | 36 | 35 | 35 | 34.6
Italy |  | MARINA DI GINOSA | MARINA DI GINOSA, Italy | 40.43N | 16.88E | 12 | 1.00 (EUW) | 82-06 | 163250 | -1.3 |  | -4.4 | 43.3 | 33.6 | 36.7 | 35.2 | 35 | 35.1667 |  | 30.9 | 33.9 | 33.2 | 33 | 32.6667
Italy |  | MESSINA | MESSINA, Italy | 38.20N | 15.55E | 51 | 1.00 (EUW) | 82-06 | 164200 | 3.9 |  | -1.2 | 43.8 | 34.6 | 35.1 | 34.9 | 35 | 34.8667 |  | 30.8 | 32.6 | 32.7 | 32 | 32.0333
Italy |  | MILANO/LINATE | MILANO/LINATE, Italy | 45.43N | 9.28E | 103 | 1.00 (EUW) | 82-06 | 160800 | -7.2 |  | -13.1 | 39.3 | 34.2 | 34.2 | 35.2 | 35 | 34.5333 |  | 32 | 32.8 | 32.9 | 33 | 32.5667
Italy |  | MILANO/MALPENSA | MILANO/MALPENSA, Italy | 45.62N | 8.73E | 211 | 1.00 (EUW) | 82-06 | 160660 | -12.1 |  | -17.5 | 37.8 | 32.8 | 33.9 | 33.1 | 33 | 33.2667 |  | 30.3 | 31.9 | 31.7 | 31 | 31.3
Italy |  | MONTE ARGENTARIO | MONTE ARGENTARIO, Italy | 42.38N | 11.17E | 631 | 1.00 (EUW) | 89-06 | 161680 | -4 |  | -8.6 | 39.4 | 32.2 | 33.2 | 34.8 | 33 | 33.4 |  | 30 | 31.1 | 31.8 | 31 | 30.9667
Italy |  | MONTE CIMONE | MONTE CIMONE, Italy | 44.20N | 10.70E | 2173 | 1.00 (EUW) | 82-06 | 161340 | -16.6 |  | -24.4 | 27.3 | 19.1 | 20.6 | 19.9 | 20 | 19.8667 |  | 17 | 18.8 | 18 | 18 | 17.9333
Italy |  | MONTE SCURO | MONTE SCURO, Italy | 39.33N | 16.40E | 1720 | 1.00 (EUW) | 88-06 | 163440 | -11.7 |  | -15.6 | 34.2 | 24.2 | 26.9 | 28 | 26 | 26.3667 |  | 22.1 | 24.2 | 25 | 24 | 23.7667
Italy |  | MONTE TERMINILLO | MONTE TERMINILLO, Italy | 42.47N | 12.98E | 1875 | 1.00 (EUW) | 82-06 | 162190 | -13.8 |  | -20.3 | 31.3 | 21.9 | 24.5 | 24.6 | 24 | 23.6667 |  | 19.4 | 22.6 | 22.9 | 22 | 21.6333
Italy |  | NAPLES | NAPLES, Italy | 40.90N | 14.30E | 93 | 1.00 (EUW) | 87-04 | 162894 | N/A |  | N/A | N/A | 34 | 35 | 35.9 | 35 | 34.9667 |  | 31.8 | 33.2 | 33.9 | 33 | 32.9667
Italy |  | NAPOLI/CAPODICHINO | NAPOLI/CAPODICHINO, Italy | 40.85N | 14.30E | 72 | 1.00 (EUW) | 82-06 | 162890 | -1.9 |  | -5.8 | 40.5 | 33.2 | 35.1 | 35.1 | 34 | 34.4667 |  | 31 | 33.1 | 33.1 | 32 | 32.4
Italy |  | NOVARA/CAMERI | NOVARA/CAMERI, Italy | 45.52N | 8.67E | 169 | 1.00 (EUW) | 82-02 | 160640 | -10.1 |  | -14.1 | 37.7 | 31.8 | 33 | 32.2 | 32 | 32.3333 |  | 29.4 | 31.3 | 31 | 31 | 30.5667
Italy |  | NOVI LIGURE | NOVI LIGURE, Italy | 44.77N | 8.78E | 187 | 1.00 (EUW) | 83-98 | 161180 | -8.4 |  | -15.8 | 35.2 | 30.9 | 32.8 | 32.9 | 32 | 32.2 |  | 29.1 | 31.6 | 31.5 | 31 | 30.7333
Italy |  | OLBIA/COSTA SMERALD | OLBIA/COSTA SMERALD, Italy | 40.90N | 9.52E | 13 | 1.00 (EUW) | 82-06 | 165310 | -1.5 |  | -4.8 | 43.3 | 34.6 | 36.9 | 37 | 36 | 36.1667 |  | 32.1 | 34.1 | 34.2 | 33 | 33.4667
Italy |  | PAGANELLA | PAGANELLA, Italy | 46.15N | 11.03E | 2129 | 1.00 (EUW) | 92-06 | 160220 | -16.7 |  | -22.9 | 27.6 | 19.9 | 20 | 20.2 | 20 | 20.0333 |  | 18.1 | 18.1 | 18.2 | 18 | 18.1333
Italy |  | PALERMO/PUNTA RAISI | PALERMO/PUNTA RAISI, Italy | 38.18N | 13.10E | 21 | 1.00 (EUW) | 82-06 | 164050 | 4.2 |  | -0.3 | 44.4 | 34.9 | 36.1 | 35.9 | 36 | 35.6333 |  | 31 | 32.8 | 33 | 32 | 32.2667
Italy |  | PANTELLERIA | PANTELLERIA, Italy | 36.82N | 11.97E | 170 | 1.00 (EUW) | 82-06 | 164700 | 4.7 |  | -0.8 | 43.9 | 38 | 37.9 | 36 | 37 | 37.3 |  | 33 | 34.9 | 32.7 | 34 | 33.5333
Italy |  | PASSO ROLLE | PASSO ROLLE, Italy | 46.30N | 11.78E | 2006 | 1.00 (EUW) | 92-06 | 160210 | -17.9 |  | -22 | 25.1 | 20.7 | 21.1 | 21.9 | 21 | 21.2333 |  | 19 | 19.9 | 20.1 | 20 | 19.6667
Italy |  | PERUGIA | PERUGIA, Italy | 43.08N | 12.50E | 205 | 1.00 (EUW) | 82-06 | 161810 | -8.4 |  | -19.4 | 41.6 | 33.8 | 36.3 | 35.1 | 35 | 35.0667 |  | 31 | 34.2 | 33.8 | 33 | 33
Italy |  | PESCARA | PESCARA, Italy | 42.43N | 14.20E | 11 | 1.00 (EUW) | 82-06 | 162300 | -4.4 |  | -10.3 | 40.9 | 32.9 | 35.1 | 35.8 | 35 | 34.6 |  | 30.8 | 33 | 32.2 | 32 | 32
Italy |  | PIACENZA | PIACENZA, Italy | 44.92N | 9.73E | 138 | 1.00 (EUW) | 82-03 | 160840 | -8.6 |  | -14.1 | 40.1 | 34 | 33.9 | 36.2 | 35 | 34.7 |  | 31.7 | 32.4 | 33.6 | 33 | 32.5667
Italy |  | PIAN ROSA | PIAN ROSA, Italy | 45.93N | 7.70E | 3488 | 1.00 (EUW) | 82-06 | 160520 | -26.7 |  | -34.7 | 19 | 9.7 | 10.8 | 10.8 | 10 | 10.4333 |  | 7.5 | 9.2 | 8.8 | 9 | 8.5
Italy |  | PISA/S. GIUSTO | PISA/S. GIUSTO, Italy | 43.68N | 10.38E | 6 | 1.00 (EUW) | 82-06 | 161580 | -5.5 |  | -11.2 | 38.6 | 32.5 | 34 | 34.2 | 34 | 33.5667 |  | 30.2 | 32.2 | 32.2 | 32 | 31.5333
Italy |  | PONZA | PONZA, Italy | 40.92N | 12.95E | 185 | 1.00 (EUW) | 82-06 | 162800 | 2.5 |  | -3.4 | 35.6 | 28.5 | 31.1 | 31.2 | 30 | 30.2667 |  | 27.1 | 29.6 | 29.6 | 29 | 28.7667
Italy |  | PRATICA DI MARE | PRATICA DI MARE, Italy | 41.65N | 12.45E | 21 | 1.00 (EUW) | 94-06 | 162450 | -1.9 |  | -6.5 | 38.7 | 31.1 | 32 | 33.2 | 32 | 32.1 |  | 30 | 30.4 | 31 | 30 | 30.4667
Italy |  | REGGIO CALABRIA | REGGIO CALABRIA, Italy | 38.07N | 15.65E | 21 | 1.00 (EUW) | 82-06 | 164220 | N/A |  | N/A | N/A | 36.9 | 38.2 | 35.8 | 37 | 36.9667 |  | 33.2 | 34.8 | 33.2 | 34 | 33.7333
Italy |  | RESIA PASS | RESIA PASS, Italy | 46.83N | 10.50E | 1800 | 1.00 (EUW) | 91-06 | 160083 | -15.3 |  | -24 | 33.5 | 26.9 | 27.2 | 28.8 | 28 | 27.6333 |  | 24.1 | 25 | 24.9 | 25 | 24.6667
Italy |  | RIMINI | RIMINI, Italy | 44.03N | 12.62E | 13 | 1.00 (EUW) | 82-06 | 161490 | -6.4 |  | -14 | 40.1 | 31.9 | 33.9 | 33.9 | 33 | 33.2333 |  | 30.1 | 31.9 | 31.8 | 31 | 31.2667
Italy |  | ROMA FIUMICINO | ROMA FIUMICINO, Italy | 41.80N | 12.23E | 3 | 1.00 (EUW) | 82-06 | 162420 | -3 |  | -7.1 | 38.9 | 31 | 32.2 | 33 | 32 | 32.0667 |  | 29.4 | 31 | 31.1 | 31 | 30.5
Italy |  | ROMA/CIAMPINO | ROMA/CIAMPINO, Italy | 41.78N | 12.58E | 105 | 1.00 (EUW) | 82-06 | 162390 | -3.4 |  | -8.6 | 40.1 | 33.7 | 35.1 | 35.2 | 35 | 34.6667 |  | 31.8 | 33.2 | 33.8 | 33 | 32.9333
Italy |  | RONCHI DEI LEGIONAR | RONCHI DEI LEGIONAR, Italy | 45.82N | 13.48E | 12 | 1.00 (EUW) | 82-06 | 161080 | -8.2 |  | -14.2 | 39.1 | 33.2 | 34.2 | 35 | 34 | 34.1333 |  | 30.9 | 32.7 | 33 | 32 | 32.2
Italy |  | S. MARIA DI LEUCA | S. MARIA DI LEUCA, Italy | 39.82N | 18.35E | 112 | 1.00 (EUW) | 82-06 | 163600 | 0.4 |  | -4.5 | 40 | 31.7 | 34.5 | 33.9 | 33 | 33.3667 |  | 29.6 | 32.1 | 31.7 | 31 | 31.1333
Italy |  | S. VALENTINO ALLA M | S. VALENTINO ALLA M, Italy | 46.75N | 10.53E | 1461 | 1.00 (EUW) | 91-06 | 160080 | -15.9 |  | -24 | 34.5 | 26.7 | 27.5 | 27.9 | 27 | 27.3667 |  | 23.9 | 24.8 | 24.3 | 24 | 24.3333
Italy |  | TORINO/BRIC DELLA C | TORINO/BRIC DELLA C, Italy | 45.03N | 7.73E | 710 | 1.00 (EUW) | 88-06 | 160610 | -6.1 |  | -10.8 | 33.8 | 29.1 | 29.9 | 30.8 | 30 | 29.9333 |  | 27.2 | 28.2 | 28.2 | 28 | 27.8667
Italy |  | TORINO/CASELLE | TORINO/CASELLE, Italy | 45.22N | 7.65E | 287 | 1.00 (EUW) | 82-06 | 160590 | -8.3 |  | -13.4 | 37.6 | 31.8 | 33 | 32.7 | 33 | 32.5 |  | 29.8 | 31.1 | 30.4 | 30 | 30.4333
Italy |  | TRAPANI/BIRGI | TRAPANI/BIRGI, Italy | 37.92N | 12.50E | 14 | 1.00 (EUW) | 82-06 | 164290 | 1.6 |  | -1.6 | 44.1 | 36.1 | 37.2 | 36.3 | 37 | 36.5333 |  | 32 | 34.1 | 33.2 | 33 | 33.1
Italy |  | TREVISO/ISTRANA | TREVISO/ISTRANA, Italy | 45.68N | 12.10E | 46 | 1.00 (EUW) | 82-06 | 160980 | -8.3 |  | -12.8 | 39 | 34.1 | 34.9 | 36.1 | 35 | 35.0333 |  | 31.9 | 33.1 | 33.5 | 33 | 32.8333
Italy |  | TREVISO/S. ANGELO | TREVISO/S. ANGELO, Italy | 45.65N | 12.18E | 23 | 1.00 (EUW) | 82-06 | 160990 | -7.7 |  | -13.2 | 39.5 | 33.9 | 34.1 | 35.1 | 34 | 34.3667 |  | 31.1 | 32.2 | 33.2 | 32 | 32.1667
Italy |  | TRIESTE | TRIESTE, Italy | 45.65N | 13.75E | 20 | 1.00 (EUW) | 90-06 | 161100 | -4.2 |  | -9.2 | 40.3 | 32.1 | 33.8 | 33.2 | 33 | 33.0333 |  | 30 | 31.2 | 31.5 | 31 | 30.9
Italy |  | UDINE/RIVOLTO | UDINE/RIVOLTO, Italy | 45.98N | 13.03E | 53 | 1.00 (EUW) | 82-99 | 160450 | -8.5 |  | -14.4 | 38.8 | 31.8 | 33.8 | 34.8 | 33 | 33.4667 |  | 29.9 | 32.2 | 32.8 | 32 | 31.6333
Italy |  | USTICA | USTICA, Italy | 38.70N | 13.18E | 251 | 1.00 (EUW) | 82-96 | 164000 | 2.5 |  | -2 | 39.3 | 30 | 33.7 | 32.7 | 32 | 32.1333 |  | 27.3 | 31.2 | 31 | 30 | 29.8333
Italy |  | VENEZIA/TESSERA | VENEZIA/TESSERA, Italy | 45.50N | 12.33E | 6 | 1.00 (EUW) | 82-06 | 161050 | -6.5 |  | -11.3 | 37.9 | 31.2 | 32.8 | 33 | 32 | 32.3333 |  | 29.2 | 31 | 31.2 | 30 | 30.4667
Italy |  | VERONA/VILLAFRANCA | VERONA/VILLAFRANCA, Italy | 45.38N | 10.87E | 68 | 1.00 (EUW) | 82-06 | 160900 | -8.2 |  | -15.3 | 39.2 | 33.9 | 34.8 | 35.2 | 35 | 34.6333 |  | 31.9 | 33 | 33.2 | 33 | 32.7
Jamaica |  | KINGSTON/NORMAN MAN | KINGSTON/NORMAN MAN, Jamaica | 17.93N | 76.78W | 14 | -5.00 (SAP) | 82-06 | 783970 | 20.4 |  | 17 | 37.4 | 33.9 | 34.2 | 34 | 34 | 34.0333 |  | 33 | 33.2 | 33.1 | 33 | 33.1
Jamaica |  | MONTEGO BAY/SANGSTE | MONTEGO BAY/SANGSTE, Jamaica | 18.50N | 77.92W | 8 | -5.00 (SAP) | 82-06 | 783880 | 20.3 |  | 15.7 | 36.9 | 33.1 | 33.1 | 33.1 | 33 | 33.1 |  | 32.2 | 32.2 | 32.2 | 32 | 32.2
Japan |  | ABASHIRI | ABASHIRI, Japan | 44.02N | 144.28E | 43 | 9.00 (JPN) | 82-06 | 474090 | -16.9 |  | -22.9 | 38 | 25.8 | 30.5 | 30.9 | 29 | 29.0667 |  | 23.1 | 26.9 | 28.2 | 26 | 26.0667
Japan |  | ABURATSU | ABURATSU, Japan | 31.58N | 131.40E | 15 | 9.00 (JPN) | 94-06 | 478350 | -1 |  | -2.6 | 37.7 | 32.2 | 34.2 | 34.6 | 34 | 33.6667 |  | 30.6 | 32.9 | 33 | 32 | 32.1667
Japan |  | AIKAWA | AIKAWA, Japan | 38.03N | 138.23E | 17 | 9.00 (JPN) | 82-06 | 476020 | -3.3 |  | -7.5 | 43.3 | 27.2 | 32.9 | 33.8 | 31 | 31.3 |  | 25.5 | 30.2 | 31.7 | 29 | 29.1333
Japan |  | AJIRO | AJIRO, Japan | 35.05N | 139.10E | 68 | 9.00 (JPN) | 94-06 | 476680 | -0.6 |  | -2.7 | 36 | 30.7 | 33.8 | 34 | 33 | 32.8333 |  | 28.3 | 32.2 | 32.4 | 31 | 30.9667
Japan |  | AKITA | AKITA, Japan | 39.72N | 140.10E | 21 | 9.00 (JPN) | 82-06 | 475820 | -7.5 |  | -11.6 | 37.8 | 28.5 | 33.4 | 34.1 | 32 | 32 |  | 26.5 | 30.8 | 32.2 | 30 | 29.8333
Japan |  | AKUNE | AKUNE, Japan | 32.03N | 130.20E | 45 | 9.00 (JPN) | 93-06 | 478230 | -0.5 |  | -2.6 | 36.2 | 30.4 | 33 | 33.7 | 32 | 32.3667 |  | 28.6 | 31.5 | 32.3 | 31 | 30.8
Japan |  | AOMORI | AOMORI, Japan | 40.82N | 140.77E | 3 | 9.00 (JPN) | 82-06 | 475750 | -9.2 |  | -12.7 | 37.3 | 28.1 | 31.9 | 32.9 | 31 | 30.9667 |  | 25.3 | 29.5 | 30.7 | 29 | 28.5
Japan |  | ASAHIKAWA | ASAHIKAWA, Japan | 43.77N | 142.37E | 116 | 9.00 (JPN) | 82-06 | 474070 | -22.2 |  | -28.5 | 36.3 | 28.3 | 31.7 | 32.4 | 31 | 30.8 |  | 26.7 | 29.6 | 30.5 | 29 | 28.9333
Japan |  | ASHIYA AB | ASHIYA AB, Japan | 33.88N | 130.65E | 33 | 9.00 (JPN) | 82-06 | 478030 | -3 |  | -5.3 | 36.3 | 30.9 | 33.1 | 34.2 | 33 | 32.7333 |  | 28.9 | 32 | 33 | 31 | 31.3
Japan |  | ASOSAN | ASOSAN, Japan | 32.88N | 131.07E | 1144 | 9.00 (JPN) | 94-06 | 478210 | -11.3 |  | -14.8 | 29.5 | 23.7 | 27.5 | 26.7 | 26 | 25.9667 |  | 22.3 | 26.1 | 25.6 | 25 | 24.6667
Japan |  | ATSUGI NAS | ATSUGI NAS, Japan | 35.45N | 139.45E | 65 | 9.00 (JPN) | 82-06 | 476790 | -3.8 |  | -6.9 | 39 | 31.1 | 34.8 | 34.8 | 34 | 33.5667 |  | 29 | 32.8 | 33 | 32 | 31.6
Japan |  | CHIBA | CHIBA, Japan | 35.60N | 140.10E | 19 | 9.00 (JPN) | 91-06 | 476820 | -1.3 |  | -3.2 | 38.4 | 30.4 | 33.9 | 34.3 | 33 | 32.8667 |  | 28.6 | 32.2 | 32.6 | 31 | 31.1333
Japan |  | CHICHIBU | CHICHIBU, Japan | 35.98N | 139.07E | 234 | 9.00 (JPN) | 91-06 | 476410 | -7.8 |  | -9.6 | 38.9 | 32.7 | 36.1 | 36 | 35 | 34.9333 |  | 30.3 | 34.6 | 34.2 | 33 | 33.0333
Japan |  | CHICHIJIMA ISLAND | CHICHIJIMA ISLAND, Japan | 27.08N | 142.18E | 8 | 9.00 (JPN) | 82-06 | 479710 | 11.3 |  | 9.1 | 34.3 | 30.5 | 31.6 | 31.2 | 31 | 31.1 |  | 29.6 | 30.6 | 30.4 | 30 | 30.2
Japan |  | CHITOSE (JASDF) | CHITOSE (JASDF), Japan | 42.82N | 141.68E | 27 | 9.00 (JPN) | 88-06 | 474340 | -21.6 |  | -28.3 | 34.5 | 25.2 | 28.2 | 30.9 | 28 | 28.1 |  | 23.2 | 26.8 | 28 | 26 | 26
Japan |  | CHITOSE AB | CHITOSE AB, Japan | 42.80N | 141.67E | 30 | 9.00 (JPN) | 82-06 | 474250 | -23 |  | -29.5 | 34.6 | 25.2 | 28.5 | 30.2 | 28 | 27.9667 |  | 23.1 | 26.2 | 28.1 | 26 | 25.8
Japan |  | CHOSHI | CHOSHI, Japan | 35.73N | 140.85E | 28 | 9.00 (JPN) | 82-06 | 476480 | -1.8 |  | -4.8 | 35.1 | 26.7 | 30.3 | 31 | 29 | 29.3333 |  | 25.2 | 29 | 29.9 | 28 | 28.0333
Japan |  | ESASHI | ESASHI, Japan | 41.87N | 140.12E | 12 | 9.00 (JPN) | 82-06 | 474280 | -8.8 |  | -13.4 | 34.5 | 23.7 | 28.4 | 29.6 | 27 | 27.2333 |  | 21.8 | 26.3 | 28.2 | 25 | 25.4333
Japan |  | FUJISAN | FUJISAN, Japan | 35.37N | 138.73E | 3773 | 9.00 (JPN) | 85-06 | 476390 | -32.1 |  | -37.3 | 18.4 | 8.5 | 12.5 | 13.3 | 11 | 11.4333 |  | 6.8 | 10.5 | 11.5 | 10 | 9.6
Japan |  | FUKAURA | FUKAURA, Japan | 40.65N | 139.93E | 67 | 9.00 (JPN) | 82-06 | 475740 | -7.1 |  | -10.7 | 36 | 25.4 | 29.7 | 31.5 | 29 | 28.8667 |  | 23.5 | 27.7 | 29.6 | 27 | 26.9333
Japan |  | FUKUE | FUKUE, Japan | 32.70N | 128.83E | 26 | 9.00 (JPN) | 82-06 | 478430 | -1.5 |  | -3.6 | 35.6 | 28.7 | 32.2 | 32.7 | 31 | 31.2 |  | 27.2 | 31.2 | 31.7 | 30 | 30.0333
Japan |  | FUKUI | FUKUI, Japan | 36.05N | 136.22E | 17 | 9.00 (JPN) | 91-06 | 476160 | -3.5 |  | -6.1 | 38.3 | 31.5 | 35 | 35.4 | 34 | 33.9667 |  | 29.7 | 33.7 | 34.3 | 33 | 32.5667
Japan |  | FUKUOKA | FUKUOKA, Japan | 33.58N | 130.38E | 15 | 9.00 (JPN) | 82-06 | 478070 | -1.1 |  | -3.7 | 38.2 | 31.9 | 34.2 | 34.9 | 34 | 33.6667 |  | 30 | 33.2 | 33.7 | 32 | 32.3
Japan |  | FUKUOKA AIRPORT | FUKUOKA AIRPORT, Japan | 33.58N | 130.45E | 12 | 9.00 (JPN) | 82-06 | 478080 | -2.8 |  | -6.3 | 38.1 | 32 | 34.8 | 35.2 | 34 | 34 |  | 30.1 | 33.2 | 34.1 | 32 | 32.4667
Japan |  | FUKUSHIMA | FUKUSHIMA, Japan | 37.77N | 140.47E | 69 | 9.00 (JPN) | 82-06 | 475950 | -6.1 |  | -9 | 39 | 31.8 | 35.1 | 35.4 | 34 | 34.1 |  | 29.6 | 33.2 | 33.8 | 32 | 32.2
Japan |  | FUKUYAMA | FUKUYAMA, Japan | 34.45N | 133.25E | 3 | 9.00 (JPN) | 94-06 | 477670 | -4.8 |  | -7.1 | 37.8 | 31.6 | 35 | 35.4 | 34 | 34 |  | 29.7 | 33.5 | 34.3 | 33 | 32.5
Japan |  | FUSHIKI | FUSHIKI, Japan | 36.80N | 137.05E | 13 | 9.00 (JPN) | 91-06 | 476060 | -4.1 |  | -7.1 | 40.5 | 30.7 | 35.1 | 35.7 | 34 | 33.8333 |  | 28.5 | 33.2 | 33.8 | 32 | 31.8333
Japan |  | FUTENMA | FUTENMA, Japan | 26.27N | 127.75E | 84 | 9.00 (JPN) | 82-06 | 479330 | 9.2 |  | 6.5 | 36.8 | 32.2 | 33.2 | 33 | 33 | 32.8 |  | 31.2 | 32.2 | 32.1 | 32 | 31.8333
Japan |  | GIFU | GIFU, Japan | 35.40N | 136.77E | 17 | 9.00 (JPN) | 91-06 | 476320 | -3.8 |  | -7 | 40.5 | 32.7 | 36.5 | 37.4 | 36 | 35.5333 |  | 30.9 | 35 | 35.5 | 34 | 33.8
Japan |  | GIFU AB | GIFU AB, Japan | 35.38N | 136.87E | 42 | 9.00 (JPN) | 82-06 | 476340 | -6.2 |  | -9.5 | 39.9 | 32.1 | 35.8 | 36.8 | 35 | 34.9 |  | 30.1 | 34.1 | 34.9 | 33 | 33.0333
Japan |  | HABORO | HABORO, Japan | 44.37N | 141.70E | 10 | 9.00 (JPN) | 92-06 | 474040 | -18.9 |  | -24.5 | 35 | 24.9 | 28 | 29.6 | 28 | 27.5 |  | 22 | 25.9 | 27.2 | 25 | 25.0333
Japan |  | HACHIJOJIMA | HACHIJOJIMA, Japan | 33.12N | 139.78E | 80 | 9.00 (JPN) | 82-06 | 476780 | 2.4 |  | -1.4 | 32.6 | 27 | 30.1 | 31.1 | 29 | 29.4 |  | 26 | 29.4 | 30.1 | 29 | 28.5
Japan |  | HACHINOHE | HACHINOHE, Japan | 40.53N | 141.52E | 28 | 9.00 (JPN) | 82-06 | 475810 | -9.5 |  | -13.3 | 37.3 | 28.5 | 32.6 | 33 | 31 | 31.3667 |  | 25.7 | 30.2 | 30.9 | 29 | 28.9333
Japan |  | HACHINOHE AB | HACHINOHE AB, Japan | 40.55N | 141.47E | 49 | 9.00 (JPN) | 82-06 | 475150 | -10.4 |  | -14.5 | 36.6 | 28.2 | 32.8 | 33 | 31 | 31.3333 |  | 25.8 | 30.1 | 30.9 | 29 | 28.9333
Japan |  | HAGI | HAGI, Japan | 34.42N | 131.40E | 7 | 9.00 (JPN) | 93-06 | 477540 | -1.7 |  | -4.9 | 37.8 | 32 | 34.2 | 34.7 | 34 | 33.6333 |  | 29.4 | 32.6 | 33.4 | 32 | 31.8
Japan |  | HAKODATE | HAKODATE, Japan | 41.82N | 140.75E | 43 | 9.00 (JPN) | 82-06 | 474300 | -12.3 |  | -16.5 | 33.7 | 25 | 29 | 30.2 | 28 | 28.0667 |  | 23 | 27.1 | 28.8 | 26 | 26.3
Japan |  | HAMADA | HAMADA, Japan | 34.90N | 132.07E | 20 | 9.00 (JPN) | 82-06 | 477550 | -2.3 |  | -5.8 | 37.3 | 29.4 | 32.7 | 34 | 32 | 32.0333 |  | 27.7 | 31 | 32.1 | 30 | 30.2667
Japan |  | HAMAMATSU | HAMAMATSU, Japan | 34.72N | 137.72E | 33 | 9.00 (JPN) | 91-06 | 476540 | -1.8 |  | -5 | 38.7 | 31.4 | 35 | 35.1 | 34 | 33.8333 |  | 29 | 32.4 | 33 | 31 | 31.4667
Japan |  | HAMAMATSU AB | HAMAMATSU AB, Japan | 34.75N | 137.70E | 48 | 9.00 (JPN) | 82-06 | 476810 | -3.1 |  | -5.4 | 39.4 | 31.1 | 34.9 | 35.1 | 34 | 33.7 |  | 28.9 | 32.8 | 33 | 32 | 31.5667
Japan |  | HIKONE | HIKONE, Japan | 35.28N | 136.25E | 89 | 9.00 (JPN) | 93-06 | 477610 | -3.6 |  | -6.5 | 37.5 | 30.6 | 34.1 | 34.6 | 33 | 33.1 |  | 28.6 | 32.9 | 33.4 | 32 | 31.6333
Japan |  | HIMEJI | HIMEJI, Japan | 34.83N | 134.67E | 40 | 9.00 (JPN) | 94-06 | 477690 | -4.5 |  | -7.1 | 37 | 30.8 | 34.4 | 35.1 | 33 | 33.4333 |  | 29.1 | 33.1 | 33.8 | 32 | 32
Japan |  | HIRADO | HIRADO, Japan | 33.37N | 129.55E | 59 | 9.00 (JPN) | 93-06 | 478050 | -0.9 |  | -4.1 | 34.2 | 27.2 | 31.4 | 32.1 | 30 | 30.2333 |  | 25.9 | 30.2 | 31.1 | 29 | 29.0667
Japan |  | HIROO | HIROO, Japan | 42.30N | 143.32E | 33 | 9.00 (JPN) | 92-06 | 474400 | -15.2 |  | -20.3 | 35.1 | 27 | 29.8 | 30.5 | 29 | 29.1 |  | 22.7 | 26.6 | 27.2 | 26 | 25.5
Japan |  | HIROSHIMA | HIROSHIMA, Japan | 34.40N | 132.47E | 53 | 9.00 (JPN) | 82-06 | 477650 | -2.8 |  | -5.9 | 39 | 31 | 34.6 | 34.8 | 33 | 33.4667 |  | 29.2 | 33.2 | 33.7 | 32 | 32.0333
Japan |  | HITA | HITA, Japan | 33.32N | 130.93E | 84 | 9.00 (JPN) | 93-06 | 478140 | -5.5 |  | -8.5 | 39.1 | 33.1 | 36.6 | 36.2 | 35 | 35.3 |  | 31.7 | 35.1 | 35.2 | 34 | 34
Japan |  | HITOYOSHI | HITOYOSHI, Japan | 32.22N | 130.75E | 147 | 9.00 (JPN) | 93-06 | 478240 | -5.6 |  | -8 | 37.4 | 31.6 | 34.6 | 34.6 | 34 | 33.6 |  | 30.2 | 33.4 | 33.5 | 32 | 32.3667
Japan |  | HOFU AB | HOFU AB, Japan | 34.03N | 131.55E | 5 | 9.00 (JPN) | 82-06 | 477880 | -4.5 |  | -8.8 | 37.4 | 30.2 | 34 | 34.1 | 33 | 32.7667 |  | 28.8 | 32.2 | 32.9 | 31 | 31.3
Japan |  | HYAKURI AB | HYAKURI AB, Japan | 36.18N | 140.42E | 35 | 9.00 (JPN) | 82-06 | 477150 | -9.5 |  | -12.4 | 38 | 30.1 | 34 | 33.9 | 33 | 32.6667 |  | 28.1 | 32 | 32.2 | 31 | 30.7667
Japan |  | IIDA | IIDA, Japan | 35.52N | 137.82E | 529 | 9.00 (JPN) | 82-06 | 476370 | -9.2 |  | -12.8 | 38.1 | 30.7 | 34.2 | 34.5 | 33 | 33.1333 |  | 28.7 | 32.6 | 33 | 31 | 31.4333
Japan |  | IIZUKA | IIZUKA, Japan | 33.65N | 130.70E | 38 | 9.00 (JPN) | 93-06 | 478090 | -3.7 |  | -5.2 | 37.3 | 31.7 | 34.9 | 35 | 34 | 33.8667 |  | 30.1 | 33.5 | 33.8 | 32 | 32.4667
Japan |  | IRAKO | IRAKO, Japan | 34.63N | 137.10E | 8 | 9.00 (JPN) | 91-06 | 476530 | -1.3 |  | -3.9 | 38.2 | 30.9 | 34.1 | 34.7 | 33 | 33.2333 |  | 28.7 | 32.5 | 32.9 | 31 | 31.3667
Japan |  | IROZAKI | IROZAKI, Japan | 34.60N | 138.85E | 56 | 9.00 (JPN) | 91-06 | 476660 | 0.8 |  | -2.4 | 33.9 | 26.8 | 30.2 | 30.6 | 29 | 29.2 |  | 25.6 | 29.2 | 29.8 | 28 | 28.2
Japan |  | IRUMA AB | IRUMA AB, Japan | 35.83N | 139.42E | 93 | 9.00 (JPN) | 82-06 | 476430 | -6.2 |  | -9.7 | 39.7 | 32.1 | 35.9 | 35.2 | 34 | 34.4 |  | 29.8 | 33.9 | 33.9 | 33 | 32.5333
Japan |  | ISHIGAKIJIMA | ISHIGAKIJIMA, Japan | 24.33N | 124.17E | 6 | 9.00 (JPN) | 82-06 | 479180 | 11.1 |  | 8.3 | 35.9 | 32 | 33.2 | 33.1 | 33 | 32.7667 |  | 31.3 | 32.6 | 32.2 | 32 | 32.0333
Japan |  | ISHINOMAKI | ISHINOMAKI, Japan | 38.43N | 141.30E | 43 | 9.00 (JPN) | 91-06 | 475920 | -7 |  | -10.4 | 35.5 | 27.2 | 31 | 31.3 | 30 | 29.8333 |  | 24.9 | 28.9 | 29.6 | 28 | 27.8
Japan |  | IWAKUNI | IWAKUNI, Japan | 34.15N | 132.23E | 3 | 9.00 (JPN) | 82-04 | 477640 | -3.2 |  | -6.4 | 37.2 | 29.9 | 33.8 | 33.9 | 33 | 32.5333 |  | 27.9 | 32.1 | 32.2 | 31 | 30.7333
Japan |  | IWAMIZAWA | IWAMIZAWA, Japan | 43.22N | 141.78E | 51 | 9.00 (JPN) | 91-06 | 474130 | -17.6 |  | -23.2 | 35.7 | 27.3 | 29.9 | 31.9 | 30 | 29.7 |  | 25.2 | 28.2 | 29.4 | 28 | 27.6
Japan |  | IWOJIMA | IWOJIMA, Japan | 24.78N | 141.32E | 116 | 10.00 (PCW) | 85-06 | 479810 | 14.6 |  | 11.3 | 33.4 | 30.8 | 31.8 | 31.2 | 31 | 31.2667 |  | 30 | 31 | 30.7 | 31 | 30.5667
Japan |  | IZUHARA | IZUHARA, Japan | 34.20N | 129.30E | 19 | 9.00 (JPN) | 82-06 | 478000 | -3.3 |  | -6.8 | 37.2 | 28.4 | 32 | 32.6 | 31 | 31 |  | 26.8 | 30.8 | 31.5 | 30 | 29.7
Japan |  | KADENA (USAF\NAVY) | KADENA (USAF\NAVY), Japan | 26.35N | 127.77E | 45 | 9.00 (JPN) | 82-06 | 479310 | 7 |  | 3.3 | 36.8 | 33.1 | 34.2 | 34.1 | 34 | 33.8 |  | 32.1 | 33.2 | 33.1 | 33 | 32.8
Japan |  | KAGOSHIMA | KAGOSHIMA, Japan | 31.55N | 130.55E | 32 | 9.00 (JPN) | 82-06 | 478270 | -1.2 |  | -4 | 37.3 | 31.9 | 34.2 | 34.5 | 34 | 33.5333 |  | 30.2 | 33.2 | 33.3 | 32 | 32.2333
Japan |  | KANAZAWA | KANAZAWA, Japan | 36.58N | 136.63E | 33 | 9.00 (JPN) | 82-06 | 476050 | -3.2 |  | -6.4 | 38.7 | 31.1 | 34.3 | 34.9 | 33 | 33.4333 |  | 28.7 | 32.7 | 33.5 | 32 | 31.6333
Japan |  | KANOYA AB | KANOYA AB, Japan | 31.37N | 130.83E | 68 | 9.00 (JPN) | 82-06 | 478500 | -3.5 |  | -6.3 | 36.8 | 30.8 | 33.4 | 33.9 | 33 | 32.7 |  | 29.1 | 32.2 | 32.8 | 31 | 31.3667
Japan |  | KANSAI INTERNATIONA | KANSAI INTERNATIONA, Japan | 34.43N | 135.25E | 8 | 9.00 (JPN) | 95-06 | 477740 | -0.8 |  | -3.6 | 37.2 | 30.2 | 34 | 34.2 | 33 | 32.8 |  | 28.9 | 32.8 | 33.1 | 32 | 31.6
Japan |  | KARUIZAWA | KARUIZAWA, Japan | 36.35N | 138.55E | 1004 | 9.00 (JPN) | 94-06 | 476220 | -15.8 |  | -19.2 | 33.6 | 27.2 | 30.4 | 30.3 | 29 | 29.3 |  | 25 | 28.8 | 28.7 | 28 | 27.5
Japan |  | KATSUURA | KATSUURA, Japan | 35.15N | 140.32E | 13 | 9.00 (JPN) | 94-06 | 476740 | -2.2 |  | -4.9 | 34.7 | 26.4 | 30.2 | 31.1 | 29 | 29.2333 |  | 24.8 | 28.9 | 30.1 | 28 | 27.9333
Japan |  | KAWAGUCHIKO | KAWAGUCHIKO, Japan | 35.50N | 138.77E | 861 | 9.00 (JPN) | 91-06 | 476400 | -11.7 |  | -15 | 35.2 | 29.4 | 32.3 | 31.6 | 31 | 31.1 |  | 26.8 | 30.5 | 30 | 29 | 29.1
Japan |  | KITAMIESASHI | KITAMIESASHI, Japan | 44.93N | 142.58E | 8 | 9.00 (JPN) | 94-06 | 474020 | -16.4 |  | -22.3 | 36.5 | 26.4 | 30 | 30.5 | 29 | 28.9667 |  | 23.3 | 26.1 | 27.6 | 26 | 25.6667
Japan |  | KOBE | KOBE, Japan | 34.70N | 135.22E | 30 | 9.00 (JPN) | 82-06 | 477700 | -2.5 |  | -5.5 | 38.5 | 30.4 | 34.2 | 34.8 | 33 | 33.1333 |  | 28.7 | 32.6 | 33.3 | 32 | 31.5333
Japan |  | KOCHI | KOCHI, Japan | 33.57N | 133.55E | 5 | 9.00 (JPN) | 82-06 | 478930 | -3 |  | -6.2 | 38.4 | 30.8 | 34.1 | 34.2 | 33 | 33.0333 |  | 28.9 | 32.5 | 32.9 | 31 | 31.4333
Japan |  | KOFU | KOFU, Japan | 35.67N | 138.55E | 281 | 9.00 (JPN) | 82-06 | 476380 | -7.1 |  | -11.3 | 40.7 | 32.8 | 36.4 | 36.1 | 35 | 35.1 |  | 30.3 | 34.3 | 34.3 | 33 | 32.9667
Japan |  | KOMATSU AB | KOMATSU AB, Japan | 36.40N | 136.40E | 9 | 9.00 (JPN) | 82-06 | 477040 | -5.2 |  | -11.7 | 39.7 | 30.9 | 34.3 | 35.2 | 33 | 33.4667 |  | 28.1 | 32.2 | 33.8 | 31 | 31.3667
Japan |  | KOMATSUSHIMA AB | KOMATSUSHIMA AB, Japan | 34.00N | 134.63E | 6 | 9.00 (JPN) | 82-06 | 478840 | -1 |  | -4.6 | 38.8 | 30.2 | 34 | 34.1 | 33 | 32.7667 |  | 28.2 | 32.8 | 33 | 31 | 31.3333
Japan |  | KUMAGAYA | KUMAGAYA, Japan | 36.15N | 139.38E | 31 | 9.00 (JPN) | 91-06 | 476260 | -4.3 |  | -6 | 41.1 | 33.3 | 37.2 | 36.9 | 36 | 35.8 |  | 31.4 | 35.6 | 35.3 | 34 | 34.1
Japan |  | KUMAMOTO | KUMAMOTO, Japan | 32.82N | 130.70E | 39 | 9.00 (JPN) | 82-06 | 478190 | -4.4 |  | -7 | 38.8 | 32.2 | 35.5 | 35.6 | 34 | 34.4333 |  | 30.7 | 34.1 | 34.5 | 33 | 33.1
Japan |  | KUMEJIMA | KUMEJIMA, Japan | 26.33N | 126.80E | 5 | 9.00 (JPN) | 94-06 | 479290 | 8.1 |  | 5.6 | 34.7 | 31.8 | 32.9 | 33.1 | 33 | 32.6 |  | 31.1 | 32.3 | 32.3 | 32 | 31.9
Japan |  | KURE | KURE, Japan | 34.23N | 132.55E | 5 | 9.00 (JPN) | 94-06 | 477660 | -2.5 |  | -5.2 | 35.6 | 29.9 | 33.5 | 33.5 | 32 | 32.3 |  | 28.3 | 32.2 | 32.6 | 31 | 31.0333
Japan |  | KUSHIRO | KUSHIRO, Japan | 42.98N | 144.38E | 39 | 9.00 (JPN) | 82-06 | 474180 | -18.9 |  | -25 | 30.4 | 20.8 | 24 | 25.8 | 24 | 23.5333 |  | 18.2 | 22 | 23.9 | 21 | 21.3667
Japan |  | KUTCHAN | KUTCHAN, Japan | 42.90N | 140.75E | 188 | 9.00 (JPN) | 91-06 | 474330 | -20.5 |  | -25.8 | 35.8 | 26 | 29.2 | 30.8 | 29 | 28.6667 |  | 24 | 27 | 28.4 | 26 | 26.4667
Japan |  | KYOTO | KYOTO, Japan | 35.02N | 135.73E | 46 | 9.00 (JPN) | 82-06 | 477590 | -2.9 |  | -5.9 | 39.7 | 32.5 | 35.7 | 36.5 | 35 | 34.9 |  | 30.7 | 34.4 | 35 | 33 | 33.3667
Japan |  | MAEBASHI | MAEBASHI, Japan | 36.40N | 139.07E | 113 | 9.00 (JPN) | 82-06 | 476240 | -5.4 |  | -8.8 | 40.7 | 33.4 | 36.6 | 36.2 | 35 | 35.4 |  | 30.7 | 34.8 | 34.4 | 33 | 33.3
Japan |  | MAIZURU | MAIZURU, Japan | 35.45N | 135.32E | 22 | 9.00 (JPN) | 82-06 | 477500 | -3.8 |  | -6.9 | 38.5 | 31.7 | 34.7 | 35.4 | 34 | 33.9333 |  | 29.5 | 33.2 | 34.1 | 32 | 32.2667
Japan |  | MAKURAZAKI | MAKURAZAKI, Japan | 31.27N | 130.30E | 31 | 9.00 (JPN) | 94-06 | 478310 | -0.6 |  | -2.3 | 35.2 | 29.5 | 32.9 | 33.1 | 32 | 31.8333 |  | 28.6 | 31.7 | 32.1 | 31 | 30.8
Japan |  | MATSUE | MATSUE, Japan | 35.45N | 133.07E | 22 | 9.00 (JPN) | 82-06 | 477410 | -3.4 |  | -6.3 | 39.2 | 30.7 | 33.7 | 34.9 | 33 | 33.1 |  | 28.8 | 32.2 | 33.5 | 32 | 31.5
Japan |  | MATSUMOTO | MATSUMOTO, Japan | 36.25N | 137.97E | 611 | 9.00 (JPN) | 82-06 | 476180 | -11.5 |  | -14.9 | 38.3 | 31 | 34.2 | 34.7 | 33 | 33.3 |  | 29 | 32.6 | 33.1 | 32 | 31.5667
Japan |  | MATSUSHIMA AB | MATSUSHIMA AB, Japan | 38.40N | 141.22E | 5 | 9.00 (JPN) | 82-06 | 475910 | -9.1 |  | -13.1 | 36.3 | 27.2 | 31.1 | 31.9 | 30 | 30.0667 |  | 25 | 28.9 | 29.9 | 28 | 27.9333
Japan |  | MATSUYAMA | MATSUYAMA, Japan | 33.85N | 132.78E | 34 | 9.00 (JPN) | 82-06 | 478870 | -2.1 |  | -4.9 | 37.4 | 31.8 | 34.1 | 34.2 | 33 | 33.3667 |  | 29.6 | 33 | 33.3 | 32 | 31.9667
Japan |  | MIHO AB | MIHO AB, Japan | 35.48N | 133.23E | 9 | 9.00 (JPN) | 82-06 | 477430 | -3.5 |  | -6.4 | 38.9 | 31 | 34 | 35 | 33 | 33.3333 |  | 28.9 | 32.2 | 33.2 | 31 | 31.4333
Japan |  | MINAMIDAITOJIMA | MINAMIDAITOJIMA, Japan | 25.83N | 131.23E | 20 | 9.00 (JPN) | 82-06 | 479450 | 7.5 |  | 4.4 | 34.8 | 31.9 | 33 | 32.6 | 33 | 32.5 |  | 31 | 32.2 | 32 | 32 | 31.7333
Japan |  | MINAMITORISHIMA | MINAMITORISHIMA, Japan | 24.28N | 153.98E | 8 | 10.00 (PCW) | 82-06 | 479910 | 15.8 |  | 11 | 36.7 | 32.1 | 32.9 | 32.3 | 32 | 32.4333 |  | 31.4 | 32 | 31.7 | 32 | 31.7
Japan |  | MISAWA AB | MISAWA AB, Japan | 40.70N | 141.37E | 39 | 9.00 (JPN) | 82-06 | 475800 | -10.5 |  | -14.4 | 36.6 | 28 | 31.8 | 32 | 31 | 30.6 |  | 25.1 | 29.1 | 29.9 | 28 | 28.0333
Japan |  | MISHIMA | MISHIMA, Japan | 35.12N | 138.93E | 22 | 9.00 (JPN) | 92-06 | 476570 | -4.8 |  | -7.5 | 37.4 | 30.7 | 34.1 | 34.3 | 33 | 33.0333 |  | 29 | 32.6 | 33 | 32 | 31.5333
Japan |  | MITO | MITO, Japan | 36.38N | 140.47E | 31 | 9.00 (JPN) | 82-06 | 476290 | -6.4 |  | -9.7 | 38.2 | 30.5 | 34.1 | 34 | 33 | 32.8667 |  | 28.2 | 32.4 | 32.5 | 31 | 31.0333
Japan |  | MIYAKEJIMA | MIYAKEJIMA, Japan | 34.12N | 139.52E | 37 | 9.00 (JPN) | 82-06 | 476770 | 1.9 |  | -1.6 | 32.5 | 27.7 | 30.2 | 30.6 | 30 | 29.5 |  | 26.5 | 29.4 | 29.9 | 29 | 28.6
Japan |  | MIYAKO | MIYAKO, Japan | 39.65N | 141.97E | 46 | 9.00 (JPN) | 82-06 | 475850 | -9.6 |  | -14 | 36.7 | 28.7 | 32.1 | 33 | 31 | 31.2667 |  | 25.5 | 29.6 | 30.9 | 29 | 28.6667
Japan |  | MIYAKOJIMA | MIYAKOJIMA, Japan | 24.80N | 125.28E | 41 | 9.00 (JPN) | 82-06 | 479270 | 11 |  | 8.1 | 34.8 | 31.9 | 33 | 32.6 | 33 | 32.5 |  | 31.1 | 32.2 | 31.9 | 32 | 31.7333
Japan |  | MIYAKONOJO | MIYAKONOJO, Japan | 31.73N | 131.08E | 156 | 9.00 (JPN) | 93-06 | 478290 | -4.8 |  | -7.2 | 37.3 | 31.5 | 34.7 | 34.2 | 33 | 33.4667 |  | 30.2 | 33.3 | 33.2 | 32 | 32.2333
Japan |  | MIYAZAKI | MIYAZAKI, Japan | 31.93N | 131.42E | 15 | 9.00 (JPN) | 82-06 | 478300 | -2.7 |  | -5.6 | 38.1 | 33.2 | 35.4 | 35.1 | 35 | 34.5667 |  | 31 | 34.1 | 33.3 | 33 | 32.8
Japan |  | MOMBETSU | MOMBETSU, Japan | 44.35N | 143.35E | 16 | 9.00 (JPN) | 91-06 | 474350 | -16.1 |  | -21 | 37.7 | 27 | 30.3 | 31.3 | 30 | 29.5333 |  | 23.2 | 26.5 | 28 | 26 | 25.9
Japan |  | MORIOKA | MORIOKA, Japan | 39.70N | 141.17E | 155 | 9.00 (JPN) | 82-06 | 475840 | -11.9 |  | -16.6 | 36.9 | 29.2 | 32.4 | 33.3 | 32 | 31.6333 |  | 27 | 30.4 | 31.6 | 30 | 29.6667
Japan |  | MURORAN | MURORAN, Japan | 42.32N | 140.98E | 49 | 9.00 (JPN) | 82-06 | 474230 | -9 |  | -12.1 | 32.4 | 23.9 | 26.8 | 28.1 | 26 | 26.2667 |  | 21.8 | 25.2 | 26.6 | 25 | 24.5333
Japan |  | MUROTOMISAKI | MUROTOMISAKI, Japan | 33.25N | 134.18E | 186 | 9.00 (JPN) | 82-06 | 478990 | -1.6 |  | -7.3 | 32.6 | 26.7 | 29.8 | 30.6 | 29 | 29.0333 |  | 25.5 | 28.9 | 29.7 | 28 | 28.0333
Japan |  | MUTSU | MUTSU, Japan | 41.28N | 141.22E | 5 | 9.00 (JPN) | 92-06 | 475760 | -11.9 |  | -17.2 | 35.3 | 26.4 | 30.2 | 31.1 | 29 | 29.2333 |  | 24.3 | 28.1 | 29.5 | 27 | 27.3
Japan |  | NAGANO | NAGANO, Japan | 36.67N | 138.20E | 419 | 9.00 (JPN) | 82-06 | 476100 | -9.1 |  | -12.1 | 38.2 | 30.6 | 34 | 34.7 | 33 | 33.1 |  | 28.5 | 32.3 | 33.1 | 31 | 31.3
Japan |  | NAGASAKI | NAGASAKI, Japan | 32.73N | 129.87E | 35 | 9.00 (JPN) | 82-06 | 478170 | -1.1 |  | -3.2 | 37.5 | 29.8 | 33.6 | 34.2 | 33 | 32.5333 |  | 28.4 | 32 | 33 | 31 | 31.1333
Japan |  | NAGOYA | NAGOYA, Japan | 35.17N | 136.97E | 56 | 9.00 (JPN) | 82-06 | 476360 | -3.4 |  | -6.1 | 40 | 32.2 | 35.7 | 36.6 | 35 | 34.8333 |  | 30.2 | 34.1 | 34.7 | 33 | 33
Japan |  | NAGOYA AIRPORT | NAGOYA AIRPORT, Japan | 35.25N | 136.92E | 17 | 9.00 (JPN) | 82-06 | 476350 | -4.9 |  | -8.4 | 40.3 | 32.8 | 36 | 36.9 | 35 | 35.2333 |  | 30.8 | 34.2 | 35 | 33 | 33.3333
Japan |  | NAHA | NAHA, Japan | 26.20N | 127.68E | 53 | 9.00 (JPN) | 82-06 | 479360 | 10.2 |  | 7.8 | 36.6 | 31.9 | 33 | 32.7 | 33 | 32.5333 |  | 31 | 32.2 | 32 | 32 | 31.7333
Japan |  | NAHA AIRPORT | NAHA AIRPORT, Japan | 26.20N | 127.65E | 6 | 9.00 (JPN) | 82-06 | 479300 | 10.6 |  | 8 | 35.3 | 31.9 | 33.1 | 33.1 | 33 | 32.7 |  | 31 | 32.2 | 32.2 | 32 | 31.8
Japan |  | NARA | NARA, Japan | 34.70N | 135.83E | 106 | 9.00 (JPN) | 93-06 | 477800 | -3.9 |  | -5.7 | 39 | 31.9 | 35.1 | 36 | 34 | 34.3333 |  | 30.1 | 33.9 | 34.6 | 33 | 32.8667
Japan |  | NAZE | NAZE, Japan | 28.38N | 129.50E | 7 | 9.00 (JPN) | 82-06 | 479090 | 7.6 |  | 5.5 | 37.5 | 33 | 33.7 | 33.2 | 33 | 33.3 |  | 32 | 33 | 32.3 | 32 | 32.4333
Japan |  | NEMURO | NEMURO, Japan | 43.33N | 145.58E | 39 | 9.00 (JPN) | 82-06 | 474200 | -13.4 |  | -19.7 | 33.1 | 22.7 | 26 | 27.4 | 25 | 25.3667 |  | 19.1 | 23.2 | 24.7 | 22 | 22.3333
Japan |  | NEW TOKYO INTERNATI | NEW TOKYO INTERNATI, Japan | 35.77N | 140.38E | 44 | 9.00 (JPN) | 82-06 | 476860 | -7.2 |  | -11.9 | 38.1 | 30.8 | 34 | 34 | 33 | 32.9333 |  | 28.2 | 32.2 | 32.2 | 31 | 30.8667
Japan |  | NIIGATA | NIIGATA, Japan | 37.92N | 139.05E | 6 | 9.00 (JPN) | 82-06 | 476040 | -4.1 |  | -8.7 | 38.8 | 30 | 34.2 | 34.9 | 33 | 33.0333 |  | 27.4 | 32.3 | 33.4 | 31 | 31.0333
Japan |  | NIKKO | NIKKO, Japan | 36.73N | 139.50E | 1294 | 9.00 (JPN) | 91-06 | 476900 | -12.9 |  | -15.8 | 29.7 | 23.4 | 26.6 | 26.8 | 26 | 25.6 |  | 21.6 | 25.2 | 25.1 | 24 | 23.9667
Japan |  | NOBEOKA | NOBEOKA, Japan | 32.58N | 131.65E | 21 | 9.00 (JPN) | 94-06 | 478220 | -3.6 |  | -6.2 | 37.6 | 32.5 | 34.2 | 34.1 | 34 | 33.6 |  | 29.9 | 32.5 | 32.9 | 32 | 31.7667
Japan |  | NYUTABARU AB | NYUTABARU AB, Japan | 32.08N | 131.45E | 82 | 9.00 (JPN) | 82-06 | 478540 | -4.3 |  | -6.8 | 38.2 | 32.1 | 34.8 | 34.2 | 34 | 33.7 |  | 29.8 | 33 | 32.1 | 32 | 31.6333
Japan |  | OBIHIRO | OBIHIRO, Japan | 42.92N | 143.22E | 43 | 9.00 (JPN) | 82-06 | 474170 | -21.8 |  | -26.5 | 37.5 | 29.5 | 31.9 | 33.2 | 32 | 31.5333 |  | 26.5 | 29.3 | 30 | 29 | 28.6
Japan |  | OFUNATO | OFUNATO, Japan | 39.07N | 141.72E | 41 | 9.00 (JPN) | 91-06 | 475120 | -7.1 |  | -10.2 | 36.8 | 28.6 | 32.8 | 32.3 | 31 | 31.2333 |  | 25.8 | 30.2 | 30.2 | 29 | 28.7333
Japan |  | OITA | OITA, Japan | 33.23N | 131.62E | 13 | 9.00 (JPN) | 82-06 | 478150 | -2.7 |  | -5.7 | 37.8 | 31.9 | 34.5 | 34.6 | 34 | 33.6667 |  | 29.5 | 33.2 | 33.3 | 32 | 32
Japan |  | OKAYAMA | OKAYAMA, Japan | 34.67N | 133.92E | 18 | 9.00 (JPN) | 93-06 | 477680 | -3.2 |  | -5.9 | 39.4 | 33 | 35.5 | 36.1 | 35 | 34.8667 |  | 30.7 | 34.3 | 34.7 | 33 | 33.2333
Japan |  | OKINOERABU | OKINOERABU, Japan | 27.43N | 128.70E | 29 | 9.00 (JPN) | 92-06 | 479420 | 9.4 |  | 6.5 | 34.2 | 31.6 | 32.5 | 32.6 | 32 | 32.2333 |  | 30.7 | 31.9 | 31.9 | 32 | 31.5
Japan |  | OMAEZAKI | OMAEZAKI, Japan | 34.60N | 138.22E | 47 | 9.00 (JPN) | 82-06 | 476550 | -2 |  | -4.6 | 36 | 27.2 | 30.9 | 31.4 | 30 | 29.8333 |  | 25.8 | 29.7 | 30.4 | 29 | 28.6333
Japan |  | OMINATO AB | OMINATO AB, Japan | 41.23N | 141.13E | 10 | 9.00 (JPN) | 82-06 | 475160 | -10.7 |  | -16.2 | 35 | 26.2 | 30.8 | 31.2 | 29 | 29.4 |  | 24.2 | 28.2 | 29.2 | 27 | 27.2
Japan |  | OMU | OMU, Japan | 44.58N | 142.97E | 15 | 9.00 (JPN) | 92-06 | 474050 | -19.5 |  | -25.6 | 36.3 | 26.9 | 29.8 | 30.2 | 29 | 28.9667 |  | 23.9 | 26.7 | 27.6 | 26 | 26.0667
Japan |  | ONAHAMA | ONAHAMA, Japan | 36.95N | 140.90E | 5 | 9.00 (JPN) | 82-06 | 475980 | -4.9 |  | -8.4 | 37.5 | 27.2 | 30.2 | 31.2 | 30 | 29.5333 |  | 24.7 | 28.2 | 29.2 | 27 | 27.3667
Japan |  | OSAKA | OSAKA, Japan | 34.68N | 135.52E | 83 | 9.00 (JPN) | 82-06 | 477720 | -1.4 |  | -4.1 | 39.4 | 32 | 35.2 | 36 | 34 | 34.4 |  | 30.2 | 33.8 | 34.6 | 33 | 32.8667
Japan |  | OSAKA INTERNATIONAL | OSAKA INTERNATIONAL, Japan | 34.78N | 135.43E | 15 | 9.00 (JPN) | 82-06 | 477710 | -3.5 |  | -6.3 | 40.2 | 32.1 | 35.9 | 36.6 | 35 | 34.8667 |  | 30.2 | 34.1 | 35 | 33 | 33.1
Japan |  | OSHIMA | OSHIMA, Japan | 34.75N | 139.38E | 79 | 9.00 (JPN) | 82-06 | 476750 | -1.4 |  | -4 | 34.2 | 27.6 | 30.7 | 30.9 | 30 | 29.7333 |  | 25.7 | 29.4 | 30 | 28 | 28.3667
Japan |  | OTARU | OTARU, Japan | 43.18N | 141.02E | 26 | 9.00 (JPN) | 92-06 | 474110 | -11.6 |  | -16.8 | 36.1 | 25.8 | 30 | 31.4 | 29 | 29.0667 |  | 23.1 | 27.4 | 28.6 | 26 | 26.3667
Japan |  | OWASE | OWASE, Japan | 34.07N | 136.20E | 27 | 9.00 (JPN) | 82-06 | 476630 | -2.6 |  | -5.7 | 38.9 | 32.5 | 34.7 | 34.6 | 34 | 33.9333 |  | 29.2 | 32.5 | 32.7 | 31 | 31.4667
Japan |  | OZUKI AB | OZUKI AB, Japan | 34.05N | 131.05E | 7 | 9.00 (JPN) | 82-06 | 477870 | -3.3 |  | -6.3 | 37.1 | 30.1 | 33.2 | 33.9 | 32 | 32.4 |  | 28.2 | 32 | 32.9 | 31 | 31.0333
Japan |  | RUMOI | RUMOI, Japan | 43.95N | 141.63E | 28 | 9.00 (JPN) | 82-06 | 474060 | -17.1 |  | -23.8 | 34.5 | 24.3 | 29.4 | 29.7 | 28 | 27.8 |  | 21.6 | 26.4 | 27.5 | 25 | 25.1667
Japan |  | SAGA | SAGA, Japan | 33.27N | 130.30E | 32 | 9.00 (JPN) | 92-06 | 478130 | -3.3 |  | -5.5 | 39.3 | 32.2 | 36.1 | 35.8 | 35 | 34.7 |  | 30.8 | 34.4 | 34.5 | 33 | 33.2333
Japan |  | SAIGO | SAIGO, Japan | 36.20N | 133.33E | 31 | 9.00 (JPN) | 82-06 | 477400 | -3.8 |  | -7.4 | 36 | 28.5 | 32 | 32.9 | 31 | 31.1333 |  | 26.7 | 30.5 | 31.7 | 30 | 29.6333
Japan |  | SAKAI | SAKAI, Japan | 35.55N | 133.23E | 3 | 9.00 (JPN) | 94-06 | 477420 | -3.6 |  | -6.9 | 37 | 31.4 | 34.5 | 35.5 | 34 | 33.8 |  | 29.5 | 33.1 | 34.1 | 32 | 32.2333
Japan |  | SAKATA | SAKATA, Japan | 38.92N | 139.85E | 4 | 9.00 (JPN) | 82-06 | 475870 | -6 |  | -10.9 | 38.6 | 28.7 | 33.2 | 34.6 | 32 | 32.1667 |  | 26.7 | 31.2 | 32.8 | 30 | 30.2333
Japan |  | SAPPORO | SAPPORO, Japan | 43.07N | 141.33E | 26 | 9.00 (JPN) | 82-06 | 474120 | -13.2 |  | -17.9 | 36.9 | 27.4 | 30.9 | 32.1 | 30 | 30.1333 |  | 25.2 | 28.8 | 29.8 | 28 | 27.9333
Japan |  | SASEBO | SASEBO, Japan | 33.15N | 129.73E | 6 | 9.00 (JPN) | 93-06 | 478120 | -1.7 |  | -3.7 | 37.5 | 30.5 | 34.7 | 34.3 | 33 | 33.1667 |  | 29 | 32.7 | 33.2 | 32 | 31.6333
Japan |  | SENDAI | SENDAI, Japan | 38.27N | 140.90E | 43 | 9.00 (JPN) | 82-06 | 475900 | -5.7 |  | -8.6 | 37.9 | 28.9 | 32.7 | 33.1 | 32 | 31.5667 |  | 26.5 | 30.7 | 31.2 | 29 | 29.4667
Japan |  | SHIMIZU | SHIMIZU, Japan | 32.72N | 133.02E | 33 | 9.00 (JPN) | 82-06 | 478980 | -0.6 |  | -3 | 35.5 | 28.1 | 31.6 | 31.8 | 31 | 30.5 |  | 27.1 | 30.2 | 30.8 | 29 | 29.3667
Japan |  | SHIMOFUSA AB | SHIMOFUSA AB, Japan | 35.80N | 140.02E | 33 | 9.00 (JPN) | 82-06 | 477270 | -4.8 |  | -9.1 | 40.1 | 31.8 | 35.2 | 35.2 | 34 | 34.0667 |  | 29.2 | 33.2 | 33.8 | 32 | 32.0667
Japan |  | SHIMONOSEKI | SHIMONOSEKI, Japan | 33.95N | 130.93E | 19 | 9.00 (JPN) | 82-06 | 477620 | -1 |  | -4.9 | 36.1 | 30 | 33 | 33.1 | 32 | 32.0333 |  | 28 | 31.6 | 32.1 | 31 | 30.5667
Japan |  | SHINJO | SHINJO, Japan | 38.75N | 140.32E | 102 | 9.00 (JPN) | 92-06 | 475200 | -10.7 |  | -15.9 | 38.2 | 29.3 | 33.2 | 34.2 | 32 | 32.2333 |  | 27.4 | 31.3 | 32.3 | 30 | 30.3333
Japan |  | SHIONOMISAKI | SHIONOMISAKI, Japan | 33.45N | 135.77E | 75 | 9.00 (JPN) | 82-06 | 477780 | -0.4 |  | -3.3 | 34.9 | 27.9 | 31.3 | 31.6 | 30 | 30.2667 |  | 26.7 | 30 | 30.6 | 29 | 29.1
Japan |  | SHIRAKAWA | SHIRAKAWA, Japan | 37.13N | 140.22E | 357 | 9.00 (JPN) | 92-06 | 475970 | -8.4 |  | -11.2 | 36.5 | 29 | 33.2 | 32.9 | 32 | 31.7 |  | 27.3 | 31.4 | 31.4 | 30 | 30.0333
Japan |  | SHIZUHAMA AB | SHIZUHAMA AB, Japan | 34.82N | 138.30E | 10 | 9.00 (JPN) | 82-06 | 476580 | -2.7 |  | -5.2 | 39.2 | 31.9 | 34.2 | 35 | 34 | 33.7 |  | 29 | 32.2 | 33 | 31 | 31.4
Japan |  | SHIZUOKA | SHIZUOKA, Japan | 34.98N | 138.40E | 15 | 9.00 (JPN) | 91-06 | 476560 | -2.6 |  | -5.3 | 39.2 | 33.4 | 35.3 | 34.9 | 35 | 34.5333 |  | 30.1 | 33.1 | 32.8 | 32 | 32
Japan |  | SUKUMO | SUKUMO, Japan | 32.92N | 132.70E | 11 | 9.00 (JPN) | 94-06 | 478970 | -1.6 |  | -3.9 | 38.4 | 29.3 | 34 | 34.5 | 33 | 32.6 |  | 28.2 | 31.4 | 32.2 | 31 | 30.6
Japan |  | SUMOTO | SUMOTO, Japan | 34.33N | 134.90E | 112 | 9.00 (JPN) | 94-06 | 477760 | -2.1 |  | -5 | 35.1 | 30.1 | 32.7 | 33.4 | 32 | 32.0667 |  | 27.7 | 31.6 | 32.2 | 31 | 30.5
Japan |  | SUTTSU | SUTTSU, Japan | 42.80N | 140.22E | 38 | 9.00 (JPN) | 82-06 | 474210 | -10.5 |  | -14.5 | 33.7 | 24.3 | 28.6 | 29.1 | 27 | 27.3333 |  | 22.1 | 25.9 | 27.1 | 25 | 25.0333
Japan |  | SUWA | SUWA, Japan | 36.05N | 138.12E | 762 | 9.00 (JPN) | 91-06 | 476200 | -12.1 |  | -15.4 | 36.1 | 29.2 | 32.8 | 33.3 | 32 | 31.7667 |  | 27.3 | 31.4 | 31.7 | 30 | 30.1333
Japan |  | TADOTSU | TADOTSU, Japan | 34.28N | 133.75E | 5 | 9.00 (JPN) | 94-06 | 478900 | -2 |  | -3.3 | 37.9 | 31.3 | 34.5 | 35.3 | 34 | 33.7 |  | 29.1 | 33.2 | 34.1 | 32 | 32.1333
Japan |  | TAKADA | TAKADA, Japan | 37.10N | 138.25E | 18 | 9.00 (JPN) | 82-06 | 476120 | -5.3 |  | -8.6 | 39 | 30.3 | 34.3 | 35.9 | 34 | 33.5 |  | 28.3 | 32.7 | 33.9 | 32 | 31.6333
Japan |  | TAKAMATSU | TAKAMATSU, Japan | 34.32N | 134.05E | 10 | 9.00 (JPN) | 82-06 | 478910 | -2.7 |  | -4.6 | 39 | 32.9 | 35.2 | 35.7 | 35 | 34.6 |  | 30.3 | 34 | 34.3 | 33 | 32.8667
Japan |  | TAKAYAMA | TAKAYAMA, Japan | 36.15N | 137.25E | 561 | 9.00 (JPN) | 91-06 | 476170 | -12.5 |  | -17.9 | 37.4 | 30.5 | 34 | 34.4 | 33 | 32.9667 |  | 28.6 | 32.4 | 32.8 | 31 | 31.2667
Japan |  | TANEGASHIMA | TANEGASHIMA, Japan | 30.73N | 130.98E | 18 | 9.00 (JPN) | 82-06 | 478370 | 3.8 |  | 1.4 | 35.3 | 30.5 | 32.6 | 33 | 32 | 32.0333 |  | 29.4 | 31.7 | 32 | 31 | 31.0333
Japan |  | TATEYAMA | TATEYAMA, Japan | 34.98N | 139.87E | 7 | 9.00 (JPN) | 82-06 | 476720 | -4.1 |  | -6.8 | 36.2 | 29 | 32.2 | 32.7 | 31 | 31.3 |  | 27 | 30.7 | 31.4 | 30 | 29.7
Japan |  | TATEYAMA AB | TATEYAMA AB, Japan | 34.98N | 139.83E | 6 | 9.00 (JPN) | 82-06 | 476880 | -2.2 |  | -4.8 | 36.4 | 29 | 32.8 | 32.9 | 32 | 31.5667 |  | 27.1 | 31.1 | 31.8 | 30 | 30
Japan |  | TOKUSHIMA | TOKUSHIMA, Japan | 34.07N | 134.57E | 6 | 9.00 (JPN) | 82-06 | 478950 | -1.4 |  | -4.2 | 38.4 | 30.7 | 34.3 | 34.7 | 33 | 33.2333 |  | 28.7 | 32.7 | 33.3 | 32 | 31.5667
Japan |  | TOKUSHIMA AB | TOKUSHIMA AB, Japan | 34.13N | 134.62E | 11 | 9.00 (JPN) | 82-06 | 478810 | -1.3 |  | -3.2 | 38.8 | 30.1 | 35 | 35.1 | 33 | 33.4 |  | 28.2 | 32.8 | 33.1 | 31 | 31.3667
Japan |  | TOKYO | TOKYO, Japan | 35.68N | 139.77E | 36 | 9.00 (JPN) | 82-06 | 476620 | -0.9 |  | -3.5 | 40 | 31.4 | 34.7 | 34.8 | 34 | 33.6333 |  | 29.4 | 33.1 | 33.3 | 32 | 31.9333
Japan |  | TOKYO INTERNATIONAL | TOKYO INTERNATIONAL, Japan | 35.55N | 139.78E | 9 | 9.00 (JPN) | 82-06 | 476710 | -1.8 |  | -5.4 | 38.3 | 30.8 | 34.1 | 34.2 | 33 | 33.0333 |  | 28.7 | 32.2 | 33 | 31 | 31.3
Japan |  | TOMAKOMAI | TOMAKOMAI, Japan | 42.62N | 141.55E | 11 | 9.00 (JPN) | 94-06 | 474240 | -15.3 |  | -20.3 | 30.8 | 24.6 | 26 | 28.4 | 26 | 26.3333 |  | 20.6 | 24.1 | 26.5 | 24 | 23.7333
Japan |  | TOTTORI | TOTTORI, Japan | 35.48N | 134.20E | 15 | 9.00 (JPN) | 82-06 | 477460 | -3.5 |  | -6.6 | 38.6 | 31.9 | 35 | 35.8 | 34 | 34.2333 |  | 29.8 | 33.4 | 34.3 | 33 | 32.5
Japan |  | TOYAMA | TOYAMA, Japan | 36.72N | 137.20E | 17 | 9.00 (JPN) | 82-06 | 476070 | -4.7 |  | -7.7 | 39.6 | 31.2 | 34.7 | 35.4 | 34 | 33.7667 |  | 28.9 | 32.9 | 33.7 | 32 | 31.8333
Japan |  | TOYOOKA | TOYOOKA, Japan | 35.53N | 134.82E | 4 | 9.00 (JPN) | 93-06 | 477470 | -4.4 |  | -7.1 | 39.7 | 32.7 | 35.7 | 36.2 | 35 | 34.8667 |  | 30.6 | 34.1 | 35 | 33 | 33.2333
Japan |  | TSU | TSU, Japan | 34.73N | 136.52E | 18 | 9.00 (JPN) | 91-06 | 476510 | -2 |  | -4.9 | 40.3 | 32.8 | 36 | 35.8 | 35 | 34.8667 |  | 29.8 | 33.9 | 33.9 | 33 | 32.5333
Japan |  | TSUIKI AB | TSUIKI AB, Japan | 33.68N | 131.05E | 20 | 9.00 (JPN) | 82-06 | 478400 | -4.9 |  | -8.4 | 36.7 | 30.9 | 33.9 | 33.9 | 33 | 32.9 |  | 28.2 | 32.2 | 32.1 | 31 | 30.8333
Japan |  | TSURUGA | TSURUGA, Japan | 35.65N | 136.07E | 12 | 9.00 (JPN) | 91-06 | 476310 | -2.2 |  | -4.8 | 37.9 | 30.9 | 34.7 | 35.2 | 34 | 33.6 |  | 29.2 | 33.3 | 33.8 | 32 | 32.1
Japan |  | TSUYAMA | TSUYAMA, Japan | 35.07N | 134.02E | 147 | 9.00 (JPN) | 94-06 | 477560 | -6.3 |  | -10.3 | 37.6 | 31.6 | 35.1 | 35.5 | 34 | 34.0667 |  | 29.8 | 33.3 | 33.9 | 32 | 32.3333
Japan |  | UENO | UENO, Japan | 34.77N | 136.15E | 161 | 9.00 (JPN) | 91-06 | 476490 | -5.2 |  | -7.4 | 38.2 | 32 | 35 | 35.7 | 34 | 34.2333 |  | 30.2 | 33.8 | 34.2 | 33 | 32.7333
Japan |  | UNZENDAKE | UNZENDAKE, Japan | 32.73N | 130.27E | 679 | 9.00 (JPN) | 91-06 | 478180 | -6.3 |  | -9.1 | 33.1 | 26.2 | 29.7 | 29.4 | 28 | 28.4333 |  | 24.8 | 28.2 | 28.3 | 27 | 27.1
Japan |  | URAKAWA | URAKAWA, Japan | 42.17N | 142.78E | 37 | 9.00 (JPN) | 82-06 | 474260 | -11.1 |  | -14.8 | 31.2 | 20.4 | 25.1 | 26.6 | 24 | 24.0333 |  | 18.9 | 23.3 | 25.2 | 22 | 22.4667
Japan |  | USHIBUKA | USHIBUKA, Japan | 31.72N | 130.03E | 14 | 9.00 (JPN) | 93-06 | 478380 | 0.2 |  | -2.2 | 38.2 | 30.1 | 34 | 34.4 | 33 | 32.8333 |  | 28.8 | 32.4 | 33.2 | 31 | 31.4667
Japan |  | UTSUNOMIYA | UTSUNOMIYA, Japan | 36.55N | 139.87E | 140 | 9.00 (JPN) | 82-06 | 476150 | -6.5 |  | -9.7 | 38.9 | 31.5 | 34.9 | 34.8 | 34 | 33.7333 |  | 29.3 | 33.1 | 33.2 | 32 | 31.8667
Japan |  | UWAJIMA | UWAJIMA, Japan | 33.23N | 132.55E | 14 | 9.00 (JPN) | 93-06 | 478920 | -2 |  | -4.5 | 37.5 | 31.8 | 34 | 34.3 | 33 | 33.3667 |  | 29.9 | 32.9 | 33.3 | 32 | 32.0333
Japan |  | WAJIMA | WAJIMA, Japan | 37.40N | 136.90E | 14 | 9.00 (JPN) | 82-06 | 476000 | -4.2 |  | -8.5 | 38 | 29.5 | 33.4 | 34.1 | 32 | 32.3333 |  | 27 | 31.7 | 32.5 | 30 | 30.4
Japan |  | WAKAMATSU | WAKAMATSU, Japan | 37.48N | 139.92E | 213 | 9.00 (JPN) | 82-06 | 475700 | -10.2 |  | -15.9 | 37.8 | 30.8 | 34.1 | 35.1 | 33 | 33.3333 |  | 28.7 | 32.6 | 33.4 | 32 | 31.5667
Japan |  | WAKAYAMA | WAKAYAMA, Japan | 34.23N | 135.17E | 18 | 9.00 (JPN) | 82-06 | 477770 | -1.4 |  | -2.8 | 38.3 | 31.1 | 34.6 | 35.2 | 34 | 33.6333 |  | 29.1 | 32.9 | 33.6 | 32 | 31.8667
Japan |  | WAKKANAI | WAKKANAI, Japan | 45.42N | 141.68E | 11 | 9.00 (JPN) | 82-06 | 474010 | -13 |  | -18.1 | 32 | 21.7 | 26 | 27.2 | 25 | 24.9667 |  | 19.6 | 23.6 | 25.5 | 23 | 22.9
Japan |  | YAKUSHIMA | YAKUSHIMA, Japan | 30.38N | 130.67E | 38 | 9.00 (JPN) | 92-06 | 478360 | 3.7 |  | 1.5 | 36 | 31.6 | 32.9 | 32.6 | 32 | 32.3667 |  | 30.1 | 31.7 | 31.7 | 31 | 31.1667
Japan |  | YAMAGATA | YAMAGATA, Japan | 38.25N | 140.35E | 153 | 9.00 (JPN) | 82-06 | 475880 | -8.1 |  | -11.7 | 38.9 | 30.7 | 34.2 | 35.3 | 33 | 33.4 |  | 28.6 | 32.3 | 33.4 | 31 | 31.4333
Japan |  | YAMAGUCHI | YAMAGUCHI, Japan | 34.17N | 131.45E | 18 | 9.00 (JPN) | 92-06 | 477840 | -3.9 |  | -7.6 | 38.3 | 31.5 | 35.4 | 34.8 | 34 | 33.9 |  | 29.9 | 33.7 | 33.8 | 32 | 32.4667
Japan |  | YOKKAICHI | YOKKAICHI, Japan | 34.93N | 136.58E | 56 | 9.00 (JPN) | 92-06 | 476840 | -3.8 |  | -6.7 | 39.6 | 31 | 35 | 35.4 | 34 | 33.8 |  | 29 | 33.1 | 33.6 | 32 | 31.9
Japan |  | YOKOHAMA | YOKOHAMA, Japan | 35.43N | 139.65E | 42 | 9.00 (JPN) | 82-06 | 476700 | -1 |  | -3.2 | 37.4 | 30.4 | 33.5 | 33.7 | 33 | 32.5333 |  | 28.4 | 31.9 | 32.3 | 31 | 30.8667
Japan |  | YOKOSUKA | YOKOSUKA, Japan | 35.28N | 139.67E | 53 | 9.00 (JPN) | 82-05 | 476960 | -1 |  | -4.9 | 42 | 31.1 | 35.1 | 36.8 | 34 | 34.3333 |  | 28.2 | 32.9 | 34.1 | 32 | 31.7333
Japan |  | YOKOTA (JASDF/USAF) | YOKOTA (JASDF/USAF), Japan | 35.75N | 139.35E | 139 | 9.00 (JPN) | 82-06 | 476420 | -6.4 |  | -9.3 | 41.7 | 32.2 | 36 | 35.8 | 35 | 34.6667 |  | 29.2 | 33.9 | 33.9 | 32 | 32.3333
Japan |  | YONAGO | YONAGO, Japan | 35.43N | 133.33E | 8 | 9.00 (JPN) | 93-06 | 477440 | -3.3 |  | -6.7 | 39.1 | 32.1 | 34.7 | 35.8 | 34 | 34.2 |  | 29.7 | 33.4 | 34.3 | 32 | 32.4667
Japan |  | YONAGUNIJIMA | YONAGUNIJIMA, Japan | 24.47N | 123.02E | 36 | 9.00 (JPN) | 94-06 | 479120 | 11.3 |  | 8.5 | 34.8 | 31.6 | 32.5 | 32.4 | 32 | 32.1667 |  | 30.9 | 31.7 | 31.6 | 31 | 31.4
Jersey |  | JERSEY AIRPORT | JERSEY AIRPORT, Jersey | 49.22N | 2.20W | 84 | 0.00 (GMT) | 82-06 | 38950 | -3.5 |  | -10.1 | 35 | 26.7 | 27.9 | 28.7 | 28 | 27.7667 |  | 23.3 | 24.9 | 24.7 | 24 | 24.3
Jordan |  | AMMAN AIRPORT | AMMAN AIRPORT, Jordan | 31.98N | 35.98E | 779 | 2.00 (JRD) | 82-06 | 402700 | -0.3 |  | -2.8 | 43.7 | 36.1 | 38 | 37.9 | 37 | 37.3333 |  | 33.9 | 35 | 35 | 35 | 34.6333
Jordan |  | AQABA AIRPORT | AQABA AIRPORT, Jordan | 29.55N | 35.00E | 51 | 2.00 (JRD) | 82-06 | 403400 | 5.3 |  | 0.6 | 48 | 42.6 | 43.1 | 42.2 | 43 | 42.6333 |  | 40.8 | 41.8 | 41.1 | 41 | 41.2333
Jordan |  | H-4 IRWAISHED | H-4 IRWAISHED, Jordan | 32.50N | 38.20E | 683 | 2.00 (JRD) | 82-06 | 402500 | N/A |  | N/A | N/A | 40.1 | 42.5 | 42.8 | 42 | 41.8 |  | 38.5 | 40.5 | 40.2 | 40 | 39.7333
Jordan |  | IRBED | IRBED, Jordan | 32.55N | 35.85E | 616 | 2.00 (JRD) | 82-06 | 402550 | -0.4 |  | -2.5 | 42.5 | 35.2 | 36 | 35 | 35 | 35.4 |  | 32.9 | 33.2 | 33.2 | 33 | 33.1
Jordan |  | MAAN | MAAN, Jordan | 30.17N | 35.78E | 1069 | 2.00 (JRD) | 83-06 | 403100 | N/A |  | N/A | N/A | 36.1 | 38.5 | 38.3 | 38 | 37.6333 |  | 34.6 | 36.1 | 36.8 | 36 | 35.8333
Jordan |  | MAFRAQ | MAFRAQ, Jordan | 32.37N | 36.25E | 683 | 2.00 (JRD) | 83-06 | 402650 | N/A |  | N/A | N/A | 36.6 | 38.9 | 37.7 | 38 | 37.7333 |  | 34.8 | 35.6 | 35.6 | 35 | 35.3333
Jordan |  | QUEEN ALIA AIRPORT | QUEEN ALIA AIRPORT, Jordan | 31.72N | 35.98E | 722 | 2.00 (JRD) | 83-06 | 402720 | -2.9 |  | -6.9 | 44.2 | 37.2 | 39.1 | 39.1 | 38 | 38.4667 |  | 35.1 | 36.1 | 36.2 | 36 | 35.8
Kazakhstan |  | AKKOL | AKKOL, Kazakhstan | 52.00N | 70.95E | 384 | 6.00 (ASC) | 83-06 | 350850 | -35 |  | -42.6 | 38.2 | 32.9 | 33.2 | 33.2 | 33 | 33.1 |  | 30.5 | 30.5 | 30.2 | 30 | 30.4
Kazakhstan |  | AKKUDUK | AKKUDUK, Kazakhstan | 42.97N | 54.12E | 78 | 5.00 (ASW) | 82-06 | 382320 | -21.2 |  | -34.5 | 46.7 | 40.3 | 42.3 | 41.9 | 42 | 41.5 |  | 38.1 | 40.2 | 39.2 | 39 | 39.1667
Kazakhstan |  | AKTOBE | AKTOBE, Kazakhstan | 50.28N | 57.15E | 219 | 5.00 (ASW) | 82-06 | 352290 | -32.9 |  | -42.2 | 42.2 | 36.2 | 36.8 | 36 | 36 | 36.3333 |  | 33.9 | 34.4 | 33.2 | 34 | 33.8333
Kazakhstan |  | ALMATY | ALMATY, Kazakhstan | 43.23N | 76.93E | 851 | 6.00 (ASC) | 82-06 | 368700 | -22.4 |  | -31.6 | 42.6 | 34.2 | 36.9 | 36 | 36 | 35.7 |  | 32 | 34 | 33.8 | 33 | 33.2667
Kazakhstan |  | AMANGELDY | AMANGELDY, Kazakhstan | 50.13N | 65.23E | 142 | 6.00 (ASC) | 82-06 | 353610 | N/A |  | N/A | N/A | 37.7 | 37.2 | 35.7 | 37 | 36.8667 |  | 35.3 | 35.1 | 33 | 34 | 34.4667
Kazakhstan |  | ARALSKOE MORE | ARALSKOE MORE, Kazakhstan | 46.78N | 61.65E | 62 | 6.00 (ASC) | 82-06 | 357460 | -27.6 |  | -36.7 | 45.4 | 39.9 | 40.2 | 39.5 | 40 | 39.8667 |  | 37.6 | 38.2 | 37.2 | 38 | 37.6667
Kazakhstan |  | ASTANA | ASTANA, Kazakhstan | 51.13N | 71.37E | 350 | 6.00 (ASC) | 82-06 | 351880 | -33.9 |  | -42.6 | 41.8 | 34.2 | 34.1 | 33.4 | 34 | 33.9 |  | 31.5 | 31.5 | 30.8 | 31 | 31.2667
Kazakhstan |  | ATBASAR | ATBASAR, Kazakhstan | 51.82N | 68.37E | 304 | 6.00 (ASC) | 82-06 | 350780 | -35.7 |  | -44.6 | 40.3 | 34 | 34.5 | 34.3 | 34 | 34.2667 |  | 31.2 | 31.7 | 31.3 | 31 | 31.4
Kazakhstan |  | ATYRAU | ATYRAU, Kazakhstan | 47.12N | 51.92E | -22 | 5.00 (ASW) | 82-06 | 357000 | -24.4 |  | -37.3 | 42.2 | 37.2 | 38.8 | 37.1 | 38 | 37.7 |  | 35.3 | 36.8 | 35.2 | 36 | 35.7667
Kazakhstan |  | BALHASH | BALHASH, Kazakhstan | 46.80N | 75.08E | 350 | 6.00 (ASC) | 82-06 | 357960 | -30.2 |  | -37.7 | 42 | 33.3 | 34.6 | 33.2 | 34 | 33.7 |  | 31.4 | 32.3 | 30.9 | 32 | 31.5333
Kazakhstan |  | BALKASINO | BALKASINO, Kazakhstan | 52.53N | 68.75E | 399 | 6.00 (ASC) | 85-06 | 289780 | -36.3 |  | -44 | 38.3 | 32 | 32.7 | 32.3 | 32 | 32.3333 |  | 29.9 | 29.9 | 29.4 | 30 | 29.7333
Kazakhstan |  | BARSHATAS | BARSHATAS, Kazakhstan | 48.17N | 78.67E | 643 | 6.00 (ASC) | 82-06 | 364980 | -32.3 |  | -44.3 | 39.2 | 33.5 | 35.5 | 34 | 34 | 34.3333 |  | 31.5 | 32.7 | 31.3 | 32 | 31.8333
Kazakhstan |  | BERLIK | BERLIK, Kazakhstan | 49.88N | 69.52E | 349 | 6.00 (ASC) | 85-06 | 353760 | -35 |  | -41.9 | 42 | 35.8 | 35.9 | 35.6 | 36 | 35.7667 |  | 32.9 | 33.4 | 33 | 33 | 33.1
Kazakhstan |  | BLACOVESCHENKA | BLACOVESCHENKA, Kazakhstan | 54.37N | 66.97E | 153 | 6.00 (ASC) | 82-06 | 287660 | -35.3 |  | -46.1 | 38.8 | 33.2 | 33.4 | 31.4 | 33 | 32.6667 |  | 31.1 | 30.6 | 28.7 | 30 | 30.1333
Kazakhstan |  | BOLSHE NARYMSKOE | BOLSHE NARYMSKOE, Kazakhstan | 49.20N | 84.52E | 401 | 6.00 (ASC) | 82-06 | 364280 | -36.8 |  | -46.6 | 43 | 32.7 | 35.1 | 34.5 | 34 | 34.1 |  | 30.7 | 32.4 | 31.7 | 32 | 31.6
Kazakhstan |  | CARDARA | CARDARA, Kazakhstan | 41.37N | 68.00E | 275 | 6.00 (ASC) | 85-06 | 384390 | -14.5 |  | -22.2 | 43.2 | 39.1 | 40 | 38.9 | 39 | 39.3333 |  | 36.7 | 38.2 | 37 | 37 | 37.3
Kazakhstan |  | CELKAR | CELKAR, Kazakhstan | 47.85N | 59.62E | 176 | 5.00 (ASW) | 84-94 | 356330 | -31.7 |  | -35.5 | 42.3 | 38.4 | 38.9 | 36.1 | 38 | 37.8 |  | 36.1 | 35.8 | 34 | 35 | 35.3
Kazakhstan |  | CIRIK-RABAT | CIRIK-RABAT, Kazakhstan | 44.07N | 62.90E | 88 | 6.00 (ASC) | 82-94 | 380490 | -23.7 |  | -36.1 | 48.7 | 41.1 | 42.3 | 40 | 41 | 41.1333 |  | 38.8 | 40.1 | 37.8 | 39 | 38.9
Kazakhstan |  | DZHAMBEJTY | DZHAMBEJTY, Kazakhstan | 50.25N | 52.57E | 32 | 5.00 (ASW) | 82-06 | 352170 | -30.4 |  | -41.2 | 42.8 | 37.9 | 38.1 | 36.5 | 38 | 37.5 |  | 35.3 | 35.6 | 33.6 | 35 | 34.8333
Kazakhstan |  | DZHUSALY | DZHUSALY, Kazakhstan | 45.50N | 64.08E | 103 | 6.00 (ASC) | 85-06 | 359530 | -26.5 |  | -37.2 | 45.9 | 39.9 | 40.9 | 39.8 | 40 | 40.2 |  | 37.7 | 38.2 | 37.6 | 38 | 37.8333
Kazakhstan |  | ESIL | ESIL, Kazakhstan | 51.88N | 66.33E | 221 | 6.00 (ASC) | 85-06 | 350670 | -35.5 |  | -42.5 | 40.3 | 34.2 | 34.6 | 34.6 | 34 | 34.4667 |  | 32.2 | 31.9 | 32 | 32 | 32.0333
Kazakhstan |  | FORT SHEVCHENKO | FORT SHEVCHENKO, Kazakhstan | 44.55N | 50.25E | -25 | 5.00 (ASW) | 82-06 | 380010 | -16.4 |  | -31 | 43.5 | 36 | 37.9 | 38.1 | 37 | 37.3333 |  | 33 | 35 | 35.1 | 34 | 34.3667
Kazakhstan |  | IRGIZ | IRGIZ, Kazakhstan | 48.62N | 61.27E | 114 | 5.00 (ASW) | 82-94 | 355420 | N/A |  | N/A | N/A | 38.8 | 39.4 | 36.1 | 38 | 38.1 |  | 36.1 | 36.2 | 33.6 | 35 | 35.3
Kazakhstan |  | IRTYSHSK | IRTYSHSK, Kazakhstan | 53.35N | 75.45E | 94 | 6.00 (ASC) | 82-06 | 298070 | -36 |  | -46.8 | 39 | 33.5 | 33.6 | 33.1 | 33 | 33.4 |  | 31.3 | 31.1 | 29.9 | 31 | 30.7667
Kazakhstan |  | ISILKUL | ISILKUL, Kazakhstan | 54.90N | 71.25E | 128 | 6.00 (ASC) | 83-06 | 286880 | -36.4 |  | -45.6 | 38.9 | 32.5 | 32.7 | 30.9 | 32 | 32.0333 |  | 30.8 | 29.9 | 28 | 30 | 29.5667
Kazakhstan |  | KARAGANDA | KARAGANDA, Kazakhstan | 49.80N | 73.15E | 553 | 6.00 (ASC) | 82-06 | 353940 | -31.9 |  | -42.5 | 40.5 | 34 | 34.5 | 33.8 | 34 | 34.1 |  | 31.3 | 31.8 | 31.1 | 31 | 31.4
Kazakhstan |  | KARSAKPAJ | KARSAKPAJ, Kazakhstan | 47.83N | 66.75E | 508 | 6.00 (ASC) | 82-94 | 356630 | N/A |  | N/A | N/A | 36.9 | 36.4 | 33.9 | 36 | 35.7333 |  | 33.4 | 33.9 | 31.6 | 33 | 32.9667
Kazakhstan |  | KAZALINSK | KAZALINSK, Kazakhstan | 45.77N | 62.12E | 68 | 6.00 (ASC) | 82-06 | 358490 | -26.8 |  | -38.6 | 46.2 | 39.1 | 39.6 | 38.4 | 39 | 39.0333 |  | 36.9 | 37.5 | 36.1 | 37 | 36.8333
Kazakhstan |  | KOKPEKTY | KOKPEKTY, Kazakhstan | 48.75N | 82.37E | 512 | 6.00 (ASC) | 85-06 | 365350 | -39 |  | -46.6 | 40.5 | 33 | 35 | 34.6 | 34 | 34.2 |  | 30.7 | 32 | 31.6 | 31 | 31.4333
Kazakhstan |  | KOKSHETAY | KOKSHETAY, Kazakhstan | 53.28N | 69.38E | 229 | 6.00 (ASC) | 82-06 | 288790 | -33.5 |  | -44.6 | 39.4 | 33.1 | 33.2 | 31.9 | 33 | 32.7333 |  | 31 | 30.6 | 29.5 | 30 | 30.3667
Kazakhstan |  | KOZASAJ | KOZASAJ, Kazakhstan | 48.22N | 57.12E | 151 | 5.00 (ASW) | 82-94 | 355290 | -31.8 |  | -36.6 | 43 | 38.5 | 39 | 36.1 | 38 | 37.8667 |  | 35.7 | 36.7 | 33.7 | 35 | 35.3667
Kazakhstan |  | KULSARY | KULSARY, Kazakhstan | 46.80N | 53.92E | 18 | 5.00 (ASW) | 82-94 | 357150 | N/A |  | N/A | N/A | 39.7 | 40.7 | 37.7 | 39 | 39.3667 |  | 37.1 | 38.9 | 35.6 | 37 | 37.2
Kazakhstan |  | KUSTANAI | KUSTANAI, Kazakhstan | 53.22N | 63.62E | 156 | 6.00 (ASC) | 82-06 | 289520 | -33.6 |  | -42.7 | 39.9 | 34.6 | 34.7 | 33.6 | 34 | 34.3 |  | 32.3 | 32.2 | 30.4 | 32 | 31.6333
Kazakhstan |  | KYZYLORDA | KYZYLORDA, Kazakhstan | 44.85N | 65.50E | 130 | 6.00 (ASC) | 82-06 | 380620 | -24.1 |  | -33.8 | 45.7 | 39.8 | 40.4 | 39.1 | 40 | 39.7667 |  | 37.3 | 37.8 | 36.9 | 37 | 37.3333
Kazakhstan |  | KZYLZAR | KZYLZAR, Kazakhstan | 48.30N | 69.65E | 361 | 6.00 (ASC) | 82-06 | 355760 | -33 |  | -40.7 | 44.6 | 38 | 37.5 | 35.5 | 37 | 37 |  | 35 | 34.9 | 32.9 | 34 | 34.2667
Kazakhstan |  | LENINOGORSK | LENINOGORSK, Kazakhstan | 50.33N | 83.55E | 811 | 6.00 (ASC) | 85-06 | 362080 | -34 |  | -47.4 | 36.5 | 28.7 | 31.5 | 31.2 | 30 | 30.4667 |  | 26.9 | 28.4 | 28.3 | 28 | 27.8667
Kazakhstan |  | MOINTY | MOINTY, Kazakhstan | 47.20N | 73.35E | 581 | 6.00 (ASC) | 82-91 | 357910 | -32.3 |  | -40.1 | 43.3 | 35.6 | 36 | 34.7 | 35 | 35.4333 |  | 33.1 | 34 | 32.4 | 33 | 33.1667
Kazakhstan |  | MUGODZARSKAJA | MUGODZARSKAJA, Kazakhstan | 48.63N | 58.50E | 398 | 5.00 (ASW) | 85-06 | 355320 | -29.7 |  | -41.5 | 39.9 | 36.1 | 35.3 | 35.9 | 36 | 35.7667 |  | 33.8 | 33.7 | 33.2 | 34 | 33.5667
Kazakhstan |  | NOVYJ USHTOGAN | NOVYJ USHTOGAN, Kazakhstan | 47.90N | 48.80E | -10 | 5.00 (ASW) | 82-06 | 346910 | -25.2 |  | -37.2 | 43.8 | 38.3 | 39.6 | 37.8 | 39 | 38.5667 |  | 35.5 | 37.5 | 35.7 | 36 | 36.2333
Kazakhstan |  | PAVLODAR | PAVLODAR, Kazakhstan | 52.30N | 76.93E | 122 | 6.00 (ASC) | 82-06 | 360030 | -34.6 |  | -45.6 | 40.3 | 34.4 | 34.6 | 34.6 | 35 | 34.5333 |  | 32.2 | 32.1 | 31.3 | 32 | 31.8667
Kazakhstan |  | PETROPAVLOVSK | PETROPAVLOVSK, Kazakhstan | 54.83N | 69.15E | 136 | 6.00 (ASC) | 82-06 | 286790 | -35.3 |  | -44.8 | 38.4 | 33.2 | 33.1 | 31.1 | 32 | 32.4667 |  | 30.9 | 30.4 | 28.6 | 30 | 29.9667
Kazakhstan |  | POLTAVKA | POLTAVKA, Kazakhstan | 54.37N | 71.75E | 124 | 6.00 (ASC) | 82-06 | 287860 | -35.6 |  | -45.9 | 39.3 | 33.5 | 34.1 | 32.2 | 33 | 33.2667 |  | 31.4 | 30.7 | 29.2 | 30 | 30.4333
Kazakhstan |  | RUZAEVKA | RUZAEVKA, Kazakhstan | 52.82N | 66.97E | 227 | 6.00 (ASC) | 85-06 | 289660 | -34.5 |  | -42.8 | 42.4 | 33.5 | 34.2 | 32.6 | 33 | 33.4333 |  | 31.7 | 31.3 | 30.4 | 31 | 31.1333
Kazakhstan |  | SAM | SAM, Kazakhstan | 45.40N | 56.12E | 88 | 5.00 (ASW) | 82-06 | 359250 | -25.8 |  | -39.7 | 46.4 | 39.6 | 41.1 | 40.6 | 40 | 40.4333 |  | 37.2 | 38.7 | 37.7 | 38 | 37.8667
Kazakhstan |  | SEMIJARKA | SEMIJARKA, Kazakhstan | 50.87N | 78.35E | 149 | 6.00 (ASC) | 85-06 | 361520 | -35.9 |  | -47.7 | 42.5 | 35.7 | 36.3 | 36.4 | 36 | 36.1333 |  | 33.1 | 33.6 | 33.7 | 33 | 33.4667
Kazakhstan |  | SEMIPALATINSK | SEMIPALATINSK, Kazakhstan | 50.42N | 80.30E | 196 | 6.00 (ASC) | 82-06 | 361770 | -34.6 |  | -44.6 | 42 | 34.6 | 36.3 | 35.3 | 35 | 35.4 |  | 32.2 | 33.1 | 32 | 32 | 32.4333
Kazakhstan |  | SHYMKENT | SHYMKENT, Kazakhstan | 42.32N | 69.70E | 604 | 6.00 (ASC) | 88-06 | 383280 | -17 |  | -28.6 | 43.5 | 38.2 | 38.9 | 39.1 | 39 | 38.7333 |  | 36.2 | 36.9 | 37 | 37 | 36.7
Kazakhstan |  | SUCINSK | SUCINSK, Kazakhstan | 52.95N | 70.22E | 384 | 6.00 (ASC) | 85-06 | 289840 | -34.8 |  | -43.8 | 38 | 32.1 | 32.3 | 30.9 | 32 | 31.7667 |  | 29.8 | 29.3 | 28.4 | 29 | 29.1667
Kazakhstan |  | TAIPAK | TAIPAK, Kazakhstan | 49.05N | 51.87E | 2 | 5.00 (ASW) | 82-06 | 354060 | -29.3 |  | -46.8 | 42.9 | 37.9 | 38.9 | 37.2 | 38 | 38 |  | 35.6 | 36.8 | 34.9 | 36 | 35.7667
Kazakhstan |  | TASTY | TASTY, Kazakhstan | 44.80N | 69.12E | 190 | 6.00 (ASC) | 82-94 | 380810 | -25.5 |  | -36.6 | 47.9 | 39.2 | 41.4 | 39.1 | 40 | 39.9 |  | 37.4 | 39 | 36.8 | 38 | 37.7333
Kazakhstan |  | TEMIR | TEMIR, Kazakhstan | 49.15N | 57.12E | 234 | 5.00 (ASW) | 85-06 | 354260 | -31.4 |  | -40.5 | 41.6 | 37 | 36.2 | 36.2 | 36 | 36.4667 |  | 34.7 | 34.5 | 33.8 | 34 | 34.3333
Kazakhstan |  | TORGAI | TORGAI, Kazakhstan | 49.63N | 63.50E | 136 | 6.00 (ASC) | 82-06 | 353580 | -31.8 |  | -39.6 | 44.2 | 37.3 | 38.2 | 36.5 | 37 | 37.3333 |  | 35.1 | 35.6 | 34 | 35 | 34.9
Kazakhstan |  | TURKESTAN | TURKESTAN, Kazakhstan | 43.27N | 68.22E | 207 | 6.00 (ASC) | 82-06 | 381980 | -20.7 |  | -34 | 46.9 | 40.6 | 41.2 | 40.3 | 41 | 40.7 |  | 38.1 | 39.3 | 38.5 | 39 | 38.6333
Kazakhstan |  | UC-ARAL | UC-ARAL, Kazakhstan | 46.17N | 80.93E | 397 | 6.00 (ASC) | 82-06 | 367290 | -29.6 |  | -40.4 | 42 | 35.8 | 36.9 | 36.4 | 36 | 36.3667 |  | 33.5 | 35 | 34.3 | 34 | 34.2667
Kazakhstan |  | UIL | UIL, Kazakhstan | 49.07N | 54.68E | 128 | 5.00 (ASW) | 82-06 | 354160 | -29.7 |  | -37.2 | 43.1 | 38.3 | 39 | 36.9 | 38 | 38.0667 |  | 35.9 | 36.3 | 34.4 | 36 | 35.5333
Kazakhstan |  | UJUK | UJUK, Kazakhstan | 43.78N | 70.93E | 366 | 6.00 (ASC) | 85-06 | 382030 | N/A |  | N/A | N/A | 38.4 | 39.9 | 37.4 | 39 | 38.5667 |  | 36 | 37.9 | 35.6 | 37 | 36.5
Kazakhstan |  | ULANBEL` | ULANBEL`, Kazakhstan | 44.80N | 71.07E | 266 | 6.00 (ASC) | 82-94 | 380910 | -24.8 |  | -35.2 | 46.6 | 39.6 | 40.7 | 38.6 | 40 | 39.6333 |  | 36.8 | 38.3 | 36.2 | 37 | 37.1
Kazakhstan |  | URALSK | URALSK, Kazakhstan | 51.25N | 51.28E | 37 | 5.00 (ASW) | 82-06 | 351080 | -31.6 |  | -41.7 | 42.8 | 37.1 | 37.2 | 35.8 | 37 | 36.7 |  | 34 | 34.3 | 32.9 | 34 | 33.7333
Kazakhstan |  | URDZHAR | URDZHAR, Kazakhstan | 47.12N | 81.62E | 491 | 6.00 (ASC) | 83-06 | 366390 | -33.5 |  | -43.8 | 42 | 34.6 | 36.7 | 36.1 | 36 | 35.8 |  | 32.3 | 34.4 | 33.9 | 34 | 33.5333
Kazakhstan |  | URICKY | URICKY, Kazakhstan | 53.32N | 65.55E | 210 | 6.00 (ASC) | 85-06 | 288670 | -32.8 |  | -43.9 | 38.6 | 33.9 | 33.3 | 31.9 | 33 | 33.0333 |  | 31.4 | 30.6 | 29.7 | 31 | 30.5667
Kazakhstan |  | VOLODARSKOE | VOLODARSKOE, Kazakhstan | 53.32N | 68.10E | 319 | 6.00 (ASC) | 83-94 | 288770 | N/A |  | N/A | N/A | 33.1 | 32.4 | 29 | 32 | 31.5 |  | 30.7 | 29.6 | 26.7 | 29 | 29
Kazakhstan |  | ZAJSAN | ZAJSAN, Kazakhstan | 47.47N | 84.92E | 603 | 6.00 (ASC) | 82-94 | 366650 | -30.1 |  | -43.5 | 41.5 | 33.1 | 34.5 | 33.9 | 34 | 33.8333 |  | 30.8 | 32.3 | 31.2 | 31 | 31.4333
Kazakhstan |  | ZHALTYR | ZHALTYR, Kazakhstan | 51.62N | 69.80E | 305 | 6.00 (ASC) | 83-06 | 351730 | -34.7 |  | -42.8 | 42.8 | 34.3 | 34.8 | 33.4 | 34 | 34.1667 |  | 31.6 | 31.8 | 31 | 31 | 31.4667
Kazakhstan |  | ZHAMBYL | ZHAMBYL, Kazakhstan | 42.85N | 71.38E | 655 | 6.00 (ASC) | 82-06 | 383410 | -22 |  | -32.5 | 43.5 | 37.1 | 37.8 | 37.5 | 37 | 37.4667 |  | 34.5 | 35.8 | 35.1 | 35 | 35.1333
Kazakhstan |  | ZHARKENT | ZHARKENT, Kazakhstan | 44.17N | 80.07E | 645 | 6.00 (ASC) | 82-06 | 368590 | -21.9 |  | -31 | 42.1 | 35.5 | 37.3 | 36.6 | 36 | 36.4667 |  | 33.6 | 35.2 | 34.5 | 34 | 34.4333
Kazakhstan |  | ZHARYK | ZHARYK, Kazakhstan | 48.85N | 72.87E | 656 | 6.00 (ASC) | 85-06 | 354970 | -31.5 |  | -40.3 | 40.1 | 33.3 | 34.6 | 33.4 | 34 | 33.7667 |  | 30.9 | 31.9 | 30.9 | 31 | 31.2333
Kazakhstan |  | ZHEZKAZGAN | ZHEZKAZGAN, Kazakhstan | 47.80N | 67.72E | 346 | 6.00 (ASC) | 82-06 | 356710 | -32.6 |  | -42.7 | 42.6 | 37.4 | 38.1 | 37 | 38 | 37.5 |  | 34.9 | 35.5 | 34.7 | 35 | 35.0333
Kazakhstan |  | ZLIKHA | ZLIKHA, Kazakhstan | 45.25N | 67.07E | 138 | 6.00 (ASC) | 84-06 | 359690 | -28.2 |  | -41.4 | 45.6 | 39.5 | 40.6 | 39.5 | 40 | 39.8667 |  | 37.5 | 38 | 37.3 | 38 | 37.6
Kazakhstan |  | ZMEINOGORSK | ZMEINOGORSK, Kazakhstan | 51.15N | 82.20E | 355 | 6.00 (ASC) | 83-06 | 360380 | -37.6 |  | -49.4 | 40.3 | 31.9 | 34.2 | 33.9 | 33 | 33.3333 |  | 29.4 | 30.7 | 30.4 | 30 | 30.1667
Kazakhstan |  | ZVERINOGOLOVSKAJA | ZVERINOGOLOVSKAJA, Kazakhstan | 54.47N | 64.87E | 117 | 6.00 (ASC) | 82-04 | 287560 | -34.4 |  | -44.4 | 41.5 | 34.4 | 34.9 | 31.7 | 34 | 33.6667 |  | 32 | 32.4 | 29.2 | 31 | 31.2
Kenya |  | EMBU | EMBU, Kenya | 0.50S | 37.45E | 1493 | 3.00 (AFE) | 82-05 | 637200 | N/A |  | N/A | N/A | 24.2 | 24.1 | 25.1 | 24 | 24.4667 |  | 23.1 | 22.8 | 23.2 | 23 | 23.0333
Kenya |  | GARISSA | GARISSA, Kenya | 0.47S | 39.63E | 147 | 3.00 (AFE) | 82-06 | 637230 | 16.2 |  | 9.1 | 41.9 | 34.2 | 33.3 | 33.5 | 34 | 33.6667 |  | 33.2 | 32.5 | 32.7 | 33 | 32.8
Kenya |  | KISUMU | KISUMU, Kenya | 0.10S | 34.75E | 1146 | 3.00 (AFE) | 82-06 | 637080 | 11.7 |  | 6.4 | 38.8 | 29.2 | 30.1 | 30.9 | 30 | 30.0667 |  | 28.5 | 29.1 | 29.8 | 29 | 29.1333
Kenya |  | KITALE | KITALE, Kenya | 1.02N | 35.00E | 1875 | 3.00 (AFE) | 82-06 | 636610 | N/A |  | N/A | N/A | 26.1 | 25.6 | 25.5 | 26 | 25.7333 |  | 24.8 | 24.2 | 24.3 | 24 | 24.4333
Kenya |  | LODWAR | LODWAR, Kenya | 3.12N | 35.62E | 515 | 3.00 (AFE) | 83-06 | 636120 | 15.8 |  | 9 | 40.7 | 35.2 | 34.4 | 35.1 | 35 | 34.9 |  | 34.7 | 33.8 | 34.2 | 34 | 34.2333
Kenya |  | MAKINDU | MAKINDU, Kenya | 2.28S | 37.83E | 1000 | 3.00 (AFE) | 83-03 | 637660 | N/A |  | N/A | N/A | 29.1 | 28.6 | 29.1 | 29 | 28.9333 |  | 28.1 | 27.2 | 28.1 | 28 | 27.8
Kenya |  | MARSABIT | MARSABIT, Kenya | 2.30N | 37.90E | 1345 | 3.00 (AFE) | 82-06 | 636410 | N/A |  | N/A | N/A | 26 | 24.5 | 25.5 | 25 | 25.3333 |  | 24.4 | 23.6 | 24.2 | 24 | 24.0667
Kenya |  | MERU | MERU, Kenya | 0.08N | 37.65E | 1554 | 3.00 (AFE) | 82-06 | 636950 | N/A |  | N/A | N/A | 24.1 | 24.1 | 24.9 | 24 | 24.3667 |  | 23.1 | 22.9 | 23.5 | 23 | 23.1667
Kenya |  | MOMBASA | MOMBASA, Kenya | 4.03S | 39.62E | 55 | 3.00 (AFE) | 82-06 | 638200 | 14 |  | 4.4 | 40.6 | 29.7 | 28.9 | 28.9 | 29 | 29.1667 |  | 29 | 28.1 | 28.1 | 28 | 28.4
Kenya |  | MOYALE | MOYALE, Kenya | 3.53N | 39.03E | 1097 | 3.00 (AFE) | 83-02 | 636190 | N/A |  | N/A | N/A | 27 | 26.6 | 27.2 | 27 | 26.9333 |  | 25.6 | 25.1 | 26 | 26 | 25.5667
Kenya |  | NAIROBI/KENYATTA AI | NAIROBI/KENYATTA AI, Kenya | 1.32S | 36.92E | 1624 | 3.00 (AFE) | 82-06 | 637400 | 7.2 |  | 4.2 | 37.4 | 25.8 | 25.9 | 26.9 | 26 | 26.2 |  | 24.4 | 24.1 | 25.2 | 25 | 24.5667
Kenya |  | NAKURU | NAKURU, Kenya | 0.27S | 36.10E | 1901 | 3.00 (AFE) | 82-06 | 637140 | 5.9 |  | 0 | 35 | 26.1 | 25.6 | 26.2 | 26 | 25.9667 |  | 24.9 | 24.2 | 24.9 | 25 | 24.6667
Kenya |  | NYERI | NYERI, Kenya | 0.50S | 36.97E | 1759 | 3.00 (AFE) | 83-06 | 637170 | N/A |  | N/A | N/A | 23.3 | 23 | 23.4 | 23 | 23.2333 |  | 22.1 | 21.5 | 22.1 | 22 | 21.9
Kenya |  | VOI | VOI, Kenya | 3.40S | 38.57E | 579 | 3.00 (AFE) | 82-06 | 637930 | N/A |  | N/A | N/A | 31.1 | 29.8 | 30.4 | 30 | 30.4333 |  | 30 | 28.7 | 29 | 29 | 29.2333
Kiribati |  | TARAWA | TARAWA, Kiribati | 1.35N | 172.92E | 4 | 14.00 (PCK) | 82-06 | 916100 | N/A |  | N/A | N/A | 32.1 | 32.2 | 32.2 | 32 | 32.1667 |  | 31.4 | 31.6 | 31.6 | 32 | 31.5333
Korea |  | ANDONG | ANDONG, Korea, Republic of | 36.57N | 128.72E | 141 | 9.00 (JPN) | 84-06 | 471360 | -14.4 |  | -18.4 | 38.1 | 32.1 | 34.2 | 34.5 | 34 | 33.6 |  | 30.2 | 32.4 | 32.8 | 32 | 31.8
Korea |  | BAENGNYEONGDO AB | BAENGNYEONGDO AB, Korea, Republic of | 37.93N | 124.67E | 171 | 9.00 (JPN) | 82-05 | 471030 | N/A |  | N/A | N/A | 27.8 | 31.1 | 31 | 30 | 29.9667 |  | 25.2 | 28.9 | 29.3 | 28 | 27.8
Korea |  | BUSAN | BUSAN, Korea, Republic of | 35.10N | 129.03E | 70 | 9.00 (JPN) | 82-06 | 471590 | -8.7 |  | -14.5 | 36.3 | 27.6 | 32.1 | 33 | 31 | 30.9 |  | 26.3 | 30.5 | 31.7 | 30 | 29.5
Korea |  | CHEJU | CHEJU, Korea, Republic of | 33.28N | 126.17E | 13 | 9.00 (JPN) | 88-06 | 471850 | -0.9 |  | -5.2 | 34.4 | 26.6 | 31 | 31.6 | 30 | 29.7333 |  | 25.2 | 29.8 | 30.6 | 29 | 28.5333
Korea |  | CHEONGJU | CHEONGJU, Korea, Republic of | 36.63N | 127.45E | 59 | 9.00 (JPN) | 82-06 | 471310 | -14.7 |  | -21.1 | 37.6 | 31.7 | 34.5 | 34.5 | 34 | 33.5667 |  | 30.1 | 32.7 | 33.1 | 32 | 31.9667
Korea |  | CHEONGJU INTL AIRPO | CHEONGJU INTL AIRPO, Korea, Republic of | 36.72N | 127.50E | 60 | 9.00 (JPN) | 82-06 | 471280 | -17.2 |  | -24.4 | 38.4 | 32.2 | 35.1 | 35.1 | 34 | 34.1333 |  | 30.9 | 33.1 | 33.9 | 33 | 32.6333
Korea |  | CHEORWON | CHEORWON, Korea, Republic of | 38.15N | 127.30E | 155 | 9.00 (JPN) | 88-06 | 470950 | -19.9 |  | -28.2 | 36.6 | 30.9 | 32.7 | 32.5 | 32 | 32.0333 |  | 29.1 | 30.9 | 31.2 | 30 | 30.4
Korea |  | CHUNCHEON | CHUNCHEON, Korea, Republic of | 37.90N | 127.73E | 78 | 9.00 (JPN) | 82-06 | 471010 | -17.9 |  | -25.3 | 38.4 | 32.6 | 34.1 | 34.3 | 34 | 33.6667 |  | 30.6 | 32.4 | 32.8 | 32 | 31.9333
Korea |  | CHUPUNGNYEONG | CHUPUNGNYEONG, Korea, Republic of | 36.22N | 128.00E | 245 | 9.00 (JPN) | 82-06 | 471350 | -13.4 |  | -18.3 | 37.1 | 31.2 | 33.5 | 33.5 | 33 | 32.7333 |  | 29.4 | 31.8 | 32 | 31 | 31.0667
Korea |  | DAEGU | DAEGU, Korea, Republic of | 35.88N | 128.62E | 59 | 9.00 (JPN) | 82-06 | 471430 | -10.4 |  | -14.5 | 39.5 | 33.2 | 36 | 36 | 35 | 35.0667 |  | 31.4 | 34.1 | 34.3 | 33 | 33.2667
Korea |  | DAEGU INTL AIRPORT | DAEGU INTL AIRPORT, Korea, Republic of | 35.90N | 128.67E | 35 | 9.00 (JPN) | 82-06 | 471420 | -11.7 |  | -14.4 | 40 | 34 | 37.1 | 37 | 36 | 36.0333 |  | 32 | 35 | 35.2 | 34 | 34.0667
Korea |  | DAEGWALLYEONG | DAEGWALLYEONG, Korea, Republic of | 37.68N | 128.77E | 844 | 9.00 (JPN) | 92-06 | 471000 | -20.8 |  | -26.6 | 33.4 | 27.6 | 28.7 | 28.5 | 28 | 28.2667 |  | 25.2 | 27.1 | 26.8 | 26 | 26.3667
Korea |  | DAEJEON | DAEJEON, Korea, Republic of | 36.37N | 127.37E | 72 | 9.00 (JPN) | 82-06 | 471330 | -14.4 |  | -19.4 | 37.9 | 31.9 | 34.6 | 34.3 | 34 | 33.6 |  | 30.1 | 32.7 | 33 | 32 | 31.9333
Korea |  | DONGHAE RADAR | DONGHAE RADAR, Korea, Republic of | 37.50N | 129.13E | 37 | 9.00 (JPN) | 92-06 | 471060 | -10.6 |  | -15.4 | 37.5 | 29.4 | 32.9 | 32.3 | 32 | 31.5333 |  | 27.3 | 31.2 | 30.5 | 30 | 29.6667
Korea |  | GANGNEUNG | GANGNEUNG, Korea, Republic of | 37.75N | 128.90E | 26 | 9.00 (JPN) | 82-06 | 471050 | -11.2 |  | -17.1 | 39.1 | 33 | 34.6 | 34.8 | 34 | 34.1333 |  | 30.1 | 33 | 32.9 | 32 | 32
Korea |  | GANGNEUNG AB | GANGNEUNG AB, Korea, Republic of | 37.75N | 128.95E | 11 | 9.00 (JPN) | 82-05 | 471070 | N/A |  | N/A | N/A | 32.7 | 34.2 | 35 | 34 | 33.9667 |  | 29.2 | 32.6 | 32.9 | 32 | 31.5667
Korea |  | GIMHAE INTL AIRPORT | GIMHAE INTL AIRPORT, Korea, Republic of | 35.18N | 128.93E | 5 | 9.00 (JPN) | 82-06 | 471530 | -9.7 |  | -13.5 | 38.5 | 30 | 34.2 | 34.2 | 33 | 32.8 |  | 28.2 | 32.2 | 33.1 | 31 | 31.1667
Korea |  | GIMPO INTL AIRPORT | GIMPO INTL AIRPORT, Korea, Republic of | 37.57N | 126.78E | 17 | 9.00 (JPN) | 82-06 | 471100 | -16.4 |  | -24 | 37.3 | 31.1 | 33.8 | 34 | 33 | 32.9667 |  | 29.2 | 31.7 | 32.4 | 31 | 31.1
Korea |  | GUNSAN | GUNSAN, Korea, Republic of | 36.00N | 126.77E | 31 | 9.00 (JPN) | 82-06 | 471400 | -10.2 |  | -15.6 | 36.1 | 29 | 32.8 | 33.3 | 32 | 31.7 |  | 27.4 | 31.4 | 32.1 | 30 | 30.3
Korea |  | GWANGJU | GWANGJU, Korea, Republic of | 35.17N | 126.90E | 74 | 9.00 (JPN) | 82-06 | 471560 | -9.3 |  | -13.6 | 38 | 31.1 | 34.3 | 34.1 | 33 | 33.1667 |  | 29.6 | 32.4 | 32.7 | 32 | 31.5667
Korea |  | GWANGJU AB | GWANGJU AB, Korea, Republic of | 35.12N | 126.82E | 13 | 9.00 (JPN) | 82-05 | 471580 | -11.9 |  | -18.2 | 38.2 | 32.1 | 37.1 | 36 | 35 | 35.0667 |  | 30.9 | 34.1 | 34.6 | 33 | 33.2
Korea |  | INCHEON | INCHEON, Korea, Republic of | 37.47N | 126.63E | 70 | 9.00 (JPN) | 82-06 | 471120 | -12.8 |  | -18.7 | 37.8 | 29.7 | 33.1 | 33 | 32 | 31.9333 |  | 28 | 30.7 | 31.6 | 30 | 30.1
Korea |  | JEJU | JEJU, Korea, Republic of | 33.52N | 126.53E | 23 | 9.00 (JPN) | 82-06 | 471840 | -1.4 |  | -4.8 | 37.4 | 30.3 | 33.1 | 33.4 | 32 | 32.2667 |  | 28.2 | 31.7 | 32 | 31 | 30.6333
Korea |  | JEJU INTL AIRPORT | JEJU INTL AIRPORT, Korea, Republic of | 33.52N | 126.50E | 24 | 9.00 (JPN) | 82-06 | 471820 | -2.3 |  | -6.4 | 37 | 30 | 33.2 | 33.2 | 32 | 32.1333 |  | 28 | 32 | 32 | 31 | 30.6667
Korea |  | JEONJU | JEONJU, Korea, Republic of | 35.82N | 127.15E | 55 | 9.00 (JPN) | 82-06 | 471460 | -12 |  | -17 | 38.7 | 31.4 | 34.9 | 34.4 | 34 | 33.5667 |  | 30.1 | 33.2 | 33.3 | 32 | 32.2
Korea |  | JINJU | JINJU, Korea, Republic of | 35.20N | 128.12E | 23 | 9.00 (JPN) | 82-06 | 471920 | -12 |  | -15.9 | 39.4 | 31.7 | 35.2 | 34.6 | 34 | 33.8333 |  | 29.8 | 32.8 | 33.1 | 32 | 31.9
Korea |  | KUNSAN (US/KOR-AFB) | KUNSAN (US/KOR-AFB), Korea, Republic of | 35.90N | 126.62E | 10 | 9.00 (JPN) | 82-06 | 471410 | -10.5 |  | -16 | 38.7 | 29 | 33.1 | 34 | 32 | 32.0333 |  | 27.1 | 31.2 | 32.2 | 30 | 30.1667
Korea |  | MASAN | MASAN, Korea, Republic of | 35.18N | 128.57E | 4 | 9.00 (JPN) | 88-06 | 471550 | -7.8 |  | -12.5 | 38.5 | 29.5 | 34.4 | 33.9 | 33 | 32.6 |  | 28.1 | 32.4 | 32.7 | 31 | 31.0667
Korea |  | MOESULPO AB | MOESULPO AB, Korea, Republic of | 33.20N | 126.27E | 27 | 9.00 (JPN) | 82-05 | 471870 | N/A |  | N/A | N/A | 27.8 | 32.8 | 32.8 | 31 | 31.1333 |  | 26.1 | 30.9 | 31.2 | 29 | 29.4
Korea |  | MOKPO | MOKPO, Korea, Republic of | 34.82N | 126.38E | 39 | 9.00 (JPN) | 82-06 | 471650 | -7.1 |  | -12.6 | 37.3 | 28.9 | 33.2 | 33.5 | 32 | 31.8667 |  | 27.7 | 31.2 | 32.2 | 30 | 30.3667
Korea |  | OSAN AB | OSAN AB, Korea, Republic of | 37.10N | 127.03E | 12 | 9.00 (JPN) | 82-06 | 471220 | -16.6 |  | -23.2 | 38.4 | 32 | 34.8 | 35.1 | 34 | 33.9667 |  | 30.1 | 32.9 | 33.2 | 32 | 32.0667
Korea |  | POHANG | POHANG, Korea, Republic of | 36.03N | 129.38E | 4 | 9.00 (JPN) | 82-06 | 471380 | -9.4 |  | -14.3 | 39.4 | 33 | 35.6 | 35.4 | 35 | 34.6667 |  | 30.6 | 33.8 | 33.7 | 33 | 32.7
Korea |  | POHANG AB | POHANG AB, Korea, Republic of | 35.98N | 129.42E | 20 | 9.00 (JPN) | 82-05 | 471390 | N/A |  | N/A | N/A | 33.9 | 35.9 | 35.9 | 35 | 35.2333 |  | 31 | 34.1 | 34 | 33 | 33.0333
Korea |  | PYONGTAEK (A-511) | PYONGTAEK (A-511), Korea, Republic of | 36.97N | 127.03E | 14 | 9.00 (JPN) | 82-06 | 471270 | -16.3 |  | -22.5 | 38.9 | 31.8 | 34.2 | 34.2 | 33 | 33.4 |  | 29.9 | 32.8 | 33.1 | 32 | 31.9333
Korea |  | SACHON (KOR-AFB) | SACHON (KOR-AFB), Korea, Republic of | 35.08N | 128.08E | 8 | 9.00 (JPN) | 82-05 | 471610 | N/A |  | N/A | N/A | 31.1 | 35.2 | 35 | 34 | 33.7667 |  | 29.8 | 33.1 | 33.5 | 32 | 32.1333
Korea |  | SEOGWIPO | SEOGWIPO, Korea, Republic of | 33.25N | 126.57E | 51 | 9.00 (JPN) | 82-06 | 471890 | -1.7 |  | -5.8 | 36.5 | 27.7 | 32.6 | 32.6 | 31 | 30.9667 |  | 26.2 | 31.2 | 31.6 | 30 | 29.6667
Korea |  | SEOSAN | SEOSAN, Korea, Republic of | 36.77N | 126.50E | 27 | 9.00 (JPN) | 82-06 | 471290 | -13.4 |  | -18.9 | 37.1 | 30.4 | 33.8 | 33.6 | 33 | 32.6 |  | 28.7 | 31.6 | 32.3 | 31 | 30.8667
Korea |  | SEOUL | SEOUL, Korea, Republic of | 37.57N | 126.97E | 86 | 9.00 (JPN) | 82-06 | 471080 | -14 |  | -20.7 | 38.3 | 31.6 | 34 | 34.1 | 33 | 33.2333 |  | 29.9 | 31.9 | 32.4 | 31 | 31.4
Korea |  | SEOUL (KOR-AF HQ) | SEOUL (KOR-AF HQ), Korea, Republic of | 37.50N | 126.93E | 49 | 9.00 (JPN) | 82-05 | 471170 | N/A |  | N/A | N/A | 33 | 35.2 | 35 | 34 | 34.4 |  | 31 | 33.8 | 33.2 | 33 | 32.6667
Korea |  | SEOUL AB | SEOUL AB, Korea, Republic of | 37.43N | 127.12E | 20 | 9.00 (JPN) | 82-05 | 471110 | N/A |  | N/A | N/A | 32.2 | 35.1 | 35.1 | 34 | 34.1333 |  | 30.9 | 33.1 | 33.8 | 33 | 32.6
Korea |  | SOKCHO | SOKCHO, Korea, Republic of | 38.25N | 128.57E | 19 | 9.00 (JPN) | 82-06 | 470900 | -11.5 |  | -16.7 | 37.3 | 30.1 | 33.1 | 32.5 | 32 | 31.9 |  | 27.5 | 30.9 | 30.7 | 30 | 29.7
Korea |  | SUWON | SUWON, Korea, Republic of | 37.27N | 126.98E | 35 | 9.00 (JPN) | 82-06 | 471190 | -14.4 |  | -21.1 | 37.2 | 30.8 | 33.6 | 33.7 | 33 | 32.7 |  | 29.1 | 31.8 | 32.5 | 31 | 31.1333
Korea |  | TONGYEONG | TONGYEONG, Korea, Republic of | 34.85N | 128.43E | 33 | 9.00 (JPN) | 82-06 | 471620 | -7.5 |  | -11.9 | 37.8 | 27.7 | 32.5 | 32.8 | 31 | 31 |  | 26.3 | 30.1 | 31.4 | 29 | 29.2667
Korea |  | ULJIN | ULJIN, Korea, Republic of | 36.98N | 129.42E | 51 | 9.00 (JPN) | 82-06 | 471300 | -10.4 |  | -15.3 | 37.3 | 30 | 33.3 | 33 | 32 | 32.1 |  | 26.8 | 30.7 | 30.5 | 29 | 29.3333
Korea |  | ULLEUNGDO | ULLEUNGDO, Korea, Republic of | 37.48N | 130.90E | 220 | 9.00 (JPN) | 82-06 | 471150 | -7.7 |  | -12.3 | 36.3 | 27.8 | 30.6 | 31.2 | 30 | 29.8667 |  | 25.7 | 29 | 29.7 | 28 | 28.1333
Korea |  | ULSAN | ULSAN, Korea, Republic of | 35.55N | 129.32E | 36 | 9.00 (JPN) | 82-06 | 471520 | -9 |  | -13.6 | 39 | 31.2 | 34.7 | 34.8 | 34 | 33.5667 |  | 29.3 | 33.2 | 33.3 | 32 | 31.9333
Korea |  | WANDO | WANDO, Korea, Republic of | 34.40N | 126.70E | 35 | 9.00 (JPN) | 84-06 | 471700 | -5.1 |  | -10.4 | 38.3 | 28.7 | 32.3 | 32.7 | 31 | 31.2333 |  | 26.9 | 30.5 | 31.1 | 30 | 29.5
Korea |  | WONJU | WONJU, Korea, Republic of | 37.33N | 127.95E | 151 | 9.00 (JPN) | 88-06 | 471140 | -16.9 |  | -22.2 | 38.7 | 32 | 34.6 | 34.4 | 34 | 33.6667 |  | 30.2 | 32.5 | 33 | 32 | 31.9
Korea |  | YECHEON AB | YECHEON AB, Korea, Republic of | 36.63N | 128.35E | 108 | 9.00 (JPN) | 82-05 | 471340 | N/A |  | N/A | N/A | 32.2 | 36 | 35.4 | 35 | 34.5333 |  | 30.8 | 33.8 | 34 | 33 | 32.8667
Korea |  | YEONGWOL | YEONGWOL, Korea, Republic of | 37.18N | 128.47E | 237 | 9.00 (JPN) | 95-06 | 471210 | -18 |  | -23.3 | 38.1 | 31.8 | 33.2 | 34 | 33 | 33 |  | 30 | 31.5 | 32.2 | 31 | 31.2333
Korea |  | YEOSU | YEOSU, Korea, Republic of | 34.73N | 127.75E | 67 | 9.00 (JPN) | 82-06 | 471680 | -7.6 |  | -12.5 | 36.7 | 27.5 | 32.2 | 32 | 31 | 30.5667 |  | 26.2 | 30.1 | 30.9 | 29 | 29.0667
Kuwait |  | KUWAIT INTERNATIONA | KUWAIT INTERNATIONA, Kuwait | 29.22N | 47.97E | 48 | 3.00 (AFE) | 82-06 | 405820 | 1.6 |  | -2.1 | 51.9 | 48 | 49.1 | 49.1 | 49 | 48.7333 |  | 46.2 | 48 | 47.8 | 47 | 47.3333
Kyrgyzstan |  | BISHKEK | BISHKEK, Kyrgyzstan | 42.85N | 74.53E | 760 | 5.00 (ASW) | 82-06 | 383530 | -22.5 |  | -34.9 | 42.3 | 37 | 37.8 | 36.8 | 37 | 37.2 |  | 34 | 35.6 | 34.6 | 35 | 34.7333
Kyrgyzstan |  | DZHALAL-ABAD | DZHALAL-ABAD, Kyrgyzstan | 40.92N | 72.95E | 765 | 5.00 (ASW) | 82-06 | 386130 | -15.3 |  | -26.1 | 41.5 | 36.9 | 38.5 | 36.2 | 37 | 37.2 |  | 34.9 | 36.2 | 34.5 | 35 | 35.2
Kyrgyzstan |  | NARYN | NARYN, Kyrgyzstan | 41.43N | 76.00E | 2041 | 5.00 (ASW) | 82-06 | 369740 | -27.9 |  | -33.8 | 36.2 | 28.5 | 30.8 | 30.7 | 30 | 30 |  | 25.7 | 28.3 | 28.9 | 28 | 27.6333
Kyrgyzstan |  | OSH | OSH, Kyrgyzstan | 40.53N | 72.80E | 875 | 5.00 (ASW) | 83-03 | 386150 | N/A |  | N/A | N/A | 35.5 | 37.1 | 35.5 | 36 | 36.0333 |  | 33.7 | 35.4 | 34.1 | 34 | 34.4
Kyrgyzstan |  | TALAS | TALAS, Kyrgyzstan | 42.52N | 72.22E | 1218 | 5.00 (ASW) | 83-06 | 383450 | -19.7 |  | -29.3 | 37 | 32.5 | 32.7 | 32.5 | 33 | 32.5667 |  | 30.3 | 30.9 | 30.3 | 31 | 30.5
Kyrgyzstan |  | TIAN-SHAN | TIAN-SHAN, Kyrgyzstan | 41.88N | 78.23E | 3639 | 5.00 (ASW) | 82-06 | 369820 | -35.1 |  | -40.9 | 22.9 | 14 | 16.5 | 16.3 | 16 | 15.6 |  | 11.4 | 13.9 | 14.2 | 13 | 13.1667
Kyrgyzstan |  | TOKMAK | TOKMAK, Kyrgyzstan | 42.83N | 75.28E | 817 | 5.00 (ASW) | 83-06 | 369110 | -19.8 |  | -29.1 | 39.9 | 35.2 | 36.5 | 35.4 | 36 | 35.7 |  | 32.8 | 34.6 | 33.6 | 34 | 33.6667
Latvia |  | AINAZI | AINAZI, Latvia | 57.87N | 24.37E | 5 | 2.00 (EUE) | 93-01 | 262290 | N/A |  | N/A | N/A | 28.1 | 28.8 | 28 | 28 | 28.3 |  | 24.8 | 26.5 | 25.1 | 25 | 25.4667
Latvia |  | DAUGAVPILS | DAUGAVPILS, Latvia | 55.87N | 26.62E | 122 | 2.00 (EUE) | 82-06 | 265440 | -25.7 |  | -37.5 | 35.7 | 27.9 | 31.1 | 28.7 | 29 | 29.2333 |  | 25.7 | 27.9 | 26.5 | 27 | 26.7
Latvia |  | GULBENE | GULBENE, Latvia | 57.13N | 26.72E | 143 | 2.00 (EUE) | 82-03 | 263480 | -23 |  | -35 | 34.9 | 27.6 | 29.8 | 27.8 | 28 | 28.4 |  | 25.2 | 27.1 | 25.9 | 26 | 26.0667
Latvia |  | KOLKA | KOLKA, Latvia | 57.75N | 22.60E | 5 | 2.00 (EUE) | 82-06 | 263130 | -16.3 |  | -32 | 32.3 | 23 | 26.3 | 25.5 | 25 | 24.9333 |  | 21 | 24.5 | 23.6 | 23 | 23.0333
Latvia |  | LIEPAJA | LIEPAJA, Latvia | 56.48N | 21.02E | 7 | 2.00 (EUE) | 82-06 | 264060 | -18.5 |  | -32.7 | 33.4 | 26.5 | 28.8 | 27.9 | 28 | 27.7333 |  | 23.2 | 26.2 | 25.2 | 25 | 24.8667
Latvia |  | MERSRAGS | MERSRAGS, Latvia | 57.35N | 23.12E | 6 | 2.00 (EUE) | 93-01 | 263240 | N/A |  | N/A | N/A | 26.2 | 29.3 | 27.8 | 28 | 27.7667 |  | 23.2 | 25.9 | 24.9 | 25 | 24.6667
Latvia |  | REZEKNE | REZEKNE, Latvia | 56.53N | 27.27E | 157 | 2.00 (EUE) | 93-01 | 264460 | N/A |  | N/A | N/A | 28.4 | 30.7 | 27.6 | 29 | 28.9 |  | 26.5 | 28.2 | 25.9 | 27 | 26.8667
Latvia |  | RIGA | RIGA, Latvia | 56.92N | 23.97E | 11 | 2.00 (EUE) | 94-06 | 264225 | -22.9 |  | -33.3 | 37 | 30.1 | 32 | 29.9 | 31 | 30.6667 |  | 27.2 | 29.2 | 28 | 28 | 28.1333
Latvia |  | RIGA | RIGA, Latvia | 56.97N | 24.05E | 26 | 2.00 (EUE) | 82-06 | 264220 | -20 |  | -35.3 | 35.4 | 28.3 | 30.7 | 28.8 | 29 | 29.2667 |  | 25.1 | 27.9 | 26.6 | 27 | 26.5333
Latvia |  | VALGA | VALGA, Latvia | 57.78N | 26.03E | 66 | 2.00 (EUE) | 82-06 | 262470 | -24.7 |  | -38.4 | 35 | 28.5 | 30.4 | 28.1 | 29 | 29 |  | 26.1 | 27.9 | 26.3 | 27 | 26.7667
Lebanon |  | BEYROUTH (AEROPORT) | BEYROUTH (AEROPORT), Lebanon | 33.82N | 35.48E | 19 | 2.00 (EUE) | 82-06 | 401000 | 6 |  | 0.9 | 41.4 | 31.8 | 32.8 | 31.9 | 32 | 32.1667 |  | 29.1 | 30.2 | 31 | 30 | 30.1
Libyan Arab Jamahiriya |  | AGEDABIA | AGEDABIA, Libyan Arab Jamahiriya | 30.72N | 20.17E | 7 | 2.00 (AFS) | 82-06 | 620550 | N/A |  | N/A | N/A | 40.8 | 39.1 | 38.7 | 40 | 39.5333 |  | 38.3 | 35.8 | 35.8 | 37 | 36.6333
Libyan Arab Jamahiriya |  | BENINA | BENINA, Libyan Arab Jamahiriya | 32.10N | 20.27E | 132 | 2.00 (AFS) | 82-06 | 620530 | 4.3 |  | -0.5 | 45.7 | 40.2 | 38 | 37.7 | 39 | 38.6333 |  | 37.3 | 35.1 | 34.9 | 36 | 35.7667
Libyan Arab Jamahiriya |  | MISURATA | MISURATA, Libyan Arab Jamahiriya | 32.42N | 15.05E | 32 | 2.00 (AFS) | 82-06 | 620160 | N/A |  | N/A | N/A | 39.7 | 38.2 | 36.8 | 38 | 38.2333 |  | 35 | 34.6 | 34.2 | 35 | 34.6
Libyan Arab Jamahiriya |  | SIRTE | SIRTE, Libyan Arab Jamahiriya | 31.20N | 16.58E | 14 | 2.00 (AFS) | 82-06 | 620190 | N/A |  | N/A | N/A | 40.7 | 35.7 | 36.7 | 38 | 37.7 |  | 35 | 32.7 | 33 | 34 | 33.5667
Libyan Arab Jamahiriya |  | TRIPOLI INTERNATION | TRIPOLI INTERNATION, Libyan Arab Jamahiriya | 32.70N | 13.08E | 63 | 2.00 (AFS) | 82-06 | 620100 | 2 |  | -1.6 | 49.5 | 44.1 | 44 | 43.2 | 44 | 43.7667 |  | 40.9 | 41.2 | 40.9 | 41 | 41
Libyan Arab Jamahiriya |  | ZUARA | ZUARA, Libyan Arab Jamahiriya | 32.88N | 12.08E | 3 | 2.00 (AFS) | 82-06 | 620070 | N/A |  | N/A | N/A | 36.1 | 36.3 | 37.4 | 37 | 36.6 |  | 30.7 | 32.3 | 33.2 | 32 | 32.0667
Liechtenstein |  | VADUZ (LIECHTENSTEIN) | VADUZ (LIECHTENSTEIN), Liechtenstein | 47.13N | 9.52E | 463 | 1.00 (EUW) | 82-06 | 69900 | -12.8 |  | -20.9 | 35.8 | 30.7 | 31.6 | 31.3 | 31 | 31.2 |  | 28.2 | 29.1 | 28.4 | 29 | 28.5667
Lithuania |  | BIRZAI | BIRZAI, Lithuania | 56.20N | 24.77E | 62 | 2.00 (EUE) | 94-06 | 265310 | -24.2 |  | -32.7 | 36.4 | 28.8 | 32 | 28.7 | 30 | 29.8333 |  | 26.6 | 29.3 | 27 | 28 | 27.6333
Lithuania |  | KAUNAS | KAUNAS, Lithuania | 54.88N | 23.83E | 770 | 2.00 (EUE) | 82-06 | 266290 | -21.1 |  | -33.2 | 35.3 | 28.1 | 31.2 | 29.5 | 30 | 29.6 |  | 25.5 | 28.3 | 27.3 | 27 | 27.0333
Lithuania |  | KLAIPEDA | KLAIPEDA, Lithuania | 55.73N | 21.07E | 7 | 2.00 (EUE) | 82-06 | 265090 | -16.8 |  | -29 | 33.4 | 26.6 | 29.1 | 27.8 | 28 | 27.8333 |  | 23.1 | 26.4 | 25.3 | 25 | 24.9333
Lithuania |  | LAUKUVA | LAUKUVA, Lithuania | 55.62N | 22.23E | 166 | 2.00 (EUE) | 94-06 | 265180 | -21.4 |  | -31.4 | 32.5 | 27.5 | 30.3 | 27.9 | 29 | 28.5667 |  | 24.8 | 28.1 | 25.6 | 26 | 26.1667
Lithuania |  | SIAULIAI | SIAULIAI, Lithuania | 55.93N | 23.32E | 107 | 2.00 (EUE) | 82-06 | 265240 | -21.7 |  | -34.8 | 35.4 | 27.7 | 31 | 29 | 29 | 29.2333 |  | 25.5 | 28.1 | 26.7 | 27 | 26.7667
Lithuania |  | UTENA | UTENA, Lithuania | 55.53N | 25.60E | 106 | 2.00 (EUE) | 94-06 | 266330 | -25.4 |  | -37.7 | 36 | 28.7 | 32.1 | 28.6 | 30 | 29.8 |  | 26.9 | 29.4 | 26.8 | 28 | 27.7
Lithuania |  | VILNIUS | VILNIUS, Lithuania | 54.63N | 25.28E | 156 | 2.00 (EUE) | 82-06 | 267300 | -22.4 |  | -33.7 | 35.4 | 28.9 | 31.2 | 29.8 | 30 | 29.9667 |  | 26.1 | 28.6 | 27.1 | 27 | 27.2667
Luxembourg |  | LUXEMBOURG/LUXEMBOU | LUXEMBOURG/LUXEMBOU, Luxembourg | 49.62N | 6.22E | 376 | 1.00 (EUW) | 82-06 | 65900 | -11.2 |  | -19.5 | 38.2 | 29.3 | 31.7 | 33 | 31 | 31.3333 |  | 27 | 29.1 | 28.9 | 28 | 28.3333
Macao |  | TAIPA GRANDE | TAIPA GRANDE, Macao | 22.15N | 113.60E | 6 | 8.00 (CHN) | 82-06 | 450110 | 5.5 |  | 2.1 | 37.3 | 33 | 34.2 | 33.9 | 34 | 33.7 |  | 32 | 32.9 | 32.7 | 33 | 32.5333
Macedonia |  | BITOLA | BITOLA, Macedonia, the former Yugoslav Republic of | 41.05N | 21.37E | 589 | 1.00 (EUW) | 82-06 | 135830 | -19.6 |  | -35.6 | 42.9 | 33.1 | 36.4 | 35.4 | 35 | 34.9667 |  | 30.7 | 33.8 | 32.9 | 32 | 32.4667
Macedonia |  | KRIVA PALANKA | KRIVA PALANKA, Macedonia, the former Yugoslav Republic of | 42.20N | 22.33E | 696 | 1.00 (EUW) | 82-06 | 134930 | -15 |  | -23.1 | 40.1 | 32.1 | 34.6 | 34.5 | 34 | 33.7333 |  | 29.7 | 32.1 | 31.8 | 31 | 31.2
Macedonia |  | OHRID | OHRID, Macedonia, the former Yugoslav Republic of | 41.12N | 20.80E | 761 | 1.00 (EUW) | 96-06 | 135780 | -12.7 |  | -19.2 | 36.9 | 31 | 32.9 | 32.7 | 32 | 32.2 |  | 29.1 | 30.9 | 30.9 | 30 | 30.3
Macedonia |  | SKOPJE- AIRPORT | SKOPJE- AIRPORT, Macedonia, the former Yugoslav Republic of | 41.97N | 21.65E | 239 | 1.00 (EUW) | 82-06 | 135860 | -15.2 |  | -28.3 | 44.2 | 35.9 | 39 | 37.8 | 38 | 37.5667 |  | 33.1 | 35.9 | 35.4 | 35 | 34.8
Madagascar |  | ANTANANARIVO/IVATO | ANTANANARIVO/IVATO, Madagascar | 18.80S | 47.48E | 1276 | 3.00 (AFE) | 82-06 | 670830 | 4.3 |  | -1.4 | 34.8 | 24.4 | 23.2 | 25.3 | 24 | 24.3 |  | 22.8 | 22 | 23.1 | 23 | 22.6333
Madagascar |  | MAHAJANGA | MAHAJANGA, Madagascar | 15.67S | 46.35E | 18 | 3.00 (AFE) | 82-06 | 670270 | N/A |  | N/A | N/A | 32.9 | 32.2 | 33.1 | 33 | 32.7333 |  | 32 | 31.3 | 32.1 | 32 | 31.8
Madagascar |  | TOAMASINA | TOAMASINA, Madagascar | 18.12S | 49.40E | 6 | 3.00 (AFE) | 82-06 | 670950 | N/A |  | N/A | N/A | 28 | 26.2 | 26.2 | 27 | 26.8 |  | 27.1 | 25.8 | 25.9 | 26 | 26.2667
Malaysia |  | BINTULU | BINTULU, Malaysia | 3.20N | 113.03E | 5 | 8.00 (MLY) | 82-06 | 964410 | 21.2 |  | 18.8 | 40.2 | 33.2 | 33.3 | 33.9 | 33 | 33.4667 |  | 32.5 | 32.3 | 32.6 | 32 | 32.4667
Malaysia |  | KOTA BHARU | KOTA BHARU, Malaysia | 6.17N | 102.28E | 5 | 8.00 (MLY) | 82-06 | 486150 | 20.8 |  | 18.5 | 37.4 | 33.2 | 33.1 | 33 | 33 | 33.1 |  | 32.6 | 32.2 | 32 | 32 | 32.2667
Malaysia |  | KOTA KINABALU | KOTA KINABALU, Malaysia | 5.93N | 116.05E | 3 | 8.00 (MLY) | 82-06 | 964710 | 20.6 |  | 17.9 | 40.2 | 33.4 | 33.4 | 33.2 | 33 | 33.3333 |  | 32.8 | 32.6 | 32.6 | 33 | 32.6667
Malaysia |  | KUALA LUMPUR SUBANG | KUALA LUMPUR SUBANG, Malaysia | 3.12N | 101.55E | 22 | 8.00 (MLY) | 82-06 | 486470 | 20.8 |  | 18.6 | 38.7 | 34.2 | 34 | 34.1 | 34 | 34.1 |  | 33.6 | 33.1 | 33.1 | 33 | 33.2667
Malaysia |  | KUANTAN | KUANTAN, Malaysia | 3.78N | 103.22E | 16 | 8.00 (MLY) | 82-06 | 486570 | 19.7 |  | 15.1 | 41.7 | 34.1 | 33.6 | 33.7 | 34 | 33.8 |  | 33.2 | 32.8 | 32.9 | 33 | 32.9667
Malaysia |  | KUCHING | KUCHING, Malaysia | 1.48N | 110.33E | 27 | 8.00 (MLY) | 82-06 | 964130 | 21.1 |  | 19.8 | 41.2 | 34.1 | 34.1 | 34.2 | 34 | 34.1333 |  | 33.2 | 33.2 | 33.3 | 33 | 33.2333
Malaysia |  | LABUAN | LABUAN, Malaysia | 5.30N | 115.25E | 30 | 8.00 (MLY) | 87-06 | 964650 | 21.4 |  | 16.8 | 40.3 | 33.1 | 33 | 33 | 33 | 33.0333 |  | 32.2 | 32 | 32.1 | 32 | 32.1
Malaysia |  | MALACCA | MALACCA, Malaysia | 2.27N | 102.25E | 9 | 8.00 (MLY) | 82-06 | 486650 | 20.2 |  | 14.2 | 39 | 33.2 | 32.7 | 32.7 | 33 | 32.8667 |  | 32.5 | 32 | 32 | 32 | 32.1667
Malaysia |  | MIRI | MIRI, Malaysia | 4.33N | 113.98E | 18 | 8.00 (MLY) | 82-06 | 964490 | 20.4 |  | 14.1 | 38.4 | 32.9 | 32.7 | 33 | 33 | 32.8667 |  | 32.1 | 32 | 32.1 | 32 | 32.0667
Malaysia |  | PENANG/BAYAN LEPAS | PENANG/BAYAN LEPAS, Malaysia | 5.30N | 100.27E | 4 | 8.00 (MLY) | 82-06 | 486010 | 21 |  | 16.6 | 40.5 | 33 | 32.3 | 32.2 | 33 | 32.5 |  | 32.1 | 31.9 | 31.9 | 32 | 31.9667
Malaysia |  | SANDAKAN | SANDAKAN, Malaysia | 5.90N | 118.07E | 13 | 8.00 (MLY) | 82-06 | 964910 | 21.3 |  | 16.4 | 41.4 | 34 | 33.8 | 34.1 | 34 | 33.9667 |  | 33 | 32.8 | 33.1 | 33 | 32.9667
Malaysia |  | SIBU | SIBU, Malaysia | 2.33N | 111.83E | 31 | 8.00 (MLY) | 82-06 | 964210 | 20.5 |  | 16.8 | 40.9 | 34.6 | 34.6 | 34.9 | 35 | 34.7 |  | 33.8 | 33.7 | 33.9 | 34 | 33.8
Malaysia |  | SITIAWAN | SITIAWAN, Malaysia | 4.22N | 100.70E | 8 | 8.00 (MLY) | 82-06 | 486200 | 20.4 |  | 16.3 | 38.2 | 33.7 | 33.3 | 33.4 | 33 | 33.4667 |  | 33 | 32.7 | 32.6 | 33 | 32.7667
Malaysia |  | TAWAU | TAWAU, Malaysia | 4.27N | 117.88E | 20 | 8.00 (MLY) | 87-06 | 964810 | 19.9 |  | 15.4 | 41 | 32.1 | 31.8 | 31.8 | 32 | 31.9 |  | 31.4 | 31.1 | 31.1 | 31 | 31.2
Maldives |  | MALE | MALE, Maldives | 4.20N | 73.53E | 2 | 5.00 (ASW) | 82-06 | 435550 | N/A |  | N/A | N/A | 32 | 31.2 | 31.2 | 31 | 31.4667 |  | 31.2 | 31.1 | 31 | 31 | 31.1
Mali |  | BAMAKO/SENOU | BAMAKO/SENOU, Mali | 12.53N | 7.95W | 381 | 0.00 (GRW) | 82-06 | 612910 | 11.8 |  | 5.5 | 44.3 | 38.3 | 35 | 33.2 | 36 | 35.5 |  | 36.7 | 33.3 | 32.1 | 34 | 34.0333
Malta |  | LUQA | LUQA, Malta | 35.85N | 14.48E | 91 | 1.00 (EUW) | 82-06 | 165970 | 4.3 |  | 1.3 | 43.7 | 35.3 | 37.1 | 36.9 | 36 | 36.4333 |  | 31.9 | 34 | 33.8 | 33 | 33.2333
Marshall Islands |  | KWAJALEIN MISSLE RAN | KWAJALEIN MISSLE RAN, Marshall Islands | 8.72N | 167.73E | 8 | 12.00 (FJI) | 82-06 | 913660 | 23.4 |  | 22.1 | 33.2 | 31.2 | 31.2 | 31.4 | 31 | 31.2667 |  | 30.8 | 30.7 | 31 | 31 | 30.8333
Marshall Islands |  | MAJURO WSO AP | MAJURO WSO AP, Marshall Islands | 7.08N | 171.38E | 3 | 12.00 (FJI) | 82-06 | 913760 | 23.3 |  | 22 | 38.2 | 30.7 | 30.9 | 31.1 | 31 | 30.9 |  | 30.3 | 30.4 | 30.6 | 30 | 30.4333
Martinique |  | LE LAMENTIN | LE LAMENTIN, Martinique | 14.60N | 61.00W | 7 | -4.00 (SAZ) | 82-06 | 789250 | 17.2 |  | 14.8 | 35.6 | 31.5 | 31.4 | 32.2 | 32 | 31.7 |  | 31 | 31 | 31.5 | 31 | 31.1667
Mauritania |  | NOUADHIBOU | NOUADHIBOU, Mauritania | 20.93N | 17.03W | 3 | 0.00 (GRW) | 82-06 | 614150 | 10.2 |  | 6 | 42.5 | 32.8 | 31.9 | 33 | 33 | 32.5667 |  | 29.1 | 29 | 30.6 | 30 | 29.5667
Mauritania |  | NOUAKCHOTT | NOUAKCHOTT, Mauritania | 18.10N | 15.95W | 3 | 0.00 (GRW) | 82-06 | 614420 | 9.5 |  | 6.1 | 47.3 | 43.9 | 41 | 39.3 | 41 | 41.4 |  | 40.1 | 34.8 | 35.5 | 37 | 36.8
Mauritius |  | AGALEGA | AGALEGA, Mauritius | 10.43S | 56.75E | 3 | 4.00 (ARN) | 83-06 | 619740 | N/A |  | N/A | N/A | 30.1 | 28.7 | 28.7 | 29 | 29.1667 |  | 29.2 | 28.2 | 28.2 | 29 | 28.5333
Mauritius |  | PLAISANCE (MAURITIUS) | PLAISANCE (MAURITIUS), Mauritius | 20.43S | 57.68E | 57 | 4.00 (ARN) | 82-06 | 619900 | 13.6 |  | 9.1 | 34.6 | 26.9 | 25.6 | 25.5 | 26 | 26 |  | 25.9 | 24.7 | 24.7 | 25 | 25.1
Mauritius |  | RODRIGUES | RODRIGUES, Mauritius | 19.68S | 63.42E | 59 | 4.00 (ARN) | 83-06 | 619880 | 16.7 |  | 12.5 | 35.1 | 27.2 | 26 | 25.8 | 26 | 26.3333 |  | 26.4 | 25.1 | 25 | 26 | 25.5
Mauritius |  | VACOAS (MAURITIUS) | VACOAS (MAURITIUS), Mauritius | 20.30S | 57.50E | 425 | 4.00 (ARN) | 83-06 | 619950 | N/A |  | N/A | N/A | 25.5 | 24.5 | 23.4 | 24 | 24.4667 |  | 23.9 | 22.6 | 22.3 | 23 | 22.9333
Mayotte |  | DZAOUDZI/PAMANZI | DZAOUDZI/PAMANZI, Mayotte | 12.80S | 45.28E | 7 | 3.00 (AFE) | 82-06 | 670050 | N/A |  | N/A | N/A | 29.5 | 28.2 | 28.5 | 29 | 28.7333 |  | 29 | 28 | 28 | 28 | 28.3333
Mexico | BCN_Baja_California_N | GENERAL ABELARDO L | GENERAL ABELARDO L, Mexico | 32.53N | 116.97W | 156 | -8.00 (MET) | 86-06 | 760013 | 3.5 |  | 0.1 | 41 | 30.8 | 31.8 | 33.1 | 32 | 31.9 |  | 27.2 | 29.8 | 30.8 | 29 | 29.2667 |  |  | MexicoBCN_Baja_California_NGENERAL ABELARDO L
Mexico | GRO_Guerrero | GENERAL JUAN N ALVA | GENERAL JUAN N ALVA, Mexico | 16.75N | 99.75W | 5 | -6.00 (MEX) | 82-06 | 768056 | 17.7 |  | 14.1 | 38.8 | 34.1 | 34 | 34.1 | 34 | 34.0667 |  | 33.2 | 33.1 | 33.2 | 33 | 33.1667 |  |  | MexicoGRO_GuerreroGENERAL JUAN N ALVA
Mexico | GUA_Guanajuato | DE GUANAJUATO INTL | DE GUANAJUATO INTL, Mexico | 20.98N | 101.48W | 1861 | -6.00 (MEX) | 92-06 | 765773 | N/A |  | N/A | N/A | 36.1 | 31.8 | 29.2 | 32 | 32.3667 |  | 33 | 29.2 | 28.5 | 30 | 30.2333 |  |  | MexicoGUA_GuanajuatoDE GUANAJUATO INTL
Mexico | GUA_Guanajuato | GUANAJUATO | GUANAJUATO, Mexico | 21.00N | 101.28W | 1999 | -6.00 (MEX) | 82-06 | 765770 | N/A |  | N/A | N/A | 33 | 29.8 | 28.8 | 31 | 30.5333 |  | 30.8 | 28.2 | 27.4 | 29 | 28.8 |  |  | MexicoGUA_GuanajuatoGUANAJUATO
Mexico | JAL_Jalisco | DON MIGUEL Y HIDALG | DON MIGUEL Y HIDALG, Mexico | 20.52N | 103.30W | 1566 | -6.00 (MEX) | 82-06 | 766133 | -0.5 |  | -5 | 38 | 34.9 | 29.2 | 29 | 31 | 31.0333 |  | 33 | 28.1 | 27.9 | 30 | 29.6667 |  |  | MexicoJAL_JaliscoDON MIGUEL Y HIDALG
Mexico | JAL_Jalisco | LICENCIADO GUSTAVO | LICENCIADO GUSTAVO, Mexico | 20.67N | 105.25W | 6 | -6.00 (MEX) | 90-06 | 766013 | 12.1 |  | 8.6 | 39.1 | 33.8 | 34.1 | 34.1 | 34 | 34 |  | 33 | 33.2 | 33.2 | 33 | 33.1333 |  |  | MexicoJAL_JaliscoLICENCIADO GUSTAVO
Mexico | JAL_Jalisco | PUERTO VALLARTA | PUERTO VALLARTA, Mexico | 20.68N | 105.25W | 6 | -7.00 (MEC) | 82-94 | 766014 | 12.5 |  | 10.3 | 37 | 33.2 | 33.9 | 33.9 | 34 | 33.6667 |  | 32.8 | 33 | 33.1 | 33 | 32.9667 |  |  | MexicoJAL_JaliscoPUERTO VALLARTA
Mexico | MEX_México | AEROP. INTERNACIONA | AEROP. INTERNACIONA, Mexico | 19.43N | 99.13W | 2235 | -6.00 (MEX) | 82-94 | 766790 | 0.4 |  | -5.6 | 34 | 29.9 | 26.2 | 26.6 | 28 | 27.5667 |  | 27.9 | 25.1 | 25.2 | 26 | 26.0667 |  |  | MexicoMEX_MéxicoAEROP. INTERNACIONA
Mexico | MEX_México | LICENCIADO ADOLFO L | LICENCIADO ADOLFO L, Mexico | 19.33N | 99.57W | 2643 | -6.00 (MEX) | 92-06 | 766753 | -6 |  | -10.2 | 32 | 27 | 23.2 | 23.2 | 24 | 24.4667 |  | 25 | 22.1 | 22.1 | 23 | 23.0667 |  |  | MexicoMEX_MéxicoLICENCIADO ADOLFO L
Mexico | MEX_México | LICENCIADO BENITO J | LICENCIADO BENITO J, Mexico | 19.43N | 99.07W | 2286 | -6.00 (MEX) | 90-06 | 766793 | 0 |  | -3.3 | 34.2 | 30.2 | 26.2 | 26.1 | 28 | 27.5 |  | 28.1 | 25.1 | 24.9 | 26 | 26.0333 |  |  | MexicoMEX_MéxicoLICENCIADO BENITO J
Mexico | NLE_Nuevo_León | GENERAL MARIANO ESC | GENERAL MARIANO ESC, Mexico | 25.77N | 100.10W | 399 | -6.00 (MEX) | 90-06 | 763943 | 0.5 |  | -5.7 | 49.2 | 40 | 39.2 | 39 | 39 | 39.4 |  | 38 | 38.1 | 37.8 | 38 | 37.9667 |  |  | MexicoNLE_Nuevo_LeónGENERAL MARIANO ESC
Mexico | NLE_Nuevo_León | MONTERREY (CITY) | MONTERREY (CITY), Mexico | 25.73N | 100.30W | 515 | -6.00 (MEX) | 88-06 | 763930 | N/A |  | N/A | N/A | 39.7 | 39 | 38.1 | 39 | 38.9333 |  | 37.3 | 37.6 | 36.9 | 37 | 37.2667 |  |  | MexicoNLE_Nuevo_LeónMONTERREY (CITY)
Mexico | ROO_Quintana_Roo | CANCUN INTL | CANCUN INTL, Mexico | 21.03N | 86.87W | 6 | -6.00 (MEX) | 91-06 | 765906 | 10.9 |  | 5.3 | 39.6 | 33.9 | 35.1 | 35.1 | 35 | 34.7 |  | 33.1 | 34 | 34.1 | 34 | 33.7333 |  |  | MexicoROO_Quintana_RooCANCUN INTL
Mexico | SIN_Sinaloa | GENERAL RAFAEL BUEL | GENERAL RAFAEL BUEL, Mexico | 23.15N | 106.27W | 12 | -7.00 (MEC) | 90-06 | 764593 | 6.9 |  | 2.8 | 38.9 | 34.9 | 34.8 | 34.2 | 35 | 34.6333 |  | 33.9 | 33.9 | 33.2 | 34 | 33.6667 |  |  | MexicoSIN_SinaloaGENERAL RAFAEL BUEL
Mexico | SIN_Sinaloa | MAZATLAN/G.BUELNA I | MAZATLAN/G.BUELNA I, Mexico | 23.15N | 106.25W | 5 | -7.00 (MEC) | 82-93 | 764594 | 8.2 |  | 5.3 | 39 | 35 | 35.8 | 35 | 35 | 35.2667 |  | 33.9 | 34.2 | 34.1 | 34 | 34.0667 |  |  | MexicoSIN_SinaloaMAZATLAN/G.BUELNA I
Mexico | SLP_San_Luis_Potosí | SAN LUIS POTOSI | SAN LUIS POTOSI, Mexico | 22.18N | 100.98W | 1883 | -6.00 (MEX) | 88-06 | 765390 | -3.9 |  | -8.8 | 38.3 | 34 | 30 | 28.6 | 31 | 30.8667 |  | 31.1 | 28.2 | 27.2 | 29 | 28.8333 |  |  | MexicoSLP_San_Luis_PotosíSAN LUIS POTOSI
Mexico | TAM_Tamaulipas | GENERAL FRANCISCO J | GENERAL FRANCISCO J, Mexico | 22.28N | 97.87W | 25 | -6.00 (MEX) | 90-05 | 765493 | 7 |  | -0.5 | 45.8 | 35 | 34.2 | 34.9 | 35 | 34.7 |  | 34 | 33.2 | 34 | 34 | 33.7333 |  |  | MexicoTAM_TamaulipasGENERAL FRANCISCO J
Mexico | TAM_Tamaulipas | TAMPICO/GEN FJ MINA | TAMPICO/GEN FJ MINA, Mexico | 22.28N | 97.85W | 24 | -6.00 (MEX) | 82-94 | 765494 | 7.5 |  | 1.3 | 43.9 | 34.1 | 33 | 33.2 | 33 | 33.4333 |  | 33.1 | 32.1 | 32.9 | 33 | 32.7 |  |  | MexicoTAM_TamaulipasTAMPICO/GEN FJ MINA
Mexico | VER_Veracruz | GENERAL HERIBERTO J | GENERAL HERIBERTO J, Mexico | 19.13N | 96.18W | 33 | -6.00 (MEX) | 90-06 | 766913 | 11.7 |  | 7.2 | 44 | 36.1 | 34.2 | 34.2 | 35 | 34.8333 |  | 34.8 | 33.2 | 33.2 | 34 | 33.7333 |  |  | MexicoVER_VeracruzGENERAL HERIBERTO J
Mexico | VER_Veracruz | VERACRUZ/GEN JARA | VERACRUZ/GEN JARA, Mexico | 19.15N | 96.18W | 29 | -6.00 (MEX) | 82-94 | 766910 | 10 |  | 3.2 | 41.9 | 35.2 | 33.2 | 33.2 | 34 | 33.8667 |  | 33.9 | 32.2 | 32.8 | 33 | 32.9667 |  |  | MexicoVER_VeracruzVERACRUZ/GEN JARA
Mexico | YUC_Yucatán | AEROP.INTERNACIONAL | AEROP.INTERNACIONAL, Mexico | 20.98N | 89.65W | 9 | -6.00 (MEX) | 82-06 | 766440 | 8.1 |  | 4.8 | 44.1 | 38.2 | 37 | 36.2 | 37 | 37.1333 |  | 36.8 | 35.3 | 35.1 | 36 | 35.7333 |  |  | MexicoYUC_YucatánAEROP.INTERNACIONAL
Mexico | ZAC_Zacatecas | GENERAL LEOBARDO C | GENERAL LEOBARDO C, Mexico | 22.88N | 102.68W | 2232 | -6.00 (MEX) | 89-06 | 765255 | -8.4 |  | -16.9 | 35.1 | 31.5 | 28.9 | 28.1 | 30 | 29.5 |  | 30 | 27.2 | 26.8 | 28 | 28 |  |  | MexicoZAC_ZacatecasGENERAL LEOBARDO C
Micronesia |  | CHUUK WSO AP | CHUUK WSO AP, Micronesia, Federated States of | 7.45N | 151.83E | 2 | 10.00 (PCW) | 82-06 | 913340 | 22.1 |  | 16.7 | 40.3 | 31.6 | 31.5 | 31.6 | 32 | 31.5667 |  | 31 | 31 | 31 | 31 | 31
Micronesia |  | POHNPEI WSO | POHNPEI WSO, Micronesia, Federated States of | 6.97N | 158.22E | 46 | 11.00 (PCC) | 88-06 | 913480 | 21.5 |  | 19.8 | 36.3 | 32.1 | 32.2 | 32.8 | 32 | 32.3667 |  | 31.2 | 31.5 | 31.9 | 32 | 31.5333
Micronesia |  | YAP ISLAND WSO AP | YAP ISLAND WSO AP, Micronesia, Federated States of | 9.48N | 138.08E | 13 | 10.00 (PCW) | 82-06 | 914130 | 21.7 |  | 18.6 | 36.3 | 32.1 | 31.9 | 31.8 | 32 | 31.9333 |  | 31.5 | 31.3 | 31.2 | 31 | 31.3333
Moldova |  | KISINEV | KISINEV, Moldova, Republic of | 47.02N | 28.98E | 173 | 2.00 (EUE) | 82-06 | 338150 | -16.1 |  | -25.6 | 38.8 | 30.8 | 33.3 | 33.9 | 33 | 32.6667 |  | 29 | 31.2 | 31.3 | 31 | 30.5
Mongolia |  | ALTAI | ALTAI, Mongolia | 46.40N | 96.25E | 2181 | 8.00 (MNG) | 82-06 | 442770 | -33.8 |  | -40 | 32.5 | 25.4 | 27.8 | 25.1 | 26 | 26.1 |  | 23 | 25.2 | 22.8 | 24 | 23.6667
Mongolia |  | ARVAIHEER | ARVAIHEER, Mongolia | 46.27N | 102.78E | 1813 | 8.00 (MNG) | 82-06 | 442880 | -28.1 |  | -34.6 | 35.6 | 28 | 30.8 | 27.8 | 29 | 28.8667 |  | 25.5 | 27.6 | 25.5 | 26 | 26.2
Mongolia |  | BAITAG | BAITAG, Mongolia | 46.12N | 91.47E | 1186 | 8.00 (MNG) | 84-06 | 442650 | -38 |  | -50.2 | 39.8 | 32.2 | 35 | 32.7 | 33 | 33.3 |  | 30.2 | 31.9 | 30.5 | 31 | 30.8667
Mongolia |  | BARUUNHARAA | BARUUNHARAA, Mongolia | 48.92N | 106.07E | 807 | 8.00 (MNG) | 82-06 | 442410 | -37.6 |  | -44.2 | 44.2 | 33.9 | 35.7 | 34.1 | 35 | 34.5667 |  | 30.9 | 31.8 | 30.4 | 31 | 31.0333
Mongolia |  | BARUUNTURUUN | BARUUNTURUUN, Mongolia | 49.65N | 94.40E | 1232 | 8.00 (MNG) | 83-06 | 442130 | -40.5 |  | -48 | 43 | 30.9 | 34.3 | 30.9 | 32 | 32.0333 |  | 28.4 | 30.2 | 28.1 | 29 | 28.9
Mongolia |  | BARUUN-URT | BARUUN-URT, Mongolia | 46.68N | 113.28E | 981 | 8.00 (MNG) | 82-06 | 443050 | -32.7 |  | -39 | 41.3 | 32.7 | 35 | 33.6 | 34 | 33.7667 |  | 30.3 | 31.7 | 30.4 | 31 | 30.8
Mongolia |  | BAYANBULAG | BAYANBULAG, Mongolia | 46.83N | 98.08E | 2255 | 8.00 (MNG) | 83-06 | 442750 | -38.1 |  | -44.8 | 32.9 | 24.8 | 27.5 | 24.1 | 25 | 25.4667 |  | 22.5 | 24.7 | 22 | 23 | 23.0667
Mongolia |  | BAYANDELGER | BAYANDELGER, Mongolia | 45.73N | 112.37E | 1101 | 8.00 (MNG) | 82-06 | 443520 | -31.5 |  | -37 | 41.6 | 32.3 | 35.3 | 32.9 | 34 | 33.5 |  | 29.9 | 32.3 | 30.5 | 31 | 30.9
Mongolia |  | BAYANHONGOR | BAYANHONGOR, Mongolia | 46.13N | 100.68E | 1859 | 8.00 (MNG) | 82-06 | 442870 | -31.8 |  | -37.5 | 35.4 | 27.9 | 30.4 | 28.2 | 29 | 28.8333 |  | 25.9 | 28.1 | 25.8 | 27 | 26.6
Mongolia |  | BAYAN-OVOO | BAYAN-OVOO, Mongolia | 47.78N | 112.12E | 926 | 8.00 (MNG) | 87-06 | 443020 | -35.6 |  | -41.8 | 40.6 | 33.3 | 35 | 33.1 | 34 | 33.8 |  | 30.4 | 31.8 | 30.6 | 31 | 30.9333
Mongolia |  | BULGAN | BULGAN, Mongolia | 48.80N | 103.55E | 1208 | 8.00 (MNG) | 82-06 | 442390 | -35 |  | -41.5 | 38.7 | 30.3 | 32.2 | 29.7 | 31 | 30.7333 |  | 27.5 | 28.4 | 26.3 | 27 | 27.4
Mongolia |  | CHOIBALSAN | CHOIBALSAN, Mongolia | 48.08N | 114.55E | 747 | 8.00 (MNG) | 82-06 | 442590 | -32.4 |  | -39.3 | 42.6 | 34.2 | 35.5 | 33.7 | 34 | 34.4667 |  | 30.7 | 31.9 | 30.8 | 31 | 31.1333
Mongolia |  | CHOIR | CHOIR, Mongolia | 46.45N | 108.22E | 1286 | 8.00 (MNG) | 82-06 | 442980 | -32.4 |  | -39 | 38.6 | 31.3 | 33.7 | 32 | 32 | 32.3333 |  | 29.1 | 31 | 29.3 | 30 | 29.8
Mongolia |  | DALANZADGAD | DALANZADGAD, Mongolia | 43.58N | 104.42E | 1465 | 8.00 (MNG) | 82-06 | 443730 | -26.5 |  | -32.1 | 39.7 | 32.3 | 35 | 32.2 | 33 | 33.1667 |  | 30.1 | 32.6 | 30.4 | 31 | 31.0333
Mongolia |  | DASHBALBAR | DASHBALBAR, Mongolia | 49.55N | 114.40E | 705 | 8.00 (MNG) | 84-06 | 442560 | -36.9 |  | -45 | 42.1 | 32.4 | 34.9 | 32.9 | 33 | 33.4 |  | 30 | 30.8 | 30.2 | 30 | 30.3333
Mongolia |  | ERDENEMANDAL | ERDENEMANDAL, Mongolia | 48.53N | 101.38E | 1509 | 8.00 (MNG) | 87-06 | 442370 | -33.2 |  | -40.3 | 38.1 | 28.7 | 30.7 | 28.6 | 29 | 29.3333 |  | 26.4 | 27 | 25.4 | 26 | 26.2667
Mongolia |  | GALUUT | GALUUT, Mongolia | 46.70N | 100.13E | 2126 | 8.00 (MNG) | 82-06 | 442840 | -37.9 |  | -45.5 | 32.9 | 25.2 | 27.7 | 25.2 | 26 | 26.0333 |  | 22.9 | 25.2 | 22.5 | 24 | 23.5333
Mongolia |  | HATGAL | HATGAL, Mongolia | 50.43N | 100.15E | 1668 | 8.00 (MNG) | 82-06 | 442070 | -38.3 |  | -45.7 | 32.3 | 24.6 | 26.4 | 23.9 | 25 | 24.9667 |  | 21.7 | 22.5 | 21.2 | 22 | 21.8
Mongolia |  | HOVD | HOVD, Mongolia | 48.02N | 91.57E | 1405 | 8.00 (MNG) | 82-06 | 442180 | -34.7 |  | -45.9 | 38.1 | 30.1 | 32.4 | 30.1 | 31 | 30.8667 |  | 27.8 | 29.5 | 27.8 | 28 | 28.3667
Mongolia |  | HUJIRT | HUJIRT, Mongolia | 46.90N | 102.77E | 1662 | 8.00 (MNG) | 82-06 | 442850 | -34.9 |  | -40.8 | 36.5 | 28.5 | 31.1 | 28.7 | 29 | 29.4333 |  | 25.9 | 27.4 | 25.4 | 26 | 26.2333
Mongolia |  | HUTAG | HUTAG, Mongolia | 49.38N | 102.70E | 938 | 8.00 (MNG) | 82-06 | 442320 | -37.5 |  | -47.1 | 41.8 | 32.6 | 33.6 | 31 | 32 | 32.4 |  | 29.7 | 29.8 | 27.6 | 29 | 29.0333
Mongolia |  | KHALKH-GOL | KHALKH-GOL, Mongolia | 47.62N | 118.62E | 688 | 8.00 (MNG) | 87-06 | 443130 | -40.5 |  | -48.7 | 41.8 | 33.9 | 35.4 | 33.9 | 34 | 34.4 |  | 31 | 32.6 | 30.7 | 31 | 31.4333
Mongolia |  | MAANTI | MAANTI, Mongolia | 47.30N | 107.48E | 1430 | 8.00 (MNG) | 82-06 | 442940 | -36.9 |  | -42.8 | 38.6 | 29.9 | 32.2 | 30 | 31 | 30.7 |  | 27.3 | 29 | 27.4 | 28 | 27.9
Mongolia |  | MANDALGOBI | MANDALGOBI, Mongolia | 45.77N | 106.28E | 1393 | 8.00 (MNG) | 82-06 | 443410 | -30.1 |  | -35.9 | 39.3 | 31.5 | 34.4 | 31.3 | 32 | 32.4 |  | 29 | 31.5 | 29.3 | 30 | 29.9333
Mongolia |  | MATAD | MATAD, Mongolia | 47.17N | 115.63E | 907 | 8.00 (MNG) | 82-06 | 443140 | -32.6 |  | -39.5 | 40.9 | 32.7 | 34.5 | 33.5 | 34 | 33.5667 |  | 29.8 | 31.3 | 30.4 | 31 | 30.5
Mongolia |  | MUREN | MUREN, Mongolia | 49.63N | 100.17E | 1283 | 8.00 (MNG) | 82-06 | 442310 | -36.4 |  | -43.7 | 39.9 | 30.7 | 32.7 | 29.9 | 31 | 31.1 |  | 28.1 | 28.8 | 26.6 | 28 | 27.8333
Mongolia |  | OMNO-GOBI | OMNO-GOBI, Mongolia | 49.02N | 91.72E | 1590 | 8.00 (MNG) | 83-06 | 442150 | -36.6 |  | -47 | 34.7 | 27.6 | 30 | 27.7 | 28 | 28.4333 |  | 25.4 | 27.2 | 25.2 | 26 | 25.9333
Mongolia |  | RINCHINLHUMBE | RINCHINLHUMBE, Mongolia | 51.12N | 99.67E | 1583 | 8.00 (MNG) | 83-06 | 442030 | -44 |  | -50.9 | 35.1 | 26.1 | 28.8 | 25.7 | 27 | 26.8667 |  | 24 | 25 | 22.6 | 24 | 23.8667
Mongolia |  | SAIKHAN-OVOO | SAIKHAN-OVOO, Mongolia | 45.45N | 103.90E | 1316 | 8.00 (MNG) | 84-06 | 443360 | -33.5 |  | -42.6 | 40.9 | 33 | 36 | 32.9 | 34 | 33.9667 |  | 30.7 | 33 | 31.1 | 32 | 31.6
Mongolia |  | SAINSHAND | SAINSHAND, Mongolia | 44.90N | 110.12E | 938 | 8.00 (MNG) | 82-06 | 443540 | -29.9 |  | -35.3 | 42.4 | 34.8 | 37.1 | 34.8 | 36 | 35.5667 |  | 32.3 | 34.6 | 32.6 | 33 | 33.1667
Mongolia |  | TARIALAN | TARIALAN, Mongolia | 49.57N | 102.00E | 1235 | 8.00 (MNG) | 87-06 | 442300 | -33.1 |  | -40.7 | 40 | 30.4 | 32.4 | 30 | 31 | 30.9333 |  | 28.1 | 28.3 | 26 | 27 | 27.4667
Mongolia |  | TOSONTSENGEL | TOSONTSENGEL, Mongolia | 48.73N | 98.20E | 1723 | 8.00 (MNG) | 83-06 | 442250 | -44.7 |  | -52.9 | 36.9 | 28 | 30.7 | 27.5 | 29 | 28.7333 |  | 25.4 | 27.4 | 24.7 | 26 | 25.8333
Mongolia |  | TSETSERLEG | TSETSERLEG, Mongolia | 47.45N | 101.47E | 1691 | 8.00 (MNG) | 82-06 | 442820 | -29.4 |  | -37.8 | 35.5 | 27.9 | 30.4 | 27.8 | 29 | 28.7 |  | 25.2 | 26.4 | 24.8 | 25 | 25.4667
Mongolia |  | TSOGT-OVOO | TSOGT-OVOO, Mongolia | 44.42N | 105.32E | 1298 | 8.00 (MNG) | 82-06 | 443470 | -28.9 |  | -35.4 | 41.8 | 33.3 | 36.5 | 33.3 | 34 | 34.3667 |  | 31 | 33.6 | 31.2 | 32 | 31.9333
Mongolia |  | ULAANBAATAR | ULAANBAATAR, Mongolia | 47.92N | 106.87E | 1306 | 8.00 (MNG) | 82-06 | 442920 | -35.2 |  | -47 | 41.2 | 31.8 | 34 | 31.9 | 33 | 32.5667 |  | 28.8 | 30.3 | 28.6 | 29 | 29.2333
Mongolia |  | ULAANGOM | ULAANGOM, Mongolia | 49.80N | 92.08E | 939 | 8.00 (MNG) | 82-06 | 442120 | -41.5 |  | -47.6 | 38.9 | 31 | 32.7 | 30.1 | 31 | 31.2667 |  | 28.6 | 30 | 27.7 | 29 | 28.7667
Mongolia |  | ULGI | ULGI, Mongolia | 48.93N | 89.93E | 1715 | 8.00 (MNG) | 82-06 | 442140 | -31.6 |  | -39.2 | 33.5 | 27.1 | 29.1 | 27.5 | 28 | 27.9 |  | 25.1 | 26.7 | 25.1 | 26 | 25.6333
Mongolia |  | ULIASTAI | ULIASTAI, Mongolia | 47.75N | 96.85E | 1759 | 8.00 (MNG) | 82-06 | 442720 | -37.1 |  | -43.7 | 36.5 | 28.3 | 31.2 | 27.9 | 29 | 29.1333 |  | 25.9 | 28.2 | 25.3 | 26 | 26.4667
Mongolia |  | UNDERKHAAN | UNDERKHAAN, Mongolia | 47.32N | 110.63E | 1033 | 8.00 (MNG) | 82-06 | 443040 | -38 |  | -44.8 | 41.4 | 32.9 | 34.2 | 32.8 | 33 | 33.3 |  | 29.7 | 30.9 | 29.7 | 30 | 30.1
Mongolia |  | ZAMYN-UUD | ZAMYN-UUD, Mongolia | 43.73N | 111.90E | 964 | 8.00 (MNG) | 82-06 | 443580 | -31.8 |  | -37.3 | 41.1 | 34.8 | 36.9 | 34.5 | 35 | 35.4 |  | 32.4 | 34.6 | 32.5 | 33 | 33.1667
Morocco |  | AGADIR | AGADIR, Morocco | 30.38N | 9.57W | 23 | 0.00 (GRW) | 82-91 | 602500 | 2.2 |  | -0.6 | 50.9 | 30.1 | 33 | 41.9 | 35 | 35 |  | 25.9 | 28.1 | 32.8 | 29 | 28.9333
Morocco |  | AGADIR AL MASSIRA | AGADIR AL MASSIRA, Morocco | 30.32N | 9.40W | 23 | 0.00 (GRW) | 92-06 | 602520 | 2.3 |  | -2.4 | 53 | 37 | 45.3 | 39.1 | 40 | 40.4667 |  | 30.9 | 37.9 | 34.2 | 34 | 34.3333
Morocco |  | AL HOCEIMA | AL HOCEIMA, Morocco | 35.18N | 3.85W | 14 | 0.00 (GRW) | 82-06 | 601070 | 4.3 |  | -1.7 | 39.4 | 30.1 | 33.6 | 32.9 | 32 | 32.2 |  | 28.1 | 30.8 | 30.4 | 30 | 29.7667
Morocco |  | BENI-MELLAL | BENI-MELLAL, Morocco | 32.37N | 6.40W | 472 | 0.00 (GRW) | 82-06 | 601910 | -0.9 |  | -4.3 | 46.3 | 41 | 43.5 | 42.7 | 42 | 42.4 |  | 37.6 | 41.7 | 40.7 | 40 | 40
Morocco |  | CASABLANCA | CASABLANCA, Morocco | 33.57N | 7.67W | 57 | 0.00 (GRW) | 82-06 | 601550 | 4 |  | -0.8 | 42.8 | 29.1 | 33.1 | 31.6 | 31 | 31.2667 |  | 26.2 | 28.9 | 27.9 | 28 | 27.6667
Morocco |  | ERRACHIDIA | ERRACHIDIA, Morocco | 31.93N | 4.40W | 1042 | 0.00 (GRW) | 82-06 | 602100 | -1.7 |  | -6.3 | 42.7 | 39.2 | 40.6 | 39.7 | 40 | 39.8333 |  | 37.5 | 39.6 | 38.7 | 39 | 38.6
Morocco |  | ESSAOUIRA | ESSAOUIRA, Morocco | 31.52N | 9.78W | 8 | 0.00 (GRW) | 82-04 | 602200 | N/A |  | N/A | N/A | 23.5 | 24.7 | 27 | 25 | 25.0667 |  | 22.1 | 22.6 | 22.9 | 23 | 22.5333
Morocco |  | FES-SAIS | FES-SAIS, Morocco | 33.93N | 4.98W | 579 | 0.00 (GRW) | 82-06 | 601410 | -1.9 |  | -6.3 | 45.9 | 39.1 | 41.8 | 41.1 | 41 | 40.6667 |  | 36.2 | 39.5 | 38.8 | 38 | 38.1667
Morocco |  | MARRAKECH | MARRAKECH, Morocco | 31.62N | 8.03W | 466 | 0.00 (GRW) | 82-06 | 602300 | 1.5 |  | -2.8 | 48.3 | 41 | 43.9 | 43.1 | 43 | 42.6667 |  | 37.9 | 41.8 | 41 | 40 | 40.2333
Morocco |  | MEKNES | MEKNES, Morocco | 33.88N | 5.53W | 560 | 0.00 (GRW) | 82-06 | 601500 | -0.4 |  | -5.2 | 46.1 | 38.8 | 41.5 | 41.3 | 41 | 40.5333 |  | 35.7 | 38.8 | 38.1 | 38 | 37.5333
Morocco |  | MIDELT | MIDELT, Morocco | 32.68N | 4.73W | 1515 | 0.00 (GRW) | 82-06 | 601950 | -4.1 |  | -8.5 | 39.5 | 34 | 36 | 35.1 | 35 | 35.0333 |  | 32.2 | 34.6 | 33.7 | 34 | 33.5
Morocco |  | NADOR-AROUI | NADOR-AROUI, Morocco | 34.98N | 3.02W | 177 | 0.00 (GRW) | 86-06 | 603400 | 2.7 |  | -0.2 | 46.1 | 32.2 | 35.9 | 35.9 | 35 | 34.6667 |  | 30.1 | 33 | 33.2 | 32 | 32.1
Morocco |  | NOUASSEUR | NOUASSEUR, Morocco | 33.37N | 7.58W | 206 | 0.00 (GRW) | 82-06 | 601560 | 1.1 |  | -2.5 | 48.8 | 35.6 | 40.2 | 38.2 | 38 | 38 |  | 31.8 | 35 | 34 | 34 | 33.6
Morocco |  | OUARZAZATE | OUARZAZATE, Morocco | 30.93N | 6.90W | 1140 | 0.00 (GRW) | 82-06 | 602650 | -1.8 |  | -6 | 42.2 | 38.1 | 40.1 | 39.2 | 39 | 39.1333 |  | 36.9 | 39 | 38.1 | 38 | 38
Morocco |  | OUJDA | OUJDA, Morocco | 34.78N | 1.93W | 470 | 0.00 (GRW) | 82-06 | 601150 | -1.4 |  | -6 | 47.5 | 36.6 | 40.5 | 40.6 | 39 | 39.2333 |  | 34 | 37.6 | 37.2 | 36 | 36.2667
Morocco |  | RABAT-SALE | RABAT-SALE, Morocco | 34.05N | 6.77W | 79 | 0.00 (GRW) | 82-06 | 601350 | 2.5 |  | -1.9 | 48.9 | 33.6 | 37.3 | 36 | 36 | 35.6333 |  | 28.3 | 31.2 | 30.7 | 30 | 30.0667
Morocco |  | SAFI | SAFI, Morocco | 32.28N | 9.23W | 45 | 0.00 (GRW) | 82-01 | 601850 | 3.6 |  | -0.3 | 49.4 | 33.8 | 37.8 | 36.8 | 36 | 36.1333 |  | 28.7 | 32.5 | 32.9 | 31 | 31.3667
Morocco |  | TANGER (AERODROME) | TANGER (AERODROME), Morocco | 35.73N | 5.90W | 21 | 0.00 (GRW) | 82-06 | 601010 | 1.8 |  | -3.7 | 43.4 | 33.2 | 35.2 | 35.8 | 35 | 34.7333 |  | 30.8 | 33.1 | 33.1 | 32 | 32.3333
Morocco |  | TAZA | TAZA, Morocco | 34.22N | 4.00W | 510 | 0.00 (GRW) | 82-06 | 601270 | 0.7 |  | -4 | 45.8 | 37.9 | 41.4 | 40.5 | 40 | 39.9333 |  | 35.4 | 39.6 | 38.6 | 38 | 37.8667
Morocco |  | TETUAN/SANIA RAMEL | TETUAN/SANIA RAMEL, Morocco | 35.58N | 5.33W | 10 | 0.00 (GRW) | 82-05 | 603180 | 3.7 |  | -1.2 | 43 | 32.9 | 35.6 | 34.9 | 34 | 34.4667 |  | 30 | 32.9 | 32.7 | 32 | 31.8667
Mozambique |  | MAPUTO/MAVALANE | MAPUTO/MAVALANE, Mozambique | 25.92S | 32.57E | 44 | 2.00 (AFS) | 82-06 | 673410 | N/A |  | N/A | N/A | 30.9 | 31.1 | 33.1 | 32 | 31.7 |  | 28.1 | 28.2 | 30.5 | 29 | 28.9333
Namibia |  | WALVIS BAY (PELICAN BAY) | WALVIS BAY (PELICAN BAY), Namibia | 22.88S | 14.43E | 0 | 1.00 (AFW) | 82-06 | 681040 | N/A |  | N/A | N/A | 33.1 | 31.3 | 30.8 | 32 | 31.7333 |  | 28.8 | 27.3 | 25.6 | 27 | 27.2333
Namibia |  | WINDHOEK | WINDHOEK, Namibia | 22.57S | 17.10E | 1700 | 1.00 (AFW) | 86-06 | 681100 | 0.5 |  | -4.4 | 39.5 | 25 | 25 | 27.6 | 26 | 25.8667 |  | 23.4 | 23.6 | 26.1 | 24 | 24.3667
Netherlands |  | AMSTERDAM AP SCHIPH | AMSTERDAM AP SCHIPH, Netherlands | 52.30N | 4.77E | -4 | 1.00 (EUW) | 82-06 | 62400 | -8.7 |  | -18.4 | 36 | 28.9 | 30.3 | 30.4 | 30 | 29.8667 |  | 25.9 | 27.6 | 27.4 | 27 | 26.9667
Netherlands |  | DE BILT | DE BILT, Netherlands | 52.10N | 5.18E | 4 | 1.00 (EUW) | 82-06 | 62600 | -10.3 |  | -19.8 | 36.7 | 29.5 | 31.3 | 30.8 | 31 | 30.5333 |  | 26.8 | 28.8 | 28.3 | 28 | 27.9667
Netherlands |  | DE KOOY | DE KOOY, Netherlands | 52.92N | 4.78E | 4 | 1.00 (EUW) | 82-06 | 62350 | -8.2 |  | -16.5 | 33.7 | 26.9 | 27.7 | 28.1 | 28 | 27.5667 |  | 23 | 25 | 25.3 | 24 | 24.4333
Netherlands |  | DEELEN | DEELEN, Netherlands | 52.07N | 5.88E | 47 | 1.00 (EUW) | 82-06 | 62750 | -11.9 |  | -22.2 | 37.2 | 29.8 | 31.6 | 31.2 | 31 | 30.8667 |  | 27.2 | 29.1 | 28.6 | 28 | 28.3
Netherlands |  | EINDHOVEN | EINDHOVEN, Netherlands | 51.45N | 5.42E | 22 | 1.00 (EUW) | 82-06 | 63700 | -10.2 |  | -19.5 | 37.5 | 30.5 | 31.8 | 31.8 | 31 | 31.3667 |  | 27.6 | 29.4 | 29.1 | 29 | 28.7
Netherlands |  | F3-FB-1 | F3-FB-1, Netherlands | 54.85N | 4.70E | 49 | 0.00 (XXX) | 94-06 | 62390 | -1.1 |  | -4.4 | 25.1 | 17.4 | 21.1 | 21.9 | 20 | 20.1333 |  | 16.5 | 20.2 | 21.2 | 19 | 19.3
Netherlands |  | GILZE RIJEN | GILZE RIJEN, Netherlands | 51.57N | 4.93E | 13 | 1.00 (EUW) | 82-06 | 63500 | -10.9 |  | -19.7 | 37.7 | 30.4 | 32.1 | 31.6 | 31 | 31.3667 |  | 27.4 | 29.2 | 28.8 | 28 | 28.4667
Netherlands |  | GRONINGEN AP EELDE | GRONINGEN AP EELDE, Netherlands | 53.13N | 6.58E | 4 | 1.00 (EUW) | 82-06 | 62800 | -11.8 |  | -22.5 | 36.1 | 29.8 | 30.4 | 31.2 | 30 | 30.4667 |  | 26 | 27.9 | 28.1 | 27 | 27.3333
Netherlands |  | HERWIJNEN AWS | HERWIJNEN AWS, Netherlands | 51.87N | 5.15E | 1 | 1.00 (EUW) | 94-06 | 63560 | N/A |  | N/A | N/A | 31 | 31.1 | 30.2 | 31 | 30.7667 |  | 27.3 | 28.4 | 27.6 | 28 | 27.7667
Netherlands |  | HOEK VAN HOLLAND | HOEK VAN HOLLAND, Netherlands | 51.98N | 4.10E | 14 | 1.00 (EUW) | 82-06 | 63300 | -6.8 |  | -15.2 | 38.5 | 28.7 | 30.6 | 30.3 | 30 | 29.8667 |  | 24.8 | 26.6 | 26.8 | 26 | 26.0667
Netherlands |  | HOOGEVEEN | HOOGEVEEN, Netherlands | 52.75N | 6.52E | 16 | 1.00 (EUW) | 94-06 | 62790 | N/A |  | N/A | N/A | 30.7 | 30.8 | 31.4 | 31 | 30.9667 |  | 26.9 | 28.4 | 27.9 | 28 | 27.7333
Netherlands |  | HOUTRIB | HOUTRIB, Netherlands | 52.53N | 5.43E | 2 | 1.00 (EUW) | 82-94 | 62680 | -8.2 |  | -19.4 | 35.4 | 26.4 | 29.1 | 28.5 | 28 | 28 |  | 23.7 | 26.3 | 25 | 25 | 25
Netherlands |  | HUPSEL AWS | HUPSEL AWS, Netherlands | 52.07N | 6.65E | 29 | 1.00 (EUW) | 94-06 | 62830 | N/A |  | N/A | N/A | 30.9 | 31.5 | 31.6 | 31 | 31.3333 |  | 27.2 | 28.9 | 28.2 | 28 | 28.1
Netherlands |  | IJMUIDEN | IJMUIDEN, Netherlands | 52.47N | 4.57E | 13 | 1.00 (EUW) | 82-95 | 62250 | -6.7 |  | -17.7 | 34.6 | 26.2 | 28.8 | 27.8 | 28 | 27.6 |  | 23.5 | 25.6 | 24.2 | 24 | 24.4333
Netherlands |  | K13-A | K13-A, Netherlands | 53.22N | 3.22E | 30 | 0.00 (XXX) | 96-06 | 62520 | -1.6 |  | -8.9 | 24.9 | 18.3 | 20.2 | 21.7 | 20 | 20.0667 |  | 16.8 | 19.4 | 20.6 | 19 | 18.9333
Netherlands |  | LEEUWARDEN | LEEUWARDEN, Netherlands | 53.22N | 5.77E | 2 | 1.00 (EUW) | 82-06 | 62700 | -10.9 |  | -20.6 | 33.7 | 28.2 | 29 | 29.5 | 29 | 28.9 |  | 24.5 | 26.6 | 26.5 | 26 | 25.8667
Netherlands |  | LELYSTAD AWS | LELYSTAD AWS, Netherlands | 52.45N | 5.53E | -3 | 1.00 (EUW) | 94-06 | 62690 | N/A |  | N/A | N/A | 30 | 30.3 | 30.6 | 30 | 30.3 |  | 26.7 | 28.1 | 27.7 | 28 | 27.5
Netherlands |  | MAASTRICHT AP ZUID | MAASTRICHT AP ZUID, Netherlands | 50.92N | 5.78E | 116 | 1.00 (EUW) | 82-06 | 63800 | -10.2 |  | -20.3 | 38.1 | 30.5 | 32.1 | 32.3 | 32 | 31.6333 |  | 27.3 | 29.2 | 29.1 | 29 | 28.5333
Netherlands |  | MARKNESSE AWS | MARKNESSE AWS, Netherlands | 52.70N | 5.88E | -3 | 1.00 (EUW) | 94-06 | 62730 | N/A |  | N/A | N/A | 29.9 | 30.1 | 29.6 | 30 | 29.8667 |  | 26.5 | 27.8 | 26.7 | 27 | 27
Netherlands |  | NIEUW BEERTA AWS | NIEUW BEERTA AWS, Netherlands | 53.20N | 7.15E | 0 | 1.00 (EUW) | 94-06 | 62860 | N/A |  | N/A | N/A | 30 | 31 | 31.8 | 31 | 30.9333 |  | 26.2 | 28.4 | 28.5 | 28 | 27.7
Netherlands |  | ROTTERDAM AP ZESTIE | ROTTERDAM AP ZESTIE, Netherlands | 51.95N | 4.45E | -4 | 1.00 (EUW) | 82-06 | 63440 | -9.3 |  | -17.4 | 35.7 | 29 | 30.7 | 30.1 | 30 | 29.9333 |  | 26.2 | 28.1 | 27.5 | 27 | 27.2667
Netherlands |  | SOESTERBERG | SOESTERBERG, Netherlands | 52.13N | 5.28E | 16 | 1.00 (EUW) | 82-06 | 62650 | -11.6 |  | -22 | 37.6 | 29.9 | 31.6 | 31.4 | 31 | 30.9667 |  | 27 | 28.9 | 28.7 | 28 | 28.2
Netherlands |  | TERSCHELLING(LGT-H) | TERSCHELLING(LGT-H), Netherlands | 53.37N | 5.22E | 27 | 1.00 (EUW) | 82-94 | 62500 | -6.2 |  | -15.6 | 33 | 24.9 | 27.2 | 25.7 | 26 | 25.9333 |  | 22.5 | 24.5 | 23 | 23 | 23.3333
Netherlands |  | TWENTHE | TWENTHE, Netherlands | 52.27N | 6.90E | 35 | 1.00 (EUW) | 82-06 | 62900 | -12.1 |  | -23.8 | 36.8 | 29.9 | 31.6 | 31.2 | 31 | 30.9 |  | 26.9 | 28.8 | 28.6 | 28 | 28.1
Netherlands |  | VALKENBURG | VALKENBURG, Netherlands | 52.18N | 4.42E | 2 | 1.00 (EUW) | 82-06 | 62100 | -8.5 |  | -17.2 | 35.4 | 28.2 | 29.7 | 29.3 | 29 | 29.0667 |  | 25.1 | 27 | 26.7 | 26 | 26.2667
Netherlands |  | VLIELAND | VLIELAND, Netherlands | 53.25N | 4.92E | 10 | 1.00 (EUW) | 96-06 | 62420 | -6 |  | -13 | 31.5 | 26.7 | 27.4 | 27.9 | 27 | 27.3333 |  | 22.6 | 24.7 | 25.4 | 24 | 24.2333
Netherlands |  | VLISSINGEN | VLISSINGEN, Netherlands | 51.45N | 3.60E | 10 | 1.00 (EUW) | 82-06 | 63100 | -5.6 |  | -14.4 | 35.4 | 26.9 | 29.2 | 28.7 | 28 | 28.2667 |  | 24.4 | 26.4 | 26.1 | 26 | 25.6333
Netherlands |  | VOLKEL | VOLKEL, Netherlands | 51.65N | 5.70E | 21 | 1.00 (EUW) | 82-06 | 63750 | -10.8 |  | -20.7 | 38.2 | 30.1 | 32.2 | 31.9 | 31 | 31.4 |  | 27.3 | 29.3 | 29 | 29 | 28.5333
Netherlands |  | WILHELMINADORP AWS | WILHELMINADORP AWS, Netherlands | 51.53N | 3.90E | 1 | 1.00 (EUW) | 94-06 | 63230 | N/A |  | N/A | N/A | 29.6 | 30.2 | 30.3 | 30 | 30.0333 |  | 26.1 | 28.1 | 27 | 27 | 27.0667
Netherlands |  | WOENSDRECHT | WOENSDRECHT, Netherlands | 51.45N | 4.33E | 17 | 1.00 (EUW) | 95-06 | 63400 | -10.8 |  | -17.2 | 37 | 31.2 | 31.9 | 31.6 | 32 | 31.5667 |  | 28 | 29.2 | 29.4 | 29 | 28.8667
Netherlands Antilles |  | HATO ARPT (CIV/MIL) | HATO ARPT (CIV/MIL), Netherlands Antilles | 12.20N | 68.97W | 9 | -4.00 (SAZ) | 82-06 | 789880 | 22 |  | 20.1 | 40.5 | 33.5 | 33.2 | 34.1 | 34 | 33.6 |  | 32.8 | 32.5 | 33.1 | 33 | 32.8
Netherlands Antilles |  | PRINSES JULIANA | PRINSES JULIANA, Netherlands Antilles | 18.03N | 63.12W | 4 | -4.00 (SAZ) | 82-06 | 788660 | 20.6 |  | 18.1 | 40.2 | 32.5 | 32.4 | 33 | 33 | 32.6333 |  | 32 | 32 | 32.2 | 32 | 32.0667
New Caledonia |  | ILE SURPRISE | ILE SURPRISE, New Caledonia | 18.48S | 163.08E | 5 | 11.00 (PCC) | 82-06 | 915700 | 17 |  | 12.3 | 35.5 | 28.4 | 27.5 | 28 | 28 | 27.9667 |  | 27.5 | 26.7 | 26.9 | 27 | 27.0333
New Caledonia |  | KOUMAC (NLLE-CALEDONIE) | KOUMAC (NLLE-CALEDONIE), New Caledonia | 20.57S | 164.28E | 18 | 11.00 (PCC) | 82-06 | 915770 | 13.2 |  | 8.8 | 36.8 | 28.1 | 27 | 26.8 | 27 | 27.3 |  | 26.5 | 25.4 | 25.5 | 26 | 25.8
New Caledonia |  | LA ROCHE (ILE MARE) | LA ROCHE (ILE MARE), New Caledonia | 21.48S | 168.03E | 42 | 11.00 (PCC) | 96-06 | 915870 | 6.6 |  | 2.9 | 32.6 | 26.5 | 25.6 | 25.5 | 26 | 25.8667 |  | 25.5 | 24.4 | 24.6 | 25 | 24.8333
New Caledonia |  | LA TONTOUTA (NLLE-CALEDONIE) | LA TONTOUTA (NLLE-CALEDONIE), New Caledonia | 22.02S | 166.22E | 14 | 11.00 (PCC) | 82-06 | 915900 | 10.2 |  | 7.5 | 39.1 | 28.8 | 27.2 | 27.7 | 28 | 27.9 |  | 26.8 | 25.7 | 26 | 26 | 26.1667
New Caledonia |  | MATTHEW (ILOT) | MATTHEW (ILOT), New Caledonia | 22.33S | 171.33E | 27 | 11.00 (PCC) | 82-06 | 915980 | N/A |  | N/A | N/A | 26.8 | 25.5 | 25.6 | 26 | 25.9667 |  | 25.1 | 24.2 | 24.3 | 25 | 24.5333
New Caledonia |  | MOUE (ILE DES PINS) | MOUE (ILE DES PINS), New Caledonia | 22.60S | 167.45E | 97 | 11.00 (PCC) | 96-06 | 915960 | 12.7 |  | 9.8 | 32.7 | 25.7 | 24.6 | 24.6 | 25 | 24.9667 |  | 24.5 | 23.5 | 23.5 | 24 | 23.8333
New Caledonia |  | NOUMEA (NLLE-CALEDONIE) | NOUMEA (NLLE-CALEDONIE), New Caledonia | 22.27S | 166.45E | 72 | 11.00 (PCC) | 82-06 | 915920 | 14.7 |  | 12.4 | 37.3 | 27.1 | 26.2 | 26.3 | 27 | 26.5333 |  | 25.4 | 24.6 | 24.7 | 25 | 24.9
New Caledonia |  | OUANAHAM (ILE LIFOU) | OUANAHAM (ILE LIFOU), New Caledonia | 20.77S | 167.23E | 29 | 11.00 (PCC) | 82-06 | 915820 | 7.7 |  | 4.2 | 34.2 | 26.6 | 25.9 | 25.8 | 26 | 26.1 |  | 25.7 | 24.8 | 24.8 | 25 | 25.1
New Caledonia |  | OULOUP (ILE OUVEA) | OULOUP (ILE OUVEA), New Caledonia | 20.65S | 166.58E | 7 | 11.00 (PCC) | 96-06 | 915790 | 10.4 |  | 6.5 | 33.9 | 27.1 | 26.2 | 26.2 | 27 | 26.5 |  | 26.3 | 25.2 | 25.4 | 26 | 25.6333
New Caledonia |  | POINDIMIE (NLLE-CAL) | POINDIMIE (NLLE-CAL), New Caledonia | 20.93S | 165.32E | 13 | 11.00 (PCC) | 82-06 | 915830 | 14.1 |  | 11.3 | 33.9 | 27.4 | 26.3 | 26.7 | 27 | 26.8 |  | 26.2 | 25.4 | 25.3 | 26 | 25.6333
New Zealand |  | AUCKLAND AERO AWS | AUCKLAND AERO AWS, New Zealand | 37.00S | 174.80E | 7 | 12.00 (NZL) | 94-06 | 931100 | 2.2 |  | 0.7 | 30.3 | 18.4 | 17.1 | 16.7 | 17 | 17.4 |  | 17 | 16 | 15.7 | 16 | 16.2333
New Zealand |  | AUCKLAND AIRPORT | AUCKLAND AIRPORT, New Zealand | 37.02S | 174.80E | 6 | 12.00 (NZL) | 82-06 | 931190 | 1.8 |  | -1 | 31 | 18.2 | 17.2 | 17.2 | 18 | 17.5333 |  | 17 | 16 | 16.1 | 16 | 16.3667
New Zealand |  | CAMPBELL ISLAND AWS | CAMPBELL ISLAND AWS, New Zealand | 52.55S | 169.15E | 19 | 12.00 (NZL) | 97-06 | 939470 | -2.7 |  | -5.6 | 20.5 | 10.1 | 9.7 | 9.9 | 10 | 9.9 |  | 9.3 | 9 | 9.2 | 9 | 9.1667
New Zealand |  | CAPE CAMPBELL AWS | CAPE CAMPBELL AWS, New Zealand | 41.73S | 174.20E | 32 | 12.00 (NZL) | 87-06 | 935970 | 3.7 |  | 1.4 | 30.1 | 15.5 | 14.1 | 14.2 | 15 | 14.6 |  | 14.5 | 13.2 | 13.2 | 14 | 13.6333
New Zealand |  | CAPE REINGA AWS | CAPE REINGA AWS, New Zealand | 34.43S | 172.68E | 216 | 12.00 (NZL) | 87-06 | 930040 | 7.1 |  | 4.8 | 26.7 | 17.7 | 16.9 | 16.6 | 17 | 17.0667 |  | 16.8 | 16 | 15.7 | 16 | 16.1667
New Zealand |  | CASTLEPOINT | CASTLEPOINT, New Zealand | 40.90S | 176.23E | 20 | 12.00 (NZL) | 95-06 | 934980 | 3.2 |  | 2.1 | 32.7 | 17 | 15.7 | 15.6 | 16 | 16.1 |  | 16 | 14.4 | 14.2 | 15 | 14.8667
New Zealand |  | CHATHAM ISLANDS AWS | CHATHAM ISLANDS AWS, New Zealand | 43.95S | 176.57W | 49 | 12.75 (NZC) | 94-06 | 939870 | 1.5 |  | -0.9 | 23.7 | 14.6 | 13.6 | 13.5 | 14 | 13.9 |  | 13.8 | 12.9 | 12.6 | 13 | 13.1
New Zealand |  | CHRISTCHURCH | CHRISTCHURCH, New Zealand | 43.48S | 172.55E | 30 | 12.00 (NZL) | 82-06 | 937800 | -4.4 |  | -6.6 | 43.2 | 18 | 16.9 | 18.3 | 18 | 17.7333 |  | 15.9 | 14.3 | 16.1 | 15 | 15.4333
New Zealand |  | CHRISTCHURCH AERO A | CHRISTCHURCH AERO A, New Zealand | 43.48S | 172.52E | 37 | 12.00 (NZL) | 94-06 | 937810 | -4.3 |  | -5.9 | 36 | 17.7 | 16.5 | 18.1 | 17 | 17.4333 |  | 15.3 | 14.2 | 16.1 | 15 | 15.2
New Zealand |  | ENDERBY ISLAND AWS | ENDERBY ISLAND AWS, New Zealand | 50.48S | 166.30E | 40 | 12.00 (NZL) | 92-06 | 939290 | -1.6 |  | -5 | 16 | 10.4 | 9.8 | 10.2 | 10 | 10.1333 |  | 9.8 | 9.4 | 9.6 | 10 | 9.6
New Zealand |  | FAREWELL SPIT AWS | FAREWELL SPIT AWS, New Zealand | 40.55S | 173.00E | 3 | 12.00 (NZL) | 90-06 | 935270 | 1.9 |  | -2.3 | 27.4 | 16.2 | 15.1 | 15.5 | 16 | 15.6 |  | 15.2 | 14.3 | 14.6 | 15 | 14.7
New Zealand |  | GISBORNE AERODROME | GISBORNE AERODROME, New Zealand | 38.65S | 177.98E | 5 | 12.00 (NZL) | 92-06 | 932920 | 0.2 |  | -2.3 | 36.4 | 19.4 | 18.1 | 18.2 | 19 | 18.5667 |  | 17.6 | 16.4 | 16.7 | 17 | 16.9
New Zealand |  | HAAST AWS | HAAST AWS, New Zealand | 43.87S | 169.00E | 5 | 12.00 (NZL) | 82-06 | 937090 | -0.9 |  | -3.6 | 27.1 | 14.2 | 14.1 | 14.7 | 14 | 14.3333 |  | 13.3 | 12.9 | 13.2 | 13 | 13.1333
New Zealand |  | HICKS BAY AWS | HICKS BAY AWS, New Zealand | 37.55S | 178.30E | 46 | 12.00 (NZL) | 91-06 | 931960 | 2.8 |  | 1 | 26.1 | 17.6 | 16.6 | 16 | 17 | 16.7333 |  | 16.7 | 15.8 | 15.2 | 16 | 15.9
New Zealand |  | HOKITIKA AERODROME | HOKITIKA AERODROME, New Zealand | 42.72S | 170.98E | 40 | 12.00 (NZL) | 92-06 | 936150 | -1.6 |  | -3.5 | 28.2 | 14.6 | 14.6 | 14.6 | 15 | 14.6 |  | 13.6 | 13.2 | 13.2 | 13 | 13.3333
New Zealand |  | INVERCARGILL AERODR | INVERCARGILL AERODR, New Zealand | 46.42S | 168.32E | 4 | 12.00 (NZL) | 82-95 | 938440 | -4.2 |  | -7 | 30.8 | 14.6 | 13 | 15 | 14 | 14.2 |  | 12.9 | 11.4 | 13.2 | 13 | 12.5
New Zealand |  | INVERCARGILL AIRPOR | INVERCARGILL AIRPOR, New Zealand | 46.42S | 168.33E | 2 | 12.00 (NZL) | 97-06 | 938450 | -4 |  | -5.9 | 32.1 | 14 | 13.7 | 15 | 14 | 14.2333 |  | 12.3 | 11.9 | 13 | 12 | 12.4
New Zealand |  | KAIKOURA | KAIKOURA, New Zealand | 42.42S | 173.70E | 101 | 12.00 (NZL) | 97-06 | 936780 | 2.2 |  | 0.2 | 33.1 | 18.2 | 17.5 | 16.9 | 18 | 17.5333 |  | 16.1 | 14.4 | 15.2 | 15 | 15.2333
New Zealand |  | KAITAIA | KAITAIA, New Zealand | 35.10S | 173.27E | 54 | 12.00 (NZL) | 85-94 | 930120 | N/A |  | N/A | N/A | 18.1 | 17 | 17.1 | 17 | 17.4 |  | 17.2 | 15.9 | 16.1 | 16 | 16.4
New Zealand |  | MOKOHINAU AWS | MOKOHINAU AWS, New Zealand | 35.90S | 175.10E | 60 | 12.00 (NZL) | 94-06 | 930690 | 8.2 |  | 5.9 | 26.7 | 18.2 | 17.2 | 16.3 | 17 | 17.2333 |  | 17.4 | 16.2 | 15.6 | 16 | 16.4
New Zealand |  | NAPIER AERODROME AW | NAPIER AERODROME AW, New Zealand | 39.45S | 176.85E | 3 | 12.00 (NZL) | 92-06 | 933730 | -1.5 |  | -3.8 | 36.2 | 19.2 | 18.5 | 18.2 | 19 | 18.6333 |  | 17.6 | 16.3 | 16.6 | 17 | 16.8333
New Zealand |  | NELSON AERODROME AW | NELSON AERODROME AW, New Zealand | 41.28S | 173.23E | 7 | 12.00 (NZL) | 92-06 | 935460 | -1.5 |  | -3.7 | 31 | 16 | 14.7 | 15.6 | 15 | 15.4333 |  | 14.6 | 13.8 | 14.2 | 14 | 14.2
New Zealand |  | NEW PLYMOUTH AWS | NEW PLYMOUTH AWS, New Zealand | 39.02S | 174.18E | 32 | 12.00 (NZL) | 92-06 | 933090 | 0.2 |  | -1.6 | 29.6 | 16.6 | 15.7 | 15.2 | 16 | 15.8333 |  | 15.8 | 14.8 | 14.4 | 15 | 15
New Zealand |  | PALMERSTON NORTH AW | PALMERSTON NORTH AW, New Zealand | 40.32S | 175.60E | 39 | 12.00 (NZL) | 92-06 | 934040 | -2.5 |  | -4.3 | 31.8 | 16.6 | 15.7 | 15.8 | 16 | 16.0333 |  | 15.1 | 14.3 | 14.7 | 15 | 14.7
New Zealand |  | PARAPARAUMU AWS | PARAPARAUMU AWS, New Zealand | 40.90S | 174.98E | 7 | 12.00 (NZL) | 95-06 | 934200 | -1.9 |  | -3.5 | 29.6 | 16.2 | 15.4 | 15.1 | 16 | 15.5667 |  | 15.6 | 14.6 | 14.2 | 15 | 14.8
New Zealand |  | PURERUA | PURERUA, New Zealand | 35.12S | 174.02E | 84 | 12.00 (NZL) | 95-06 | 930230 | 4.7 |  | 2.2 | 29 | 18.6 | 17.4 | 16.9 | 18 | 17.6333 |  | 17.7 | 16.7 | 16.2 | 17 | 16.8667
New Zealand |  | PUYSEGUR POINT AWS | PUYSEGUR POINT AWS, New Zealand | 46.17S | 166.63E | 44 | 12.00 (NZL) | 91-06 | 938050 | 2 |  | -1.8 | 26.2 | 14.9 | 14.5 | 14.6 | 15 | 14.6667 |  | 13.3 | 13.2 | 13.2 | 13 | 13.2333
New Zealand |  | QUEENSTOWN AERODROM | QUEENSTOWN AERODROM, New Zealand | 45.02S | 168.73E | 358 | 12.00 (NZL) | 95-06 | 938310 | -5.4 |  | -7.4 | 33 | 13.6 | 12.4 | 14.8 | 14 | 13.6 |  | 11.8 | 10.8 | 12.4 | 12 | 11.6667
New Zealand |  | RAOUL ISLAND (AUT) | RAOUL ISLAND (AUT), New Zealand | 29.25S | 177.92W | 49 | 12.00 (NZL) | 90-06 | 939940 | 9.5 |  | 7 | 30.6 | 21.9 | 20.8 | 20.5 | 21 | 21.0667 |  | 21.1 | 20.1 | 19.6 | 20 | 20.2667
New Zealand |  | SECRETARY ISLAND AW | SECRETARY ISLAND AW, New Zealand | 45.22S | 166.88E | 19 | 12.00 (NZL) | 94-06 | 938000 | 1.7 |  | 0 | 28.1 | 14.6 | 14.4 | 14.5 | 15 | 14.5 |  | 13.6 | 13.3 | 13.3 | 13 | 13.4
New Zealand |  | SOUTH WEST CAPE AWS | SOUTH WEST CAPE AWS, New Zealand | 47.27S | 167.45E | 102 | 12.00 (NZL) | 96-06 | 939090 | 1.5 |  | -0.7 | 27.9 | 13.7 | 12.9 | 13.3 | 13 | 13.3 |  | 12.2 | 11.9 | 12.2 | 12 | 12.1
New Zealand |  | TAIAROA HEAD | TAIAROA HEAD, New Zealand | 45.77S | 170.73E | 76 | 12.00 (NZL) | 82-02 | 938960 | 1.3 |  | -1 | 30.6 | 15.4 | 14.6 | 15.4 | 15 | 15.1333 |  | 13.7 | 12.3 | 13.6 | 13 | 13.2
New Zealand |  | TAUPO AWS | TAUPO AWS, New Zealand | 38.73S | 176.07E | 401 | 12.00 (NZL) | 96-06 | 932450 | -4.5 |  | -5.7 | 30.8 | 15.6 | 14.2 | 13.9 | 15 | 14.5667 |  | 14 | 12.8 | 12.8 | 13 | 13.2
New Zealand |  | TAURANGA AERO AWS | TAURANGA AERO AWS, New Zealand | 37.67S | 176.20E | 5 | 12.00 (NZL) | 95-06 | 931860 | 1.3 |  | -0.1 | 30 | 17.7 | 16.9 | 16.7 | 17 | 17.1 |  | 16.8 | 15.8 | 15.7 | 16 | 16.1
New Zealand |  | TIMARU AERODROME AW | TIMARU AERODROME AW, New Zealand | 44.30S | 171.23E | 27 | 12.00 (NZL) | 96-06 | 937730 | -5.2 |  | -8.5 | 38.6 | 17.1 | 15.9 | 18.6 | 17 | 17.2 |  | 14.4 | 13.2 | 15.5 | 14 | 14.3667
New Zealand |  | WAIOURU AWS | WAIOURU AWS, New Zealand | 39.47S | 175.68E | 823 | 12.00 (NZL) | 88-06 | 933340 | -6.7 |  | -8 | 28.5 | 13.9 | 11.6 | 12.1 | 13 | 12.5333 |  | 11.6 | 10.2 | 10.6 | 11 | 10.8
New Zealand |  | WELLINGTON AIRPORT | WELLINGTON AIRPORT, New Zealand | 41.33S | 174.80E | 8 | 12.00 (NZL) | 89-06 | 934360 | 1.7 |  | -1.6 | 28.4 | 16.8 | 16 | 15.9 | 16 | 16.2333 |  | 15.9 | 14.9 | 14.9 | 15 | 15.2333
New Zealand |  | WESTPORT AERODROME | WESTPORT AERODROME, New Zealand | 41.73S | 171.57E | 5 | 12.00 (NZL) | 95-06 | 935150 | 0.5 |  | -1.4 | 26.4 | 15.1 | 15 | 15 | 15 | 15.0333 |  | 14.2 | 13.9 | 13.8 | 14 | 13.9667
Nicaragua |  | MANAGUA A.C.SANDINO | MANAGUA A.C.SANDINO, Nicaragua | 12.15N | 86.17W | 56 | -6.00 (CAM) | 82-06 | 787410 | 16.4 |  | 11.3 | 38 | 34.8 | 34.1 | 34.9 | 35 | 34.6 |  | 33.2 | 33.1 | 33.8 | 33 | 33.3667
Niger |  | AGADEZ | AGADEZ, Niger | 16.97N | 7.97E | 502 | 1.00 (AFW) | 82-06 | 610240 | N/A |  | N/A | N/A | 43 | 42.1 | 40.3 | 42 | 41.8 |  | 42.1 | 40.9 | 39.4 | 41 | 40.8
Niger |  | BIRNI-NKONNI | BIRNI-NKONNI, Niger | 13.80N | 5.25E | 273 | 1.00 (AFW) | 82-06 | 610750 | N/A |  | N/A | N/A | 40.7 | 38 | 36.6 | 38 | 38.4333 |  | 39.3 | 36.6 | 34.6 | 37 | 36.8333
Niger |  | GAYA | GAYA, Niger | 11.88N | 3.45E | 203 | 1.00 (AFW) | 82-06 | 610990 | N/A |  | N/A | N/A | 38.7 | 35.7 | 34 | 36 | 36.1333 |  | 37.2 | 34.2 | 32.6 | 35 | 34.6667
Niger |  | GOURE | GOURE, Niger | 13.98N | 10.30E | 460 | 1.00 (AFW) | 84-06 | 610450 | N/A |  | N/A | N/A | 41.7 | 39.9 | 38.3 | 40 | 39.9667 |  | 40.7 | 38.4 | 36.6 | 39 | 38.5667
Niger |  | MAGARIA | MAGARIA, Niger | 12.98N | 8.93E | 403 | 1.00 (AFW) | 82-06 | 610910 | N/A |  | N/A | N/A | 40.8 | 38 | 36.3 | 38 | 38.3667 |  | 39.3 | 36.2 | 34.2 | 37 | 36.5667
Niger |  | MAINE-SOROA | MAINE-SOROA, Niger | 13.23N | 11.98E | 337 | 1.00 (AFW) | 82-06 | 610960 | 8.8 |  | 2.6 | 45.7 | 42 | 39.6 | 38.3 | 40 | 39.9667 |  | 40.9 | 38.1 | 35.8 | 38 | 38.2667
Niger |  | MARADI | MARADI, Niger | 13.47N | 7.08E | 373 | 1.00 (AFW) | 82-06 | 610800 | N/A |  | N/A | N/A | 39.6 | 36.6 | 36.5 | 38 | 37.5667 |  | 38.5 | 35.2 | 33.7 | 36 | 35.8
Niger |  | NGUIGMI | NGUIGMI, Niger | 14.25N | 13.12E | 286 | 1.00 (AFW) | 82-06 | 610490 | N/A |  | N/A | N/A | 43.1 | 42 | 40 | 42 | 41.7 |  | 42.1 | 40.4 | 38 | 40 | 40.1667
Niger |  | NIAMEY-AERO | NIAMEY-AERO, Niger | 13.48N | 2.17E | 227 | 1.00 (AFW) | 82-06 | 610520 | 12.2 |  | 7 | 47.6 | 41.2 | 37.9 | 36.6 | 39 | 38.5667 |  | 39.9 | 36.6 | 35 | 37 | 37.1667
Niger |  | TAHOUA | TAHOUA, Niger | 14.90N | 5.25E | 391 | 1.00 (AFW) | 82-06 | 610430 | 11.3 |  | 8.7 | 45.7 | 41.2 | 38.7 | 37.7 | 39 | 39.2 |  | 39.9 | 37.4 | 35.6 | 38 | 37.6333
Niger |  | TILLABERY | TILLABERY, Niger | 14.20N | 1.45E | 210 | 1.00 (AFW) | 82-06 | 610360 | N/A |  | N/A | N/A | 42.1 | 39.5 | 38.2 | 40 | 39.9333 |  | 40.7 | 38.3 | 36.4 | 38 | 38.4667
Niger |  | ZINDER | ZINDER, Niger | 13.78N | 8.98E | 453 | 1.00 (AFW) | 82-06 | 610900 | N/A |  | N/A | N/A | 41.2 | 38.8 | 36.8 | 39 | 38.9333 |  | 40.1 | 37.1 | 35 | 37 | 37.4
Niue |  | ALOFI | ALOFI, Niue | 19.07S | 169.92W | 22 | -10.00 (PCH) | 83-06 | 918220 | N/A |  | N/A | N/A | 29.1 | 28.6 | 28.5 | 29 | 28.7333 |  | 28.1 | 27.5 | 27.6 | 28 | 27.7333
Norfolk Island |  | NORFOLK ISLAND AERO | NORFOLK ISLAND AERO, Norfolk Island | 29.03S | 167.93E | 110 | 11.50 (AUN) | 82-06 | 949960 | 11 |  | 9.3 | 29 | 21.1 | 20.1 | 19.3 | 20 | 20.1667 |  | 20.3 | 19.2 | 18.8 | 19 | 19.4333
North Korea |  | ANJU | ANJU, Korea, Democratic People's Republic of | 39.62N | 125.65E | 27 | 9.00 (JPN) | 82-06 | 470500 | -21.2 |  | -31.8 | 35.9 | 30.1 | 32.3 | 32.3 | 32 | 31.5667 |  | 28.2 | 30 | 30.6 | 30 | 29.6
North Korea |  | CHANGJIN | CHANGJIN, Korea, Democratic People's Republic of | 40.37N | 127.25E | 1080 | 9.00 (JPN) | 82-06 | 470310 | -31.3 |  | -37.7 | 32.9 | 25.8 | 27.2 | 27.6 | 27 | 26.8667 |  | 23.7 | 25.2 | 25.5 | 25 | 24.8
North Korea |  | CHANGJON | CHANGJON, Korea, Democratic People's Republic of | 38.73N | 128.18E | 34 | 9.00 (JPN) | 82-06 | 470610 | -11.7 |  | -17.6 | 38.5 | 31.3 | 32.5 | 33.1 | 32 | 32.3 |  | 28.8 | 31.1 | 31.1 | 30 | 30.3333
North Korea |  | CHONGJIN | CHONGJIN, Korea, Democratic People's Republic of | 41.78N | 129.82E | 43 | 9.00 (JPN) | 82-06 | 470080 | -16 |  | -22.1 | 35.6 | 27 | 29.2 | 30.2 | 29 | 28.8 |  | 24.7 | 27.1 | 28 | 27 | 26.6
North Korea |  | CHUNGGANG | CHUNGGANG, Korea, Democratic People's Republic of | 41.78N | 126.88E | 331 | 9.00 (JPN) | 82-06 | 470140 | -30.1 |  | -36.9 | 36.5 | 30.5 | 32.5 | 33.4 | 32 | 32.1333 |  | 28.8 | 30.2 | 30.9 | 30 | 29.9667
North Korea |  | HAEJU | HAEJU, Korea, Democratic People's Republic of | 38.03N | 125.70E | 81 | 9.00 (JPN) | 82-06 | 470690 | -13.8 |  | -20.2 | 37.1 | 30.4 | 32.4 | 32.6 | 32 | 31.8 |  | 28.4 | 30.2 | 31.1 | 30 | 29.9
North Korea |  | HAMHEUNG | HAMHEUNG, Korea, Democratic People's Republic of | 39.93N | 127.55E | 22 | 9.00 (JPN) | 82-06 | 470410 | -16.5 |  | -22.2 | 38.1 | 33.1 | 33.5 | 33.1 | 33 | 33.2333 |  | 29.8 | 31.3 | 31 | 31 | 30.7
North Korea |  | HUICHON | HUICHON, Korea, Democratic People's Republic of | 40.17N | 126.25E | 155 | 9.00 (JPN) | 82-06 | 470390 | -24.4 |  | -35 | 36.7 | 31.7 | 33.2 | 33.9 | 33 | 32.9333 |  | 29.6 | 31.2 | 31.7 | 31 | 30.8333
North Korea |  | HYESAN | HYESAN, Korea, Democratic People's Republic of | 41.40N | 128.17E | 714 | 9.00 (JPN) | 82-06 | 470160 | -30.5 |  | -36 | 37.1 | 29.9 | 32.6 | 31.8 | 31 | 31.4333 |  | 28 | 29.9 | 29.6 | 29 | 29.1667
North Korea |  | KAESONG | KAESONG, Korea, Democratic People's Republic of | 37.97N | 126.57E | 70 | 9.00 (JPN) | 82-06 | 470700 | -15.9 |  | -23.7 | 37.3 | 30.6 | 32.9 | 32.8 | 32 | 32.1 |  | 28.7 | 30.7 | 31.2 | 30 | 30.2
North Korea |  | KANGGYE | KANGGYE, Korea, Democratic People's Republic of | 40.97N | 126.60E | 306 | 9.00 (JPN) | 82-06 | 470200 | -26.4 |  | -32.9 | 39.3 | 32.5 | 34.5 | 33.9 | 34 | 33.6333 |  | 30.3 | 31.9 | 31.5 | 31 | 31.2333
North Korea |  | KIMCHAEK | KIMCHAEK, Korea, Democratic People's Republic of | 40.67N | 129.20E | 23 | 9.00 (JPN) | 82-06 | 470250 | -15.7 |  | -21.4 | 37.1 | 26.9 | 30.6 | 30.9 | 29 | 29.4667 |  | 23.9 | 27.8 | 27.7 | 26 | 26.4667
North Korea |  | KUSONG | KUSONG, Korea, Democratic People's Republic of | 39.98N | 125.25E | 99 | 9.00 (JPN) | 82-06 | 470370 | -20.8 |  | -29 | 38.1 | 31.1 | 33.3 | 33.7 | 33 | 32.7 |  | 29.2 | 31 | 31.8 | 31 | 30.6667
North Korea |  | NAMPO | NAMPO, Korea, Democratic People's Republic of | 38.72N | 125.38E | 47 | 9.00 (JPN) | 82-06 | 470600 | -14.6 |  | -22 | 36 | 29.6 | 31.8 | 31.7 | 31 | 31.0333 |  | 27.9 | 29.8 | 30.4 | 29 | 29.3667
North Korea |  | PUNGSAN | PUNGSAN, Korea, Democratic People's Republic of | 40.82N | 128.15E | 1200 | 9.00 (JPN) | 82-06 | 470220 | -29.2 |  | -34.8 | 32.2 | 25.7 | 27.1 | 27.9 | 27 | 26.9 |  | 23.7 | 25.4 | 26 | 25 | 25.0333
North Korea |  | PYONGGANG | PYONGGANG, Korea, Democratic People's Republic of | 38.42N | 127.28E | 352 | 9.00 (JPN) | 82-06 | 470750 | -22.7 |  | -32 | 37 | 29.4 | 31.3 | 31.5 | 31 | 30.7333 |  | 27.5 | 29.1 | 29.9 | 29 | 28.8333
North Korea |  | PYONGYANG | PYONGYANG, Korea, Democratic People's Republic of | 39.03N | 125.78E | 36 | 9.00 (JPN) | 82-06 | 470580 | -18 |  | -27.2 | 36.6 | 31.6 | 33 | 32.8 | 32 | 32.4667 |  | 29.7 | 31.1 | 31.3 | 31 | 30.7
North Korea |  | RYONGYON | RYONGYON, Korea, Democratic People's Republic of | 38.15N | 124.88E | 6 | 9.00 (JPN) | 82-06 | 470680 | -15.8 |  | -22.9 | 38.4 | 30.4 | 31.8 | 31.7 | 31 | 31.3 |  | 28.3 | 29.7 | 30.4 | 29 | 29.4667
North Korea |  | SAMJIYON | SAMJIYON, Korea, Democratic People's Republic of | 41.82N | 128.30E | 1381 | 9.00 (JPN) | 82-06 | 470050 | -33.2 |  | -40.4 | 33.9 | 24.5 | 26.1 | 26.6 | 26 | 25.7333 |  | 22.6 | 24.3 | 24.4 | 24 | 23.7667
North Korea |  | SARIWON | SARIWON, Korea, Democratic People's Republic of | 38.52N | 125.77E | 52 | 9.00 (JPN) | 82-06 | 470650 | -16.7 |  | -24.8 | 37.5 | 31.1 | 32.8 | 32.5 | 32 | 32.1333 |  | 29.5 | 30.9 | 31.3 | 31 | 30.5667
North Korea |  | SENBONG | SENBONG, Korea, Democratic People's Republic of | 42.32N | 130.40E | 3 | 9.00 (JPN) | 82-06 | 470030 | -18.6 |  | -24.6 | 35.9 | 27.8 | 28.8 | 30.1 | 29 | 28.9 |  | 23.8 | 26.4 | 27.8 | 26 | 26
North Korea |  | SINGYE | SINGYE, Korea, Democratic People's Republic of | 38.50N | 126.53E | 97 | 9.00 (JPN) | 82-06 | 470670 | -19.2 |  | -29.3 | 37.9 | 31.9 | 33.6 | 33.3 | 33 | 32.9333 |  | 29.9 | 31 | 31.5 | 31 | 30.8
North Korea |  | SINPO | SINPO, Korea, Democratic People's Republic of | 40.03N | 128.18E | 19 | 9.00 (JPN) | 82-06 | 470460 | -15.3 |  | -22.5 | 36 | 27.4 | 29.8 | 29.9 | 29 | 29.0333 |  | 25 | 28.2 | 28.2 | 27 | 27.1333
North Korea |  | SINUIJU | SINUIJU, Korea, Democratic People's Republic of | 40.10N | 124.38E | 7 | 9.00 (JPN) | 82-06 | 470350 | -19.4 |  | -27.2 | 37.5 | 30.9 | 33.1 | 32.8 | 32 | 32.2667 |  | 28.3 | 30.7 | 31.1 | 30 | 30.0333
North Korea |  | SUPUNG | SUPUNG, Korea, Democratic People's Republic of | 40.45N | 124.93E | 76 | 9.00 (JPN) | 82-06 | 470280 | -21.5 |  | -29.1 | 37.5 | 30.9 | 33.2 | 33.4 | 33 | 32.5 |  | 29.3 | 30.9 | 31.2 | 30 | 30.4667
North Korea |  | WONSAN | WONSAN, Korea, Democratic People's Republic of | 39.18N | 127.43E | 36 | 9.00 (JPN) | 82-06 | 470550 | -13.7 |  | -20.4 | 38.5 | 32.6 | 33.2 | 33.5 | 33 | 33.1 |  | 29.7 | 31.5 | 31.2 | 31 | 30.8
North Korea |  | YANGDOK | YANGDOK, Korea, Democratic People's Republic of | 39.22N | 126.65E | 279 | 9.00 (JPN) | 82-06 | 470520 | -23.4 |  | -32.4 | 36.2 | 31 | 31.8 | 32.2 | 32 | 31.6667 |  | 29.1 | 29.9 | 30.5 | 30 | 29.8333
Northern Mariana Islands |  | SAIPAN | SAIPAN, Northern Mariana Islands | 15.12N | 145.70E | 32 | 10.00 (PCW) | 86-99 | 912320 | 21.2 |  | 19.4 | 41 | 33.5 | 33 | 33.6 | 33 | 33.3667 |  | 32.1 | 32 | 32.1 | 32 | 32.0667
Norway |  | ALTA LUFTHAVN | ALTA LUFTHAVN, Norway | 69.98N | 23.37E | 3 | 1.00 (EUW) | 84-06 | 10490 | -23.3 |  | -31.8 | 32.8 | 23.2 | 26.8 | 25.1 | 25 | 25.0333 |  | 20.2 | 23.5 | 21.7 | 22 | 21.8
Norway |  | ANDOYA | ANDOYA, Norway | 69.30N | 16.13E | 14 | 1.00 (EUW) | 82-06 | 10100 | -13.2 |  | -18.7 | 27.7 | 20.1 | 21.6 | 21.1 | 21 | 20.9333 |  | 17 | 19 | 18.4 | 18 | 18.1333
Norway |  | BANAK | BANAK, Norway | 70.07N | 24.98E | 8 | 1.00 (EUW) | 84-06 | 10590 | -27.3 |  | -36.5 | 34.3 | 24.1 | 27.2 | 25.5 | 26 | 25.6 |  | 20.9 | 24.1 | 21.7 | 22 | 22.2333
Norway |  | BARDUFOSS | BARDUFOSS, Norway | 69.07N | 18.53E | 79 | 1.00 (EUW) | 82-06 | 10230 | -28.7 |  | -35.5 | 30.8 | 24.8 | 26.1 | 25.6 | 26 | 25.5 |  | 22.1 | 23.7 | 22.1 | 23 | 22.6333
Norway |  | BERGEN/FLESLAND | BERGEN/FLESLAND, Norway | 60.28N | 5.23E | 50 | 1.00 (EUW) | 82-06 | 13110 | -9.8 |  | -18.3 | 30.7 | 24.1 | 25.1 | 26.1 | 25 | 25.1 |  | 21.1 | 22.5 | 23 | 22 | 22.2
Norway |  | BERGEN/FLORIDA | BERGEN/FLORIDA, Norway | 60.38N | 5.33E | 36 | 1.00 (EUW) | 82-06 | 13170 | -8.8 |  | -15.6 | 31.8 | 25.5 | 26.3 | 26.8 | 26 | 26.2 |  | 22.5 | 23.8 | 24.1 | 23 | 23.4667
Norway |  | BODO VI | BODO VI, Norway | 67.27N | 14.37E | 13 | 1.00 (EUW) | 82-06 | 11520 | -12.8 |  | -18.1 | 30.7 | 23.1 | 24.8 | 23.7 | 24 | 23.8667 |  | 20.2 | 22 | 20.9 | 21 | 21.0333
Norway |  | EKOFISK OIL PLTFRM | EKOFISK OIL PLTFRM, Norway | 56.55N | 3.25E | 3 | 0.00 (XXX) | 82-06 | 14033 | -2.2 |  | -7.5 | 26.5 | 17.9 | 20.2 | 21.2 | 20 | 19.7667 |  | 16.1 | 19.1 | 20.2 | 18 | 18.4667
Norway |  | FAGERNES | FAGERNES, Norway | 60.98N | 9.23E | 365 | 1.00 (EUW) | 85-06 | 13670 | -25.7 |  | -36.8 | 32.9 | 26.6 | 28 | 26.4 | 27 | 27 |  | 23.7 | 25.4 | 24.2 | 24 | 24.4333
Norway |  | FERDER FYR | FERDER FYR, Norway | 59.03N | 10.53E | 8 | 1.00 (EUW) | 82-06 | 14820 | -10.3 |  | -20.3 | 29.5 | 23.2 | 24.2 | 24.5 | 24 | 23.9667 |  | 21.2 | 22.6 | 23.1 | 22 | 22.3
Norway |  | FOKSTUA II | FOKSTUA II, Norway | 62.12N | 9.28E | 974 | 1.00 (EUW) | 88-06 | 12380 | -22.3 |  | -29.6 | 28.1 | 21.3 | 22.7 | 22.1 | 22 | 22.0333 |  | 18 | 20.8 | 19.8 | 20 | 19.5333
Norway |  | FRUHOLMEN FYR | FRUHOLMEN FYR, Norway | 71.10N | 24.00E | 14 | 1.00 (EUW) | 82-06 | 10550 | -10.7 |  | -16.7 | 26.9 | 18 | 21.7 | 20.2 | 20 | 19.9667 |  | 14.8 | 18.6 | 17.5 | 17 | 16.9667
Norway |  | GEILO-GEILOSTOLEN | GEILO-GEILOSTOLEN, Norway | 60.52N | 8.22E | 810 | 1.00 (EUW) | 88-05 | 13640 | N/A |  | N/A | N/A | 21.3 | 23.7 | 22.8 | 23 | 22.6 |  | 19.1 | 21.5 | 20.3 | 20 | 20.3
Norway |  | GULLFAX (PLATFORM) | GULLFAX (PLATFORM), Norway | 61.03N | 2.03E | 10 | 0.00 (XXX) | 90-06 | 13755 | -3.4 |  | -7.9 | 26.5 | 19.1 | 19 | 21.1 | 20 | 19.7333 |  | 16.5 | 16.9 | 18.2 | 17 | 17.2
Norway |  | HAMMERFEST | HAMMERFEST, Norway | 70.67N | 23.67E | 81 | 1.00 (EUW) | 84-06 | 10520 | N/A |  | N/A | N/A | 22 | 25.2 | 24 | 24 | 23.7333 |  | 19.1 | 22.8 | 20.8 | 21 | 20.9
Norway |  | JAN MAYEN | JAN MAYEN, Norway | 70.93N | 8.67W | 9 | -1.00 (AZR) | 82-06 | 10010 | -17.5 |  | -27.1 | 17.4 | 9.5 | 10.3 | 10.3 | 10 | 10.0333 |  | 6.8 | 8.8 | 9 | 8 | 8.2
Norway |  | KAUTOKEINO | KAUTOKEINO, Norway | 69.00N | 23.03E | 307 | 1.00 (EUW) | 83-06 | 10470 | -38.9 |  | -51.9 | 29.3 | 24.7 | 25.1 | 23.5 | 24 | 24.4333 |  | 21.9 | 23.1 | 21 | 22 | 22
Norway |  | KIRKENES | KIRKENES, Norway | 69.73N | 29.90E | 91 | 1.00 (EUW) | 82-06 | 10890 | -29.6 |  | -39.4 | 32.3 | 25 | 25.9 | 25.6 | 26 | 25.5 |  | 20.7 | 23 | 21.9 | 22 | 21.8667
Norway |  | KONGSBERG IV | KONGSBERG IV, Norway | 59.67N | 9.65E | 169 | 1.00 (EUW) | 82-02 | 14770 | -21.6 |  | -31.9 | 33.2 | 27.1 | 28.6 | 28.3 | 28 | 28 |  | 24.9 | 26.6 | 25.7 | 26 | 25.7333
Norway |  | KRISTIANSAND/KJEVIK | KRISTIANSAND/KJEVIK, Norway | 58.20N | 8.08E | 17 | 1.00 (EUW) | 82-06 | 14520 | -16.7 |  | -28.3 | 31.6 | 25.2 | 26.4 | 26.9 | 26 | 26.1667 |  | 22.9 | 24.9 | 24.8 | 24 | 24.2
Norway |  | LISTA FYR | LISTA FYR, Norway | 58.12N | 6.57E | 14 | 1.00 (EUW) | 82-06 | 14270 | -9.3 |  | -18.3 | 29.8 | 22.2 | 25.1 | 24.6 | 24 | 23.9667 |  | 19.9 | 21.9 | 22.4 | 21 | 21.4
Norway |  | LYNGOR FYR | LYNGOR FYR, Norway | 58.63N | 9.15E | 5 | 1.00 (EUW) | 85-06 | 14670 | -11.3 |  | -16.5 | 29.7 | 22.9 | 24 | 24.1 | 24 | 23.6667 |  | 20.7 | 22.3 | 22.8 | 22 | 21.9333
Norway |  | MYKEN | MYKEN, Norway | 66.77N | 12.48E | 13 | 1.00 (EUW) | 82-06 | 11150 | -6.5 |  | -9.5 | 26 | 18.1 | 20.1 | 20.2 | 19 | 19.4667 |  | 16.3 | 18.1 | 18.6 | 18 | 17.6667
Norway |  | OKSOY FYR | OKSOY FYR, Norway | 58.07N | 8.05E | 8 | 1.00 (EUW) | 82-06 | 14480 | -10.4 |  | -19.6 | 29.2 | 22.1 | 23.3 | 24.3 | 23 | 23.2333 |  | 20.3 | 21.9 | 22.7 | 22 | 21.6333
Norway |  | ORLAND III | ORLAND III, Norway | 63.70N | 9.60E | 7 | 1.00 (EUW) | 82-06 | 12410 | -13.6 |  | -21.2 | 31.7 | 24.8 | 25.2 | 25.7 | 25 | 25.2333 |  | 21.2 | 22.8 | 22.6 | 22 | 22.2
Norway |  | OSLO/FORNEBU | OSLO/FORNEBU, Norway | 59.90N | 10.62E | 17 | 1.00 (EUW) | 82-98 | 14880 | -18.7 |  | -29.6 | 36.4 | 28.1 | 28.9 | 28.9 | 29 | 28.6333 |  | 26 | 26.9 | 26 | 26 | 26.3
Norway |  | OSLO/GARDERMOEN | OSLO/GARDERMOEN, Norway | 60.20N | 11.08E | 204 | 1.00 (EUW) | 82-06 | 13840 | -23.2 |  | -34.5 | 33.5 | 26.2 | 28.2 | 28 | 27 | 27.4667 |  | 24.1 | 26.1 | 25.8 | 25 | 25.3333
Norway |  | OSLO-BLINDERN | OSLO-BLINDERN, Norway | 59.95N | 10.72E | 96 | 1.00 (EUW) | 96-06 | 14920 | -17 |  | -23 | 35.1 | 25.7 | 29.2 | 28.2 | 28 | 27.7 |  | 24 | 26.7 | 26.5 | 26 | 25.7333
Norway |  | RENA-HAUGEDALEN | RENA-HAUGEDALEN, Norway | 61.17N | 11.45E | 240 | 1.00 (EUW) | 88-06 | 13890 | -27.2 |  | -34.5 | 32.6 | 26.5 | 28.2 | 26.6 | 27 | 27.1 |  | 24 | 25.8 | 24.4 | 25 | 24.7333
Norway |  | RYGGE | RYGGE, Norway | 59.38N | 10.78E | 53 | 1.00 (EUW) | 82-06 | 14940 | -20.1 |  | -33 | 34 | 26.1 | 28 | 27.4 | 27 | 27.1667 |  | 23.8 | 25.2 | 24.9 | 25 | 24.6333
Norway |  | SKLINNA FYR | SKLINNA FYR, Norway | 65.20N | 11.00E | 16 | 1.00 (EUW) | 82-06 | 11020 | -8.3 |  | -16.6 | 26.8 | 19.7 | 21.1 | 21.1 | 21 | 20.6333 |  | 16.9 | 18.6 | 18.8 | 18 | 18.1
Norway |  | SKROVA FYR | SKROVA FYR, Norway | 68.15N | 14.65E | 11 | 1.00 (EUW) | 82-06 | 11600 | -8 |  | -14.1 | 28.2 | 21.8 | 23.2 | 22.2 | 22 | 22.4 |  | 19.4 | 21.1 | 20.1 | 20 | 20.2
Norway |  | SLATTEROY FYR | SLATTEROY FYR, Norway | 59.92N | 5.07E | 16 | 1.00 (EUW) | 89-06 | 14060 | -4.8 |  | -11 | 34.6 | 23 | 22.4 | 24.8 | 23 | 23.4 |  | 19.2 | 20.1 | 21.8 | 20 | 20.3667
Norway |  | SLETTNES FYR | SLETTNES FYR, Norway | 71.10N | 28.22E | 10 | 1.00 (EUW) | 82-06 | 10780 | -14.6 |  | -21 | 28.5 | 19.6 | 22 | 20.8 | 21 | 20.8 |  | 15.2 | 18.5 | 17.6 | 17 | 17.1
Norway |  | SORTLAND | SORTLAND, Norway | 68.70N | 15.42E | 3 | 1.00 (EUW) | 85-06 | 11670 | -12.2 |  | -17.9 | 30.1 | 21.9 | 23.4 | 23.3 | 23 | 22.8667 |  | 18.3 | 20.2 | 20.4 | 20 | 19.6333
Norway |  | STAVANGER/SOLA | STAVANGER/SOLA, Norway | 58.88N | 5.63E | 9 | 1.00 (EUW) | 82-06 | 14150 | -11.5 |  | -19.7 | 31.8 | 24.9 | 26 | 26.8 | 26 | 25.9 |  | 21.7 | 23 | 23.9 | 23 | 22.8667
Norway |  | SULA | SULA, Norway | 63.85N | 8.47E | 6 | 1.00 (EUW) | 82-06 | 12280 | -6.2 |  | -9.9 | 25.9 | 21 | 20.2 | 21.8 | 21 | 21 |  | 17.2 | 18.2 | 19.4 | 18 | 18.2667
Norway |  | SVINOY FYR | SVINOY FYR, Norway | 62.33N | 5.27E | 41 | 1.00 (EUW) | 82-06 | 12050 | -4.4 |  | -10.3 | 26.8 | 20.1 | 20.1 | 21.3 | 21 | 20.5 |  | 16.6 | 18.1 | 19.3 | 18 | 18
Norway |  | TAFJORD | TAFJORD, Norway | 62.23N | 7.42E | 17 | 1.00 (EUW) | 82-06 | 12180 | -10.7 |  | -14.5 | 29.6 | 24.4 | 24.7 | 25 | 25 | 24.7 |  | 21.2 | 22.3 | 22.6 | 22 | 22.0333
Norway |  | TORSVAG FYR | TORSVAG FYR, Norway | 70.25N | 19.50E | 24 | 1.00 (EUW) | 82-06 | 10330 | -8 |  | -12.5 | 27.2 | 19.7 | 22.7 | 19.6 | 21 | 20.6667 |  | 17.3 | 20.4 | 18.1 | 19 | 18.6
Norway |  | TROMSO/LANGNES | TROMSO/LANGNES, Norway | 69.68N | 18.92E | 10 | 1.00 (EUW) | 82-06 | 10250 | -15.1 |  | -19.8 | 28.5 | 21.6 | 23 | 22.5 | 22 | 22.3667 |  | 18.6 | 20.6 | 19.2 | 19 | 19.4667
Norway |  | TRONDHEIM/VERNES | TRONDHEIM/VERNES, Norway | 63.47N | 10.93E | 17 | 1.00 (EUW) | 82-06 | 12710 | -19.2 |  | -28.3 | 33.2 | 26.1 | 27.8 | 27.1 | 27 | 27 |  | 23 | 24.7 | 24 | 24 | 23.9
Norway |  | TVEITSUND | TVEITSUND, Norway | 59.03N | 8.52E | 255 | 1.00 (EUW) | 89-06 | 14550 | N/A |  | N/A | N/A | 24.8 | 26.7 | 26.3 | 26 | 25.9333 |  | 21.9 | 24.6 | 24.6 | 24 | 23.7
Norway |  | UTSIRA FYR | UTSIRA FYR, Norway | 59.30N | 4.88E | 56 | 1.00 (EUW) | 82-06 | 14030 | -5.1 |  | -13 | 27.9 | 21.3 | 22.1 | 23 | 22 | 22.1333 |  | 17.7 | 19.7 | 20.9 | 19 | 19.4333
Norway |  | VARDO | VARDO, Norway | 70.37N | 31.10E | 15 | 1.00 (EUW) | 82-06 | 10980 | -14.7 |  | -21.6 | 26.7 | 17.7 | 19.3 | 19.2 | 19 | 18.7333 |  | 14.1 | 16.6 | 16.1 | 16 | 15.6
Oman |  | BURAIMI | BURAIMI, Oman | 24.23N | 55.78E | 299 | 4.00 (ARN) | 87-06 | 412440 | 6.9 |  | 3.1 | 49.1 | 46.6 | 46.9 | 46.1 | 47 | 46.5333 |  | 45 | 45.2 | 44.7 | 45 | 44.9667
Oman |  | FAHUD | FAHUD, Oman | 22.33N | 56.48E | 170 | 4.00 (ARN) | 87-06 | 412620 | N/A |  | N/A | N/A | 47.9 | 47.7 | 46.7 | 47 | 47.4333 |  | 46.4 | 46.5 | 45.3 | 46 | 46.0667
Oman |  | MASIRAH | MASIRAH, Oman | 20.67N | 58.90E | 19 | 4.00 (ARN) | 83-06 | 412880 | 14.5 |  | 10.6 | 45 | 38.9 | 34.9 | 32.8 | 36 | 35.5333 |  | 36.2 | 32.9 | 31.1 | 33 | 33.4
Oman |  | SALALAH | SALALAH, Oman | 17.03N | 54.08E | 23 | 4.00 (ARN) | 82-06 | 413160 | 15.1 |  | 11.9 | 47.3 | 33.4 | 31.1 | 29.2 | 31 | 31.2333 |  | 32.9 | 30.1 | 28.2 | 30 | 30.4
Oman |  | SEEB INTL AIRPORT | SEEB INTL AIRPORT, Oman | 23.58N | 58.28E | 15 | 4.00 (ARN) | 83-06 | 412560 | 12.8 |  | 10.4 | 49.2 | 44.9 | 43.3 | 42 | 43 | 43.4 |  | 42.9 | 41.2 | 39.8 | 41 | 41.3
Oman |  | SOHAR MAJIS | SOHAR MAJIS, Oman | 24.47N | 56.63E | 4 | 4.00 (ARN) | 83-06 | 412460 | 9.8 |  | 5.6 | 49.5 | 41.8 | 41.5 | 38.1 | 40 | 40.4667 |  | 38.6 | 38.2 | 36.4 | 38 | 37.7333
Oman |  | SUR | SUR, Oman | 22.53N | 59.47E | 14 | 4.00 (ARN) | 83-06 | 412680 | 13.8 |  | 10.6 | 49.2 | 45.2 | 44.6 | 43.3 | 44 | 44.3667 |  | 43.3 | 42.4 | 40.6 | 42 | 42.1
Oman |  | THUMRAIT | THUMRAIT, Oman | 17.67N | 54.02E | 467 | 4.00 (ARN) | 83-06 | 413140 | 6.6 |  | 1.3 | 47.5 | 43.5 | 43 | 42.2 | 43 | 42.9 |  | 42.2 | 41.5 | 40.7 | 41 | 41.4667
Pakistan |  | ISLAMABAD AIRPORT | ISLAMABAD AIRPORT, Pakistan | 33.62N | 73.10E | 508 | 5.00 (ASW) | 85-06 | 415710 | 0.3 |  | -1.3 | 47.7 | 43.9 | 40.2 | 37 | 40 | 40.3667 |  | 42 | 38.1 | 35.9 | 39 | 38.6667
Pakistan |  | KARACHI AIRPORT | KARACHI AIRPORT, Pakistan | 24.90N | 67.13E | 22 | 5.00 (ASW) | 82-06 | 417800 | 7.1 |  | -0.2 | 45.4 | 40.2 | 36.9 | 35.9 | 38 | 37.6667 |  | 37 | 35 | 33.3 | 35 | 35.1
Pakistan |  | LAHORE AIRPORT | LAHORE AIRPORT, Pakistan | 31.52N | 74.40E | 217 | 5.00 (ASW) | 92-06 | 416410 | N/A |  | N/A | N/A | 45.6 | 40.1 | 38 | 41 | 41.2333 |  | 43.7 | 38.2 | 36.9 | 40 | 39.6
Palau |  | KOROR WSO | KOROR WSO, Palau | 7.33N | 134.48E | 33 | 9.00 (JPN) | 82-06 | 914080 | 22.9 |  | 21.7 | 33.6 | 31.7 | 31.6 | 31.6 | 32 | 31.6333 |  | 31.2 | 31 | 31 | 31 | 31.0667
Palestinian Territory |  | JERUSALEM AIRPORT | JERUSALEM AIRPORT, Palestinian Territory, Occupied | 31.87N | 35.22E | 759 | 2.00 (PSE) | 82-00 | 402900 | -1.2 |  | -5.3 | 38.9 | 33 | 34.9 | 34.1 | 34 | 34 |  | 31.1 | 32 | 32 | 32 | 31.7
Panama |  | MARCOS A GELABERT I | MARCOS A GELABERT I, Panama | 8.97N | 79.55W | 10 | -5.00 (SAP) | 82-99 | 783842 | 20.9 |  | 18.4 | 38.7 | 33.2 | 33.8 | 33.1 | 33 | 33.3667 |  | 32.2 | 32.2 | 32.1 | 32 | 32.1667
Panama |  | TOCUMEN | TOCUMEN, Panama | 9.05N | 79.37W | 45 | -5.00 (SAP) | 82-06 | 787920 | 18.6 |  | 10.1 | 39.1 | 33.2 | 34 | 34 | 34 | 33.7333 |  | 32.2 | 32.8 | 32.8 | 33 | 32.6
Paraguay |  | ASUNCION/AEROPUERTO | ASUNCION/AEROPUERTO, Paraguay | 25.25S | 57.52W | 101 | -4.00 (PAR) | 82-06 | 862180 | 1.9 |  | -2.1 | 41.9 | 30.2 | 32 | 35.1 | 32 | 32.4333 |  | 28.9 | 29.9 | 32.9 | 31 | 30.5667
Paraguay |  | VILLARRICA | VILLARRICA, Paraguay | 25.75S | 56.43W | 161 | -4.00 (PAR) | 86-06 | 862330 | N/A |  | N/A | N/A | 29.4 | 30.5 | 33.2 | 31 | 31.0333 |  | 28.1 | 28.8 | 31.3 | 29 | 29.4
Peru |  | AREQUIPA | AREQUIPA, Peru | 16.33S | 71.57W | 2520 | -5.00 (SAP) | 82-06 | 847520 | 2.2 |  | -3.2 | 29.1 | 24 | 23.8 | 24.1 | 24 | 23.9667 |  | 22.9 | 22.6 | 23.1 | 23 | 22.8667
Peru |  | CHICLAYO | CHICLAYO, Peru | 6.78S | 79.82W | 30 | -5.00 (SAP) | 82-06 | 844520 | 14.7 |  | 11.4 | 38.8 | 30.1 | 28.9 | 28 | 29 | 29 |  | 28.3 | 26.4 | 26 | 27 | 26.9
Peru |  | CUZCO | CUZCO, Peru | 13.53S | 71.93W | 3249 | -5.00 (SAP) | 82-06 | 846860 | -2.1 |  | -5.8 | 28.3 | 21.9 | 21.8 | 22.8 | 22 | 22.1667 |  | 20.2 | 20.5 | 21.2 | 21 | 20.6333
Peru |  | IQUITOS | IQUITOS, Peru | 3.78S | 73.30W | 126 | -5.00 (SAP) | 82-06 | 843770 | 16.2 |  | 10.2 | 39.4 | 33 | 33.1 | 33.9 | 33 | 33.3333 |  | 32 | 32.1 | 32.9 | 32 | 32.3333
Peru |  | LIMA-CALLAO/AEROP. | LIMA-CALLAO/AEROP., Peru | 12.00S | 77.12W | 13 | -5.00 (SAP) | 82-06 | 846280 | 12.1 |  | 7.1 | 33.7 | 26.9 | 25 | 23.9 | 25 | 25.2667 |  | 24.8 | 22.8 | 21.7 | 23 | 23.1
Peru |  | PISCO | PISCO, Peru | 13.73S | 76.22W | 7 | -5.00 (SAP) | 82-06 | 846910 | 10 |  | 8.1 | 35.2 | 26.8 | 24.9 | 23.8 | 25 | 25.1667 |  | 24.2 | 22.8 | 21.9 | 23 | 22.9667
Peru |  | PIURA | PIURA, Peru | 5.20S | 80.60W | 55 | -5.00 (SAP) | 82-06 | 844010 | 14.9 |  | 10.5 | 37.1 | 31.1 | 30.2 | 30.2 | 31 | 30.5 |  | 29.8 | 28.8 | 28.7 | 29 | 29.1
Peru |  | PUCALLPA | PUCALLPA, Peru | 8.37S | 74.57W | 149 | -5.00 (SAP) | 82-06 | 845150 | 15 |  | 10.4 | 40.9 | 33.2 | 34 | 35.1 | 34 | 34.1 |  | 32.4 | 33 | 34 | 33 | 33.1333
Peru |  | SAN JUAN | SAN JUAN, Peru | 15.38S | 75.17W | 60 | -5.00 (SAP) | 82-97 | 847210 | N/A |  | N/A | N/A | 24.2 | 22.8 | 21.1 | 23 | 22.7 |  | 23 | 20.9 | 20 | 21 | 21.3
Peru |  | TACNA | TACNA, Peru | 18.05S | 70.27W | 458 | -5.00 (SAP) | 82-00 | 847820 | 8.3 |  | 5.1 | 31.8 | 23.1 | 21.6 | 23.1 | 23 | 22.6 |  | 21.6 | 20 | 20.9 | 21 | 20.8333
Peru |  | TALARA | TALARA, Peru | 4.57S | 81.23W | 85 | -5.00 (SAP) | 82-00 | 843900 | 14.5 |  | 9.3 | 36.7 | 30 | 29.1 | 28.1 | 29 | 29.0667 |  | 28.8 | 27.8 | 26.5 | 28 | 27.7
Peru |  | TRUJILLO | TRUJILLO, Peru | 8.08S | 79.10W | 30 | -5.00 (SAP) | 82-00 | 845010 | N/A |  | N/A | N/A | 28.1 | 25.6 | 24.9 | 26 | 26.2 |  | 26.9 | 24.6 | 23.9 | 25 | 25.1333
Peru |  | TUMBES | TUMBES, Peru | 3.55S | 80.40W | 27 | -5.00 (SAP) | 82-00 | 843700 | N/A |  | N/A | N/A | 31.8 | 31.6 | 31.5 | 32 | 31.6333 |  | 30.6 | 30.3 | 30.1 | 30 | 30.3333
Philippines |  | BAGUIO | BAGUIO, Philippines | 16.42N | 120.60E | 1501 | 8.00 (CHN) | 82-06 | 983280 | 10 |  | 6.3 | 36.3 | 28.2 | 27.9 | 27.1 | 28 | 27.7333 |  | 25.5 | 24.9 | 24.2 | 25 | 24.8667
Philippines |  | CAGAYAN DE ORO | CAGAYAN DE ORO, Philippines | 8.48N | 124.63E | 6 | 8.00 (CHN) | 83-01 | 987480 | N/A |  | N/A | N/A | 34.7 | 34.4 | 35.4 | 35 | 34.8333 |  | 33.7 | 33.4 | 34 | 34 | 33.7
Philippines |  | CALAPAN | CALAPAN, Philippines | 13.42N | 121.18E | 41 | 8.00 (CHN) | 83-06 | 984310 | 20.9 |  | 19.3 | 40.6 | 33.5 | 33.2 | 33.4 | 33 | 33.3667 |  | 32.5 | 32.1 | 32.2 | 32 | 32.2667
Philippines |  | CATANDUANES RADAR | CATANDUANES RADAR, Philippines | 13.98N | 124.32E | 233 | 8.00 (CHN) | 82-06 | 984470 | N/A |  | N/A | N/A | 31.1 | 30.7 | 31.1 | 31 | 30.9667 |  | 30.1 | 29.8 | 30.1 | 30 | 30
Philippines |  | CATBALOGAN | CATBALOGAN, Philippines | 11.78N | 124.88E | 5 | 8.00 (CHN) | 82-06 | 985480 | N/A |  | N/A | N/A | 34.8 | 33.7 | 33.8 | 34 | 34.1 |  | 33.7 | 32.9 | 33.1 | 33 | 33.2333
Philippines |  | CLARK AB | CLARK AB, Philippines | 15.17N | 120.57E | 155 | 8.00 (CHN) | 82-06 | 983270 | 17.1 |  | 11.5 | 39.4 | 35.9 | 34.1 | 33.1 | 34 | 34.3667 |  | 33.9 | 32.7 | 32 | 33 | 32.8667
Philippines |  | CUBI POINT NF | CUBI POINT NF, Philippines | 14.80N | 120.27E | 14 | 8.00 (CHN) | 82-99 | 984260 | 18.8 |  | 16.7 | 40.4 | 36.2 | 34.1 | 34.2 | 35 | 34.8333 |  | 34.8 | 33.1 | 33 | 34 | 33.6333
Philippines |  | DAET | DAET, Philippines | 14.13N | 122.98E | 4 | 8.00 (CHN) | 82-06 | 984400 | N/A |  | N/A | N/A | 34.6 | 33.2 | 33.4 | 34 | 33.7333 |  | 33.1 | 32.2 | 32.3 | 33 | 32.5333
Philippines |  | DAGUPAN | DAGUPAN, Philippines | 16.05N | 120.33E | 2 | 8.00 (CHN) | 82-06 | 983250 | 18.2 |  | 13.3 | 39.5 | 35 | 33.8 | 32.3 | 34 | 33.7 |  | 33.7 | 32.4 | 31.6 | 33 | 32.5667
Philippines |  | DAVAO AIRPORT | DAVAO AIRPORT, Philippines | 7.12N | 125.65E | 18 | 8.00 (CHN) | 82-06 | 987530 | 20.4 |  | 14.9 | 39.2 | 33.2 | 33 | 33 | 33 | 33.0667 |  | 32.2 | 32 | 32.1 | 32 | 32.1
Philippines |  | DUMAGUETE | DUMAGUETE, Philippines | 9.30N | 123.30E | 8 | 8.00 (CHN) | 83-06 | 986420 | N/A |  | N/A | N/A | 33.9 | 33 | 33.7 | 34 | 33.5333 |  | 32.5 | 32.2 | 32.7 | 32 | 32.4667
Philippines |  | GEN. SANTOS | GEN. SANTOS, Philippines | 6.12N | 125.18E | 15 | 8.00 (CHN) | 88-06 | 988510 | N/A |  | N/A | N/A | 34.2 | 33 | 33.2 | 33 | 33.4667 |  | 32.8 | 32 | 32.4 | 32 | 32.4
Philippines |  | IBA | IBA, Philippines | 15.33N | 119.97E | 5 | 8.00 (CHN) | 82-06 | 983240 | N/A |  | N/A | N/A | 33.2 | 32.1 | 31.2 | 32 | 32.1667 |  | 32.2 | 31.3 | 30.6 | 31 | 31.3667
Philippines |  | ILOILO | ILOILO, Philippines | 10.70N | 122.57E | 8 | 8.00 (CHN) | 82-06 | 986370 | N/A |  | N/A | N/A | 34.7 | 32.9 | 33.2 | 34 | 33.6 |  | 33.3 | 32.1 | 32 | 32 | 32.4667
Philippines |  | INFANTA | INFANTA, Philippines | 14.75N | 121.65E | 7 | 8.00 (CHN) | 83-06 | 984340 | N/A |  | N/A | N/A | 35.2 | 35 | 35 | 35 | 35.0667 |  | 34.4 | 34 | 33.9 | 34 | 34.1
Philippines |  | LAOAG | LAOAG, Philippines | 18.18N | 120.53E | 5 | 8.00 (CHN) | 82-06 | 982230 | 15.6 |  | 10.9 | 40.2 | 34.9 | 34.2 | 33.6 | 34 | 34.2333 |  | 34 | 33.3 | 32.7 | 33 | 33.3333
Philippines |  | LEGASPI | LEGASPI, Philippines | 13.13N | 123.73E | 17 | 8.00 (CHN) | 83-06 | 984440 | 20.2 |  | 15.6 | 41.2 | 33.7 | 33.3 | 33.5 | 34 | 33.5 |  | 33 | 32.4 | 32.4 | 33 | 32.6
Philippines |  | LUMBIA AIRPORT | LUMBIA AIRPORT, Philippines | 8.43N | 124.28E | 188 | 8.00 (CHN) | 82-06 | 987470 | 16.5 |  | 9.9 | 38.6 | 33.2 | 33.2 | 34.1 | 34 | 33.5 |  | 32.2 | 32 | 32.5 | 32 | 32.2333
Philippines |  | MACTAN | MACTAN, Philippines | 10.30N | 123.97E | 24 | 8.00 (CHN) | 82-06 | 986460 | 19.9 |  | 14.5 | 40.7 | 34 | 33 | 33.2 | 33 | 33.4 |  | 33 | 32.1 | 32.4 | 33 | 32.5
Philippines |  | MALAYBALAY | MALAYBALAY, Philippines | 8.15N | 125.08E | 627 | 8.00 (CHN) | 90-06 | 987510 | N/A |  | N/A | N/A | 31.7 | 30.7 | 30.7 | 31 | 31.0333 |  | 30.3 | 29.4 | 29.5 | 30 | 29.7333
Philippines |  | MANILA | MANILA, Philippines | 14.58N | 120.98E | 13 | 8.00 (CHN) | 82-06 | 984250 | 19 |  | 14.1 | 40 | 35.1 | 33.5 | 33 | 34 | 33.8667 |  | 33.9 | 32.4 | 32.1 | 33 | 32.8
Philippines |  | MASBATE | MASBATE, Philippines | 12.37N | 123.62E | 6 | 8.00 (CHN) | 88-06 | 985430 | 21.4 |  | 18.8 | 38.9 | 34.4 | 33.7 | 33.7 | 34 | 33.9333 |  | 33.6 | 32.7 | 32.8 | 33 | 33.0333
Philippines |  | MUNOZ | MUNOZ, Philippines | 15.72N | 120.90E | 76 | 8.00 (CHN) | 82-03 | 983290 | N/A |  | N/A | N/A | 35 | 34.1 | 33.4 | 34 | 34.1667 |  | 34.1 | 33.1 | 32.2 | 33 | 33.1333
Philippines |  | NINOY AQUINO INTERN | NINOY AQUINO INTERN, Philippines | 14.52N | 121.00E | 15 | 8.00 (CHN) | 82-06 | 984290 | 19.2 |  | 15.8 | 39.6 | 35 | 34 | 33 | 34 | 34 |  | 33.9 | 32.8 | 32 | 33 | 32.9
Philippines |  | PUERTO PRINCESA | PUERTO PRINCESA, Philippines | 9.75N | 118.73E | 15 | 8.00 (CHN) | 82-06 | 986180 | 20 |  | 15.8 | 40.6 | 33 | 32.7 | 32.5 | 33 | 32.7333 |  | 32.1 | 31.9 | 31.7 | 32 | 31.9
Philippines |  | ROXAS | ROXAS, Philippines | 11.58N | 122.75E | 4 | 8.00 (CHN) | 83-06 | 985380 | 21 |  | 16.5 | 41.8 | 33.6 | 32.9 | 32.7 | 33 | 33.0667 |  | 32.8 | 32.1 | 32.1 | 32 | 32.3333
Philippines |  | SAN JOSE | SAN JOSE, Philippines | 12.35N | 121.03E | 3 | 8.00 (CHN) | 83-06 | 985310 | N/A |  | N/A | N/A | 35.1 | 33.7 | 32.7 | 34 | 33.8333 |  | 33.8 | 32.3 | 31.7 | 33 | 32.6
Philippines |  | SANGLEY POINT | SANGLEY POINT, Philippines | 14.50N | 120.92E | 2 | 8.00 (CHN) | 82-99 | 984280 | N/A |  | N/A | N/A | 35.1 | 34 | 33.8 | 34 | 34.3 |  | 34 | 32.7 | 32.6 | 33 | 33.1
Philippines |  | SCIENCE GARDEN | SCIENCE GARDEN, Philippines | 14.63N | 121.02E | 46 | 8.00 (CHN) | 86-06 | 984300 | N/A |  | N/A | N/A | 35.2 | 33.8 | 33 | 34 | 34 |  | 34.2 | 32.7 | 32.1 | 33 | 33
Philippines |  | SINAIT | SINAIT, Philippines | 17.88N | 120.45E | 58 | 8.00 (CHN) | 88-06 | 982220 | N/A |  | N/A | N/A | 33.4 | 33.1 | 32.1 | 33 | 32.8667 |  | 32.5 | 32.1 | 31.4 | 32 | 32
Philippines |  | TACLOBAN | TACLOBAN, Philippines | 11.25N | 125.00E | 3 | 8.00 (CHN) | 82-06 | 985500 | 18.2 |  | 9.1 | 40.6 | 34.2 | 34.1 | 34 | 34 | 34.1 |  | 33.2 | 33 | 32.9 | 33 | 33.0333
Philippines |  | TAGBILARAN | TAGBILARAN, Philippines | 9.60N | 123.85E | 8 | 8.00 (CHN) | 82-06 | 986440 | N/A |  | N/A | N/A | 34.1 | 33.9 | 34.6 | 34 | 34.2 |  | 33 | 33 | 33.4 | 33 | 33.1333
Philippines |  | TAYABAS | TAYABAS, Philippines | 14.03N | 121.58E | 158 | 8.00 (CHN) | 83-06 | 984270 | N/A |  | N/A | N/A | 33.3 | 32.5 | 32.6 | 33 | 32.8 |  | 32.4 | 31.5 | 31.8 | 32 | 31.9
Philippines |  | ZAMBOANGA | ZAMBOANGA, Philippines | 6.90N | 122.07E | 6 | 8.00 (CHN) | 82-06 | 988360 | 19.7 |  | 14.9 | 39.2 | 34.1 | 33.3 | 33.9 | 34 | 33.7667 |  | 33 | 32.5 | 32.9 | 33 | 32.8
Poland |  | BIALYSTOK | BIALYSTOK, Poland | 53.10N | 23.17E | 151 | 1.00 (EUW) | 82-06 | 122950 | -21.4 |  | -34.4 | 35.9 | 28.7 | 31.6 | 30.4 | 30 | 30.2333 |  | 26.3 | 28.8 | 27.6 | 28 | 27.5667
Poland |  | BIELSKO-BIALA | BIELSKO-BIALA, Poland | 49.80N | 19.00E | 399 | 1.00 (EUW) | 85-06 | 126000 | -18 |  | -27.1 | 34.9 | 29.1 | 30.9 | 30.9 | 30 | 30.3 |  | 26.3 | 28.3 | 28.1 | 28 | 27.5667
Poland |  | CHOJNICE | CHOJNICE, Poland | 53.72N | 17.55E | 172 | 1.00 (EUW) | 82-06 | 122350 | -16.8 |  | -30.2 | 36.5 | 29.1 | 31.5 | 30.3 | 30 | 30.3 |  | 25.6 | 28.7 | 27.5 | 27 | 27.2667
Poland |  | CZESTOCHOWA | CZESTOCHOWA, Poland | 50.82N | 19.10E | 295 | 1.00 (EUW) | 85-06 | 125500 | -17.2 |  | -32.1 | 35.9 | 28.7 | 31.6 | 30.2 | 30 | 30.1667 |  | 26.2 | 29.4 | 28.2 | 28 | 27.9333
Poland |  | ELBLAG | ELBLAG, Poland | 54.17N | 19.43E | 43 | 1.00 (EUW) | 86-06 | 121600 | -19.9 |  | -39.1 | 35.2 | 28.9 | 30.4 | 30 | 30 | 29.7667 |  | 25.4 | 27.8 | 26.9 | 27 | 26.7
Poland |  | GDANSK-REBIECHOWO | GDANSK-REBIECHOWO, Poland | 54.38N | 18.47E | 138 | 1.00 (EUW) | 82-06 | 121500 | -20 |  | -33.6 | 35.7 | 28 | 30.1 | 29 | 29 | 29.0333 |  | 25 | 27.2 | 26.7 | 26 | 26.3
Poland |  | GDANSK-SWIBNO | GDANSK-SWIBNO, Poland | 54.33N | 18.93E | 7 | 1.00 (EUW) | 82-92 | 121550 | -15.9 |  | -32.7 | 35.4 | 25.9 | 29 | 28.8 | 28 | 27.9 |  | 22.7 | 25.5 | 25.9 | 25 | 24.7
Poland |  | GORZOW WLKP | GORZOW WLKP, Poland | 52.75N | 15.28E | 73 | 1.00 (EUW) | 82-06 | 123000 | -14.5 |  | -26.7 | 38 | 30.8 | 32.8 | 31.8 | 32 | 31.8 |  | 27.6 | 29.9 | 28.8 | 29 | 28.7667
Poland |  | HEL | HEL, Poland | 54.60N | 18.82E | 3 | 1.00 (EUW) | 82-06 | 121350 | -10.8 |  | -20.7 | 32.9 | 25.6 | 28 | 26.9 | 27 | 26.8333 |  | 22.7 | 25.6 | 24.9 | 24 | 24.4
Poland |  | JELENIA GORA | JELENIA GORA, Poland | 50.90N | 15.80E | 344 | 1.00 (EUW) | 85-06 | 125000 | -21.3 |  | -31.7 | 35.8 | 29.9 | 31.6 | 31.2 | 31 | 30.9 |  | 26.7 | 28.7 | 28.2 | 28 | 27.8667
Poland |  | KALISZ | KALISZ, Poland | 51.78N | 18.08E | 140 | 1.00 (EUW) | 82-06 | 124350 | -16.4 |  | -28.7 | 38 | 30.7 | 32.9 | 32.5 | 32 | 32.0333 |  | 27.3 | 29.8 | 29.3 | 29 | 28.8
Poland |  | KASPROWY WIERCH | KASPROWY WIERCH, Poland | 49.23N | 19.98E | 1989 | 1.00 (EUW) | 82-06 | 126500 | -22.2 |  | -29.7 | 24.5 | 17.2 | 18.2 | 18 | 18 | 17.8 |  | 15.2 | 16.2 | 16.1 | 16 | 15.8333
Poland |  | KATOWICE | KATOWICE, Poland | 50.23N | 19.03E | 284 | 1.00 (EUW) | 82-06 | 125600 | -19.2 |  | -30 | 35.9 | 30.1 | 31.6 | 31.7 | 31 | 31.1333 |  | 27.2 | 29.3 | 28.7 | 28 | 28.4
Poland |  | KETRZYN | KETRZYN, Poland | 54.07N | 21.37E | 110 | 1.00 (EUW) | 82-06 | 121850 | -19.1 |  | -34.4 | 35.9 | 26.9 | 30.1 | 29.9 | 29 | 28.9667 |  | 24.9 | 27.4 | 27.2 | 27 | 26.5
Poland |  | KIELCE | KIELCE, Poland | 50.82N | 20.70E | 261 | 1.00 (EUW) | 82-06 | 125700 | -20.7 |  | -34 | 35.8 | 29.5 | 31.7 | 31.3 | 31 | 30.8333 |  | 26.9 | 29.1 | 28.5 | 28 | 28.1667
Poland |  | KLODZKO | KLODZKO, Poland | 50.43N | 16.62E | 357 | 1.00 (EUW) | 82-06 | 125200 | -19.7 |  | -31.6 | 35.7 | 28.4 | 31 | 30.8 | 30 | 30.0667 |  | 25.8 | 28 | 28.1 | 27 | 27.3
Poland |  | KOLO | KOLO, Poland | 52.20N | 18.67E | 117 | 1.00 (EUW) | 85-06 | 123450 | -16.7 |  | -29.7 | 38.3 | 31.4 | 32.7 | 32.1 | 32 | 32.0667 |  | 27.3 | 29.9 | 29 | 29 | 28.7333
Poland |  | KOLOBRZEG | KOLOBRZEG, Poland | 54.18N | 15.58E | 5 | 1.00 (EUW) | 82-06 | 121000 | -12 |  | -24.5 | 37.9 | 27.6 | 29.4 | 28.8 | 29 | 28.6 |  | 23.4 | 25.3 | 25.7 | 25 | 24.8
Poland |  | KOSZALIN | KOSZALIN, Poland | 54.20N | 16.15E | 34 | 1.00 (EUW) | 82-06 | 121050 | -14.6 |  | -26.2 | 36.2 | 29.2 | 30.7 | 29.8 | 30 | 29.9 |  | 25.5 | 27.5 | 26.8 | 27 | 26.6
Poland |  | KOZIENICE | KOZIENICE, Poland | 51.57N | 21.55E | 126 | 1.00 (EUW) | 86-06 | 124880 | N/A |  | N/A | N/A | 30.7 | 33 | 31.1 | 32 | 31.6 |  | 28.1 | 30.7 | 28.4 | 29 | 29.0667
Poland |  | KRAKOW | KRAKOW, Poland | 50.08N | 19.80E | 237 | 1.00 (EUW) | 82-06 | 125660 | -19.8 |  | -31 | 36.5 | 30.2 | 32.1 | 32.1 | 31 | 31.4667 |  | 27.7 | 29.8 | 29.6 | 29 | 29.0333
Poland |  | LEBA | LEBA, Poland | 54.75N | 17.53E | 6 | 1.00 (EUW) | 82-06 | 121200 | -14 |  | -25.6 | 35.9 | 27.3 | 29.4 | 28.1 | 28 | 28.2667 |  | 23.7 | 25.8 | 25 | 25 | 24.8333
Poland |  | LEBORK | LEBORK, Poland | 54.55N | 17.75E | 41 | 1.00 (EUW) | 85-06 | 121250 | -15.4 |  | -30.1 | 37.3 | 27.8 | 30.1 | 29.7 | 29 | 29.2 |  | 25.2 | 27.7 | 26.7 | 27 | 26.5333
Poland |  | LEGNICA | LEGNICA, Poland | 51.20N | 16.20E | 124 | 1.00 (EUW) | 85-06 | 124150 | -17.1 |  | -27.6 | 38.8 | 30.7 | 33.5 | 32.7 | 32 | 32.3 |  | 27.5 | 30.2 | 29.8 | 29 | 29.1667
Poland |  | LESKO | LESKO, Poland | 49.47N | 22.35E | 422 | 1.00 (EUW) | 86-06 | 126900 | N/A |  | N/A | N/A | 28.5 | 29.6 | 29.7 | 29 | 29.2667 |  | 26.4 | 27.9 | 26.8 | 27 | 27.0333
Poland |  | LESZNO | LESZNO, Poland | 51.83N | 16.53E | 92 | 1.00 (EUW) | 86-06 | 124180 | -17.6 |  | -29.7 | 38.6 | 31.2 | 33.4 | 31.5 | 32 | 32.0333 |  | 27.5 | 30.6 | 29 | 29 | 29.0333
Poland |  | LODZ | LODZ, Poland | 51.73N | 19.40E | 190 | 1.00 (EUW) | 82-06 | 124650 | -18.1 |  | -32.2 | 37.8 | 30.5 | 32.6 | 32.2 | 32 | 31.7667 |  | 27.2 | 29.7 | 28.9 | 29 | 28.6
Poland |  | LUBLIN RADAWIEC | LUBLIN RADAWIEC, Poland | 51.22N | 22.40E | 240 | 1.00 (EUW) | 82-06 | 124950 | -19.6 |  | -31.6 | 34.9 | 28.6 | 31 | 31 | 30 | 30.2 |  | 26.3 | 28.7 | 28.2 | 28 | 27.7333
Poland |  | MIKOLAJKI | MIKOLAJKI, Poland | 53.78N | 21.58E | 132 | 1.00 (EUW) | 85-06 | 122800 | -19.7 |  | -31.3 | 34.5 | 27.9 | 30.6 | 29.4 | 29 | 29.3 |  | 25.4 | 28.3 | 26.9 | 27 | 26.8667
Poland |  | MLAWA | MLAWA, Poland | 53.10N | 20.35E | 149 | 1.00 (EUW) | 82-06 | 122700 | -18.6 |  | -30.9 | 36.3 | 29 | 31.7 | 31.2 | 31 | 30.6333 |  | 26 | 29.1 | 28.1 | 28 | 27.7333
Poland |  | NOWY SACZ | NOWY SACZ, Poland | 49.62N | 20.70E | 295 | 1.00 (EUW) | 85-06 | 126600 | -20.3 |  | -31.7 | 36.5 | 30.4 | 32.3 | 32.9 | 32 | 31.8667 |  | 27.8 | 30 | 29.7 | 29 | 29.1667
Poland |  | OLSZTYN | OLSZTYN, Poland | 53.77N | 20.42E | 137 | 1.00 (EUW) | 85-06 | 122720 | -20.6 |  | -33.2 | 36.3 | 29.1 | 31.6 | 30.4 | 30 | 30.3667 |  | 26 | 28.8 | 27.5 | 27 | 27.4333
Poland |  | OPOLE | OPOLE, Poland | 50.80N | 17.97E | 163 | 1.00 (EUW) | 85-06 | 125300 | -17.6 |  | -28.3 | 37.7 | 31.3 | 33.5 | 32 | 32 | 32.2667 |  | 28.2 | 30.5 | 29.5 | 29 | 29.4
Poland |  | OSTROLEKA | OSTROLEKA, Poland | 53.08N | 21.57E | 97 | 1.00 (EUW) | 85-06 | 122850 | -19.6 |  | -34.3 | 36.7 | 29.1 | 31.6 | 32.1 | 31 | 30.9333 |  | 26.4 | 29.2 | 28.4 | 28 | 28
Poland |  | PILA | PILA, Poland | 53.13N | 16.75E | 73 | 1.00 (EUW) | 86-06 | 122300 | N/A |  | N/A | N/A | 31.4 | 32 | 30.7 | 31 | 31.3667 |  | 27.2 | 29.8 | 28 | 28 | 28.3333
Poland |  | PLOCK | PLOCK, Poland | 52.58N | 19.73E | 109 | 1.00 (EUW) | 82-06 | 123600 | -17.9 |  | -32.9 | 36.4 | 29.2 | 31.9 | 31.4 | 31 | 30.8333 |  | 26.2 | 29.3 | 28.4 | 28 | 27.9667
Poland |  | POZNAN | POZNAN, Poland | 52.42N | 16.85E | 84 | 1.00 (EUW) | 82-06 | 123300 | -16.9 |  | -29.9 | 38.4 | 31.6 | 33.2 | 32.2 | 32 | 32.3333 |  | 28 | 30.3 | 29.2 | 29 | 29.1667
Poland |  | PRZEMYSL | PRZEMYSL, Poland | 49.80N | 22.77E | 280 | 1.00 (EUW) | 82-06 | 126950 | -18.3 |  | -31.9 | 33.4 | 27.8 | 30.1 | 29.2 | 29 | 29.0333 |  | 25.7 | 27.9 | 27.2 | 27 | 26.9333
Poland |  | RACIBORZ | RACIBORZ, Poland | 50.05N | 18.20E | 206 | 1.00 (EUW) | 86-06 | 125400 | N/A |  | N/A | N/A | 30.4 | 32.3 | 31.8 | 32 | 31.5 |  | 27.6 | 29.9 | 29 | 29 | 28.8333
Poland |  | RESKO | RESKO, Poland | 53.77N | 15.42E | 56 | 1.00 (EUW) | 86-06 | 122100 | N/A |  | N/A | N/A | 29.9 | 30.7 | 29.5 | 30 | 30.0333 |  | 26.3 | 28.5 | 27.3 | 27 | 27.3667
Poland |  | RZESZOW-JASIONKA | RZESZOW-JASIONKA, Poland | 50.10N | 22.05E | 201 | 1.00 (EUW) | 85-06 | 125800 | -21.3 |  | -33.8 | 37.8 | 30.3 | 32 | 32 | 31 | 31.4333 |  | 27.6 | 29.8 | 29.2 | 29 | 28.8667
Poland |  | SANDOMIERZ | SANDOMIERZ, Poland | 50.70N | 21.72E | 218 | 1.00 (EUW) | 85-06 | 125850 | -18.8 |  | -27.4 | 34.7 | 29.5 | 31.6 | 31.5 | 31 | 30.8667 |  | 27 | 29.5 | 28.8 | 28 | 28.4333
Poland |  | SIEDLCE | SIEDLCE, Poland | 52.25N | 22.25E | 155 | 1.00 (EUW) | 82-06 | 123850 | -20.2 |  | -32.9 | 35.5 | 29.3 | 31.9 | 31 | 31 | 30.7333 |  | 26.9 | 29.3 | 28.3 | 28 | 28.1667
Poland |  | SNIEZKA | SNIEZKA, Poland | 50.73N | 15.73E | 1613 | 1.00 (EUW) | 82-06 | 125100 | -19.6 |  | -29.3 | 24.6 | 18.9 | 20.5 | 20 | 20 | 19.8 |  | 16.6 | 18.1 | 17.5 | 17 | 17.4
Poland |  | SULEJOW | SULEJOW, Poland | 51.35N | 19.87E | 189 | 1.00 (EUW) | 86-06 | 124690 | N/A |  | N/A | N/A | 30.5 | 32 | 31.2 | 31 | 31.2333 |  | 27.1 | 29.7 | 28.6 | 28 | 28.4667
Poland |  | SUWALKI | SUWALKI, Poland | 54.13N | 22.95E | 186 | 1.00 (EUW) | 82-06 | 121950 | -22.2 |  | -33.9 | 35.4 | 28 | 31.1 | 29.9 | 30 | 29.6667 |  | 25.4 | 28.3 | 27.2 | 27 | 26.9667
Poland |  | SWINOUJSCIE | SWINOUJSCIE, Poland | 53.92N | 14.23E | 5 | 1.00 (EUW) | 85-06 | 122000 | -12.2 |  | -23.5 | 38.1 | 29 | 29.8 | 29.8 | 30 | 29.5333 |  | 24.6 | 26.4 | 26 | 26 | 25.6667
Poland |  | SZCZECIN | SZCZECIN, Poland | 53.40N | 14.62E | 7 | 1.00 (EUW) | 82-06 | 122050 | -15 |  | -27.2 | 38.4 | 30 | 32.4 | 31.8 | 31 | 31.4 |  | 26.9 | 29.3 | 28.1 | 28 | 28.1
Poland |  | SZCZECINEK | SZCZECINEK, Poland | 53.72N | 16.68E | 144 | 1.00 (EUW) | 85-06 | 122150 | -15.6 |  | -34.4 | 37.1 | 28.8 | 30.4 | 30.6 | 30 | 29.9333 |  | 26 | 27.9 | 27.5 | 27 | 27.1333
Poland |  | TARNOW | TARNOW, Poland | 50.03N | 20.98E | 209 | 1.00 (EUW) | 82-06 | 125750 | -19.2 |  | -33.4 | 35.6 | 28.8 | 31.5 | 31.8 | 31 | 30.7 |  | 26.7 | 29.3 | 29.1 | 28 | 28.3667
Poland |  | TERESPOL | TERESPOL, Poland | 52.07N | 23.62E | 137 | 1.00 (EUW) | 86-06 | 123990 | N/A |  | N/A | N/A | 30 | 32 | 30.9 | 31 | 30.9667 |  | 27.6 | 29.8 | 28.1 | 29 | 28.5
Poland |  | TORUN | TORUN, Poland | 53.05N | 18.58E | 72 | 1.00 (EUW) | 82-06 | 122500 | -18.5 |  | -33.1 | 37.3 | 31.3 | 32.7 | 32 | 32 | 32 |  | 27.4 | 30.2 | 29.1 | 29 | 28.9
Poland |  | USTKA | USTKA, Poland | 54.58N | 16.87E | 11 | 1.00 (EUW) | 85-06 | 121150 | -12.5 |  | -23.7 | 36.5 | 27.5 | 29.9 | 28 | 28 | 28.4667 |  | 23.3 | 25.6 | 25.1 | 25 | 24.6667
Poland |  | WARSZAWA-OKECIE | WARSZAWA-OKECIE, Poland | 52.17N | 20.97E | 106 | 1.00 (EUW) | 82-06 | 123750 | -18.4 |  | -30.9 | 37.4 | 30.2 | 32.5 | 31.9 | 32 | 31.5333 |  | 27.7 | 30 | 28.9 | 29 | 28.8667
Poland |  | WIELUN | WIELUN, Poland | 51.22N | 18.57E | 201 | 1.00 (EUW) | 85-06 | 124550 | -17.5 |  | -28.7 | 37.5 | 30.6 | 32.7 | 32.1 | 32 | 31.8 |  | 27.3 | 29.8 | 29.1 | 29 | 28.7333
Poland |  | WLODAWA | WLODAWA, Poland | 51.55N | 23.53E | 179 | 1.00 (EUW) | 85-06 | 124970 | -20.9 |  | -33.1 | 35.9 | 29.8 | 32 | 31.7 | 31 | 31.1667 |  | 27.2 | 29.8 | 28.9 | 29 | 28.6333
Poland |  | WROCLAW II | WROCLAW II, Poland | 51.10N | 16.88E | 124 | 1.00 (EUW) | 82-06 | 124240 | -17.6 |  | -30.1 | 38.3 | 31 | 33.3 | 32.3 | 32 | 32.2 |  | 27.8 | 30.1 | 29.3 | 29 | 29.0667
Poland |  | ZAKOPANE | ZAKOPANE, Poland | 49.30N | 19.97E | 857 | 1.00 (EUW) | 82-06 | 126250 | -20.3 |  | -31.7 | 32.8 | 26.5 | 27.8 | 27.7 | 27 | 27.3333 |  | 24.3 | 25.7 | 25 | 25 | 25
Poland |  | ZAMOSC | ZAMOSC, Poland | 50.70N | 23.25E | 213 | 1.00 (EUW) | 82-06 | 125950 | -20.3 |  | -33.5 | 34.9 | 29.6 | 31.2 | 31.1 | 31 | 30.6333 |  | 26.9 | 28.2 | 28.3 | 28 | 27.8
Poland |  | ZIELONA GORA | ZIELONA GORA, Poland | 51.93N | 15.53E | 192 | 1.00 (EUW) | 82-06 | 124000 | -14.2 |  | -25.1 | 37.6 | 30.3 | 32.6 | 32 | 32 | 31.6333 |  | 27.2 | 29.7 | 28.5 | 28 | 28.4667
Portugal |  | BEJA | BEJA, Portugal | 38.02N | 7.87W | 247 | 0.00 (GMT) | 82-06 | 85620 | 0 |  | -4 | 44.7 | 37.6 | 39.8 | 39.3 | 39 | 38.9 |  | 35.1 | 37.4 | 37 | 37 | 36.5
Portugal |  | BRAGANCA | BRAGANCA, Portugal | 41.80N | 6.73W | 692 | 0.00 (GMT) | 82-06 | 85750 | -6 |  | -10.6 | 39.4 | 33.1 | 35.4 | 36.3 | 35 | 34.9333 |  | 30.9 | 33.7 | 33.7 | 33 | 32.7667
Portugal |  | CASTELO BRANCO | CASTELO BRANCO, Portugal | 39.83N | 7.48W | 384 | 0.00 (GMT) | 90-06 | 85700 | -1.5 |  | -5.1 | 42.5 | 36.7 | 38.1 | 38.4 | 38 | 37.7333 |  | 34.8 | 36.2 | 36.6 | 36 | 35.8667
Portugal |  | COIMBRA | COIMBRA, Portugal | 40.20N | 8.42W | 140 | 0.00 (GMT) | 82-96 | 85490 | 0.1 |  | -3 | 41.6 | 33.5 | 36.5 | 36.2 | 35 | 35.4 |  | 30.4 | 34 | 32.6 | 32 | 32.3333
Portugal |  | EVORA | EVORA, Portugal | 38.57N | 7.90W | 321 | 0.00 (GMT) | 82-92 | 85570 | 1.1 |  | -3.4 | 41.8 | 34.4 | 37.9 | 37.5 | 37 | 36.6 |  | 32.1 | 35.9 | 35.2 | 34 | 34.4
Portugal |  | EVORA/C. COORD | EVORA/C. COORD, Portugal | 38.53N | 7.90W | 246 | 0.00 (GMT) | 96-06 | 85580 | -1.9 |  | -6.4 | 45 | 38.2 | 40.2 | 39.6 | 39 | 39.3333 |  | 35.9 | 37.8 | 37.8 | 37 | 37.1667
Portugal |  | FARO/AEROPORTO | FARO/AEROPORTO, Portugal | 37.02N | 7.97W | 8 | 0.00 (GMT) | 82-06 | 85540 | 2.5 |  | -1.9 | 42.5 | 31.9 | 35.2 | 34 | 34 | 33.7 |  | 29.3 | 32.2 | 31.6 | 31 | 31.0333
Portugal |  | FLORES (ACORES) | FLORES (ACORES), Portugal | 39.45N | 31.13W | 29 | -1.00 (AZR) | 82-06 | 85010 | 7.6 |  | 5.6 | 30.7 | 24.1 | 27.4 | 27.8 | 26 | 26.4333 |  | 23.1 | 26.2 | 26.8 | 25 | 25.3667
Portugal |  | FUNCHAL | FUNCHAL, Portugal | 32.63N | 16.90W | 56 | 0.00 (GMT) | 97-06 | 85220 | 11.2 |  | 8.3 | 36.1 | 26 | 29.5 | 28.9 | 28 | 28.1333 |  | 24.7 | 26.7 | 27.6 | 26 | 26.3333
Portugal |  | FUNCHAL/S.CATARINA | FUNCHAL/S.CATARINA, Portugal | 32.68N | 16.77W | 49 | 0.00 (GMT) | 82-06 | 85210 | 9.9 |  | 6.3 | 37.3 | 26.9 | 29.7 | 28.3 | 28 | 28.3 |  | 24.5 | 26.2 | 26.8 | 26 | 25.8333
Portugal |  | HORTA/CASTELO BRANC | HORTA/CASTELO BRANC, Portugal | 38.52N | 28.72W | 41 | -1.00 (AZR) | 82-04 | 85050 | 7.9 |  | 5 | 29.8 | 23.5 | 26 | 26.5 | 25 | 25.3333 |  | 22.5 | 25.1 | 25.9 | 25 | 24.5
Portugal |  | LAJES (ACORES) | LAJES (ACORES), Portugal | 38.77N | 27.10W | 54 | -1.00 (AZR) | 82-06 | 85090 | 5.8 |  | 2.8 | 31.9 | 25.2 | 27.8 | 28.4 | 27 | 27.1333 |  | 24 | 26.4 | 27.1 | 26 | 25.8333
Portugal |  | LISBOA/PORTELA | LISBOA/PORTELA, Portugal | 38.77N | 9.13W | 114 | 0.00 (GMT) | 82-06 | 85360 | 1.9 |  | -2 | 43.6 | 34.9 | 37.1 | 37.1 | 36 | 36.3667 |  | 31.9 | 34.2 | 34 | 33 | 33.3667
Portugal |  | PONTA DELGADA/NORDE | PONTA DELGADA/NORDE, Portugal | 37.73N | 25.70W | 72 | -1.00 (AZR) | 82-06 | 85120 | 6.7 |  | 4.2 | 29.1 | 23.5 | 26 | 26.7 | 25 | 25.4 |  | 22.4 | 25.1 | 25.9 | 24 | 24.4667
Portugal |  | PORTALEGRE | PORTALEGRE, Portugal | 39.28N | 7.42W | 590 | 0.00 (GMT) | 82-06 | 85710 | -0.7 |  | -5.3 | 42 | 35.2 | 37.3 | 37.4 | 37 | 36.6333 |  | 32.5 | 35.3 | 35.1 | 34 | 34.3
Portugal |  | PORTO SANTO | PORTO SANTO, Portugal | 33.07N | 16.35W | 82 | 0.00 (GMT) | 82-06 | 85240 | 9.9 |  | 7 | 35.2 | 24.8 | 26.1 | 27 | 26 | 25.9667 |  | 23.5 | 24.9 | 25.9 | 25 | 24.7667
Portugal |  | PORTO/PEDRAS RUBRAS | PORTO/PEDRAS RUBRAS, Portugal | 41.23N | 8.68W | 77 | 0.00 (GMT) | 82-06 | 85450 | -0.7 |  | -4 | 39.1 | 31.5 | 33 | 33.3 | 33 | 32.6 |  | 28.5 | 29.9 | 29.9 | 29 | 29.4333
Portugal |  | SAGRES | SAGRES, Portugal | 37.00N | 8.95W | 25 | 0.00 (GMT) | 82-01 | 85380 | 3.3 |  | -0.7 | 35.5 | 27.2 | 30.8 | 29.9 | 29 | 29.3 |  | 25.2 | 27.8 | 27.6 | 27 | 26.8667
Portugal |  | SANTA MARIA (ACORES) | SANTA MARIA (ACORES), Portugal | 36.97N | 25.17W | 100 | -1.00 (AZR) | 82-06 | 85150 | 8.6 |  | 6.3 | 29.3 | 24.1 | 26.9 | 27.2 | 26 | 26.0667 |  | 23.1 | 25.8 | 26.5 | 25 | 25.1333
Portugal |  | SINES/MONTES CHAOS | SINES/MONTES CHAOS, Portugal | 37.95N | 8.87W | 103 | 0.00 (GMT) | 90-06 | 85410 | 1.4 |  | -3.5 | 41.8 | 31.2 | 31.8 | 32.7 | 32 | 31.9 |  | 27.5 | 28.5 | 29.3 | 28 | 28.4333
Portugal |  | VIANA DO CASTELO | VIANA DO CASTELO, Portugal | 41.70N | 8.80W | 18 | 0.00 (GMT) | 82-06 | 85430 | -1.8 |  | -5.3 | 39.7 | 34.1 | 35.2 | 35.8 | 35 | 35.0333 |  | 31.3 | 32.6 | 31.6 | 32 | 31.8333
Portugal |  | VILA REAL | VILA REAL, Portugal | 41.32N | 7.73W | 481 | 0.00 (GMT) | 82-92 | 85660 | -3.4 |  | -7.2 | 40.7 | 32 | 36.1 | 36.1 | 35 | 34.7333 |  | 30 | 33.8 | 33.1 | 32 | 32.3
Portugal |  | VILA REAL | VILA REAL, Portugal | 41.27N | 7.72W | 562 | 0.00 (GMT) | 92-06 | 85670 | -3.4 |  | -6 | 39.5 | 33.6 | 35 | 36 | 35 | 34.8667 |  | 31.3 | 33.2 | 33.6 | 33 | 32.7
Portugal |  | VISEU | VISEU, Portugal | 40.72N | 7.88W | 644 | 0.00 (GMT) | 97-06 | 85600 | -2.4 |  | -7.5 | 39.8 | 33.2 | 34.9 | 36 | 35 | 34.7 |  | 30.9 | 32.7 | 33.5 | 32 | 32.3667
Puerto Rico |  | AQUADILLA/BORINQUEN | AQUADILLA/BORINQUEN, Puerto Rico | 18.50N | 67.13W | 72 | -4.00 (SAW) | 83-06 | 785140 | N/A |  | N/A | N/A | 31.3 | 31.3 | 31.8 | 31 | 31.4667 |  | 30.8 | 30.9 | 31.1 | 31 | 30.9333
Puerto Rico |  | ROOSEVELT ROADS | ROOSEVELT ROADS, Puerto Rico | 18.25N | 65.63W | 12 | -4.00 (SAW) | 82-06 | 785350 | 18.3 |  | 15.8 | 34.5 | 32.1 | 32.9 | 33.1 | 33 | 32.7 |  | 31.2 | 31.9 | 32.1 | 32 | 31.7333
Puerto Rico |  | SAN JUAN INTL ARPT | SAN JUAN INTL ARPT, Puerto Rico | 18.42N | 66.00W | 19 | -4.00 (SAW) | 82-06 | 785260 | 19.3 |  | 16.7 | 37.1 | 33.7 | 33 | 33.1 | 33 | 33.2667 |  | 32.1 | 31.7 | 31.9 | 32 | 31.9
Puerto Rico |  | SAN JUAN L M MARIN INTL AP | SAN JUAN L M MARIN INTL AP, Puerto Rico | 18.43N | 66.00W | 3 | -4.00 (SAW) | 96-06 | 785263 | 18.9 |  | 14.6 | 35.3 | 33.1 | 32.8 | 33 | 33 | 32.9667 |  | 31.8 | 31.6 | 31.7 | 32 | 31.7
Qatar |  | DOHA INTERNATIONAL | DOHA INTERNATIONAL, Qatar | 25.25N | 51.57E | 10 | 3.00 (AFE) | 83-06 | 411700 | 9 |  | 4.6 | 48.9 | 45.1 | 45.1 | 44.7 | 45 | 44.9667 |  | 43.1 | 43.5 | 42.8 | 43 | 43.1333
Réunion |  | SAINT-DENIS/GILLOT | SAINT-DENIS/GILLOT, Réunion | 20.88S | 55.52E | 25 | 3.00 (AFE) | 82-06 | 619800 | 14.4 |  | 9.8 | 34.8 | 27.2 | 26.2 | 26.4 | 27 | 26.6 |  | 26.6 | 25.6 | 25.6 | 26 | 25.9333
Romania |  | ARAD | ARAD, Romania | 46.13N | 21.35E | 117 | 2.00 (EUE) | 82-06 | 152000 | -16.6 |  | -27.2 | 40.8 | 34.1 | 35.2 | 36 | 35 | 35.1 |  | 31.3 | 33.2 | 33.4 | 33 | 32.6333
Romania |  | BACAU | BACAU, Romania | 46.53N | 26.92E | 190 | 2.00 (EUE) | 82-06 | 151500 | -19.5 |  | -28 | 39.3 | 31.2 | 33.3 | 33.8 | 33 | 32.7667 |  | 29.2 | 31.2 | 31.1 | 31 | 30.5
Romania |  | BAIA MARE | BAIA MARE, Romania | 47.67N | 23.50E | 218 | 2.00 (EUE) | 86-06 | 150140 | N/A |  | N/A | N/A | 32.2 | 33.8 | 31.8 | 33 | 32.6 |  | 30 | 31.8 | 30.1 | 31 | 30.6333
Romania |  | BARLAD | BARLAD, Romania | 46.23N | 27.65E | 173 | 2.00 (EUE) | 82-02 | 151970 | -16.9 |  | -23.2 | 39.3 | 31.4 | 33.5 | 33.7 | 33 | 32.8667 |  | 29.4 | 31.5 | 31.5 | 31 | 30.8
Romania |  | BISTRITA | BISTRITA, Romania | 47.15N | 24.50E | 367 | 2.00 (EUE) | 82-02 | 150850 | -21.8 |  | -31.6 | 38.1 | 29.8 | 31.6 | 32 | 31 | 31.1333 |  | 27.6 | 29.4 | 29.8 | 29 | 28.9333
Romania |  | BLAJ | BLAJ, Romania | 46.18N | 23.93E | 334 | 2.00 (EUE) | 82-02 | 152090 | -18.4 |  | -25.7 | 39.9 | 31.5 | 33.8 | 33.6 | 33 | 32.9667 |  | 28.7 | 30.8 | 31.1 | 30 | 30.2
Romania |  | BOTOSANI | BOTOSANI, Romania | 47.73N | 26.65E | 162 | 2.00 (EUE) | 82-06 | 150200 | -20.2 |  | -29.3 | 39.7 | 31.4 | 33.6 | 33.4 | 33 | 32.8 |  | 29.2 | 30.8 | 30.8 | 30 | 30.2667
Romania |  | BUCURESTI AFUMATI | BUCURESTI AFUMATI, Romania | 44.48N | 26.18E | 90 | 2.00 (EUE) | 82-06 | 154210 | -18 |  | -28.4 | 41.4 | 34 | 36.2 | 35.8 | 35 | 35.3333 |  | 31.8 | 33.1 | 33.1 | 33 | 32.6667
Romania |  | BUCURESTI INMH-BANE | BUCURESTI INMH-BANE, Romania | 44.48N | 26.12E | 91 | 2.00 (EUE) | 82-06 | 154200 | -17.8 |  | -26.6 | 41.8 | 34.2 | 36.8 | 35.9 | 36 | 35.6333 |  | 31.9 | 33.8 | 33.4 | 33 | 33.0333
Romania |  | BUZAU | BUZAU, Romania | 45.13N | 26.85E | 97 | 2.00 (EUE) | 82-06 | 153500 | -15.8 |  | -23.2 | 40.8 | 33.4 | 35.2 | 35.1 | 35 | 34.5667 |  | 30.9 | 32.8 | 32.8 | 32 | 32.1667
Romania |  | CALAFAT | CALAFAT, Romania | 43.98N | 22.95E | 63 | 2.00 (EUE) | 82-02 | 154820 | -15.8 |  | -24.8 | 43.1 | 34.1 | 36.9 | 35.9 | 36 | 35.6333 |  | 31.8 | 34.3 | 33.5 | 33 | 33.2
Romania |  | CALARASI | CALARASI, Romania | 44.20N | 27.33E | 20 | 2.00 (EUE) | 82-06 | 154600 | -16.3 |  | -24 | 42.4 | 33.9 | 37.1 | 35.8 | 36 | 35.6 |  | 31.7 | 33.9 | 33.6 | 33 | 33.0667
Romania |  | CARANSEBES | CARANSEBES, Romania | 45.42N | 22.25E | 242 | 2.00 (EUE) | 82-06 | 152920 | -15.2 |  | -23.4 | 40.4 | 32.4 | 34.8 | 34.9 | 34 | 34.0333 |  | 30.1 | 32 | 32.2 | 31 | 31.4333
Romania |  | CEAHLAU TOACA | CEAHLAU TOACA, Romania | 46.98N | 25.95E | 1898 | 2.00 (EUE) | 82-06 | 151080 | -23.3 |  | -30.1 | 27.8 | 19.4 | 21.4 | 21.4 | 21 | 20.7333 |  | 17 | 18.8 | 19 | 18 | 18.2667
Romania |  | CLUJ-NAPOCA | CLUJ-NAPOCA, Romania | 46.78N | 23.57E | 413 | 2.00 (EUE) | 82-06 | 151200 | -19.1 |  | -26.9 | 38.5 | 31.1 | 31.9 | 32.2 | 32 | 31.7333 |  | 28.8 | 30 | 29.9 | 30 | 29.5667
Romania |  | CONSTANTA | CONSTANTA, Romania | 44.22N | 28.65E | 14 | 2.00 (EUE) | 82-06 | 154800 | -11.9 |  | -17.9 | 39.3 | 29.8 | 31.8 | 31.4 | 31 | 31 |  | 27.7 | 29.9 | 29.4 | 29 | 29
Romania |  | CRAIOVA | CRAIOVA, Romania | 44.32N | 23.87E | 195 | 2.00 (EUE) | 82-06 | 154500 | -15.8 |  | -26.2 | 42.6 | 34.2 | 36.5 | 35.6 | 35 | 35.4333 |  | 31.5 | 33.6 | 33.2 | 33 | 32.7667
Romania |  | DEVA | DEVA, Romania | 45.87N | 22.90E | 231 | 2.00 (EUE) | 82-06 | 152300 | -16.3 |  | -26.4 | 38.5 | 31.5 | 33.8 | 33.8 | 33 | 33.0333 |  | 29 | 31.2 | 31.3 | 31 | 30.5
Romania |  | DROBETA TURNU SEVER | DROBETA TURNU SEVER, Romania | 44.63N | 22.63E | 79 | 2.00 (EUE) | 82-06 | 154100 | -12.8 |  | -20.4 | 42.5 | 34.4 | 36.9 | 36.2 | 36 | 35.8333 |  | 31.8 | 34.2 | 34.1 | 33 | 33.3667
Romania |  | FAGARAS | FAGARAS, Romania | 45.83N | 24.93E | 429 | 2.00 (EUE) | 82-02 | 152350 | -22.3 |  | -31.9 | 38.7 | 30.2 | 32.6 | 32 | 32 | 31.6 |  | 27.8 | 30 | 29.8 | 29 | 29.2
Romania |  | FETESTI | FETESTI, Romania | 44.37N | 27.85E | 61 | 2.00 (EUE) | 82-99 | 154440 | -15.9 |  | -25 | 40.7 | 32.7 | 34.9 | 34.9 | 34 | 34.1667 |  | 30.5 | 32.4 | 32.4 | 32 | 31.7667
Romania |  | GALATI | GALATI, Romania | 45.48N | 28.03E | 72 | 2.00 (EUE) | 82-06 | 153100 | -16.1 |  | -23.6 | 40.3 | 32.4 | 34.7 | 34.7 | 34 | 33.9333 |  | 30.6 | 32.5 | 32.4 | 32 | 31.8333
Romania |  | GIURGIU | GIURGIU, Romania | 43.88N | 25.95E | 24 | 2.00 (EUE) | 82-02 | 154910 | -16.5 |  | -25.1 | 42.9 | 34.1 | 37 | 35.6 | 36 | 35.5667 |  | 31.8 | 34.3 | 33.5 | 33 | 33.2
Romania |  | GRIVITA | GRIVITA, Romania | 44.75N | 27.30E | 51 | 2.00 (EUE) | 82-02 | 154050 | -16.2 |  | -20.5 | 40.2 | 33.1 | 35.4 | 34.4 | 34 | 34.3 |  | 30.9 | 32.7 | 32.2 | 32 | 31.9333
Romania |  | IASI | IASI, Romania | 47.17N | 27.63E | 104 | 2.00 (EUE) | 82-06 | 150900 | -18.9 |  | -29.1 | 40.1 | 32.2 | 34.2 | 34.4 | 34 | 33.6 |  | 30.1 | 31.9 | 32 | 31 | 31.3333
Romania |  | INTORSURA BUZAULUI | INTORSURA BUZAULUI, Romania | 45.68N | 26.02E | 710 | 2.00 (EUE) | 82-02 | 152610 | -28.6 |  | -40.9 | 34.5 | 28.3 | 30 | 29.4 | 29 | 29.2333 |  | 26.1 | 27.8 | 27.4 | 27 | 27.1
Romania |  | JURILOVCA | JURILOVCA, Romania | 44.77N | 28.88E | 38 | 2.00 (EUE) | 82-99 | 154090 | -14.2 |  | -22.9 | 39.4 | 29.7 | 31.2 | 31.7 | 31 | 30.8667 |  | 27.8 | 29.4 | 29.8 | 29 | 29
Romania |  | KOGALNICEANU | KOGALNICEANU, Romania | 44.33N | 28.43E | 102 | 2.00 (EUE) | 82-06 | 154810 | -14.9 |  | -22.9 | 40.3 | 32 | 34.9 | 34.1 | 34 | 33.6667 |  | 30 | 32 | 31.8 | 31 | 31.2667
Romania |  | MANGALIA | MANGALIA, Romania | 43.82N | 28.58E | 9 | 2.00 (EUE) | 82-02 | 154990 | -11.9 |  | -18.3 | 37.3 | 28.5 | 29 | 29.7 | 29 | 29.0667 |  | 26.1 | 27.7 | 27.9 | 27 | 27.2333
Romania |  | MIERCUREA CIUC | MIERCUREA CIUC, Romania | 46.37N | 25.73E | 662 | 2.00 (EUE) | 82-06 | 151700 | -27.8 |  | -36.4 | 35.2 | 28.2 | 30.5 | 30 | 30 | 29.5667 |  | 25.8 | 28 | 27.7 | 27 | 27.1667
Romania |  | ORADEA | ORADEA, Romania | 47.03N | 21.90E | 140 | 2.00 (EUE) | 82-06 | 150800 | -16.7 |  | -24.5 | 39.1 | 33.7 | 34.7 | 34.8 | 34 | 34.4 |  | 30.7 | 32.7 | 32.5 | 32 | 31.9667
Romania |  | ORAVITA | ORAVITA, Romania | 45.03N | 21.68E | 309 | 2.00 (EUE) | 82-02 | 153380 | -12 |  | -17.3 | 41.7 | 31.1 | 34.3 | 34.4 | 33 | 33.2667 |  | 29 | 31.3 | 32 | 31 | 30.7667
Romania |  | PETROSANI | PETROSANI, Romania | 45.42N | 23.38E | 599 | 2.00 (EUE) | 82-02 | 152960 | -17.7 |  | -22.7 | 37.5 | 29 | 31.6 | 30.9 | 31 | 30.5 |  | 26.8 | 28.9 | 28.6 | 28 | 28.1
Romania |  | PLOIESTI | PLOIESTI, Romania | 44.95N | 26.00E | 178 | 2.00 (EUE) | 82-02 | 153770 | -18.3 |  | -26.9 | 41.3 | 32.2 | 34.2 | 33.5 | 33 | 33.3 |  | 29.9 | 31.8 | 31.6 | 31 | 31.1
Romania |  | PREDEAL | PREDEAL, Romania | 45.50N | 25.58E | 1093 | 2.00 (EUE) | 82-02 | 153020 | -18.9 |  | -23.8 | 32.1 | 25.4 | 27.1 | 26.2 | 26 | 26.2333 |  | 23.3 | 24.8 | 24.2 | 24 | 24.1
Romania |  | RARAU (MONASTERY) | RARAU (MONASTERY), Romania | 47.45N | 25.57E | 1541 | 2.00 (EUE) | 82-99 | 150520 | -20.8 |  | -29.6 | 30.3 | 21.6 | 24.2 | 23.2 | 23 | 23 |  | 18.7 | 21 | 21.1 | 20 | 20.2667
Romania |  | RIMNICU VALCEA | RIMNICU VALCEA, Romania | 45.10N | 24.37E | 239 | 2.00 (EUE) | 82-06 | 153460 | -15.3 |  | -24.3 | 38.6 | 32.8 | 34.2 | 33.9 | 34 | 33.6333 |  | 29.9 | 31.8 | 31.7 | 31 | 31.1333
Romania |  | ROMAN | ROMAN, Romania | 46.97N | 26.92E | 217 | 2.00 (EUE) | 82-02 | 151110 | -20.6 |  | -29.3 | 38.4 | 30.5 | 32.2 | 32.3 | 32 | 31.6667 |  | 28.4 | 30.2 | 30 | 30 | 29.5333
Romania |  | ROSIORI DE VEDE | ROSIORI DE VEDE, Romania | 44.10N | 24.98E | 103 | 2.00 (EUE) | 82-06 | 154700 | -18.1 |  | -27.9 | 43.4 | 35 | 37.3 | 36 | 36 | 36.1 |  | 31.9 | 34.2 | 33.8 | 33 | 33.3
Romania |  | SATU MARE | SATU MARE, Romania | 47.72N | 22.88E | 124 | 2.00 (EUE) | 82-06 | 150100 | -20.2 |  | -31.9 | 39 | 32.6 | 33.8 | 33.9 | 33 | 33.4333 |  | 29.9 | 31.7 | 31.5 | 31 | 31.0333
Romania |  | SIBIU | SIBIU, Romania | 45.80N | 24.15E | 444 | 2.00 (EUE) | 82-06 | 152600 | -21.9 |  | -29.8 | 38.5 | 31 | 32.9 | 32.2 | 32 | 32.0333 |  | 28.5 | 30.1 | 30.1 | 30 | 29.5667
Romania |  | SIGHETUL MARMATIEI | SIGHETUL MARMATIEI, Romania | 47.93N | 23.92E | 276 | 2.00 (EUE) | 82-05 | 150040 | -20.9 |  | -31 | 36.7 | 31.2 | 32.5 | 32.8 | 32 | 32.1667 |  | 29.1 | 30.3 | 30.2 | 30 | 29.8667
Romania |  | SUCEAVA | SUCEAVA, Romania | 47.63N | 26.25E | 350 | 2.00 (EUE) | 86-06 | 150230 | N/A |  | N/A | N/A | 29.9 | 31.9 | 30.2 | 31 | 30.6667 |  | 27.8 | 29.2 | 28.1 | 28 | 28.3667
Romania |  | SULINA | SULINA, Romania | 45.17N | 29.73E | 9 | 2.00 (EUE) | 82-06 | 153600 | -11.9 |  | -19.8 | 34.3 | 27.7 | 29.5 | 29.5 | 29 | 28.9 |  | 25.9 | 28.2 | 27.9 | 27 | 27.3333
Romania |  | TARGOVISTE | TARGOVISTE, Romania | 44.93N | 25.43E | 297 | 2.00 (EUE) | 82-02 | 153750 | -16.4 |  | -21.4 | 40.7 | 31.4 | 34.3 | 33.3 | 33 | 33 |  | 29.1 | 31.1 | 31.4 | 31 | 30.5333
Romania |  | TG. JIU | TG. JIU, Romania | 45.03N | 23.27E | 206 | 2.00 (EUE) | 82-02 | 153400 | -17.1 |  | -24.8 | 39.6 | 32 | 34.9 | 34.6 | 34 | 33.8333 |  | 29.8 | 32.3 | 32.4 | 32 | 31.5
Romania |  | TG. MURES | TG. MURES, Romania | 46.53N | 24.53E | 309 | 2.00 (EUE) | 82-06 | 151450 | -19.6 |  | -27.9 | 39.5 | 32.1 | 33.4 | 32.9 | 33 | 32.8 |  | 29.4 | 31.4 | 30.8 | 31 | 30.5333
Romania |  | TIMISOARA | TIMISOARA, Romania | 45.77N | 21.25E | 88 | 2.00 (EUE) | 82-06 | 152470 | -15.9 |  | -25.2 | 40.4 | 34.1 | 35.4 | 36 | 35 | 35.1667 |  | 31.2 | 33.6 | 33.5 | 33 | 32.7667
Romania |  | TR. MAGURELE | TR. MAGURELE, Romania | 43.75N | 24.88E | 31 | 2.00 (EUE) | 82-02 | 154900 | -16.2 |  | -23.8 | 43.3 | 34.9 | 37.6 | 35.8 | 36 | 36.1 |  | 32.1 | 34.5 | 33.5 | 33 | 33.3667
Romania |  | TULCEA | TULCEA, Romania | 45.18N | 28.82E | 6 | 2.00 (EUE) | 82-06 | 153350 | -15.1 |  | -23.8 | 40 | 32.2 | 33.7 | 34.1 | 33 | 33.3333 |  | 30.2 | 31.6 | 31.9 | 31 | 31.2333
Romania |  | VARFU OMU | VARFU OMU, Romania | 45.45N | 25.45E | 2509 | 2.00 (EUE) | 82-06 | 152800 | -25.7 |  | -34.5 | 25.6 | 14.1 | 16.3 | 16.4 | 16 | 15.6 |  | 11.7 | 13.7 | 14.1 | 13 | 13.1667
Romania |  | ZALAU | ZALAU, Romania | 47.18N | 23.08E | 294 | 2.00 (EUE) | 82-02 | 150630 | -14.5 |  | -21.6 | 36.9 | 30.7 | 32 | 32.9 | 32 | 31.8667 |  | 28.4 | 30.2 | 30.7 | 30 | 29.7667
Russia |  | ABAKAN | ABAKAN, Russian Federation | 53.75N | 91.40E | 256 | 7.00 (ASN) | 82-94 | 298650 | -35.9 |  | -44.6 | 34 | 32.2 | 31.8 | 29.4 | 31 | 31.1333 |  | 29.6 | 30.1 | 26.6 | 29 | 28.7667
Russia |  | ACINSK | ACINSK, Russian Federation | 56.28N | 90.50E | 272 | 7.00 (ASN) | 83-05 | 294670 | -35.3 |  | -47.8 | 35.6 | 30.1 | 31.4 | 28.8 | 30 | 30.1 |  | 27 | 29 | 26.3 | 27 | 27.4333
Russia |  | ADLER | ADLER, Russian Federation | 43.43N | 39.90E | 13 | 3.00 (RUS) | 82-06 | 371710 | -5 |  | -9.5 | 38.2 | 28.9 | 31.7 | 31.1 | 31 | 30.5667 |  | 26.6 | 29.8 | 29.7 | 29 | 28.7
Russia |  | AGATA | AGATA, Russian Federation | 66.88N | 93.47E | 278 | 7.00 (ASN) | 82-06 | 233830 | -53.6 |  | -57.9 | 33.1 | 26.8 | 28.3 | 24 | 26 | 26.3667 |  | 23.1 | 25.8 | 20.8 | 23 | 23.2333
Russia |  | AGINSKOE | AGINSKOE, Russian Federation | 55.25N | 94.88E | 337 | 7.00 (ASN) | 82-06 | 296760 | -42 |  | -51.5 | 34.8 | 29.2 | 30.1 | 28.2 | 29 | 29.1667 |  | 27.1 | 28 | 25.5 | 27 | 26.8667
Russia |  | AGINSKOE | AGINSKOE, Russian Federation | 51.10N | 114.52E | 681 | 9.00 (YAK) | 82-06 | 308590 | -37.7 |  | -46.2 | 39.8 | 31.1 | 32.7 | 30.6 | 31 | 31.4667 |  | 28.5 | 29.2 | 27 | 28 | 28.2333
Russia |  | AGZU | AGZU, Russian Federation | 47.60N | 138.40E | 165 | 10.00 (ASV) | 82-06 | 318250 | -35.7 |  | -42.5 | 38.9 | 30.4 | 32 | 32.6 | 32 | 31.6667 |  | 27.4 | 29.1 | 28.7 | 28 | 28.4
Russia |  | AJAN | AJAN, Russian Federation | 56.45N | 138.15E | 8 | 10.00 (ASV) | 82-06 | 311680 | -30.5 |  | -37.9 | 32 | 21.7 | 24 | 23.6 | 23 | 23.1 |  | 18.3 | 20.3 | 21.1 | 20 | 19.9
Russia |  | AKJAR | AKJAR, Russian Federation | 51.87N | 58.18E | 341 | 5.00 (EKT) | 83-06 | 350370 | -32.3 |  | -41.6 | 37.1 | 34.1 | 33.1 | 32.3 | 33 | 33.1667 |  | 31.3 | 31.2 | 30 | 31 | 30.8333
Russia |  | AKSA | AKSA, Russian Federation | 50.27N | 113.27E | 732 | 9.00 (YAK) | 82-06 | 309570 | -39.2 |  | -48.2 | 40 | 31.5 | 33.2 | 31.1 | 32 | 31.9333 |  | 29 | 29.3 | 27.7 | 29 | 28.6667
Russia |  | ALATYR` | ALATYR`, Russian Federation | 54.82N | 46.58E | 180 | 3.00 (RUS) | 82-06 | 276790 | -29.7 |  | -38.3 | 37.8 | 32.5 | 32.2 | 30.7 | 32 | 31.8 |  | 29.2 | 29.7 | 27.4 | 29 | 28.7667
Russia |  | ALDAN | ALDAN, Russian Federation | 58.62N | 125.37E | 679 | 9.00 (YAK) | 82-06 | 310040 | -42.4 |  | -50.5 | 33.4 | 28.6 | 30.1 | 28.2 | 29 | 28.9667 |  | 26.4 | 28.1 | 25.3 | 27 | 26.6
Russia |  | ALEJSKAJA | ALEJSKAJA, Russian Federation | 52.52N | 82.77E | 175 | 6.00 (ASR) | 82-06 | 299370 | -34.5 |  | -46.7 | 39.9 | 32.2 | 33.4 | 33.6 | 33 | 33.0667 |  | 29.9 | 31 | 30.1 | 30 | 30.3333
Russia |  | ALEKSANDROV-GAJ | ALEKSANDROV-GAJ, Russian Federation | 50.15N | 48.55E | 25 | 3.00 (RUS) | 82-06 | 343910 | -28 |  | -36.8 | 42.6 | 37.7 | 37.9 | 36.4 | 37 | 37.3333 |  | 34.8 | 35.4 | 34 | 35 | 34.7333
Russia |  | ALEKSANDROVSKIJ ZAV | ALEKSANDROVSKIJ ZAV, Russian Federation | 50.92N | 117.93E | 807 | 9.00 (YAK) | 82-06 | 309710 | -40.2 |  | -46.6 | 35.1 | 28.3 | 30.3 | 29 | 29 | 29.2 |  | 26.1 | 27.1 | 26.3 | 27 | 26.5
Russia |  | ALEKSANDROVSKOE | ALEKSANDROVSKOE, Russian Federation | 60.43N | 77.87E | 48 | 7.00 (ASN) | 82-06 | 239550 | -42.3 |  | -54 | 34.4 | 30.3 | 30.1 | 27.6 | 29 | 29.3333 |  | 27.7 | 28.2 | 25.1 | 27 | 27
Russia |  | ALEKSANDROVSK-SAHAL | ALEKSANDROVSK-SAHAL, Russian Federation | 50.90N | 142.17E | 31 | 10.00 (ASV) | 82-06 | 320610 | -29.7 |  | -36.2 | 31.5 | 23.1 | 25 | 25.7 | 25 | 24.6 |  | 20.2 | 22.4 | 23.7 | 22 | 22.1
Russia |  | AMDERMA | AMDERMA, Russian Federation | 69.75N | 61.70E | 49 | 3.00 (RUS) | 82-06 | 230220 | -35.6 |  | -43.1 | 36.2 | 20.9 | 25.9 | 20.1 | 22 | 22.3 |  | 15.7 | 21.3 | 17.2 | 18 | 18.0667
Russia |  | AMGA | AMGA, Russian Federation | 60.90N | 131.98E | 146 | 9.00 (YAK) | 82-06 | 249620 | -55.4 |  | -61.4 | 39.6 | 30.7 | 33.9 | 30 | 32 | 31.5333 |  | 28.6 | 31.4 | 27.5 | 29 | 29.1667
Russia |  | ANADYR | ANADYR, Russian Federation | 64.78N | 177.57E | 61 | 12.00 (KAM) | 82-06 | 255630 | -39.6 |  | -45.4 | 29.7 | 19.9 | 23.5 | 20.6 | 21 | 21.3333 |  | 16.3 | 20.2 | 17.6 | 18 | 18.0333
Russia |  | ANAPA | ANAPA, Russian Federation | 44.88N | 37.28E | 32 | 3.00 (RUS) | 87-06 | 370010 | N/A |  | N/A | N/A | 30.2 | 35.2 | 35 | 33 | 33.4667 |  | 28.2 | 33.1 | 33.1 | 31 | 31.4667
Russia |  | ANDREYA ISLAND | ANDREYA ISLAND, Russian Federation | 76.80N | 110.83E | 6 | 7.00 (ASN) | 82-94 | 213010 | N/A |  | N/A | N/A | 9.4 | 17.6 | 17.6 | 15 | 14.8667 |  | 5.3 | 13.5 | 12.6 | 10 | 10.4667
Russia |  | ANTIPAJETA | ANTIPAJETA, Russian Federation | 69.08N | 76.85E | 3 | 5.00 (EKT) | 82-94 | 230580 | N/A |  | N/A | N/A | 22.4 | 29 | 21.3 | 24 | 24.2333 |  | 17.4 | 25.4 | 18.2 | 20 | 20.3333
Russia |  | ANUCINO | ANUCINO, Russian Federation | 43.97N | 133.07E | 188 | 10.00 (ASV) | 82-06 | 319810 | -34 |  | -41.1 | 37.3 | 30.8 | 33.4 | 32.7 | 32 | 32.3 |  | 28.8 | 30.7 | 30.4 | 30 | 29.9667
Russia |  | APUKA | APUKA, Russian Federation | 60.43N | 169.67E | 5 | 12.00 (KAM) | 82-06 | 259560 | -30.8 |  | -38.1 | 25.7 | 15.8 | 19.4 | 17.4 | 18 | 17.5333 |  | 13.6 | 16.9 | 15.6 | 15 | 15.3667
Russia |  | ARHANGELSK | ARHANGELSK, Russian Federation | 64.55N | 40.58E | 4 | 3.00 (RUS) | 82-06 | 225500 | -35.8 |  | -45.2 | 34.5 | 29.6 | 30 | 26.7 | 29 | 28.7667 |  | 26.8 | 27.3 | 23.7 | 26 | 25.9333
Russia |  | ARHARA | ARHARA, Russian Federation | 49.42N | 130.08E | 135 | 9.00 (YAK) | 82-06 | 315940 | -39.5 |  | -46.6 | 36.7 | 30.8 | 32 | 30.3 | 31 | 31.0333 |  | 28.5 | 29.6 | 28.2 | 29 | 28.7667
Russia |  | ARKA | ARKA, Russian Federation | 60.08N | 142.33E | 198 | 10.00 (ASV) | 82-06 | 249880 | -44.4 |  | -49.7 | 36.4 | 29 | 30.1 | 26.1 | 28 | 28.4 |  | 25.2 | 26.6 | 23.8 | 25 | 25.2
Russia |  | ARMAVIR | ARMAVIR, Russian Federation | 44.98N | 41.12E | 159 | 3.00 (RUS) | 82-06 | 370310 | -19.9 |  | -30.7 | 42.8 | 32.6 | 36.5 | 36.1 | 35 | 35.0667 |  | 30.4 | 34.1 | 33.8 | 33 | 32.7667
Russia |  | ASTRAHAN | ASTRAHAN, Russian Federation | 46.28N | 48.05E | -23 | 5.00 (EKT) | 82-06 | 348800 | -20.3 |  | -31.9 | 43 | 36.1 | 37.6 | 35.8 | 37 | 36.5 |  | 33.7 | 35.4 | 33.7 | 34 | 34.2667
Russia |  | ASTRAHANKA | ASTRAHANKA, Russian Federation | 44.72N | 132.07E | 78 | 10.00 (ASV) | 82-06 | 319210 | -29.1 |  | -37.1 | 36.6 | 29.2 | 31.2 | 31.1 | 31 | 30.5 |  | 27 | 29.1 | 28.7 | 28 | 28.2667
Russia |  | ATKA | ATKA, Russian Federation | 60.85N | 151.77E | 901 | 11.00 (MAG) | 82-95 | 259020 | -42.5 |  | -49.4 | 31.2 | 25.1 | 25.7 | 24.4 | 25 | 25.0667 |  | 22.6 | 23.7 | 21.2 | 23 | 22.5
Russia |  | B. PRONCHISHCHEVOY | B. PRONCHISHCHEVOY, Russian Federation | 75.53N | 113.52E | 15 | 7.00 (ASN) | 82-92 | 214050 | N/A |  | N/A | N/A | 11.4 | 18.3 | 16.4 | 15 | 15.3667 |  | 8.1 | 13.2 | 12.2 | 11 | 11.1667
Russia |  | BABAEVO | BABAEVO, Russian Federation | 59.40N | 35.93E | 136 | 3.00 (RUS) | 84-00 | 270080 | N/A |  | N/A | N/A | 30.8 | 29.8 | 26.4 | 29 | 29 |  | 28.4 | 27.1 | 24.8 | 27 | 26.7667
Russia |  | BABUSKIN | BABUSKIN, Russian Federation | 51.72N | 105.85E | 467 | 8.00 (ASE) | 82-06 | 308220 | -28.4 |  | -35.3 | 32.2 | 21.5 | 24.7 | 24.8 | 24 | 23.6667 |  | 18.8 | 22.4 | 21.5 | 21 | 20.9
Russia |  | BAEVO | BAEVO, Russian Federation | 53.27N | 80.77E | 122 | 6.00 (ASR) | 82-06 | 298270 | -38.4 |  | -50.7 | 38.6 | 31.9 | 32.2 | 31.8 | 32 | 31.9667 |  | 29.6 | 30.3 | 29.2 | 30 | 29.7
Russia |  | BAGDARIN | BAGDARIN, Russian Federation | 54.47N | 113.58E | 903 | 8.00 (ASE) | 82-06 | 305540 | -43.4 |  | -51.4 | 35 | 27.8 | 29.9 | 27.3 | 28 | 28.3333 |  | 25.9 | 27.1 | 24.9 | 26 | 25.9667
Russia |  | BAJANDAJ | BAJANDAJ, Russian Federation | 53.10N | 105.53E | 762 | 8.00 (ASE) | 82-06 | 306270 | -38.8 |  | -46 | 33.5 | 29.6 | 28.7 | 27.1 | 28 | 28.4667 |  | 26.5 | 26.3 | 24.6 | 26 | 25.8
Russia |  | BAKALY | BAKALY, Russian Federation | 55.18N | 53.80E | 126 | 5.00 (EKT) | 82-05 | 286150 | -35.3 |  | -44.2 | 38.7 | 32.7 | 32.4 | 31.7 | 32 | 32.2667 |  | 30.1 | 30.4 | 28.6 | 30 | 29.7
Russia |  | BAKCHAR | BAKCHAR, Russian Federation | 57.08N | 81.92E | 110 | 7.00 (ASN) | 82-06 | 293280 | -40.7 |  | -50.7 | 35.9 | 30.5 | 30.8 | 29.1 | 30 | 30.1333 |  | 27.8 | 28.5 | 26.4 | 28 | 27.5667
Russia |  | BALAGANSK | BALAGANSK, Russian Federation | 54.00N | 103.07E | 427 | 8.00 (ASE) | 82-06 | 306120 | -38.7 |  | -48.5 | 36.2 | 29.5 | 30.9 | 28.1 | 30 | 29.5 |  | 27 | 28.9 | 25.9 | 27 | 27.2667
Russia |  | BALASOV | BALASOV, Russian Federation | 51.55N | 43.15E | 159 | 3.00 (RUS) | 82-06 | 341520 | -27.2 |  | -37.7 | 39.4 | 33.2 | 33.9 | 32.9 | 33 | 33.3333 |  | 30.2 | 31.2 | 30.2 | 31 | 30.5333
Russia |  | BARABINSK | BARABINSK, Russian Federation | 55.33N | 78.37E | 120 | 6.00 (ASR) | 82-06 | 296120 | -37.2 |  | -49.6 | 36.9 | 31.4 | 31.6 | 29.9 | 31 | 30.9667 |  | 29.2 | 29.4 | 27.2 | 29 | 28.6
Russia |  | BARENCBURG | BARENCBURG, Russian Federation | 78.07N | 14.25E | 75 | 1.00 (EUW) | 82-06 | 201070 | -28.1 |  | -39.5 | 20.7 | 9.1 | 13 | 11.9 | 11 | 11.3333 |  | 7.3 | 11.2 | 10.1 | 10 | 9.5333
Russia |  | BARNAUL | BARNAUL, Russian Federation | 53.43N | 83.52E | 184 | 6.00 (ASR) | 82-06 | 298380 | -34.4 |  | -49 | 39.1 | 31.2 | 32.1 | 32.1 | 32 | 31.8 |  | 29 | 29.8 | 28.8 | 29 | 29.2
Russia |  | BATAMAJ | BATAMAJ, Russian Federation | 63.52N | 129.48E | 79 | 9.00 (YAK) | 82-06 | 246560 | -55.5 |  | -62.4 | 34.5 | 27.8 | 30.3 | 28.1 | 29 | 28.7333 |  | 25.3 | 28.4 | 25.2 | 26 | 26.3
Russia |  | BEJA | BEJA, Russian Federation | 53.05N | 90.92E | 469 | 7.00 (ASN) | 83-01 | 299620 | N/A |  | N/A | N/A | 29.9 | 30.9 | 30.3 | 30 | 30.3667 |  | 27.6 | 28.1 | 27.5 | 28 | 27.7333
Russia |  | BELOGORSK | BELOGORSK, Russian Federation | 50.92N | 128.47E | 178 | 9.00 (YAK) | 82-06 | 315130 | -36.6 |  | -43.7 | 39.4 | 31.4 | 31 | 29.9 | 31 | 30.7667 |  | 29.6 | 29.4 | 27.8 | 29 | 28.9333
Russia |  | BELYJ | BELYJ, Russian Federation | 55.85N | 32.95E | 222 | 3.00 (RUS) | 82-01 | 265850 | -28.6 |  | -36.3 | 34.1 | 28.6 | 30 | 27.5 | 29 | 28.7 |  | 26.2 | 27.1 | 25.3 | 26 | 26.2
Russia |  | BEREZOVO | BEREZOVO, Russian Federation | 63.93N | 65.05E | 32 | 5.00 (EKT) | 82-06 | 236310 | -43.6 |  | -51.9 | 34.8 | 28.4 | 29.9 | 26.1 | 28 | 28.1333 |  | 25.5 | 27.5 | 22.7 | 25 | 25.2333
Russia |  | BERINGOVSKAJA | BERINGOVSKAJA, Russian Federation | 63.05N | 179.32E | 82 | 12.00 (KAM) | 82-95 | 256770 | -31 |  | -36.2 | 29.5 | 18.1 | 20.7 | 19.7 | 20 | 19.5 |  | 15.6 | 17.6 | 16.6 | 17 | 16.6
Russia |  | BEZECK | BEZECK, Russian Federation | 57.80N | 36.70E | 147 | 3.00 (RUS) | 82-93 | 272170 | -31.2 |  | -43.8 | 32 | 27.4 | 28.4 | 27.3 | 28 | 27.7 |  | 25.2 | 26.8 | 25.1 | 26 | 25.7
Russia |  | BIJSK ZONALNAJA | BIJSK ZONALNAJA, Russian Federation | 52.68N | 84.95E | 228 | 6.00 (ASR) | 84-06 | 299390 | -39.4 |  | -48.9 | 38.9 | 31.7 | 33.5 | 33.6 | 33 | 32.9333 |  | 29.3 | 30.8 | 29.9 | 30 | 30
Russia |  | BIKIN | BIKIN, Russian Federation | 46.80N | 134.27E | 68 | 10.00 (ASV) | 82-06 | 318320 | -35.5 |  | -39.1 | 36.9 | 30.6 | 31.8 | 33 | 32 | 31.8 |  | 28.7 | 30.1 | 29.6 | 29 | 29.4667
Russia |  | BIRILIUSSY | BIRILIUSSY, Russian Federation | 57.13N | 90.70E | 182 | 7.00 (ASN) | 82-02 | 293670 | -42.9 |  | -53.9 | 33.9 | 28.6 | 31.2 | 27.4 | 29 | 29.0667 |  | 26.4 | 29.1 | 25.3 | 27 | 26.9333
Russia |  | BIROBIDZHAN | BIROBIDZHAN, Russian Federation | 48.73N | 132.95E | 80 | 10.00 (ASV) | 82-06 | 317130 | -37.2 |  | -42.8 | 36.7 | 31 | 32.5 | 30.7 | 31 | 31.4 |  | 28.9 | 30.3 | 28.3 | 29 | 29.1667
Russia |  | BIRSK | BIRSK, Russian Federation | 55.42N | 55.53E | 187 | 5.00 (EKT) | 82-06 | 286210 | -31.3 |  | -40.3 | 37.7 | 32.2 | 31.4 | 30.6 | 31 | 31.4 |  | 29.6 | 29.7 | 27.7 | 29 | 29
Russia |  | BLAGOVESCENSK | BLAGOVESCENSK, Russian Federation | 50.25N | 127.57E | 132 | 9.00 (YAK) | 82-06 | 315100 | -34.6 |  | -43 | 38.4 | 32.1 | 33.2 | 30.6 | 32 | 31.9667 |  | 29.8 | 30.6 | 28.7 | 30 | 29.7
Russia |  | BODAJBO | BODAJBO, Russian Federation | 57.85N | 114.23E | 275 | 8.00 (ASE) | 82-05 | 302530 | -45.9 |  | -52.6 | 38.2 | 31.7 | 33.1 | 31 | 32 | 31.9333 |  | 28.9 | 30.9 | 27.2 | 29 | 29
Russia |  | BOGORODSKOE | BOGORODSKOE, Russian Federation | 52.38N | 140.47E | 35 | 10.00 (ASV) | 82-06 | 314390 | -37.9 |  | -45.2 | 34.2 | 28.3 | 29.2 | 28.1 | 29 | 28.5333 |  | 25.7 | 27.4 | 25.9 | 26 | 26.3333
Russia |  | BOGOTOL | BOGOTOL, Russian Federation | 56.23N | 89.58E | 291 | 7.00 (ASN) | 82-06 | 295530 | -36.7 |  | -48.9 | 34 | 29 | 29.7 | 28.1 | 29 | 28.9333 |  | 26.6 | 27.8 | 25.6 | 27 | 26.6667
Russia |  | BOGUCANY | BOGUCANY, Russian Federation | 58.38N | 97.45E | 133 | 7.00 (ASN) | 82-06 | 292820 | -43.6 |  | -54.1 | 36.7 | 31.3 | 32.2 | 29.4 | 31 | 30.9667 |  | 28.4 | 30 | 26.6 | 28 | 28.3333
Russia |  | BOGUCAR | BOGUCAR, Russian Federation | 49.93N | 40.57E | 84 | 3.00 (RUS) | 82-06 | 343360 | -26.3 |  | -37.1 | 41.6 | 34.1 | 36.6 | 34.6 | 35 | 35.1 |  | 31.5 | 33.1 | 31.8 | 32 | 32.1333
Russia |  | BOL`SIE-UKI | BOL`SIE-UKI, Russian Federation | 56.93N | 72.67E | 87 | 6.00 (ASR) | 82-06 | 284910 | -38.6 |  | -50.5 | 37 | 31.1 | 31 | 28.5 | 30 | 30.2 |  | 28.7 | 28.7 | 26.1 | 28 | 27.8333
Russia |  | BOLOGOE | BOLOGOE, Russian Federation | 57.90N | 34.05E | 188 | 3.00 (RUS) | 82-06 | 262980 | -29.4 |  | -39.2 | 34.8 | 29.6 | 30.2 | 27.2 | 29 | 29 |  | 26.7 | 27.6 | 25.2 | 27 | 26.5
Russia |  | BOLSHAJA MURTA | BOLSHAJA MURTA, Russian Federation | 56.90N | 93.13E | 180 | 7.00 (ASN) | 82-06 | 294710 | -41.7 |  | -53.8 | 35.5 | 30.1 | 30.9 | 29.1 | 30 | 30.0333 |  | 27.5 | 28.7 | 26.7 | 28 | 27.6333
Russia |  | BOLSHERECHE | BOLSHERECHE, Russian Federation | 56.10N | 74.63E | 78 | 6.00 (ASR) | 82-06 | 285930 | -38.3 |  | -50.4 | 37.8 | 31.4 | 31.7 | 29.9 | 31 | 31 |  | 29.3 | 29.2 | 26.8 | 28 | 28.4333
Russia |  | BOLSOJ SANTAR | BOLSOJ SANTAR, Russian Federation | 54.83N | 137.53E | 21 | 10.00 (ASV) | 82-06 | 311740 | -37.6 |  | -47 | 31.2 | 21.8 | 23.6 | 23.4 | 23 | 22.9333 |  | 18.4 | 20.5 | 20.7 | 20 | 19.8667
Russia |  | BOMNAK | BOMNAK, Russian Federation | 54.72N | 128.93E | 357 | 9.00 (YAK) | 82-06 | 312530 | -43.2 |  | -48.9 | 36.9 | 29.1 | 30.7 | 28.5 | 29 | 29.4333 |  | 27.1 | 28.7 | 25.9 | 27 | 27.2333
Russia |  | BOR | BOR, Russian Federation | 61.60N | 90.02E | 58 | 7.00 (ASN) | 82-06 | 238840 | -47.9 |  | -58.4 | 37.9 | 31.9 | 32 | 29.6 | 31 | 31.1667 |  | 28.5 | 29.7 | 26.2 | 28 | 28.1333
Russia |  | BORZJA | BORZJA, Russian Federation | 50.40N | 116.52E | 676 | 9.00 (YAK) | 82-06 | 309650 | -40.6 |  | -47.9 | 39.1 | 31.5 | 33.6 | 31.7 | 32 | 32.2667 |  | 29 | 29.9 | 28.4 | 29 | 29.1
Russia |  | BRATOLJUBOVKA | BRATOLJUBOVKA, Russian Federation | 50.78N | 129.33E | 227 | 9.00 (YAK) | 82-95 | 315210 | -42.2 |  | -46.5 | 35.2 | 30.7 | 30 | 29.3 | 30 | 30 |  | 28.6 | 28.6 | 26.9 | 28 | 28.0333
Russia |  | BRATSK | BRATSK, Russian Federation | 56.28N | 101.75E | 416 | 8.00 (ASE) | 82-06 | 303090 | -37.8 |  | -49.9 | 35.4 | 29.3 | 30.9 | 28.2 | 29 | 29.4667 |  | 26.9 | 28.6 | 25.7 | 27 | 27.0667
Russia |  | BRJANSK | BRJANSK, Russian Federation | 53.25N | 34.32E | 216 | 3.00 (RUS) | 82-06 | 268980 | -24.8 |  | -33.3 | 36 | 29.8 | 31.4 | 29.2 | 30 | 30.1333 |  | 27.3 | 28.6 | 26.9 | 28 | 27.6
Russia |  | BUDENNOVSK | BUDENNOVSK, Russian Federation | 44.78N | 44.13E | 136 | 3.00 (RUS) | 84-06 | 370610 | -20.1 |  | -30 | 42.4 | 35.7 | 37.9 | 37 | 37 | 36.8667 |  | 32.8 | 35.8 | 34.8 | 34 | 34.4667
Russia |  | BUGULMA | BUGULMA, Russian Federation | 54.58N | 52.80E | 312 | 4.00 (CAU) | 82-06 | 287110 | -30.1 |  | -38.5 | 37.2 | 31.7 | 31 | 30.5 | 31 | 31.0667 |  | 28.8 | 29.2 | 27.6 | 29 | 28.5333
Russia |  | BUHTA PROVIDENJA | BUHTA PROVIDENJA, Russian Federation | 64.42N | 173.23W | 40 | 12.00 (KAM) | 82-06 | 255940 | -31.8 |  | -40.6 | 26.9 | 16.5 | 19.9 | 16.1 | 18 | 17.5 |  | 13.7 | 16.3 | 14 | 15 | 14.6667
Russia |  | BUJ | BUJ, Russian Federation | 58.48N | 41.53E | 97 | 3.00 (RUS) | 82-06 | 272420 | -33.7 |  | -45.1 | 37.7 | 30.9 | 30.9 | 28.2 | 30 | 30 |  | 28.2 | 28.8 | 25.5 | 28 | 27.5
Russia |  | BURUKAN | BURUKAN, Russian Federation | 53.05N | 136.03E | 153 | 10.00 (ASV) | 82-06 | 313480 | -45.4 |  | -51.3 | 36.2 | 31.4 | 31.2 | 30.1 | 31 | 30.9 |  | 28.4 | 29.2 | 27 | 28 | 28.2
Russia |  | BUZULUK | BUZULUK, Russian Federation | 52.82N | 52.22E | 80 | 5.00 (EKT) | 82-06 | 289090 | -32.1 |  | -40.6 | 41 | 35.3 | 34.8 | 34.2 | 35 | 34.7667 |  | 32.2 | 32.3 | 30.8 | 32 | 31.7667
Russia |  | CAJVO | CAJVO, Russian Federation | 52.37N | 143.18E | 6 | 10.00 (ASV) | 83-92 | 320360 | N/A |  | N/A | N/A | 26.7 | 26.5 | 26.8 | 27 | 26.6667 |  | 22.5 | 23.4 | 24.1 | 23 | 23.3333
Russia |  | CAPE BOLVANSKIJ | CAPE BOLVANSKIJ, Russian Federation | 70.45N | 59.07E | 13 | 3.00 (RUS) | 82-94 | 209460 | N/A |  | N/A | N/A | 13.8 | 18.8 | 15.4 | 16 | 16 |  | 9.2 | 15.6 | 13.1 | 13 | 12.6333
Russia |  | CAPE KAMENNYJ | CAPE KAMENNYJ, Russian Federation | 68.47N | 73.60E | 5 | 5.00 (EKT) | 82-94 | 231460 | -42.9 |  | -52.2 | 29.6 | 13.9 | 24.7 | 19.2 | 19 | 19.2667 |  | 10.2 | 20.8 | 16.8 | 16 | 15.9333
Russia |  | CAPE MENSHIKOVA | CAPE MENSHIKOVA, Russian Federation | 70.72N | 57.62E | 14 | 3.00 (RUS) | 82-94 | 209430 | N/A |  | N/A | N/A | 10.5 | 15.9 | 13 | 13 | 13.1333 |  | 7.7 | 11.6 | 11.3 | 10 | 10.2
Russia |  | CAPE STERLEGOVA | CAPE STERLEGOVA, Russian Federation | 75.42N | 88.90E | 11 | 7.00 (ASN) | 82-94 | 204760 | N/A |  | N/A | N/A | 13.4 | 20.3 | 15.6 | 16 | 16.4333 |  | 8 | 15.6 | 12.4 | 12 | 12
Russia |  | CAPE VASILEVA | CAPE VASILEVA, Russian Federation | 50.02N | 155.40E | 11 | 12.00 (KAM) | 82-94 | 322170 | -14.4 |  | -17.3 | 24.4 | 16.4 | 16.2 | 17.2 | 17 | 16.6 |  | 13 | 14.4 | 15 | 14 | 14.1333
Russia |  | CEKUNDA | CEKUNDA, Russian Federation | 50.87N | 132.25E | 272 | 9.00 (YAK) | 82-06 | 315320 | N/A |  | N/A | N/A | 30.1 | 32.8 | 31.2 | 31 | 31.3667 |  | 28.2 | 31.2 | 29 | 29 | 29.4667
Russia |  | CELINA | CELINA, Russian Federation | 46.55N | 41.05E | 112 | 3.00 (RUS) | 82-98 | 347470 | -21.1 |  | -28.7 | 40.5 | 33.5 | 36.6 | 35.2 | 35 | 35.1 |  | 31.1 | 33.8 | 32.3 | 32 | 32.4
Russia |  | CEMAL | CEMAL, Russian Federation | 51.43N | 86.00E | 420 | 6.00 (ASR) | 84-06 | 360580 | -31.4 |  | -40.7 | 40.3 | 31.5 | 34.1 | 33.7 | 33 | 33.1 |  | 29.5 | 30.2 | 29.5 | 30 | 29.7333
Russia |  | CENTRALNYJ RUDNIK | CENTRALNYJ RUDNIK, Russian Federation | 55.22N | 87.65E | 495 | 7.00 (ASN) | 85-06 | 296540 | -36.5 |  | -48.9 | 34.6 | 28.4 | 29.5 | 30.2 | 29 | 29.3667 |  | 25.7 | 26.9 | 27.1 | 27 | 26.5667
Russia |  | CEREPOVEC | CEREPOVEC, Russian Federation | 59.25N | 37.97E | 114 | 3.00 (RUS) | 82-06 | 271130 | -35.1 |  | -46.8 | 34.7 | 29.3 | 30.3 | 26.7 | 29 | 28.7667 |  | 26.9 | 27.8 | 24.6 | 26 | 26.4333
Russia |  | CERLAK | CERLAK, Russian Federation | 54.17N | 74.80E | 115 | 6.00 (ASR) | 82-06 | 287990 | -34.8 |  | -45.5 | 39.8 | 32.7 | 32.9 | 31.5 | 32 | 32.3667 |  | 30.6 | 30.3 | 29 | 30 | 29.9667
Russia |  | CERNUSKA | CERNUSKA, Russian Federation | 56.50N | 56.13E | 142 | 5.00 (EKT) | 82-06 | 284280 | -37.4 |  | -47.3 | 37.3 | 32.6 | 31.7 | 30.7 | 32 | 31.6667 |  | 29.4 | 30 | 27.2 | 29 | 28.8667
Russia |  | CHANY | CHANY, Russian Federation | 55.28N | 76.60E | 111 | 6.00 (ASR) | 82-06 | 296020 | -37.2 |  | -50.7 | 37.4 | 31.1 | 32.1 | 29.8 | 31 | 31 |  | 28.8 | 29.7 | 27.1 | 29 | 28.5333
Russia |  | CHARA | CHARA, Russian Federation | 56.90N | 118.27E | 711 | 9.00 (YAK) | 82-06 | 303720 | -47.3 |  | -56.2 | 34.7 | 28.7 | 30.5 | 28.4 | 29 | 29.2 |  | 26.6 | 28.1 | 25.5 | 27 | 26.7333
Russia |  | CHELJABINSK-BALANDI | CHELJABINSK-BALANDI, Russian Federation | 55.30N | 61.53E | 227 | 5.00 (EKT) | 82-06 | 286420 | -31.5 |  | -41.4 | 38.3 | 32.4 | 32.5 | 31.8 | 32 | 32.2333 |  | 30 | 30 | 28.2 | 29 | 29.4
Russia |  | CHERDYN | CHERDYN, Russian Federation | 60.40N | 56.52E | 207 | 5.00 (EKT) | 82-06 | 239140 | -36.1 |  | -47.1 | 34.9 | 30 | 30.2 | 27.7 | 29 | 29.3 |  | 27.4 | 28.6 | 24.6 | 27 | 26.8667
Russia |  | CHERNISHEVSKIJ | CHERNISHEVSKIJ, Russian Federation | 63.03N | 112.50E | 422 | 9.00 (YAK) | 82-06 | 247240 | -46.1 |  | -56.3 | 34.6 | 28.4 | 30.7 | 26.9 | 29 | 28.6667 |  | 25.5 | 28.7 | 24.4 | 26 | 26.2
Russia |  | CHERNJAEVO | CHERNJAEVO, Russian Federation | 52.78N | 126.00E | 210 | 9.00 (YAK) | 82-06 | 313710 | -42.5 |  | -50.1 | 38.5 | 30.9 | 33.3 | 30.6 | 32 | 31.6 |  | 28.9 | 30.2 | 27.9 | 29 | 29
Russia |  | CHERSKIJ | CHERSKIJ, Russian Federation | 68.75N | 161.28E | 28 | 11.00 (MAG) | 82-06 | 251230 | -45.5 |  | -51.9 | 34.4 | 26.8 | 29 | 26.1 | 27 | 27.3 |  | 23.7 | 26 | 21.8 | 24 | 23.8333
Russia |  | CHITA | CHITA, Russian Federation | 52.08N | 113.48E | 671 | 9.00 (YAK) | 82-06 | 307580 | -38.7 |  | -46 | 39.8 | 33.1 | 34.6 | 31.1 | 33 | 32.9333 |  | 30 | 30.8 | 28.3 | 30 | 29.7
Russia |  | CHOKURDAH | CHOKURDAH, Russian Federation | 70.62N | 147.88E | 61 | 11.00 (MAG) | 82-06 | 219460 | -46.7 |  | -51.3 | 31.8 | 25.5 | 27 | 24.2 | 26 | 25.5667 |  | 21.8 | 24.6 | 20 | 22 | 22.1333
Russia |  | CJULBJU | CJULBJU, Russian Federation | 57.77N | 130.90E | 255 | 9.00 (YAK) | 82-06 | 311230 | -49 |  | -54.6 | 37.6 | 31 | 32.3 | 29.2 | 31 | 30.8333 |  | 28.3 | 30 | 26.2 | 28 | 28.1667
Russia |  | CUGUEVKA | CUGUEVKA, Russian Federation | 44.15N | 133.87E | 259 | 10.00 (ASV) | 82-96 | 319390 | -37 |  | -44.7 | 39.3 | 30.5 | 33.1 | 34.3 | 33 | 32.6333 |  | 28.7 | 30.7 | 31.3 | 30 | 30.2333
Russia |  | CULMAN | CULMAN, Russian Federation | 56.83N | 124.87E | 858 | 9.00 (YAK) | 82-06 | 303930 | -45 |  | -52.6 | 33.2 | 27.2 | 29.1 | 26.8 | 28 | 27.7 |  | 25.2 | 26.8 | 24.4 | 25 | 25.4667
Russia |  | CULYM | CULYM, Russian Federation | 55.10N | 80.97E | 140 | 6.00 (ASR) | 82-06 | 296250 | -38.4 |  | -49.7 | 36.9 | 29.9 | 31.1 | 29 | 30 | 30 |  | 27.7 | 28.9 | 26.9 | 28 | 27.8333
Russia |  | CURAPCA | CURAPCA, Russian Federation | 62.03N | 132.60E | 186 | 9.00 (YAK) | 82-06 | 247680 | -55.5 |  | -60.4 | 37.8 | 30.9 | 33.3 | 29.7 | 31 | 31.3 |  | 28.4 | 30.9 | 26.9 | 29 | 28.7333
Russia |  | DALNERECHENSK | DALNERECHENSK, Russian Federation | 45.87N | 133.73E | 101 | 10.00 (ASV) | 82-06 | 318730 | -31.3 |  | -37.2 | 37.6 | 29.9 | 31.4 | 31.8 | 31 | 31.0333 |  | 28 | 29.4 | 29 | 29 | 28.8
Russia |  | DEMJANSKOE | DEMJANSKOE, Russian Federation | 59.60N | 69.28E | 57 | 5.00 (EKT) | 82-06 | 280760 | -40.2 |  | -52 | 37 | 30.5 | 31.1 | 27.7 | 30 | 29.7667 |  | 28.5 | 29.1 | 25 | 28 | 27.5333
Russia |  | DIVNOE | DIVNOE, Russian Federation | 45.92N | 43.35E | 87 | 3.00 (RUS) | 82-06 | 348580 | -19.7 |  | -31.6 | 42.6 | 35.4 | 38.1 | 37.3 | 37 | 36.9333 |  | 33 | 35.7 | 34.6 | 34 | 34.4333
Russia |  | DUDINKA | DUDINKA, Russian Federation | 69.40N | 86.17E | 19 | 7.00 (ASN) | 82-06 | 230740 | -48 |  | -54.9 | 35 | 27.6 | 28.7 | 25 | 27 | 27.1 |  | 23.5 | 26.1 | 21.1 | 24 | 23.5667
Russia |  | DUKI | DUKI, Russian Federation | 51.72N | 135.93E | 132 | 10.00 (ASV) | 82-94 | 314820 | -43.4 |  | -51.5 | 38.1 | 31.9 | 32.7 | 32 | 32 | 32.2 |  | 29.5 | 30.6 | 28.6 | 30 | 29.5667
Russia |  | DUVAN | DUVAN, Russian Federation | 55.70N | 57.90E | 326 | 5.00 (EKT) | 82-05 | 285370 | -33.5 |  | -41.9 | 34.3 | 31.4 | 30.7 | 29.8 | 31 | 30.6333 |  | 28.6 | 28.7 | 26.8 | 28 | 28.0333
Russia |  | DZALINDA | DZALINDA, Russian Federation | 53.47N | 123.90E | 266 | 9.00 (YAK) | 82-06 | 306950 | -41.5 |  | -48.4 | 39.8 | 30.8 | 33.1 | 29.8 | 31 | 31.2333 |  | 28.8 | 29.9 | 27.2 | 29 | 28.6333
Russia |  | DZARDZAN | DZARDZAN, Russian Federation | 68.73N | 124.00E | 39 | 9.00 (YAK) | 82-06 | 241430 | N/A |  | N/A | N/A | 27.7 | 29.4 | 26.7 | 28 | 27.9333 |  | 24.4 | 27 | 23.7 | 25 | 25.0333
Russia |  | DZERZHINSKOE | DZERZHINSKOE, Russian Federation | 56.85N | 95.22E | 188 | 7.00 (ASN) | 82-06 | 294810 | -43.7 |  | -54.8 | 36.3 | 30.9 | 32.2 | 29.3 | 31 | 30.8 |  | 28.2 | 30.1 | 26.6 | 28 | 28.3
Russia |  | EGVEKINOT | EGVEKINOT, Russian Federation | 66.35N | 179.12W | 26 | 12.00 (KAM) | 82-06 | 253780 | -37.2 |  | -48 | 29.3 | 19.7 | 21.5 | 20.1 | 20 | 20.4333 |  | 16 | 18.6 | 16.4 | 17 | 17
Russia |  | EKATERINBURG | EKATERINBURG, Russian Federation | 56.83N | 60.63E | 283 | 5.00 (EKT) | 82-06 | 284400 | -33.5 |  | -43.7 | 36.9 | 31.5 | 31.5 | 30 | 31 | 31 |  | 28.8 | 29.2 | 26.8 | 28 | 28.2667
Russia |  | EKATERINO-NIKOLSKOE | EKATERINO-NIKOLSKOE, Russian Federation | 47.73N | 130.97E | 73 | 10.00 (ASV) | 82-06 | 317070 | -33.1 |  | -38.2 | 38.5 | 31.9 | 32.8 | 31.7 | 32 | 32.1333 |  | 29.1 | 30 | 29 | 29 | 29.3667
Russia |  | EKIMCHAN | EKIMCHAN, Russian Federation | 53.07N | 132.98E | 542 | 9.00 (YAK) | 82-06 | 313290 | -44.5 |  | -50.8 | 33.9 | 29.5 | 30.4 | 27.7 | 29 | 29.2 |  | 27.1 | 28.6 | 25.3 | 27 | 27
Russia |  | ELABUGA | ELABUGA, Russian Federation | 55.77N | 52.07E | 192 | 4.00 (CAU) | 82-06 | 285060 | -31 |  | -41 | 37.7 | 32.1 | 31.8 | 30.7 | 32 | 31.5333 |  | 29.2 | 29.8 | 27.4 | 29 | 28.8
Russia |  | ELAT`MA | ELAT`MA, Russian Federation | 54.95N | 41.77E | 136 | 3.00 (RUS) | 82-06 | 276480 | -30 |  | -39.8 | 37.1 | 31.4 | 31.7 | 29.9 | 31 | 31 |  | 28.5 | 29.2 | 27.1 | 28 | 28.2667
Russia |  | ELEC | ELEC, Russian Federation | 52.63N | 38.52E | 168 | 3.00 (RUS) | 82-06 | 279280 | -26.9 |  | -37.7 | 36.4 | 31.5 | 32.6 | 31 | 32 | 31.7 |  | 29.1 | 30.2 | 28.4 | 29 | 29.2333
Russia |  | ENISEJSK | ENISEJSK, Russian Federation | 58.45N | 92.15E | 79 | 7.00 (ASN) | 82-06 | 292630 | -43 |  | -54 | 35.5 | 30.6 | 31.3 | 28.8 | 30 | 30.2333 |  | 27.6 | 29.2 | 26.2 | 28 | 27.6667
Russia |  | ERBOGACEN | ERBOGACEN, Russian Federation | 61.27N | 108.02E | 291 | 8.00 (ASE) | 82-06 | 248170 | -51.5 |  | -60.9 | 35.7 | 30.6 | 32 | 28.2 | 30 | 30.2667 |  | 28.1 | 29.5 | 25.8 | 28 | 27.8
Russia |  | ERMAKOVSKOE | ERMAKOVSKOE, Russian Federation | 53.30N | 92.42E | 298 | 7.00 (ASN) | 82-06 | 298690 | -39.1 |  | -46.5 | 36.5 | 30.7 | 31.4 | 30.7 | 31 | 30.9333 |  | 28.4 | 29.2 | 27.7 | 28 | 28.4333
Russia |  | EROFEJ PAVLOVIC | EROFEJ PAVLOVIC, Russian Federation | 53.97N | 121.93E | 522 | 9.00 (YAK) | 85-06 | 306830 | -39.4 |  | -46.1 | 36.7 | 28.8 | 31.4 | 29.1 | 30 | 29.7667 |  | 27.1 | 29.1 | 26.8 | 28 | 27.6667
Russia |  | ERSOV | ERSOV, Russian Federation | 51.37N | 48.30E | 111 | 3.00 (RUS) | 82-06 | 341860 | -27.8 |  | -36.1 | 41.5 | 35.8 | 36.1 | 34.9 | 36 | 35.6 |  | 32.6 | 33.5 | 32.2 | 33 | 32.7667
Russia |  | GAJNY | GAJNY, Russian Federation | 60.28N | 54.35E | 198 | 5.00 (EKT) | 82-06 | 239090 | -35.7 |  | -46.4 | 34.3 | 29.9 | 30.2 | 27.5 | 29 | 29.2 |  | 27.3 | 28.7 | 24.5 | 27 | 26.8333
Russia |  | GAR | GAR, Russian Federation | 52.57N | 129.07E | 246 | 9.00 (YAK) | 82-95 | 313840 | -45.2 |  | -51.6 | 37.5 | 30.4 | 30.2 | 29.3 | 30 | 29.9667 |  | 28.2 | 28.7 | 26.8 | 28 | 27.9
Russia |  | GARI | GARI, Russian Federation | 59.43N | 62.33E | 131 | 5.00 (EKT) | 82-06 | 280490 | -34.8 |  | -43.8 | 37.4 | 31 | 31 | 29.4 | 30 | 30.4667 |  | 28.8 | 29.1 | 25.3 | 28 | 27.7333
Russia |  | GLAZOV | GLAZOV, Russian Federation | 58.13N | 52.58E | 170 | 4.00 (CAU) | 82-06 | 282140 | -35.9 |  | -45 | 36.9 | 31.1 | 31.1 | 28.7 | 30 | 30.3 |  | 27.7 | 29.4 | 25.7 | 28 | 27.6
Russia |  | GMO IM.E.K. FEDOROV | GMO IM.E.K. FEDOROV, Russian Federation | 77.72N | 104.30E | 15 | 7.00 (ASN) | 82-06 | 202920 | -42 |  | -48.4 | 23.4 | 5.8 | 13.9 | 12.9 | 11 | 10.8667 |  | 3.8 | 9.5 | 8.6 | 7 | 7.3
Russia |  | GORIN | GORIN, Russian Federation | 51.20N | 136.80E | 92 | 10.00 (ASV) | 82-05 | 314890 | -39.9 |  | -42.4 | 39.3 | 31.4 | 33.2 | 31.7 | 32 | 32.1 |  | 28.9 | 31 | 28.5 | 29 | 29.4667
Russia |  | GORJACINSK | GORJACINSK, Russian Federation | 52.98N | 108.28E | 487 | 8.00 (ASE) | 82-04 | 307310 | -30.4 |  | -40.5 | 34.8 | 23 | 27.2 | 26.3 | 26 | 25.5 |  | 19.8 | 24.1 | 23.1 | 22 | 22.3333
Russia |  | GOR'KIJ | GOR'KIJ, Russian Federation | 56.22N | 43.82E | 82 | 3.00 (RUS) | 82-94 | 275530 | -29.7 |  | -34.7 | 36.7 | 31 | 30.5 | 29.7 | 30 | 30.4 |  | 28.3 | 28.5 | 26.7 | 28 | 27.8333
Russia |  | GRIDINO | GRIDINO, Russian Federation | 65.90N | 34.77E | 12 | 3.00 (RUS) | 82-00 | 224220 | N/A |  | N/A | N/A | 24.6 | 27.6 | 22.4 | 25 | 24.8667 |  | 20.8 | 22.7 | 19.7 | 21 | 21.0667
Russia |  | GROSSEVICHI | GROSSEVICHI, Russian Federation | 47.97N | 139.53E | 3 | 10.00 (ASV) | 82-94 | 318230 | N/A |  | N/A | N/A | 16.7 | 20.6 | 24.3 | 21 | 20.5333 |  | 14.1 | 17.6 | 21.3 | 18 | 17.6667
Russia |  | GROZNYJ | GROZNYJ, Russian Federation | 43.35N | 45.68E | 163 | 3.00 (RUS) | 82-94 | 372350 | -19.1 |  | -25.7 | 41.4 | 33 | 36 | 34.4 | 34 | 34.4667 |  | 30.9 | 33.5 | 32.5 | 32 | 32.3
Russia |  | GUGA | GUGA, Russian Federation | 52.70N | 137.53E | 60 | 10.00 (ASV) | 82-94 | 314210 | -43.3 |  | -49.7 | 40.8 | 32.9 | 33.1 | 32 | 33 | 32.6667 |  | 30.3 | 31.3 | 28.3 | 30 | 29.9667
Russia |  | GVASJUGI | GVASJUGI, Russian Federation | 47.67N | 136.18E | 180 | 10.00 (ASV) | 82-06 | 318010 | -40.7 |  | -44.9 | 37 | 31.2 | 32.5 | 31.8 | 32 | 31.8333 |  | 28.8 | 30.7 | 28.6 | 29 | 29.3667
Russia |  | HABAROVSK | HABAROVSK, Russian Federation | 48.52N | 135.17E | 76 | 10.00 (ASV) | 82-06 | 317350 | -33.2 |  | -37.6 | 38.1 | 31.1 | 33.1 | 31.8 | 32 | 32 |  | 29.1 | 31 | 29.1 | 30 | 29.7333
Russia |  | HADAMA | HADAMA, Russian Federation | 53.95N | 98.82E | 705 | 8.00 (ASE) | 82-96 | 298920 | -39.6 |  | -47.5 | 35.1 | 29.5 | 30.1 | 28 | 29 | 29.2 |  | 26.2 | 27.7 | 24.9 | 26 | 26.2667
Russia |  | HAKASSKAJA | HAKASSKAJA, Russian Federation | 53.77N | 91.32E | 256 | 7.00 (ASN) | 96-06 | 298620 | -38.3 |  | -47.1 | 39.7 | 31.2 | 33.9 | 32.1 | 32 | 32.4 |  | 29.5 | 31 | 29.5 | 30 | 30
Russia |  | HANTY-MANSIJSK | HANTY-MANSIJSK, Russian Federation | 61.02N | 69.03E | 46 | 5.00 (EKT) | 82-06 | 239330 | -40.5 |  | -50.6 | 36.6 | 30.2 | 31 | 28.1 | 30 | 29.7667 |  | 27.6 | 28.7 | 24.7 | 27 | 27
Russia |  | HATANGA | HATANGA, Russian Federation | 71.98N | 102.47E | 33 | 7.00 (ASN) | 82-06 | 208910 | -49.6 |  | -57.8 | 34.6 | 26 | 29.1 | 24.1 | 26 | 26.4 |  | 21.9 | 25.7 | 21 | 23 | 22.8667
Russia |  | HILOK | HILOK, Russian Federation | 51.35N | 110.47E | 802 | 9.00 (YAK) | 82-06 | 308440 | -42 |  | -46.8 | 37.3 | 31.2 | 31.5 | 28.8 | 31 | 30.5 |  | 27.9 | 28.9 | 26.1 | 28 | 27.6333
Russia |  | HOLM | HOLM, Russian Federation | 57.15N | 31.18E | 71 | 3.00 (RUS) | 82-97 | 263780 | -31.8 |  | -43.4 | 35.5 | 28 | 29.2 | 28.1 | 28 | 28.4333 |  | 25.7 | 27.3 | 25.7 | 26 | 26.2333
Russia |  | HOLMSK | HOLMSK, Russian Federation | 47.05N | 142.05E | 44 | 10.00 (ASV) | 82-06 | 321280 | -17.2 |  | -22.8 | 31.3 | 21.4 | 24.8 | 25.7 | 24 | 23.9667 |  | 19.2 | 22.3 | 24 | 22 | 21.8333
Russia |  | HORINSK | HORINSK, Russian Federation | 52.17N | 109.78E | 666 | 8.00 (ASE) | 82-06 | 307390 | -40.6 |  | -48.5 | 37.6 | 31.6 | 32.4 | 29.8 | 31 | 31.2667 |  | 28.8 | 29.7 | 27.1 | 29 | 28.5333
Russia |  | HOSEDA-HARD | HOSEDA-HARD, Russian Federation | 67.08N | 59.38E | 84 | 3.00 (RUS) | 82-06 | 232190 | -45 |  | -51.3 | 36.9 | 26.7 | 31.7 | 23.5 | 27 | 27.3 |  | 23.6 | 27.7 | 21 | 24 | 24.1
Russia |  | HULARIN | HULARIN, Russian Federation | 51.42N | 135.08E | 269 | 10.00 (ASV) | 82-06 | 314840 | -38.5 |  | -46.2 | 37.4 | 32 | 32.6 | 31.5 | 32 | 32.0333 |  | 29.3 | 29.9 | 28.4 | 29 | 29.2
Russia |  | ICA | ICA, Russian Federation | 55.58N | 155.58E | 6 | 12.00 (KAM) | 82-05 | 324110 | -26.5 |  | -31 | 25 | 14.5 | 18.8 | 17.6 | 17 | 16.9667 |  | 12.2 | 15.7 | 15.9 | 15 | 14.6
Russia |  | IDRINSKOE | IDRINSKOE, Russian Federation | 54.37N | 92.13E | 282 | 7.00 (ASN) | 82-06 | 297660 | -38.5 |  | -47.4 | 38.7 | 31.5 | 32.1 | 30.8 | 31 | 31.4667 |  | 29 | 30.1 | 28.1 | 29 | 29.0667
Russia |  | IGARKA | IGARKA, Russian Federation | 67.47N | 86.57E | 31 | 7.00 (ASN) | 82-06 | 232740 | -49.1 |  | -58.9 | 35.3 | 28.4 | 28.6 | 25.8 | 28 | 27.6 |  | 25.4 | 26.1 | 22 | 25 | 24.5
Russia |  | IGNASINO | IGNASINO, Russian Federation | 53.47N | 122.40E | 295 | 9.00 (YAK) | 82-06 | 306860 | -44.2 |  | -49.3 | 39.4 | 31.4 | 33.6 | 31.8 | 32 | 32.2667 |  | 29.3 | 30.6 | 28.4 | 29 | 29.4333
Russia |  | IKEJ | IKEJ, Russian Federation | 54.18N | 100.08E | 527 | 8.00 (ASE) | 82-94 | 305070 | -41 |  | -48.5 | 35.9 | 29.2 | 29.7 | 26.7 | 29 | 28.5333 |  | 26.6 | 27.5 | 24.2 | 26 | 26.1
Russia |  | ILYINSKIY | ILYINSKIY, Russian Federation | 47.98N | 142.20E | 18 | 10.00 (ASV) | 82-06 | 321210 | -26.3 |  | -32.2 | 28.9 | 19.7 | 22.9 | 24 | 22 | 22.2 |  | 17.3 | 21 | 22.6 | 20 | 20.3
Russia |  | IM POLINY OSIPENKO | IM POLINY OSIPENKO, Russian Federation | 52.42N | 136.50E | 73 | 10.00 (ASV) | 82-06 | 314160 | -42.9 |  | -49.9 | 37.3 | 31.2 | 32.4 | 30.8 | 31 | 31.4667 |  | 28.9 | 30.4 | 27.9 | 29 | 29.0667
Russia |  | IM. M.V. POPOVA | IM. M.V. POPOVA, Russian Federation | 73.33N | 70.05E | 7 | 5.00 (EKT) | 82-06 | 206670 | -40.9 |  | -47.6 | 25.5 | 10.8 | 20.1 | 14.8 | 15 | 15.2333 |  | 6.3 | 15.5 | 11.5 | 11 | 11.1
Russia |  | IRBEJSKOE | IRBEJSKOE, Russian Federation | 55.63N | 95.47E | 252 | 7.00 (ASN) | 82-01 | 295870 | N/A |  | N/A | N/A | 28.4 | 31.1 | 29.1 | 30 | 29.5333 |  | 26.8 | 29.2 | 26.2 | 27 | 27.4
Russia |  | IRKUTSK | IRKUTSK, Russian Federation | 52.27N | 104.32E | 469 | 8.00 (ASE) | 82-06 | 307100 | -38.2 |  | -48.2 | 35.5 | 30.2 | 31 | 28.5 | 30 | 29.9 |  | 27.9 | 28.2 | 26.3 | 27 | 27.4667
Russia |  | ISIM | ISIM, Russian Federation | 56.10N | 69.43E | 83 | 5.00 (EKT) | 82-06 | 285730 | -37 |  | -48 | 37.3 | 31.9 | 31.8 | 30 | 31 | 31.2333 |  | 29.8 | 29.4 | 27 | 29 | 28.7333
Russia |  | ISIT | ISIT, Russian Federation | 60.82N | 125.32E | 118 | 9.00 (YAK) | 82-06 | 249510 | -49.4 |  | -56.5 | 37 | 29.1 | 31.7 | 29 | 30 | 29.9333 |  | 26.6 | 29.1 | 26 | 27 | 27.2333
Russia |  | IVDEL | IVDEL, Russian Federation | 60.68N | 60.45E | 95 | 5.00 (EKT) | 82-06 | 239210 | -40.1 |  | -49.2 | 38.2 | 30.7 | 31.5 | 28.4 | 30 | 30.2 |  | 28.4 | 29.6 | 25 | 28 | 27.6667
Russia |  | IZHEVSK | IZHEVSK, Russian Federation | 56.83N | 53.45E | 159 | 4.00 (CAU) | 82-06 | 284110 | -32.7 |  | -41.4 | 37.7 | 31.6 | 31.5 | 29.9 | 31 | 31 |  | 28.7 | 29.7 | 26.7 | 28 | 28.3667
Russia |  | JAKUTSK | JAKUTSK, Russian Federation | 62.02N | 129.72E | 101 | 9.00 (YAK) | 82-06 | 249590 | -51.1 |  | -58.3 | 37.8 | 30.7 | 33.2 | 29.9 | 31 | 31.2667 |  | 28.3 | 30.9 | 27.1 | 29 | 28.7667
Russia |  | JALTUROVOSK | JALTUROVOSK, Russian Federation | 56.68N | 66.35E | 60 | 5.00 (EKT) | 82-06 | 284650 | N/A |  | N/A | N/A | 32.1 | 32.5 | 29.1 | 31 | 31.2333 |  | 29.8 | 30.3 | 26.7 | 29 | 28.9333
Russia |  | JANAUL | JANAUL, Russian Federation | 56.27N | 54.90E | 99 | 5.00 (EKT) | 82-05 | 284190 | -37.1 |  | -47.5 | 40.1 | 32.5 | 32 | 31 | 32 | 31.8333 |  | 29.4 | 30.1 | 27.6 | 29 | 29.0333
Russia |  | JARCEVO | JARCEVO, Russian Federation | 60.25N | 90.23E | 58 | 7.00 (ASN) | 95-06 | 239870 | N/A |  | N/A | N/A | 30.6 | 32.2 | 29.2 | 31 | 30.6667 |  | 27.8 | 29.9 | 26.3 | 28 | 28
Russia |  | JARENSK | JARENSK, Russian Federation | 62.17N | 49.12E | 92 | 3.00 (RUS) | 83-99 | 227980 | -37.2 |  | -42.2 | 37.1 | 31.3 | 29.9 | 25.7 | 29 | 28.9667 |  | 27.6 | 26.7 | 23.4 | 26 | 25.9
Russia |  | JASKUL | JASKUL, Russian Federation | 46.18N | 45.35E | -7 | 3.00 (RUS) | 82-06 | 348660 | -22.1 |  | -35.7 | 44.1 | 37.9 | 38.9 | 38.2 | 38 | 38.3333 |  | 34.9 | 36.9 | 35.7 | 36 | 35.8333
Russia |  | JUBILEJNAJA | JUBILEJNAJA, Russian Federation | 70.77N | 136.22E | 24 | 10.00 (ASV) | 82-06 | 219310 | -48.6 |  | -54.5 | 36.9 | 26.1 | 30.1 | 27.9 | 28 | 28.0333 |  | 22 | 26.5 | 22.6 | 24 | 23.7
Russia |  | JUR`EVEC | JUR`EVEC, Russian Federation | 57.33N | 43.12E | 132 | 3.00 (RUS) | 82-06 | 273550 | -30.6 |  | -41.1 | 33.9 | 29.8 | 29.9 | 27.9 | 29 | 29.2 |  | 27.2 | 28 | 25.4 | 27 | 26.8667
Russia |  | JUZHNO-KURILSK | JUZHNO-KURILSK, Russian Federation | 44.02N | 145.87E | 49 | 11.00 (MAG) | 82-06 | 321650 | -13 |  | -19.2 | 30.3 | 17.4 | 21.1 | 24.2 | 21 | 20.9 |  | 14.9 | 19 | 21.4 | 18 | 18.4333
Russia |  | JUZHNO-SAHALINSK | JUZHNO-SAHALINSK, Russian Federation | 46.95N | 142.72E | 24 | 10.00 (ASV) | 82-06 | 321500 | -28.7 |  | -36.6 | 34.4 | 25.4 | 27.1 | 29 | 27 | 27.1667 |  | 22.5 | 25 | 26.3 | 25 | 24.6
Russia |  | KACUG | KACUG, Russian Federation | 53.97N | 105.90E | 533 | 8.00 (ASE) | 82-06 | 306220 | -43.2 |  | -52 | 36.2 | 30.5 | 31.7 | 29 | 30 | 30.4 |  | 27.7 | 29.2 | 26.5 | 28 | 27.8
Russia |  | KAJLASTUJ | KAJLASTUJ, Russian Federation | 49.83N | 118.38E | 550 | 9.00 (YAK) | 82-06 | 309780 | -37.1 |  | -45.2 | 38.7 | 31.2 | 32.6 | 31.3 | 32 | 31.7 |  | 29.3 | 29.8 | 29 | 29 | 29.3667
Russia |  | KALAC | KALAC, Russian Federation | 50.42N | 41.05E | 92 | 3.00 (RUS) | 82-06 | 342470 | -28.1 |  | -38.1 | 40.4 | 33.4 | 35.7 | 33.9 | 34 | 34.3333 |  | 30.9 | 32.4 | 31.3 | 32 | 31.5333
Russia |  | KALACINSK | KALACINSK, Russian Federation | 55.03N | 74.58E | 107 | 6.00 (ASR) | 82-06 | 286960 | -36.9 |  | -49.3 | 39.2 | 32.3 | 33 | 31.8 | 32 | 32.3667 |  | 30.1 | 30.3 | 28.5 | 30 | 29.6333
Russia |  | KALAKAN | KALAKAN, Russian Federation | 55.12N | 116.77E | 613 | 9.00 (YAK) | 82-06 | 304690 | -48.8 |  | -58 | 35.6 | 30.2 | 31.2 | 28.7 | 30 | 30.0333 |  | 27.7 | 28.7 | 26.1 | 28 | 27.5
Russia |  | KALEVALA | KALEVALA, Russian Federation | 65.22N | 31.17E | 120 | 3.00 (RUS) | 82-06 | 224080 | -35.5 |  | -46.9 | 32.2 | 27.2 | 27.5 | 25.5 | 27 | 26.7333 |  | 24.4 | 25.2 | 22.7 | 24 | 24.1
Russia |  | KALININGRAD | KALININGRAD, Russian Federation | 54.72N | 20.55E | 21 | 2.00 (EUE) | 82-06 | 267020 | -19.3 |  | -32.4 | 36.4 | 28.2 | 30.9 | 29.6 | 30 | 29.5667 |  | 25.1 | 28.1 | 26.9 | 27 | 26.7
Russia |  | KALUGA | KALUGA, Russian Federation | 54.57N | 36.40E | 201 | 3.00 (RUS) | 82-06 | 277030 | -28.7 |  | -37.2 | 34.7 | 29.2 | 30.8 | 28.6 | 30 | 29.5333 |  | 26.7 | 28 | 26.2 | 27 | 26.9667
Russia |  | KAMEN-NA-OBI | KAMEN-NA-OBI, Russian Federation | 53.82N | 81.27E | 129 | 6.00 (ASR) | 82-06 | 298220 | -40.6 |  | -51.5 | 38.4 | 32.2 | 32.6 | 32.2 | 32 | 32.3333 |  | 29.6 | 30.3 | 29.5 | 30 | 29.8
Russia |  | KAMENSKOE | KAMENSKOE, Russian Federation | 62.43N | 166.08E | 10 | 12.00 (KAM) | 82-05 | 257440 | -43.8 |  | -49.6 | 31.6 | 22.8 | 25.5 | 22.3 | 24 | 23.5333 |  | 20.8 | 23.1 | 19.9 | 21 | 21.2667
Russia |  | KAMYSIN | KAMYSIN, Russian Federation | 50.07N | 45.37E | 119 | 3.00 (RUS) | 82-06 | 343630 | -25.2 |  | -33.5 | 43.4 | 35.2 | 35.9 | 34.7 | 35 | 35.2667 |  | 32 | 33.5 | 32.1 | 33 | 32.5333
Russia |  | KAMYSLOV | KAMYSLOV, Russian Federation | 56.85N | 62.72E | 126 | 5.00 (EKT) | 82-06 | 284510 | -35.3 |  | -44.3 | 38.5 | 32 | 32.5 | 31 | 32 | 31.8333 |  | 30 | 30.2 | 27.7 | 29 | 29.3
Russia |  | KANDALAKSA | KANDALAKSA, Russian Federation | 67.15N | 32.35E | 25 | 3.00 (RUS) | 82-06 | 222170 | -32.3 |  | -42.3 | 31.8 | 25.4 | 26.5 | 24.5 | 25 | 25.4667 |  | 22.2 | 23.6 | 21.3 | 22 | 22.3667
Russia |  | KANIN NOS | KANIN NOS, Russian Federation | 68.65N | 43.30E | 49 | 3.00 (RUS) | 82-06 | 221650 | -22.5 |  | -30.7 | 29 | 20.9 | 22 | 18.6 | 21 | 20.5 |  | 18 | 17.9 | 16.1 | 17 | 17.3333
Russia |  | KANSK | KANSK, Russian Federation | 56.20N | 95.63E | 207 | 7.00 (ASN) | 82-06 | 295810 | -41.1 |  | -51 | 36.2 | 30 | 31.5 | 29.7 | 30 | 30.4 |  | 27.9 | 29.6 | 26.8 | 28 | 28.1
Russia |  | KARASUK | KARASUK, Russian Federation | 53.70N | 78.07E | 115 | 6.00 (ASR) | 82-06 | 298140 | -36.2 |  | -47.9 | 38.7 | 32.6 | 32.9 | 31.8 | 32 | 32.4333 |  | 30.3 | 30.5 | 29.1 | 30 | 29.9667
Russia |  | KARGASOK | KARGASOK, Russian Federation | 59.05N | 80.95E | 59 | 7.00 (ASN) | 82-06 | 291220 | -42 |  | -53.9 | 33.9 | 30.2 | 29.8 | 27.8 | 29 | 29.2667 |  | 27.6 | 28 | 25.4 | 27 | 27
Russia |  | KARGOPOL | KARGOPOL, Russian Federation | 61.50N | 38.93E | 126 | 3.00 (RUS) | 82-06 | 228450 | -33.9 |  | -44 | 35.2 | 29.8 | 29.5 | 26.7 | 29 | 28.6667 |  | 26.6 | 27.1 | 23.8 | 26 | 25.8333
Russia |  | KAZACHINSK | KAZACHINSK, Russian Federation | 56.32N | 107.62E | 362 | 8.00 (ASE) | 82-99 | 303370 | -45.1 |  | -54.8 | 35.9 | 30.4 | 31.8 | 28.9 | 30 | 30.3667 |  | 27.7 | 29.1 | 26.2 | 28 | 27.6667
Russia |  | KAZAN` | KAZAN`, Russian Federation | 55.60N | 49.28E | 116 | 4.00 (CAU) | 82-06 | 275950 | -30.4 |  | -38.2 | 36.6 | 31.9 | 32.2 | 30.3 | 31 | 31.4667 |  | 29 | 30 | 27.6 | 29 | 28.8667
Russia |  | KEDON | KEDON, Russian Federation | 64.00N | 158.92E | 683 | 11.00 (MAG) | 82-00 | 256210 | -50.1 |  | -54.8 | 33.7 | 26 | 27.1 | 24.2 | 26 | 25.7667 |  | 23.5 | 24.6 | 20.5 | 23 | 22.8667
Russia |  | KEM | KEM, Russian Federation | 64.95N | 34.65E | 8 | 3.00 (RUS) | 82-06 | 225220 | -30.1 |  | -43.4 | 32 | 27.1 | 26.7 | 25.1 | 26 | 26.3 |  | 23.4 | 23.2 | 21.8 | 23 | 22.8
Russia |  | KEMCHUG | KEMCHUG, Russian Federation | 56.10N | 91.67E | 332 | 7.00 (ASN) | 82-06 | 295620 | -38 |  | -50.1 | 34.8 | 29.8 | 30.8 | 28.4 | 30 | 29.6667 |  | 27.1 | 28.2 | 25.6 | 27 | 26.9667
Russia |  | KEMEROVO | KEMEROVO, Russian Federation | 55.23N | 86.12E | 260 | 7.00 (ASN) | 82-06 | 296420 | -35.5 |  | -46.5 | 35.5 | 30.3 | 30.8 | 30.2 | 30 | 30.4333 |  | 27.3 | 28.7 | 27.1 | 28 | 27.7
Russia |  | KESTENGA | KESTENGA, Russian Federation | 65.88N | 31.83E | 129 | 3.00 (RUS) | 82-90 | 224030 | -32.4 |  | -41.8 | 31.5 | 25.9 | 26.1 | 23.8 | 25 | 25.2667 |  | 23.4 | 24.4 | 21.5 | 23 | 23.1
Russia |  | KINGISEPP | KINGISEPP, Russian Federation | 59.37N | 28.60E | 19 | 3.00 (RUS) | 82-06 | 260590 | -26.3 |  | -38.2 | 35.6 | 29.1 | 29.8 | 27.8 | 29 | 28.9 |  | 26.5 | 27.5 | 25.8 | 27 | 26.6
Russia |  | KIRENSK | KIRENSK, Russian Federation | 57.77N | 108.07E | 259 | 8.00 (ASE) | 82-06 | 302300 | -48.1 |  | -54.7 | 36.8 | 31.1 | 32.6 | 29.5 | 31 | 31.0667 |  | 28.7 | 30.1 | 26.7 | 29 | 28.5
Russia |  | KIROV | KIROV, Russian Federation | 58.65N | 49.62E | 164 | 4.00 (CAU) | 82-94 | 271960 | -35.1 |  | -45 | 35.7 | 30.6 | 30.6 | 27.2 | 29 | 29.4667 |  | 27.7 | 28.4 | 24.9 | 27 | 27
Russia |  | KIROV | KIROV, Russian Federation | 58.60N | 49.63E | 158 | 4.00 (CAU) | 94-06 | 271990 | -31.8 |  | -42.1 | 34.8 | 30.1 | 31.2 | 29.6 | 30 | 30.3 |  | 28.1 | 29.9 | 26.1 | 28 | 28.0333
Russia |  | KIROVSKIJ | KIROVSKIJ, Russian Federation | 45.08N | 133.53E | 98 | 10.00 (ASV) | 82-06 | 318780 | -33.6 |  | -40.3 | 36.7 | 30.5 | 32.5 | 32.4 | 32 | 31.8 |  | 28.5 | 30.2 | 29.9 | 30 | 29.5333
Russia |  | KIRS | KIRS, Russian Federation | 59.37N | 52.22E | 167 | 4.00 (CAU) | 82-06 | 280090 | -38.6 |  | -50.1 | 34.6 | 30.7 | 31 | 28.5 | 30 | 30.0667 |  | 27.9 | 29.3 | 24.8 | 27 | 27.3333
Russia |  | KJAHTA | KJAHTA, Russian Federation | 50.37N | 106.45E | 797 | 8.00 (ASE) | 82-06 | 309250 | -32.2 |  | -38.4 | 39.5 | 31.4 | 32.4 | 30.5 | 31 | 31.4333 |  | 28.7 | 29.4 | 27.5 | 29 | 28.5333
Russia |  | KJUSJUR | KJUSJUR, Russian Federation | 70.68N | 127.40E | 33 | 9.00 (YAK) | 83-06 | 219210 | -52.8 |  | -60.9 | 34.5 | 28 | 30.1 | 25.6 | 28 | 27.9 |  | 24.1 | 27.3 | 21.8 | 24 | 24.4
Russia |  | KLJUCHI | KLJUCHI, Russian Federation | 56.32N | 160.83E | 29 | 12.00 (KAM) | 82-06 | 323890 | -35 |  | -42.6 | 31.9 | 26.5 | 27.3 | 25.3 | 26 | 26.3667 |  | 23.9 | 25.4 | 22.6 | 24 | 23.9667
Russia |  | KLJUCI | KLJUCI, Russian Federation | 52.25N | 79.13E | 143 | 6.00 (ASR) | 82-06 | 360210 | -35.3 |  | -43.7 | 40.7 | 34.3 | 33.7 | 35 | 34 | 34.3333 |  | 31.5 | 31.7 | 32 | 32 | 31.7333
Russia |  | KOCHKI | KOCHKI, Russian Federation | 54.30N | 80.50E | 164 | 6.00 (ASR) | 83-06 | 297240 | -37.2 |  | -48 | 38.5 | 31.7 | 32.1 | 30.9 | 32 | 31.5667 |  | 28.7 | 30 | 28.5 | 29 | 29.0667
Russia |  | KOCUBEJ | KOCUBEJ, Russian Federation | 44.40N | 46.55E | -21 | 3.00 (RUS) | 84-06 | 370850 | N/A |  | N/A | N/A | 35 | 36.9 | 36.3 | 36 | 36.0667 |  | 32.9 | 34.8 | 33.7 | 34 | 33.8
Russia |  | KOJNAS | KOJNAS, Russian Federation | 64.75N | 47.65E | 64 | 3.00 (RUS) | 82-06 | 225830 | -42 |  | -53.8 | 36.2 | 29.9 | 31.2 | 27 | 29 | 29.3667 |  | 27.6 | 28.6 | 23.6 | 27 | 26.6
Russia |  | KOLBA | KOLBA, Russian Federation | 55.08N | 93.37E | 477 | 7.00 (ASN) | 82-06 | 296750 | -41.1 |  | -52.7 | 36.1 | 29.3 | 29.9 | 28.9 | 29 | 29.3667 |  | 27 | 27.4 | 25.5 | 27 | 26.6333
Russia |  | KOLPASEVO | KOLPASEVO, Russian Federation | 58.32N | 82.95E | 75 | 7.00 (ASN) | 82-06 | 292310 | -41.9 |  | -53.6 | 36 | 30.3 | 30.4 | 28.5 | 30 | 29.7333 |  | 27.8 | 28.3 | 25.9 | 27 | 27.3333
Russia |  | KOLYVAN | KOLYVAN, Russian Federation | 55.30N | 82.75E | 137 | 6.00 (ASR) | 82-06 | 296310 | -37.3 |  | -49.5 | 38.7 | 30.7 | 31.6 | 30.1 | 31 | 30.8 |  | 28.1 | 29.1 | 27.4 | 28 | 28.2
Russia |  | KOMMUNAR | KOMMUNAR, Russian Federation | 54.33N | 89.28E | 847 | 7.00 (ASN) | 82-06 | 297590 | -31.9 |  | -42.7 | 33 | 26.6 | 27.9 | 26.8 | 27 | 27.1 |  | 24.7 | 25.2 | 23.8 | 25 | 24.5667
Russia |  | KORF | KORF, Russian Federation | 60.35N | 166.00E | 4 | 12.00 (KAM) | 82-06 | 259540 | -30.9 |  | -38.2 | 27.9 | 21 | 22.8 | 20.4 | 21 | 21.4 |  | 17.9 | 19.8 | 17.7 | 18 | 18.4667
Russia |  | KOTEL`NIKOVO | KOTEL`NIKOVO, Russian Federation | 47.63N | 43.15E | 49 | 3.00 (RUS) | 82-94 | 346550 | -22.3 |  | -31.1 | 42.6 | 34.8 | 37 | 34.8 | 36 | 35.5333 |  | 32.7 | 34.4 | 33 | 33 | 33.3667
Russia |  | KOTLAS | KOTLAS, Russian Federation | 61.23N | 46.72E | 56 | 3.00 (RUS) | 82-06 | 228870 | -37.2 |  | -47.6 | 37.1 | 30.4 | 30.8 | 27.8 | 30 | 29.6667 |  | 27.7 | 28.7 | 24.6 | 27 | 27
Russia |  | KOZ`MODEM`JANSK | KOZ`MODEM`JANSK, Russian Federation | 56.33N | 46.58E | 114 | 4.00 (CAU) | 82-06 | 274790 | -29.8 |  | -39.1 | 35.9 | 31.1 | 30.8 | 29 | 30 | 30.3 |  | 28.4 | 28.7 | 26 | 28 | 27.7
Russia |  | KRASNODAR | KRASNODAR, Russian Federation | 45.03N | 39.15E | 34 | 3.00 (RUS) | 82-06 | 349290 | -19.1 |  | -33.8 | 42.3 | 32.1 | 36.2 | 36.1 | 35 | 34.8 |  | 30.1 | 33.9 | 33.8 | 33 | 32.6
Russia |  | KRASNOJARSK | KRASNOJARSK, Russian Federation | 56.00N | 92.88E | 277 | 7.00 (ASN) | 82-94 | 295740 | -35.3 |  | -45.6 | 36.9 | 29.6 | 31.1 | 27.7 | 29 | 29.4667 |  | 27.7 | 29 | 25.5 | 27 | 27.4
Russia |  | KRASNOJARSK OPYTNOE | KRASNOJARSK OPYTNOE, Russian Federation | 56.03N | 92.75E | 276 | 7.00 (ASN) | 96-06 | 295700 | -37.5 |  | -48.3 | 37.4 | 30.7 | 31.7 | 30 | 31 | 30.8 |  | 28.3 | 29.5 | 27.2 | 28 | 28.3333
Russia |  | KRASNOOZERSK | KRASNOOZERSK, Russian Federation | 53.97N | 79.23E | 144 | 6.00 (ASR) | 83-06 | 298130 | -36.9 |  | -46.3 | 38.3 | 31.8 | 32.6 | 31.3 | 32 | 31.9 |  | 29.4 | 30 | 28.3 | 29 | 29.2333
Russia |  | KRASNOSCELE | KRASNOSCELE, Russian Federation | 67.35N | 37.05E | 156 | 3.00 (RUS) | 82-06 | 222350 | -37.9 |  | -47.7 | 30.2 | 26.1 | 26.9 | 25.2 | 26 | 26.0667 |  | 23.5 | 24.8 | 21.7 | 23 | 23.3333
Russia |  | KRASNOUFIMSK | KRASNOUFIMSK, Russian Federation | 56.65N | 57.78E | 207 | 5.00 (EKT) | 82-06 | 284340 | -39.5 |  | -47.6 | 37.2 | 32.2 | 31.7 | 30.3 | 31 | 31.4 |  | 29.3 | 29.7 | 27 | 29 | 28.6667
Russia |  | KRASNYE BAKI | KRASNYE BAKI, Russian Federation | 57.13N | 45.17E | 111 | 3.00 (RUS) | 90-06 | 273690 | -32.1 |  | -40.5 | 37.4 | 32.1 | 31.6 | 29.4 | 31 | 31.0333 |  | 28.9 | 29.4 | 26.2 | 28 | 28.1667
Russia |  | KRASNYJ CHIKOJ | KRASNYJ CHIKOJ, Russian Federation | 50.37N | 108.75E | 771 | 9.00 (YAK) | 82-06 | 309350 | -39.9 |  | -46.2 | 38 | 30.8 | 31.8 | 29.5 | 31 | 30.7 |  | 28 | 28.8 | 26.3 | 28 | 27.7
Russia |  | KRASNYJ JAR | KRASNYJ JAR, Russian Federation | 46.53N | 135.32E | 130 | 10.00 (ASV) | 82-06 | 318450 | -40.8 |  | -44.7 | 36.8 | 31.9 | 33.3 | 33.3 | 33 | 32.8333 |  | 29.9 | 31 | 30.2 | 30 | 30.3667
Russia |  | KRESCHENKA | KRESCHENKA, Russian Federation | 55.85N | 80.03E | 129 | 6.00 (ASR) | 82-06 | 295240 | -40.9 |  | -52.5 | 35.7 | 30.2 | 30.9 | 28.6 | 30 | 29.9 |  | 28.1 | 28.5 | 26 | 28 | 27.5333
Russia |  | KUDYMKAR | KUDYMKAR, Russian Federation | 58.98N | 54.65E | 187 | 5.00 (EKT) | 82-06 | 281160 | -36.3 |  | -47.2 | 34.5 | 30.5 | 30.6 | 28.8 | 30 | 29.9667 |  | 27.5 | 29 | 25.4 | 27 | 27.3
Russia |  | KUPINO | KUPINO, Russian Federation | 54.37N | 77.28E | 115 | 6.00 (ASR) | 82-06 | 297060 | -36.1 |  | -49.3 | 40.8 | 32.5 | 33.3 | 32.2 | 33 | 32.6667 |  | 30.2 | 30.4 | 29.1 | 30 | 29.9
Russia |  | KUR | KUR, Russian Federation | 49.93N | 134.63E | 283 | 10.00 (ASV) | 82-06 | 316320 | -40.5 |  | -46.5 | 37.1 | 31.7 | 32.3 | 31.1 | 32 | 31.7 |  | 28.5 | 29.8 | 28.2 | 29 | 28.8333
Russia |  | KURGAN | KURGAN, Russian Federation | 55.47N | 65.40E | 79 | 5.00 (EKT) | 82-06 | 286610 | -35.1 |  | -45.2 | 38.6 | 33.2 | 33.3 | 31.8 | 33 | 32.7667 |  | 30.8 | 30.8 | 28.9 | 30 | 30.1667
Russia |  | KURSK | KURSK, Russian Federation | 51.77N | 36.17E | 247 | 3.00 (RUS) | 82-06 | 340090 | -25.1 |  | -36.7 | 36.7 | 30 | 31.9 | 30.9 | 31 | 30.9333 |  | 27.9 | 29.2 | 28.1 | 28 | 28.4
Russia |  | KYRA | KYRA, Russian Federation | 49.57N | 111.97E | 908 | 9.00 (YAK) | 82-06 | 309490 | -35 |  | -40.9 | 37.7 | 30.2 | 31.7 | 29.8 | 31 | 30.5667 |  | 27.3 | 28.3 | 26.6 | 27 | 27.4
Russia |  | KYSTOVKA | KYSTOVKA, Russian Federation | 56.60N | 76.57E | 116 | 6.00 (ASR) | 82-06 | 294050 | -40.6 |  | -52.1 | 37 | 30.8 | 30.7 | 29.3 | 30 | 30.2667 |  | 28.7 | 28.9 | 26.5 | 28 | 28.0333
Russia |  | KYZYL | KYZYL, Russian Federation | 51.72N | 94.50E | 628 | 7.00 (ASN) | 82-06 | 360960 | -40.8 |  | -46.3 | 41.1 | 33.3 | 35.6 | 32.2 | 34 | 33.7 |  | 29.9 | 32.1 | 28.8 | 30 | 30.2667
Russia |  | LAKE TAJMYR | LAKE TAJMYR, Russian Federation | 74.50N | 102.50E | 11 | 7.00 (ASN) | 82-94 | 205940 | N/A |  | N/A | N/A | 10.6 | 16.9 | 14.9 | 14 | 14.1333 |  | 7.6 | 14.4 | 12.5 | 12 | 11.5
Russia |  | LENSK | LENSK, Russian Federation | 60.72N | 114.88E | 234 | 9.00 (YAK) | 82-06 | 249230 | -49.1 |  | -59.3 | 38 | 30.6 | 32.7 | 28.7 | 31 | 30.6667 |  | 28.3 | 30.1 | 25.6 | 28 | 28
Russia |  | LEUSI | LEUSI, Russian Federation | 59.62N | 65.72E | 72 | 5.00 (EKT) | 82-06 | 280640 | -38.6 |  | -49.5 | 36.6 | 31 | 32.1 | 29 | 31 | 30.7 |  | 28.6 | 29.5 | 25.2 | 28 | 27.7667
Russia |  | LJUBAN | LJUBAN, Russian Federation | 59.35N | 31.23E | 39 | 3.00 (RUS) | 82-95 | 260780 | -28.9 |  | -42.9 | 33.9 | 28.4 | 29.3 | 27.9 | 29 | 28.5333 |  | 25.9 | 27.1 | 25.8 | 26 | 26.2667
Russia |  | LOKSAK | LOKSAK, Russian Federation | 54.73N | 130.45E | 464 | 9.00 (YAK) | 82-03 | 312630 | -47.1 |  | -52.4 | 34.3 | 29.9 | 31.4 | 28.7 | 30 | 30 |  | 27.8 | 29.2 | 26.3 | 28 | 27.7667
Russia |  | LOSINOBORSKOE | LOSINOBORSKOE, Russian Federation | 58.43N | 89.37E | 137 | 7.00 (ASN) | 84-06 | 292530 | -46.1 |  | -56 | 34.7 | 30 | 30.7 | 27.8 | 30 | 29.5 |  | 27.3 | 28.6 | 25.6 | 27 | 27.1667
Russia |  | LOVOZERO | LOVOZERO, Russian Federation | 68.00N | 35.03E | 162 | 3.00 (RUS) | 82-06 | 221270 | -37.2 |  | -47.6 | 31.5 | 25.9 | 26.4 | 25 | 26 | 25.7667 |  | 22.8 | 24.2 | 21.7 | 23 | 22.9
Russia |  | LUKOJANOV | LUKOJANOV, Russian Federation | 55.03N | 44.50E | 220 | 3.00 (RUS) | 82-06 | 276650 | -29.3 |  | -39.2 | 38.2 | 31.9 | 30.6 | 29.9 | 31 | 30.8 |  | 28.3 | 28.7 | 26.6 | 28 | 27.8667
Russia |  | MAGADAN | MAGADAN, Russian Federation | 59.55N | 150.78E | 116 | 11.00 (MAG) | 82-06 | 259130 | -36 |  | -54.5 | 32.6 | 23 | 25.1 | 23.1 | 24 | 23.7333 |  | 18.9 | 22 | 20 | 20 | 20.3
Russia |  | MAGDAGACI | MAGDAGACI, Russian Federation | 53.47N | 125.82E | 370 | 9.00 (YAK) | 82-06 | 312950 | -38.3 |  | -46.8 | 37.2 | 30.4 | 32.2 | 30.1 | 31 | 30.9 |  | 28.4 | 29.9 | 27.5 | 29 | 28.6
Russia |  | MAGNITOGORSK | MAGNITOGORSK, Russian Federation | 53.35N | 59.08E | 382 | 5.00 (EKT) | 82-06 | 288380 | -32.1 |  | -39.7 | 41 | 32.9 | 32.2 | 31.2 | 32 | 32.1 |  | 29.9 | 29.9 | 28.3 | 29 | 29.3667
Russia |  | MAHACKALA | MAHACKALA, Russian Federation | 43.02N | 47.48E | 32 | 3.00 (RUS) | 82-06 | 374720 | -13.4 |  | -22.3 | 40.1 | 31.2 | 33.2 | 33.6 | 33 | 32.6667 |  | 28.9 | 31.3 | 31.1 | 30 | 30.4333
Russia |  | MAJSK | MAJSK, Russian Federation | 57.78N | 77.28E | 100 | 7.00 (ASN) | 82-06 | 292090 | -44 |  | -56 | 35.7 | 30.4 | 31.4 | 27.7 | 30 | 29.8333 |  | 28.6 | 29.3 | 25.3 | 28 | 27.7333
Russia |  | MAKUSINO | MAKUSINO, Russian Federation | 55.25N | 67.30E | 143 | 5.00 (EKT) | 85-06 | 286660 | -34.3 |  | -42.6 | 38.4 | 32.8 | 33.4 | 31.7 | 33 | 32.6333 |  | 30.7 | 31 | 29.3 | 30 | 30.3333
Russia |  | MALYE KARMAKULY | MALYE KARMAKULY, Russian Federation | 72.37N | 52.70E | 15 | 3.00 (RUS) | 82-06 | 207440 | -29.2 |  | -35.6 | 27.5 | 15.6 | 20.2 | 17 | 18 | 17.6 |  | 12.3 | 17.1 | 14.1 | 15 | 14.5
Russia |  | MAMA | MAMA, Russian Federation | 58.32N | 112.87E | 224 | 8.00 (ASE) | 82-06 | 301570 | -44.1 |  | -52.2 | 37.9 | 31.7 | 33.3 | 30.2 | 32 | 31.7333 |  | 29.1 | 31 | 27.1 | 29 | 29.0667
Russia |  | MARESALE | MARESALE, Russian Federation | 69.72N | 66.80E | 25 | 5.00 (EKT) | 82-06 | 230320 | -40.4 |  | -48.5 | 29.9 | 18.9 | 24.2 | 18.3 | 20 | 20.4667 |  | 14.5 | 21.2 | 15.6 | 17 | 17.1
Russia |  | MARIINSK | MARIINSK, Russian Federation | 56.22N | 87.75E | 140 | 7.00 (ASN) | 82-06 | 295510 | -40 |  | -50.6 | 36 | 31 | 31.5 | 29.9 | 31 | 30.8 |  | 28 | 29.3 | 27 | 28 | 28.1
Russia |  | MARKOVO | MARKOVO, Russian Federation | 64.68N | 170.42E | 26 | 12.00 (KAM) | 82-06 | 255510 | -48.7 |  | -55.4 | 32.6 | 26.4 | 28.6 | 24.7 | 27 | 26.5667 |  | 23.6 | 26 | 21.6 | 24 | 23.7333
Russia |  | MASLJANINO | MASLJANINO, Russian Federation | 54.33N | 84.22E | 198 | 6.00 (ASR) | 82-06 | 297360 | -40.5 |  | -50.8 | 35.2 | 30.5 | 31.2 | 30.9 | 31 | 30.8667 |  | 28.3 | 29.2 | 27.6 | 28 | 28.3667
Russia |  | MATUA | MATUA, Russian Federation | 48.07N | 153.22E | 58 | 11.00 (MAG) | 82-95 | 322070 | -12.8 |  | -17.8 | 29.2 | 18 | 23 | 20.6 | 21 | 20.5333 |  | 14.2 | 18.7 | 18.4 | 17 | 17.1
Russia |  | MEDVEZEGORSK | MEDVEZEGORSK, Russian Federation | 62.92N | 34.43E | 81 | 3.00 (RUS) | 82-06 | 227210 | -32.4 |  | -43.8 | 33.8 | 28.6 | 28.3 | 26.3 | 28 | 27.7333 |  | 25.6 | 26.3 | 23.5 | 25 | 25.1333
Russia |  | MELEUZ | MELEUZ, Russian Federation | 52.95N | 55.97E | 179 | 5.00 (EKT) | 82-05 | 289250 | -37.2 |  | -47 | 39.9 | 34.5 | 33.5 | 33.7 | 34 | 33.9 |  | 31.4 | 31.2 | 30.7 | 31 | 31.1
Russia |  | MEZEN | MEZEN, Russian Federation | 65.87N | 44.22E | 19 | 3.00 (RUS) | 82-00 | 224710 | -35.5 |  | -46.6 | 32.9 | 28.1 | 29 | 24.5 | 27 | 27.2 |  | 25.7 | 25.5 | 22.1 | 24 | 24.4333
Russia |  | MINERALNYE VODY | MINERALNYE VODY, Russian Federation | 44.23N | 43.07E | 316 | 3.00 (RUS) | 82-06 | 370540 | -21 |  | -31.7 | 42.2 | 32.5 | 35.9 | 35.9 | 35 | 34.7667 |  | 30 | 33.3 | 33.1 | 32 | 32.1333
Russia |  | MOGOCA | MOGOCA, Russian Federation | 53.75N | 119.73E | 625 | 9.00 (YAK) | 82-06 | 306730 | -43.9 |  | -51.6 | 35.7 | 29.4 | 30.7 | 29.1 | 30 | 29.7333 |  | 26.9 | 28.4 | 26.2 | 27 | 27.1667
Russia |  | MONDY | MONDY, Russian Federation | 51.68N | 100.98E | 1304 | 8.00 (ASE) | 82-06 | 308020 | -35.8 |  | -43.9 | 31.6 | 26.8 | 27.1 | 25.6 | 27 | 26.5 |  | 24.3 | 25 | 23.2 | 24 | 24.1667
Russia |  | MOROZOVSK | MOROZOVSK, Russian Federation | 48.35N | 41.87E | 90 | 3.00 (RUS) | 82-06 | 345450 | -24.8 |  | -34.7 | 42.5 | 34.7 | 37.1 | 36.1 | 36 | 35.9667 |  | 32.3 | 34.7 | 33.3 | 33 | 33.4333
Russia |  | MOSKVA | MOSKVA, Russian Federation | 55.83N | 37.62E | 156 | 3.00 (RUS) | 82-06 | 276120 | -25.1 |  | -32.5 | 35.6 | 30.2 | 30.9 | 28.3 | 30 | 29.8 |  | 27.9 | 28.8 | 26.3 | 28 | 27.6667
Russia |  | MOZDOK | MOZDOK, Russian Federation | 43.73N | 44.67E | 136 | 3.00 (RUS) | 85-01 | 371450 | -18.7 |  | -30.7 | 41.9 | 34.5 | 37.3 | 36.3 | 36 | 36.0333 |  | 32.3 | 35.4 | 34 | 34 | 33.9
Russia |  | MURMANSK | MURMANSK, Russian Federation | 68.97N | 33.05E | 51 | 3.00 (RUS) | 82-06 | 221130 | -31.7 |  | -47.6 | 34.5 | 26.5 | 27.7 | 25.8 | 27 | 26.6667 |  | 22.6 | 24.8 | 22.2 | 23 | 23.2
Russia |  | MUZI | MUZI, Russian Federation | 65.38N | 64.72E | 19 | 5.00 (EKT) | 82-06 | 234260 | -44 |  | -51.7 | 34.5 | 26.6 | 29.6 | 24.7 | 27 | 26.9667 |  | 23.6 | 26.9 | 21.7 | 24 | 24.0667
Russia |  | MYS SHALAUROVA | MYS SHALAUROVA, Russian Federation | 73.18N | 143.23E | 22 | 10.00 (ASV) | 82-00 | 216470 | -42.9 |  | -49.1 | 26.8 | 10.5 | 13.3 | 14.5 | 13 | 12.7667 |  | 7.4 | 10.3 | 10.5 | 9 | 9.4
Russia |  | MYS SHMIDTA | MYS SHMIDTA, Russian Federation | 68.90N | 179.37W | 4 | 12.00 (KAM) | 82-06 | 251730 | -40.2 |  | -45 | 32.5 | 17.3 | 21.8 | 17.2 | 19 | 18.7667 |  | 13.2 | 16.9 | 12.4 | 14 | 14.1667
Russia |  | MYS UELEN | MYS UELEN, Russian Federation | 66.17N | 169.83W | 3 | 12.00 (KAM) | 82-06 | 253990 | -37 |  | -44.6 | 22.2 | 12.7 | 17.8 | 15.6 | 15 | 15.3667 |  | 10 | 14.7 | 12.9 | 13 | 12.5333
Russia |  | MYS ZELANIJA | MYS ZELANIJA, Russian Federation | 76.85N | 68.55E | 10 | 5.00 (EKT) | 82-96 | 203530 | -34.4 |  | -38.7 | 19.4 | 7.9 | 12.9 | 11.7 | 11 | 10.8333 |  | 5.3 | 9.5 | 7.9 | 8 | 7.5667
Russia |  | NAGORNYJ | NAGORNYJ, Russian Federation | 55.97N | 124.88E | 861 | 9.00 (YAK) | 82-06 | 304930 | -44.8 |  | -50 | 35.7 | 27 | 28.6 | 26 | 27 | 27.2 |  | 25 | 26.1 | 23.5 | 25 | 24.8667
Russia |  | NAJAHAN | NAJAHAN, Russian Federation | 61.95N | 158.97E | 23 | 11.00 (MAG) | 82-93 | 258210 | -33.3 |  | -38.2 | 26.8 | 20.7 | 22.7 | 20.3 | 21 | 21.2333 |  | 18.1 | 19.9 | 18 | 19 | 18.6667
Russia |  | NAPAS | NAPAS, Russian Federation | 59.85N | 81.95E | 76 | 7.00 (ASN) | 82-06 | 290230 | -43.6 |  | -54.7 | 34.4 | 29.8 | 30.8 | 28.4 | 30 | 29.6667 |  | 27.6 | 28.7 | 25.6 | 27 | 27.3
Russia |  | NARJAN-MAR | NARJAN-MAR, Russian Federation | 67.63N | 53.03E | 12 | 3.00 (RUS) | 82-06 | 232050 | -40 |  | -49.5 | 35.2 | 27.3 | 30.1 | 24.3 | 27 | 27.2333 |  | 24.5 | 27.8 | 21.6 | 25 | 24.6333
Russia |  | NAZYVOEVSK | NAZYVOEVSK, Russian Federation | 55.57N | 71.37E | 129 | 6.00 (ASR) | 82-06 | 285880 | -36.5 |  | -44.4 | 38.4 | 32.1 | 32.4 | 29.1 | 31 | 31.2 |  | 29.6 | 29.5 | 27.1 | 29 | 28.7333
Russia |  | NELKAN | NELKAN, Russian Federation | 57.67N | 136.15E | 318 | 10.00 (ASV) | 83-98 | 311520 | N/A |  | N/A | N/A | 30.9 | 32 | 28 | 30 | 30.3 |  | 28.8 | 29.9 | 25.9 | 28 | 28.2
Russia |  | NERCHINSKIJ ZAVOD | NERCHINSKIJ ZAVOD, Russian Federation | 51.32N | 119.62E | 619 | 9.00 (YAK) | 82-06 | 308790 | -37.7 |  | -45.2 | 36.7 | 29.5 | 31.4 | 29 | 30 | 29.9667 |  | 27.4 | 28.5 | 26.3 | 27 | 27.4
Russia |  | NIKOL`SK | NIKOL`SK, Russian Federation | 59.53N | 45.47E | 136 | 3.00 (RUS) | 82-06 | 270660 | -35.5 |  | -47.1 | 35.2 | 30.7 | 30.6 | 28.2 | 30 | 29.8333 |  | 28 | 28.6 | 25.2 | 27 | 27.2667
Russia |  | NIKOLAEVSK-NA-AMURE | NIKOLAEVSK-NA-AMURE, Russian Federation | 53.15N | 140.70E | 68 | 10.00 (ASV) | 82-06 | 313690 | -35.4 |  | -42 | 34.9 | 27.5 | 28.2 | 28.2 | 28 | 27.9667 |  | 24.1 | 25.8 | 25.8 | 25 | 25.2333
Russia |  | NIKOLAEVSKOE | NIKOLAEVSKOE, Russian Federation | 58.57N | 29.80E | 91 | 3.00 (RUS) | 82-06 | 261670 | -26.8 |  | -37.9 | 34.4 | 28.5 | 29.7 | 27.6 | 29 | 28.6 |  | 26.1 | 27.2 | 25.4 | 26 | 26.2333
Russia |  | NIKOLO-POLOMA | NIKOLO-POLOMA, Russian Federation | 58.35N | 43.38E | 144 | 3.00 (RUS) | 90-06 | 272520 | -32.9 |  | -41.1 | 36 | 30.7 | 30.6 | 27.9 | 30 | 29.7333 |  | 27.8 | 28.5 | 24.9 | 27 | 27.0667
Russia |  | NIKOLSKOE | NIKOLSKOE, Russian Federation | 55.20N | 165.98E | 18 | 12.00 (KAM) | 82-06 | 326180 | -12.4 |  | -17.7 | 23.1 | 11.8 | 16 | 16.2 | 15 | 14.6667 |  | 9.9 | 13.7 | 14.6 | 13 | 12.7333
Russia |  | NIZHNEANGARSK | NIZHNEANGARSK, Russian Federation | 55.78N | 109.55E | 487 | 8.00 (ASE) | 82-06 | 304330 | -33.4 |  | -42.5 | 34.6 | 26.7 | 29.8 | 27.2 | 28 | 27.9 |  | 23.9 | 26.6 | 24.6 | 25 | 25.0333
Russia |  | NIZHNEUDINSK | NIZHNEUDINSK, Russian Federation | 54.88N | 99.03E | 411 | 8.00 (ASE) | 82-06 | 296980 | -39.7 |  | -49.7 | 37.9 | 30.4 | 31.9 | 29.5 | 31 | 30.6 |  | 27.9 | 29.1 | 26.6 | 28 | 27.8667
Russia |  | NIZHNYJ TAGIL | NIZHNYJ TAGIL, Russian Federation | 57.88N | 60.07E | 258 | 5.00 (EKT) | 82-06 | 282400 | -35 |  | -46.2 | 36.5 | 30.8 | 30.6 | 28.6 | 30 | 30 |  | 28.5 | 28.5 | 25.7 | 28 | 27.5667
Russia |  | NIZNIJ NOVGOROD | NIZNIJ NOVGOROD, Russian Federation | 56.27N | 44.00E | 157 | 3.00 (RUS) | 94-06 | 274590 | -30 |  | -37.6 | 36.7 | 31.8 | 31.6 | 29.9 | 31 | 31.1 |  | 29 | 29.8 | 26.8 | 29 | 28.5333
Russia |  | NJAKSIMVOL | NJAKSIMVOL, Russian Federation | 62.43N | 60.87E | 51 | 5.00 (EKT) | 82-06 | 237240 | -42.4 |  | -53.3 | 36.2 | 30.4 | 32.1 | 27.8 | 30 | 30.1 |  | 27.7 | 30 | 24.3 | 27 | 27.3333
Russia |  | NJANDOMA | NJANDOMA, Russian Federation | 61.67N | 40.18E | 233 | 3.00 (RUS) | 82-06 | 228540 | -31.6 |  | -41.6 | 34.1 | 29.1 | 29.1 | 26.1 | 28 | 28.1 |  | 25.9 | 26.6 | 23.4 | 25 | 25.3
Russia |  | NJURBA | NJURBA, Russian Federation | 63.28N | 118.33E | 119 | 9.00 (YAK) | 82-06 | 246390 | -53.2 |  | -62.8 | 37.5 | 30.3 | 32.5 | 29.3 | 31 | 30.7 |  | 27.9 | 30.3 | 26.3 | 28 | 28.1667
Russia |  | NOGLIKI | NOGLIKI, Russian Federation | 51.92N | 143.13E | 34 | 10.00 (ASV) | 82-06 | 320530 | -33.7 |  | -42.2 | 34.5 | 27.2 | 28.5 | 27.9 | 28 | 27.8667 |  | 23.7 | 25.3 | 25.2 | 25 | 24.7333
Russia |  | NOLINSK | NOLINSK, Russian Federation | 57.55N | 49.95E | 136 | 4.00 (CAU) | 82-06 | 273930 | -33.1 |  | -43 | 36.2 | 30.9 | 31.4 | 29.1 | 30 | 30.4667 |  | 28.2 | 29.3 | 26.1 | 28 | 27.8667
Russia |  | NORSK | NORSK, Russian Federation | 52.35N | 129.92E | 208 | 9.00 (YAK) | 82-06 | 313880 | -44.5 |  | -50.9 | 34.3 | 30.1 | 30.9 | 29.1 | 30 | 30.0333 |  | 28.4 | 29.5 | 27.1 | 28 | 28.3333
Russia |  | NOVOKUZNETSK | NOVOKUZNETSK, Russian Federation | 53.82N | 86.88E | 308 | 7.00 (ASN) | 82-06 | 298460 | -34 |  | -46.5 | 36.9 | 30.1 | 31.4 | 31.1 | 31 | 30.8667 |  | 28 | 29.1 | 27.6 | 28 | 28.2333
Russia |  | NOVOSELENGINSK | NOVOSELENGINSK, Russian Federation | 51.10N | 106.65E | 556 | 8.00 (ASE) | 82-06 | 308290 | -37 |  | -43.2 | 40.3 | 33.1 | 33.4 | 30.7 | 32 | 32.4 |  | 30 | 30.3 | 28.2 | 30 | 29.5
Russia |  | NOVOSIBIRSK | NOVOSIBIRSK, Russian Federation | 55.08N | 82.90E | 176 | 6.00 (ASR) | 82-06 | 296340 | -36.3 |  | -49.9 | 37.9 | 30.9 | 31.2 | 30.8 | 31 | 30.9667 |  | 28.6 | 29.1 | 27.4 | 28 | 28.3667
Russia |  | NOZOVKA | NOZOVKA, Russian Federation | 57.08N | 54.75E | 130 | 5.00 (EKT) | 82-06 | 283190 | -33.3 |  | -43 | 35.7 | 31 | 31.6 | 30.4 | 31 | 31 |  | 28.4 | 29.9 | 26.8 | 28 | 28.3667
Russia |  | OBJACEVO | OBJACEVO, Russian Federation | 60.37N | 49.65E | 152 | 3.00 (RUS) | 84-06 | 229960 | N/A |  | N/A | N/A | 31 | 31.1 | 26.6 | 30 | 29.5667 |  | 27.9 | 29.1 | 23.5 | 27 | 26.8333
Russia |  | OBLUCE | OBLUCE, Russian Federation | 49.00N | 131.08E | 257 | 9.00 (YAK) | 83-06 | 317020 | -38.4 |  | -44.2 | 39.3 | 30.7 | 32.1 | 30.2 | 31 | 31 |  | 28 | 29.4 | 28 | 28 | 28.4667
Russia |  | ODESSKOE | ODESSKOE, Russian Federation | 54.20N | 72.97E | 125 | 6.00 (ASR) | 82-06 | 287970 | -35.8 |  | -45.4 | 38.2 | 33.3 | 33.7 | 32.4 | 33 | 33.1333 |  | 31.2 | 30.5 | 29.1 | 30 | 30.2667
Russia |  | OHANSK | OHANSK, Russian Federation | 57.72N | 55.38E | 164 | 5.00 (EKT) | 82-06 | 283210 | -34.5 |  | -43.5 | 38.7 | 30.9 | 31.6 | 29.5 | 31 | 30.6667 |  | 28.7 | 29.7 | 26.3 | 28 | 28.2333
Russia |  | OHOTSK | OHOTSK, Russian Federation | 59.37N | 143.20E | 6 | 10.00 (ASV) | 82-06 | 310880 | -33.5 |  | -37.9 | 30.1 | 18.7 | 21 | 23.4 | 21 | 21.0333 |  | 15.2 | 18.7 | 19.8 | 18 | 17.9
Russia |  | OKTJABRSKOE | OKTJABRSKOE, Russian Federation | 62.45N | 66.05E | 72 | 5.00 (EKT) | 82-06 | 237340 | -40.2 |  | -50.5 | 34.5 | 29.5 | 30.2 | 26.7 | 29 | 28.8 |  | 26.9 | 28 | 23.7 | 26 | 26.2
Russia |  | OLEKMINSK | OLEKMINSK, Russian Federation | 60.40N | 120.42E | 226 | 9.00 (YAK) | 82-06 | 249440 | -49.3 |  | -57.9 | 37.3 | 30.4 | 33 | 30.1 | 31 | 31.1667 |  | 28 | 30.7 | 26.9 | 29 | 28.5333
Russia |  | OLENEK | OLENEK, Russian Federation | 68.50N | 112.43E | 220 | 9.00 (YAK) | 82-06 | 241250 | -53.3 |  | -63.6 | 35.9 | 29.4 | 30.7 | 26.1 | 29 | 28.7333 |  | 25.3 | 28.6 | 23.2 | 26 | 25.7
Russia |  | OLOVJANNAJA | OLOVJANNAJA, Russian Federation | 50.95N | 115.58E | 640 | 9.00 (YAK) | 82-06 | 309610 | -36.9 |  | -44.6 | 38.4 | 30.6 | 33.8 | 31.4 | 32 | 31.9333 |  | 28.1 | 30.1 | 28 | 29 | 28.7333
Russia |  | OMSK | OMSK, Russian Federation | 55.02N | 73.38E | 122 | 6.00 (ASR) | 82-06 | 286980 | -34.8 |  | -44.6 | 39.5 | 32.9 | 33.4 | 32.3 | 33 | 32.8667 |  | 30.7 | 30.8 | 28.5 | 30 | 30
Russia |  | ONEGA | ONEGA, Russian Federation | 63.90N | 38.12E | 13 | 3.00 (RUS) | 82-06 | 226410 | -33 |  | -46.4 | 33.5 | 29.2 | 29.5 | 26.9 | 29 | 28.5333 |  | 26.4 | 27 | 23.8 | 26 | 25.7333
Russia |  | ONGUDAJ | ONGUDAJ, Russian Federation | 50.73N | 86.15E | 832 | 6.00 (ASR) | 82-94 | 362310 | -34.6 |  | -42.5 | 45 | 29.8 | 31.6 | 29.2 | 30 | 30.2 |  | 26.9 | 28.1 | 26.6 | 27 | 27.2
Russia |  | OPARINO | OPARINO, Russian Federation | 59.85N | 48.28E | 183 | 4.00 (CAU) | 82-06 | 270830 | -36.2 |  | -48.3 | 35 | 30.2 | 30.3 | 27.1 | 29 | 29.2 |  | 27.3 | 28.2 | 24.2 | 27 | 26.5667
Russia |  | ORDYNSKOE | ORDYNSKOE, Russian Federation | 54.37N | 81.95E | 134 | 6.00 (ASR) | 82-06 | 297260 | -39.4 |  | -49.5 | 39 | 31.3 | 32.4 | 31.6 | 32 | 31.7667 |  | 28.7 | 30 | 28.7 | 29 | 29.1333
Russia |  | OREL | OREL, Russian Federation | 52.93N | 36.00E | 203 | 3.00 (RUS) | 82-06 | 279060 | -26.6 |  | -36.1 | 36 | 30.2 | 31.1 | 29.6 | 30 | 30.3 |  | 27.8 | 28.9 | 27.5 | 28 | 28.0667
Russia |  | ORENBURG | ORENBURG, Russian Federation | 51.68N | 55.10E | 117 | 5.00 (EKT) | 82-06 | 351210 | -32.4 |  | -42.3 | 42.4 | 36.2 | 36 | 35.4 | 36 | 35.8667 |  | 33.4 | 33.6 | 32.2 | 33 | 33.0667
Russia |  | OSTASKOV | OSTASKOV, Russian Federation | 57.13N | 33.12E | 218 | 3.00 (RUS) | 90-06 | 263890 | -30.3 |  | -38.4 | 34.9 | 29.2 | 30.9 | 27.7 | 29 | 29.2667 |  | 26.9 | 28.1 | 25.4 | 27 | 26.8
Russia |  | OSTROV CHETYREHSTOL | OSTROV CHETYREHSTOL, Russian Federation | 70.63N | 162.48E | 41 | 11.00 (MAG) | 82-95 | 219650 | -41.1 |  | -44.3 | 24.6 | 10.6 | 15.5 | 12.7 | 13 | 12.9333 |  | 7.6 | 11.6 | 10.3 | 10 | 9.8333
Russia |  | OSTROV DIKSON | OSTROV DIKSON, Russian Federation | 73.50N | 80.40E | 47 | 7.00 (ASN) | 82-06 | 206740 | -39.9 |  | -45.9 | 26.2 | 15.6 | 20.3 | 17.4 | 18 | 17.7667 |  | 9.9 | 17.2 | 14.2 | 14 | 13.7667
Russia |  | OSTROV GOLOMJANNYJ | OSTROV GOLOMJANNYJ, Russian Federation | 79.55N | 90.62E | 8 | 7.00 (ASN) | 82-06 | 200870 | -42.2 |  | -49 | 11.8 | 3.2 | 6.5 | 4.8 | 5 | 4.8333 |  | 1.9 | 4.6 | 3.4 | 3 | 3.3
Russia |  | OSTROV KOTELNYJ | OSTROV KOTELNYJ, Russian Federation | 76.00N | 137.87E | 8 | 10.00 (ASV) | 82-06 | 214320 | -40.7 |  | -43.7 | 25.8 | 11.8 | 18 | 14.4 | 15 | 14.7333 |  | 6.9 | 12.7 | 10.5 | 10 | 10.0333
Russia |  | OSTROV PREOBRAZENIJ | OSTROV PREOBRAZENIJ, Russian Federation | 74.67N | 112.93E | 57 | 9.00 (YAK) | 82-96 | 215040 | -42.2 |  | -48 | 27.5 | 12.5 | 20 | 14.8 | 16 | 15.7667 |  | 8.3 | 13 | 11.7 | 11 | 11
Russia |  | OSTROV UEDINENIJA | OSTROV UEDINENIJA, Russian Federation | 77.50N | 82.20E | 23 | 7.00 (ASN) | 82-96 | 202740 | -40.2 |  | -48.4 | 11.8 | 4 | 6.5 | 6.2 | 6 | 5.5667 |  | 2 | 4.9 | 4.4 | 4 | 3.7667
Russia |  | OSTROV VIZE | OSTROV VIZE, Russian Federation | 79.50N | 76.98E | 10 | 6.00 (ASR) | 82-06 | 200690 | -40.2 |  | -47.7 | 10.4 | 2.6 | 4.5 | 3.7 | 4 | 3.6 |  | 1.6 | 3 | 2.8 | 2 | 2.4667
Russia |  | OSTROV VRANGELJA | OSTROV VRANGELJA, Russian Federation | 70.98N | 178.48W | 5 | 12.00 (KAM) | 82-06 | 219820 | -37.3 |  | -43.4 | 15 | 7.5 | 9.2 | 9.7 | 9 | 8.8 |  | 5.7 | 7.5 | 8 | 7 | 7.0667
Russia |  | OZERNAJA | OZERNAJA, Russian Federation | 51.48N | 156.48E | 28 | 12.00 (KAM) | 82-06 | 325940 | -18.9 |  | -24 | 25.7 | 14.2 | 18.2 | 19.1 | 17 | 17.1667 |  | 11.7 | 15.2 | 16.5 | 14 | 14.4667
Russia |  | PADUN | PADUN, Russian Federation | 68.60N | 31.85E | 63 | 3.00 (RUS) | 87-06 | 221060 | -36.4 |  | -47.3 | 32.9 | 26 | 27.8 | 25.7 | 27 | 26.5 |  | 22.7 | 25.2 | 22.1 | 23 | 23.3333
Russia |  | PARTIZANSK | PARTIZANSK, Russian Federation | 43.15N | 133.02E | 208 | 10.00 (ASV) | 82-06 | 319870 | -24.3 |  | -31.5 | 35.3 | 28.9 | 30.4 | 31.2 | 30 | 30.1667 |  | 26.1 | 28.2 | 29.1 | 28 | 27.8
Russia |  | PAVELEC | PAVELEC, Russian Federation | 53.78N | 39.25E | 210 | 3.00 (RUS) | 82-04 | 278230 | -27.8 |  | -36.7 | 35.2 | 30.1 | 31.6 | 29.9 | 31 | 30.5333 |  | 28.2 | 29.6 | 27.4 | 28 | 28.4
Russia |  | PECHORA | PECHORA, Russian Federation | 65.12N | 57.10E | 59 | 3.00 (RUS) | 82-06 | 234180 | -43.3 |  | -52.9 | 36.6 | 29.6 | 32.2 | 26.2 | 29 | 29.3333 |  | 26.5 | 29.4 | 23.2 | 26 | 26.3667
Russia |  | PENZA | PENZA, Russian Federation | 53.12N | 45.02E | 174 | 3.00 (RUS) | 82-06 | 279620 | -29.7 |  | -38.6 | 39.2 | 33.1 | 33 | 32 | 33 | 32.7 |  | 29.9 | 30.7 | 28.9 | 30 | 29.8333
Russia |  | PERM | PERM, Russian Federation | 57.95N | 56.20E | 170 | 5.00 (EKT) | 82-06 | 282250 | -33.8 |  | -43.6 | 37.1 | 31.2 | 31.9 | 30.6 | 31 | 31.2333 |  | 28.9 | 30 | 26.5 | 28 | 28.4667
Russia |  | PERVOMAJSKOE | PERVOMAJSKOE, Russian Federation | 57.07N | 86.22E | 114 | 7.00 (ASN) | 82-06 | 293480 | -39.6 |  | -50.6 | 35.5 | 30.9 | 31.7 | 29.7 | 31 | 30.7667 |  | 28.2 | 29.2 | 27 | 28 | 28.1333
Russia |  | PETROPAVLOVSK-KAMCH | PETROPAVLOVSK-KAMCH, Russian Federation | 53.08N | 158.58E | 84 | 12.00 (KAM) | 82-06 | 325400 | -21.1 |  | -32.4 | 32.9 | 25.8 | 26.9 | 24.9 | 26 | 25.8667 |  | 21.7 | 23.9 | 21.9 | 23 | 22.5
Russia |  | PETROPAVLOVSK-KAMCH | PETROPAVLOVSK-KAMCH, Russian Federation | 52.98N | 158.65E | 24 | 12.00 (KAM) | 96-06 | 325830 | -18.6 |  | -27.3 | 29.1 | 22.5 | 23.8 | 22.4 | 23 | 22.9 |  | 19.6 | 21.1 | 20.1 | 20 | 20.2667
Russia |  | PETROVSKIJ ZAVOD | PETROVSKIJ ZAVOD, Russian Federation | 51.32N | 108.87E | 806 | 9.00 (YAK) | 82-06 | 308380 | -41.6 |  | -48.4 | 37.7 | 30.4 | 30.5 | 28.9 | 30 | 29.9333 |  | 27.3 | 27.8 | 26 | 27 | 27.0333
Russia |  | PETROZAVODSK | PETROZAVODSK, Russian Federation | 61.82N | 34.27E | 110 | 3.00 (RUS) | 82-06 | 228200 | -29.3 |  | -41.7 | 33.3 | 27.7 | 28 | 25.7 | 27 | 27.1333 |  | 24.9 | 25.8 | 23.5 | 25 | 24.7333
Russia |  | PIHTOVKA | PIHTOVKA, Russian Federation | 55.98N | 82.70E | 127 | 6.00 (ASR) | 82-91 | 295340 | -41.1 |  | -53.1 | 34.1 | 29.1 | 30.6 | 27.3 | 29 | 29 |  | 26.9 | 27.9 | 25.8 | 27 | 26.8667
Russia |  | PILVO | PILVO, Russian Federation | 50.05N | 142.17E | 4 | 10.00 (ASV) | 82-06 | 320690 | -30.2 |  | -37.8 | 28.2 | 21 | 23.6 | 24.6 | 23 | 23.0667 |  | 18 | 21 | 22.8 | 21 | 20.6
Russia |  | PINEGA | PINEGA, Russian Federation | 64.70N | 43.38E | 31 | 3.00 (RUS) | 85-06 | 225630 | -36.5 |  | -48.4 | 34.9 | 29.4 | 28.7 | 27.8 | 29 | 28.6333 |  | 26.8 | 26.7 | 24.3 | 26 | 25.9333
Russia |  | PIROVSKOE | PIROVSKOE, Russian Federation | 57.63N | 92.27E | 179 | 7.00 (ASN) | 82-01 | 293630 | -45.2 |  | -53.7 | 34.3 | 29.3 | 31.4 | 28 | 30 | 29.5667 |  | 26.8 | 29.3 | 25.8 | 27 | 27.3
Russia |  | PJALICA | PJALICA, Russian Federation | 66.18N | 39.53E | 9 | 3.00 (RUS) | 82-06 | 223490 | -26.2 |  | -37 | 26.7 | 19.3 | 21.5 | 18.9 | 20 | 19.9 |  | 16.7 | 18.8 | 16.3 | 17 | 17.2667
Russia |  | POGIBI | POGIBI, Russian Federation | 52.22N | 141.63E | 6 | 10.00 (ASV) | 82-06 | 320270 | -35.8 |  | -44 | 28 | 18.1 | 21.5 | 22.2 | 21 | 20.6 |  | 16.2 | 19.5 | 20.6 | 19 | 18.7667
Russia |  | POGRANICHNOE | POGRANICHNOE, Russian Federation | 50.40N | 143.77E | 8 | 10.00 (ASV) | 82-06 | 320760 | -31.7 |  | -37.9 | 36.9 | 24.4 | 26.1 | 27.6 | 26 | 26.0333 |  | 18.1 | 19.5 | 23.1 | 20 | 20.2333
Russia |  | POGRANICHNYJ | POGRANICHNYJ, Russian Federation | 44.40N | 131.38E | 211 | 10.00 (ASV) | 82-06 | 319150 | -26.5 |  | -32.3 | 37.6 | 31 | 32.5 | 31.7 | 32 | 31.7333 |  | 28.5 | 30.1 | 29.3 | 29 | 29.3
Russia |  | POJARKOVO | POJARKOVO, Russian Federation | 49.62N | 128.65E | 115 | 9.00 (YAK) | 82-06 | 315870 | -37.6 |  | -43 | 37.9 | 31.9 | 32.5 | 30.4 | 32 | 31.6 |  | 29.7 | 30.1 | 28.4 | 29 | 29.4
Russia |  | POKROVSKAJA | POKROVSKAJA, Russian Federation | 61.48N | 129.15E | 115 | 9.00 (YAK) | 82-06 | 248560 | -54.4 |  | -61.6 | 37.4 | 30.8 | 33.1 | 29.7 | 31 | 31.2 |  | 28.1 | 30.6 | 26.7 | 28 | 28.4667
Russia |  | POLARGMO IM. E.T. K | POLARGMO IM. E.T. K, Russian Federation | 80.62N | 58.05E | 22 | 3.00 (RUS) | 82-06 | 200460 | -38.7 |  | -44 | 13.1 | 4.3 | 5.5 | 4.7 | 5 | 4.8333 |  | 2.5 | 3.6 | 3.4 | 3 | 3.1667
Russia |  | POLTAVKA | POLTAVKA, Russian Federation | 44.03N | 131.32E | 109 | 10.00 (ASV) | 82-97 | 319170 | N/A |  | N/A | N/A | 32.1 | 32.8 | 33.3 | 33 | 32.7333 |  | 28.7 | 30.1 | 30.8 | 30 | 29.8667
Russia |  | PORONAJSK | PORONAJSK, Russian Federation | 49.22N | 143.10E | 8 | 10.00 (ASV) | 82-06 | 320980 | -32.1 |  | -39.2 | 35.4 | 22.9 | 23.7 | 26 | 24 | 24.2 |  | 17.9 | 20.1 | 22.7 | 20 | 20.2333
Russia |  | POSET | POSET, Russian Federation | 42.65N | 130.80E | 35 | 10.00 (ASV) | 82-06 | 319690 | -19.8 |  | -25.1 | 33.2 | 28 | 29.1 | 30.2 | 29 | 29.1 |  | 24.7 | 27 | 27.9 | 27 | 26.5333
Russia |  | PREOBRAZHENIE | PREOBRAZHENIE, Russian Federation | 42.90N | 133.90E | 43 | 10.00 (ASV) | 82-97 | 319890 | -19.9 |  | -26.3 | 31.3 | 21.4 | 26 | 27.2 | 25 | 24.8667 |  | 19.2 | 23.4 | 25.1 | 23 | 22.5667
Russia |  | PRIARGUNSK | PRIARGUNSK, Russian Federation | 50.40N | 119.07E | 521 | 9.00 (YAK) | 82-06 | 309750 | -41.2 |  | -48 | 40.1 | 31.1 | 33.6 | 31.8 | 32 | 32.1667 |  | 28.9 | 29.9 | 28.8 | 29 | 29.2
Russia |  | PRIMORSKO-AHTARSK | PRIMORSKO-AHTARSK, Russian Federation | 46.03N | 38.15E | 5 | 3.00 (RUS) | 82-06 | 348240 | -16.3 |  | -27.4 | 40.1 | 32.4 | 36.1 | 34.3 | 34 | 34.2667 |  | 29.9 | 33.6 | 32 | 32 | 31.8333
Russia |  | PSKOV | PSKOV, Russian Federation | 57.82N | 28.42E | 45 | 3.00 (RUS) | 82-06 | 262580 | -26.1 |  | -38.8 | 36.3 | 29.1 | 31.1 | 28.6 | 30 | 29.6 |  | 26.6 | 28.3 | 26.6 | 27 | 27.1667
Russia |  | PUDINO | PUDINO, Russian Federation | 57.53N | 79.37E | 97 | 7.00 (ASN) | 82-06 | 293130 | -41.5 |  | -52.7 | 37.1 | 30.9 | 31 | 29 | 30 | 30.3 |  | 28.9 | 28.8 | 26.2 | 28 | 27.9667
Russia |  | PUDOZ | PUDOZ, Russian Federation | 61.80N | 36.52E | 44 | 3.00 (RUS) | 90-06 | 228310 | -35.2 |  | -44.5 | 37 | 30.8 | 30.8 | 27 | 30 | 29.5333 |  | 27.8 | 28.2 | 24.6 | 27 | 26.8667
Russia |  | RA-IZ | RA-IZ, Russian Federation | 66.90N | 65.67E | 890 | 5.00 (EKT) | 82-97 | 233310 | -36.3 |  | -47.1 | 32.6 | 17.8 | 24.1 | 17.1 | 20 | 19.6667 |  | 16 | 21.6 | 14.7 | 17 | 17.4333
Russia |  | REBOLY | REBOLY, Russian Federation | 63.83N | 30.82E | 182 | 3.00 (RUS) | 82-06 | 226020 | -32.7 |  | -41 | 31.5 | 26.7 | 27 | 25.5 | 26 | 26.4 |  | 23.9 | 24.9 | 22.8 | 24 | 23.8667
Russia |  | REBRIHA | REBRIHA, Russian Federation | 53.07N | 82.30E | 219 | 6.00 (ASR) | 82-06 | 299230 | -39.3 |  | -48.5 | 39.8 | 31.9 | 32.9 | 32.4 | 32 | 32.4 |  | 29.5 | 30.5 | 29.3 | 30 | 29.7667
Russia |  | REMONTNOE | REMONTNOE, Russian Federation | 46.57N | 43.67E | 106 | 3.00 (RUS) | 82-06 | 347590 | -22.4 |  | -35.1 | 41.2 | 35.3 | 37.5 | 35.9 | 36 | 36.2333 |  | 32.7 | 35.5 | 33.5 | 34 | 33.9
Russia |  | RJAZAN' | RJAZAN', Russian Federation | 54.62N | 39.72E | 160 | 3.00 (RUS) | 82-94 | 277310 | -26.3 |  | -35 | 34.8 | 31.1 | 30.2 | 29.8 | 30 | 30.3667 |  | 28.1 | 28.2 | 27.2 | 28 | 27.8333
Russia |  | RJAZAN` | RJAZAN`, Russian Federation | 54.63N | 39.70E | 158 | 3.00 (RUS) | 94-06 | 277300 | -27.8 |  | -40 | 39.8 | 30.6 | 31.9 | 29 | 31 | 30.5 |  | 28.4 | 29.8 | 26.9 | 28 | 28.3667
Russia |  | ROMANOVKA | ROMANOVKA, Russian Federation | 53.20N | 112.78E | 923 | 8.00 (ASE) | 82-06 | 306500 | -42.8 |  | -50.4 | 34.6 | 28.5 | 30 | 27.5 | 29 | 28.6667 |  | 26.2 | 27.5 | 24.5 | 26 | 26.0667
Russia |  | ROSLAVL | ROSLAVL, Russian Federation | 53.93N | 32.83E | 224 | 3.00 (RUS) | 82-06 | 268820 | -24.7 |  | -33.3 | 35.3 | 28.6 | 30.7 | 28.2 | 29 | 29.1667 |  | 26.5 | 27.8 | 26.1 | 27 | 26.8
Russia |  | ROSTOV | ROSTOV, Russian Federation | 57.20N | 39.42E | 102 | 3.00 (RUS) | 82-06 | 273290 | -30.5 |  | -39.6 | 34.8 | 30 | 30.4 | 27.9 | 29 | 29.4333 |  | 27.5 | 28.3 | 25.8 | 27 | 27.2
Russia |  | ROSTOV-NA-DONU | ROSTOV-NA-DONU, Russian Federation | 47.25N | 39.82E | 77 | 3.00 (RUS) | 82-06 | 347310 | -19.4 |  | -28.6 | 41.8 | 33 | 36.9 | 36 | 35 | 35.3 |  | 30.9 | 33.9 | 32.9 | 33 | 32.5667
Russia |  | RUBCOVSK | RUBCOVSK, Russian Federation | 51.50N | 81.22E | 219 | 6.00 (ASR) | 82-06 | 360340 | -35.6 |  | -49.5 | 39.7 | 32.9 | 33.8 | 33.8 | 34 | 33.5 |  | 30.7 | 31.1 | 30.7 | 31 | 30.8333
Russia |  | RUDNAJA PRISTAN | RUDNAJA PRISTAN, Russian Federation | 44.37N | 135.85E | 34 | 10.00 (ASV) | 82-06 | 319590 | -23.7 |  | -31.1 | 36.6 | 26.3 | 28.5 | 29.4 | 28 | 28.0667 |  | 21.2 | 24.7 | 26.7 | 24 | 24.2
Russia |  | RUSSKAYA GAVAN` | RUSSKAYA GAVAN`, Russian Federation | 76.18N | 62.57E | 9 | 5.00 (EKT) | 82-93 | 203570 | -34.2 |  | -40.4 | 20.9 | 12.3 | 13.7 | 12.9 | 13 | 12.9667 |  | 9.9 | 11.7 | 9.9 | 11 | 10.5
Russia |  | RYBINSK | RYBINSK, Russian Federation | 58.10N | 38.68E | 105 | 3.00 (RUS) | 82-06 | 272250 | -30.9 |  | -40.9 | 34.3 | 29.4 | 29.9 | 27.7 | 29 | 29 |  | 27 | 27.6 | 25 | 27 | 26.5333
Russia |  | RZEV | RZEV, Russian Federation | 56.27N | 34.32E | 196 | 3.00 (RUS) | 82-98 | 264980 | -28 |  | -36.3 | 33.7 | 28.5 | 28.8 | 27.8 | 28 | 28.3667 |  | 26.1 | 26.5 | 25.6 | 26 | 26.0667
Russia |  | SADRINSK | SADRINSK, Russian Federation | 56.07N | 63.65E | 81 | 5.00 (EKT) | 82-06 | 285520 | -33.4 |  | -41.4 | 39.1 | 32.8 | 33.4 | 31.6 | 33 | 32.6 |  | 30.5 | 30.6 | 28.1 | 30 | 29.7333
Russia |  | SAIM | SAIM, Russian Federation | 60.32N | 64.22E | 53 | 5.00 (EKT) | 85-06 | 239290 | -40.9 |  | -49.7 | 37.6 | 31.5 | 31.9 | 29.9 | 31 | 31.1 |  | 29 | 30 | 25.8 | 28 | 28.2667
Russia |  | SAKUN`JA | SAKUN`JA, Russian Federation | 57.67N | 46.63E | 176 | 3.00 (RUS) | 82-06 | 273730 | -32 |  | -43.1 | 36.3 | 30.3 | 30.4 | 28.3 | 30 | 29.6667 |  | 27.5 | 28.7 | 25.3 | 27 | 27.1667
Russia |  | SALEHARD | SALEHARD, Russian Federation | 66.53N | 66.67E | 16 | 5.00 (EKT) | 82-06 | 233300 | -42.7 |  | -51.1 | 34.1 | 25.7 | 29.6 | 24.5 | 27 | 26.6 |  | 22.4 | 26.2 | 21.2 | 23 | 23.2667
Russia |  | SAMARA | SAMARA, Russian Federation | 53.25N | 50.45E | 40 | 4.00 (CAU) | 82-06 | 289000 | -30.1 |  | -38.1 | 39.7 | 34 | 33.8 | 32.8 | 34 | 33.5333 |  | 31.2 | 31.5 | 29.5 | 31 | 30.7333
Russia |  | SAMARY | SAMARY, Russian Federation | 57.35N | 58.22E | 244 | 5.00 (EKT) | 82-06 | 283340 | -37.5 |  | -48 | 36.3 | 31.8 | 31.2 | 29.8 | 31 | 30.9333 |  | 29 | 29.4 | 26.6 | 28 | 28.3333
Russia |  | SANGARY | SANGARY, Russian Federation | 63.97N | 127.47E | 96 | 9.00 (YAK) | 82-06 | 246520 | -50.3 |  | -56.8 | 34.2 | 28.2 | 30.6 | 28.1 | 29 | 28.9667 |  | 26 | 28.8 | 25.2 | 27 | 26.6667
Russia |  | SAR`JA | SAR`JA, Russian Federation | 58.37N | 45.53E | 125 | 3.00 (RUS) | 82-06 | 272710 | -35.3 |  | -45.6 | 36.2 | 30.5 | 30.3 | 28.6 | 30 | 29.8 |  | 27.6 | 28.5 | 25.5 | 27 | 27.2
Russia |  | SARAN-PAUL | SARAN-PAUL, Russian Federation | 64.28N | 60.88E | 29 | 5.00 (EKT) | 82-06 | 235270 | N/A |  | N/A | N/A | 29.1 | 31 | 26.5 | 29 | 28.8667 |  | 26 | 28.5 | 23.4 | 26 | 25.9667
Russia |  | SARATOV | SARATOV, Russian Federation | 51.57N | 46.03E | 156 | 3.00 (RUS) | 82-06 | 341720 | -25.4 |  | -33.8 | 39.8 | 34 | 34.2 | 33.1 | 34 | 33.7667 |  | 30.8 | 31.9 | 30.3 | 31 | 31
Russia |  | SARGATSKOE | SARGATSKOE, Russian Federation | 55.60N | 73.48E | 87 | 6.00 (ASR) | 82-05 | 285980 | -38.5 |  | -48.3 | 37.9 | 31.9 | 33.2 | 31.1 | 32 | 32.0667 |  | 29.8 | 30.2 | 27.6 | 29 | 29.2
Russia |  | SEGEZA | SEGEZA, Russian Federation | 63.77N | 34.28E | 112 | 3.00 (RUS) | 82-06 | 226210 | -32.1 |  | -43.3 | 32.6 | 28 | 28.3 | 26.4 | 28 | 27.5667 |  | 25 | 26.1 | 23.5 | 25 | 24.8667
Russia |  | SEJAHA | SEJAHA, Russian Federation | 70.17N | 72.52E | 16 | 5.00 (EKT) | 82-94 | 209670 | N/A |  | N/A | N/A | 16.2 | 25.2 | 18.6 | 20 | 20 |  | 12.4 | 20.7 | 15.5 | 16 | 16.2
Russia |  | SEJMCHAN | SEJMCHAN, Russian Federation | 62.92N | 152.42E | 205 | 11.00 (MAG) | 82-06 | 257030 | -52.6 |  | -57.3 | 37.6 | 30.6 | 32.3 | 27.3 | 30 | 30.0667 |  | 27.8 | 29.5 | 24.6 | 27 | 27.3
Russia |  | SEKTAGLI | SEKTAGLI, Russian Federation | 50.43N | 131.02E | 230 | 9.00 (YAK) | 82-06 | 315340 | -41.5 |  | -46.1 | 36 | 31.5 | 31.8 | 29.9 | 31 | 31.0667 |  | 28.9 | 29.6 | 27.6 | 29 | 28.7
Russia |  | SELAGONCY | SELAGONCY, Russian Federation | 66.25N | 114.28E | 236 | 9.00 (YAK) | 82-06 | 243290 | -56.3 |  | -61.4 | 37.8 | 29.5 | 31.5 | 27.2 | 29 | 29.4 |  | 26 | 29.3 | 24.2 | 27 | 26.5
Russia |  | SELEMDZA | SELEMDZA, Russian Federation | 53.13N | 133.97E | 682 | 9.00 (YAK) | 82-94 | 313380 | -50.8 |  | -58.6 | 33.4 | 29.2 | 29.3 | 26.8 | 28 | 28.4333 |  | 27 | 27.4 | 24.6 | 26 | 26.3333
Russia |  | SEMJACHIK | SEMJACHIK, Russian Federation | 54.12N | 159.98E | 27 | 12.00 (KAM) | 82-06 | 325090 | -16.9 |  | -24.8 | 34.4 | 22.6 | 24.7 | 23.7 | 24 | 23.6667 |  | 17.5 | 19.3 | 20.4 | 19 | 19.0667
Russia |  | SENKURSK | SENKURSK, Russian Federation | 62.10N | 42.90E | 45 | 3.00 (RUS) | 82-06 | 227680 | -37.5 |  | -47.3 | 35.8 | 30.8 | 30.7 | 27.5 | 30 | 29.6667 |  | 28.1 | 28.3 | 24.8 | 27 | 27.0667
Russia |  | SERAFIMOVIC | SERAFIMOVIC, Russian Federation | 49.57N | 42.75E | 200 | 3.00 (RUS) | 82-06 | 343570 | -24.5 |  | -34.2 | 40.9 | 34.7 | 35.8 | 34.7 | 35 | 35.0667 |  | 31.5 | 33.5 | 32.1 | 32 | 32.3667
Russia |  | SERBAKUL | SERBAKUL, Russian Federation | 54.63N | 72.43E | 115 | 6.00 (ASR) | 82-06 | 287910 | -35.5 |  | -47.1 | 37.5 | 32.6 | 32.8 | 30.1 | 32 | 31.8333 |  | 30.6 | 30 | 27.7 | 29 | 29.4333
Russia |  | SEROV | SEROV, Russian Federation | 59.60N | 60.53E | 132 | 5.00 (EKT) | 82-06 | 280440 | N/A |  | N/A | N/A | 31.6 | 31.6 | 29 | 31 | 30.7333 |  | 29 | 29.4 | 25.9 | 28 | 28.1
Russia |  | SEVERNOE | SEVERNOE, Russian Federation | 56.35N | 78.35E | 126 | 6.00 (ASR) | 82-06 | 294180 | -40.3 |  | -52.3 | 37.4 | 30.5 | 30.8 | 29 | 30 | 30.1 |  | 28.2 | 28.5 | 26.3 | 28 | 27.6667
Russia |  | SEVERO-KURILSK | SEVERO-KURILSK, Russian Federation | 50.68N | 156.13E | 23 | 12.00 (KAM) | 83-06 | 322150 | -12.5 |  | -17.5 | 27.3 | 19.8 | 22.2 | 19.8 | 21 | 20.6 |  | 16.2 | 18.3 | 17.7 | 17 | 17.4
Russia |  | SHEREMETYEVO | SHEREMETYEVO, Russian Federation | 55.97N | 37.42E | 197 | 3.00 (RUS) | 82-06 | 275155 | -28.4 |  | -37.3 | 35.8 | 30.1 | 31.2 | 28.2 | 30 | 29.8333 |  | 27.9 | 28.9 | 26.1 | 28 | 27.6333
Russia |  | SHILKA | SHILKA, Russian Federation | 51.87N | 116.03E | 597 | 9.00 (YAK) | 82-06 | 308620 | -37.9 |  | -45.5 | 39.1 | 31.2 | 33.3 | 31.5 | 32 | 32 |  | 28.9 | 29.8 | 28 | 29 | 28.9
Russia |  | SIMANOVSK | SIMANOVSK, Russian Federation | 51.98N | 127.65E | 281 | 9.00 (YAK) | 83-06 | 314420 | -41.3 |  | -52.4 | 34.3 | 29.6 | 32 | 29.4 | 30 | 30.3333 |  | 27.9 | 29.5 | 27 | 28 | 28.1333
Russia |  | SIMUSIR | SIMUSIR, Russian Federation | 46.85N | 151.87E | 25 | 11.00 (MAG) | 82-97 | 321950 | -11.5 |  | -15.6 | 29.9 | 16.5 | 21.1 | 24.1 | 21 | 20.5667 |  | 13 | 17.4 | 19.8 | 17 | 16.7333
Russia |  | SIRA | SIRA, Russian Federation | 54.50N | 89.93E | 475 | 7.00 (ASN) | 83-01 | 297560 | -34.7 |  | -43.5 | 36.4 | 30 | 31.1 | 30.5 | 31 | 30.5333 |  | 27.2 | 28.8 | 27.8 | 28 | 27.9333
Russia |  | SKOVORODINO | SKOVORODINO, Russian Federation | 54.00N | 123.97E | 398 | 9.00 (YAK) | 82-06 | 306920 | -43.5 |  | -49 | 39.8 | 29.2 | 31.1 | 30 | 30 | 30.1 |  | 27.7 | 28.9 | 26.9 | 28 | 27.8333
Russia |  | SLAVGOROD | SLAVGOROD, Russian Federation | 52.97N | 78.65E | 126 | 6.00 (ASR) | 83-06 | 299150 | -36.5 |  | -46.3 | 40.5 | 34.1 | 33.7 | 33.9 | 34 | 33.9 |  | 31.4 | 31.6 | 30.8 | 31 | 31.2667
Russia |  | SMIDOVICH | SMIDOVICH, Russian Federation | 48.62N | 133.83E | 52 | 10.00 (ASV) | 82-06 | 317250 | -35.4 |  | -41.4 | 36.1 | 30.6 | 32 | 31.3 | 31 | 31.3 |  | 28.3 | 29.8 | 28.8 | 29 | 28.9667
Russia |  | SMOLENSK | SMOLENSK, Russian Federation | 54.75N | 32.07E | 239 | 3.00 (RUS) | 82-06 | 267810 | -25.6 |  | -34.3 | 34.6 | 28 | 30.1 | 27.8 | 29 | 28.6333 |  | 25.9 | 27.4 | 25.6 | 26 | 26.3
Russia |  | SOFIJSKIJ PRIISK | SOFIJSKIJ PRIISK, Russian Federation | 52.27N | 133.98E | 902 | 10.00 (ASV) | 82-06 | 314780 | -45.7 |  | -50 | 32.1 | 27.4 | 27.7 | 26.4 | 27 | 27.1667 |  | 24.8 | 25.7 | 23.4 | 25 | 24.6333
Russia |  | SOJNA | SOJNA, Russian Federation | 67.88N | 44.13E | 8 | 3.00 (RUS) | 82-06 | 222710 | -32.4 |  | -44.5 | 31 | 22.6 | 24.8 | 20 | 22 | 22.4667 |  | 19.7 | 21.2 | 16.7 | 19 | 19.2
Russia |  | SOLNETHNAYA | SOLNETHNAYA, Russian Federation | 54.03N | 108.27E | 464 | 8.00 (ASE) | 82-05 | 305370 | -29.9 |  | -39.3 | 30.1 | 19.5 | 22.9 | 23.2 | 22 | 21.8667 |  | 17.2 | 20.7 | 20.7 | 20 | 19.5333
Russia |  | SOLOVEVSK | SOLOVEVSK, Russian Federation | 49.90N | 115.75E | 623 | 9.00 (YAK) | 82-98 | 309670 | -36.9 |  | -43.9 | 37.3 | 31 | 32.3 | 31.3 | 32 | 31.5333 |  | 28.8 | 29.6 | 28.4 | 29 | 28.9333
Russia |  | SORTAVALA | SORTAVALA, Russian Federation | 61.72N | 30.72E | 19 | 3.00 (RUS) | 82-06 | 228020 | -29.2 |  | -41.8 | 32.4 | 27.7 | 28.1 | 26.1 | 27 | 27.3 |  | 24.7 | 26.1 | 24.1 | 25 | 24.9667
Russia |  | SOSNOVO-OZERSKOE | SOSNOVO-OZERSKOE, Russian Federation | 52.53N | 111.55E | 952 | 8.00 (ASE) | 82-06 | 307450 | -38.3 |  | -46.6 | 38 | 28.3 | 29.1 | 26.5 | 28 | 27.9667 |  | 25.3 | 26.5 | 23.9 | 25 | 25.2333
Russia |  | SOSUNOVO | SOSUNOVO, Russian Federation | 46.53N | 138.33E | 4 | 10.00 (ASV) | 82-96 | 318660 | N/A |  | N/A | N/A | 24.2 | 26.1 | 28.5 | 26 | 26.2667 |  | 19.3 | 21.3 | 25.4 | 22 | 22
Russia |  | SOSVA | SOSVA, Russian Federation | 63.65N | 62.10E | 28 | 5.00 (EKT) | 82-06 | 236250 | N/A |  | N/A | N/A | 29 | 32.1 | 26.6 | 29 | 29.2333 |  | 25.9 | 30 | 24.1 | 27 | 26.6667
Russia |  | SOVETSKAYA GAVAN | SOVETSKAYA GAVAN, Russian Federation | 48.97N | 140.30E | 22 | 10.00 (ASV) | 83-92 | 317700 | N/A |  | N/A | N/A | 27.9 | 27.9 | 29.3 | 28 | 28.3667 |  | 23.7 | 24.3 | 26.4 | 25 | 24.8
Russia |  | SREDNY VASJUGAN | SREDNY VASJUGAN, Russian Federation | 59.22N | 78.23E | 69 | 7.00 (ASN) | 82-06 | 291110 | -40.7 |  | -54.2 | 35 | 29.9 | 31.1 | 28.2 | 30 | 29.7333 |  | 28 | 29.3 | 26.1 | 28 | 27.8
Russia |  | SRETENSK | SRETENSK, Russian Federation | 52.23N | 117.70E | 525 | 9.00 (YAK) | 82-06 | 307770 | -42.2 |  | -49.5 | 39 | 31.2 | 33.2 | 31.1 | 32 | 31.8333 |  | 28.7 | 29.7 | 27.5 | 29 | 28.6333
Russia |  | ST.PETERSBURG | ST.PETERSBURG, Russian Federation | 59.97N | 30.30E | 6 | 3.00 (RUS) | 82-06 | 260630 | -26 |  | -37.7 | 36 | 29.2 | 30.4 | 28.1 | 29 | 29.2333 |  | 26.8 | 27.7 | 26 | 27 | 26.8333
Russia |  | STARAJA RUSSA | STARAJA RUSSA, Russian Federation | 58.02N | 31.32E | 25 | 3.00 (RUS) | 90-06 | 262750 | -28.1 |  | -38.8 | 36.7 | 29.8 | 31.4 | 28.9 | 30 | 30.0333 |  | 27.6 | 29 | 26.3 | 28 | 27.6333
Russia |  | STAVROPOL | STAVROPOL, Russian Federation | 45.12N | 42.08E | 452 | 3.00 (RUS) | 87-06 | 349490 | -17.9 |  | -30.9 | 41.4 | 32 | 35.2 | 35.9 | 34 | 34.3667 |  | 29.1 | 33.2 | 33.9 | 32 | 32.0667
Russia |  | STERLITAMAK | STERLITAMAK, Russian Federation | 53.58N | 56.00E | 130 | 5.00 (EKT) | 83-06 | 288250 | -34.4 |  | -44.3 | 39.4 | 34 | 33 | 32.1 | 33 | 33.0333 |  | 31.1 | 31.1 | 29.3 | 31 | 30.5
Russia |  | STRELKA | STRELKA, Russian Federation | 58.08N | 93.00E | 90 | 7.00 (ASN) | 82-01 | 292740 | -41.5 |  | -54.7 | 36.8 | 28.8 | 32.2 | 28.6 | 30 | 29.8667 |  | 26.1 | 29.8 | 26.2 | 27 | 27.3667
Russia |  | SUHAJA | SUHAJA, Russian Federation | 52.57N | 107.13E | 461 | 8.00 (ASE) | 82-06 | 307260 | -31 |  | -38.9 | 31.8 | 20.8 | 23.1 | 22.2 | 22 | 22.0333 |  | 18.2 | 21.2 | 20.6 | 20 | 20
Russia |  | SUHINICI | SUHINICI, Russian Federation | 54.10N | 35.58E | 239 | 3.00 (RUS) | 82-06 | 277070 | -26.6 |  | -35.5 | 34.5 | 28.8 | 30.6 | 28.3 | 29 | 29.2333 |  | 26.6 | 27.8 | 25.9 | 27 | 26.7667
Russia |  | SUHOBUZIMSKOE | SUHOBUZIMSKOE, Russian Federation | 56.50N | 93.28E | 164 | 7.00 (ASN) | 84-01 | 294770 | N/A |  | N/A | N/A | 28.7 | 32.4 | 29.9 | 30 | 30.3333 |  | 27 | 30.2 | 27.6 | 28 | 28.2667
Russia |  | SUMIHA | SUMIHA, Russian Federation | 55.23N | 63.32E | 176 | 5.00 (EKT) | 82-04 | 286550 | -32.3 |  | -40.1 | 37.9 | 32.8 | 33.5 | 31.2 | 33 | 32.5 |  | 30.8 | 30.8 | 28.1 | 30 | 29.9
Russia |  | SUNTAR | SUNTAR, Russian Federation | 62.15N | 117.65E | 133 | 9.00 (YAK) | 82-06 | 247380 | -52.2 |  | -61.7 | 38 | 31.2 | 33.3 | 29.5 | 31 | 31.3333 |  | 28.9 | 31.1 | 26.7 | 29 | 28.9
Russia |  | SURA | SURA, Russian Federation | 63.58N | 45.63E | 62 | 3.00 (RUS) | 82-06 | 226760 | -41.2 |  | -54.5 | 35.3 | 29.9 | 30.1 | 27.1 | 29 | 29.0333 |  | 27.3 | 27.7 | 24.3 | 26 | 26.4333
Russia |  | SURGUT | SURGUT, Russian Federation | 61.25N | 73.50E | 56 | 5.00 (EKT) | 82-06 | 238490 | -42.8 |  | -53.2 | 36 | 29.8 | 31.3 | 27.9 | 30 | 29.6667 |  | 27.8 | 29.2 | 25.2 | 27 | 27.4
Russia |  | SUTUR | SUTUR, Russian Federation | 50.07N | 132.13E | 347 | 10.00 (ASV) | 82-95 | 315380 | -40 |  | -44.7 | 36.1 | 31.1 | 30.7 | 29.7 | 31 | 30.5 |  | 28.6 | 29.2 | 27.4 | 28 | 28.4
Russia |  | SVETLOGRAD | SVETLOGRAD, Russian Federation | 45.35N | 42.85E | 140 | 3.00 (RUS) | 84-06 | 349540 | -18.9 |  | -31.4 | 41.8 | 34.3 | 37.6 | 36.1 | 36 | 36 |  | 31.7 | 35.7 | 33.8 | 34 | 33.7333
Russia |  | SVOBODNYJ | SVOBODNYJ, Russian Federation | 51.45N | 128.12E | 197 | 9.00 (YAK) | 82-06 | 314450 | -40.7 |  | -49.6 | 38.3 | 31.1 | 31.8 | 29.5 | 31 | 30.8 |  | 28.8 | 29.6 | 27.3 | 29 | 28.5667
Russia |  | SYKTYVKAR | SYKTYVKAR, Russian Federation | 61.68N | 50.78E | 119 | 3.00 (RUS) | 82-06 | 238040 | -37.2 |  | -46.7 | 36 | 30.1 | 31.2 | 27.4 | 30 | 29.5667 |  | 27.7 | 29.2 | 24.4 | 27 | 27.1
Russia |  | SYM | SYM, Russian Federation | 60.35N | 88.37E | 86 | 7.00 (ASN) | 82-06 | 239750 | -49.7 |  | -63.7 | 37.1 | 32.5 | 32.5 | 28.8 | 31 | 31.2667 |  | 29 | 29.8 | 25.8 | 28 | 28.2
Russia |  | SYZRAN` | SYZRAN`, Russian Federation | 53.18N | 48.40E | 104 | 3.00 (RUS) | 90-06 | 279830 | -28.5 |  | -38.2 | 38 | 33.5 | 32.3 | 31.7 | 33 | 32.5 |  | 30.2 | 30.1 | 28.9 | 30 | 29.7333
Russia |  | TADIBE-YAKHA | TADIBE-YAKHA, Russian Federation | 70.35N | 74.13E | 4 | 5.00 (EKT) | 82-94 | 209640 | N/A |  | N/A | N/A | 19.7 | 24.4 | 19.3 | 21 | 21.1333 |  | 14.2 | 21.2 | 15.6 | 17 | 17
Russia |  | TAJSHET | TAJSHET, Russian Federation | 55.95N | 98.00E | 307 | 8.00 (ASE) | 82-06 | 295940 | -40.1 |  | -49.8 | 36.5 | 30.7 | 31.3 | 29.3 | 30 | 30.4333 |  | 28.3 | 29.3 | 26.4 | 28 | 28
Russia |  | TAMBEY | TAMBEY, Russian Federation | 71.48N | 71.82E | 8 | 5.00 (EKT) | 82-93 | 208640 | N/A |  | N/A | N/A | 14.7 | 23.6 | 17.2 | 19 | 18.5 |  | 10.1 | 17.2 | 14.3 | 14 | 13.8667
Russia |  | TAMBOV | TAMBOV, Russian Federation | 52.80N | 41.33E | 128 | 3.00 (RUS) | 82-06 | 279470 | -29.4 |  | -39.4 | 38.3 | 32.2 | 33.5 | 32.2 | 33 | 32.6333 |  | 29.5 | 30.4 | 29.1 | 30 | 29.6667
Russia |  | TANGUJ | TANGUJ, Russian Federation | 55.38N | 101.03E | 423 | 8.00 (ASE) | 82-06 | 304050 | -40.7 |  | -49.8 | 35.6 | 30.5 | 31.6 | 29 | 30 | 30.3667 |  | 27.8 | 29.3 | 26.4 | 28 | 27.8333
Russia |  | TANHOJ | TANHOJ, Russian Federation | 51.57N | 105.12E | 472 | 8.00 (ASE) | 82-06 | 308240 | -31 |  | -39.6 | 31.6 | 23.1 | 24.9 | 22.5 | 24 | 23.5 |  | 20.2 | 22.8 | 20.9 | 21 | 21.3
Russia |  | TARA | TARA, Russian Federation | 56.90N | 74.38E | 74 | 6.00 (ASR) | 82-06 | 284930 | -39.8 |  | -51.8 | 37.1 | 31.2 | 31.3 | 29.2 | 31 | 30.5667 |  | 29.2 | 29.2 | 26.6 | 28 | 28.3333
Russia |  | TARKO-SALE | TARKO-SALE, Russian Federation | 64.92N | 77.82E | 27 | 5.00 (EKT) | 82-06 | 235520 | -46.8 |  | -58.2 | 35.6 | 29.1 | 31.4 | 27.7 | 29 | 29.4 |  | 26.6 | 29 | 24.2 | 27 | 26.6
Russia |  | TASTYP | TASTYP, Russian Federation | 52.80N | 89.92E | 455 | 7.00 (ASN) | 82-06 | 299560 | -37.8 |  | -48.3 | 35.5 | 30.3 | 30.2 | 29.4 | 30 | 29.9667 |  | 27.7 | 27.9 | 26.5 | 27 | 27.3667
Russia |  | TATARSK | TATARSK, Russian Federation | 55.20N | 75.97E | 112 | 6.00 (ASR) | 82-06 | 296050 | -35.9 |  | -48.4 | 37.1 | 32.1 | 32 | 30.2 | 31 | 31.4333 |  | 30 | 29.9 | 27.2 | 29 | 29.0333
Russia |  | TAZOVSKOE | TAZOVSKOE, Russian Federation | 67.47N | 78.73E | 8 | 5.00 (EKT) | 85-06 | 232560 | -45.7 |  | -56 | 35.1 | 27 | 29.2 | 25 | 27 | 27.0667 |  | 23.1 | 26.1 | 21.9 | 24 | 23.7
Russia |  | TERIBERKA | TERIBERKA, Russian Federation | 69.20N | 35.12E | 30 | 3.00 (RUS) | 84-06 | 220280 | -21.7 |  | -30.1 | 35 | 24.4 | 26.2 | 25.3 | 25 | 25.3 |  | 20.8 | 22.8 | 20.7 | 21 | 21.4333
Russia |  | TERNEJ | TERNEJ, Russian Federation | 45.00N | 136.60E | 68 | 10.00 (ASV) | 82-06 | 319090 | -23.1 |  | -28.5 | 37.3 | 27.7 | 29.4 | 30.7 | 29 | 29.2667 |  | 22.5 | 25.1 | 27.5 | 25 | 25.0333
Russia |  | TEVRIZ | TEVRIZ, Russian Federation | 57.52N | 72.40E | 66 | 6.00 (ASR) | 83-06 | 283830 | -39 |  | -49.7 | 35.2 | 30.2 | 31 | 28.7 | 30 | 29.9667 |  | 28.4 | 28.7 | 26.2 | 28 | 27.7667
Russia |  | TIHORECK | TIHORECK, Russian Federation | 45.85N | 40.08E | 78 | 3.00 (RUS) | 82-06 | 348380 | -18.6 |  | -32 | 40.9 | 32.6 | 36.6 | 36.2 | 35 | 35.1333 |  | 30.6 | 34.2 | 33.4 | 33 | 32.7333
Russia |  | TIHVIN | TIHVIN, Russian Federation | 59.65N | 33.55E | 61 | 3.00 (RUS) | 82-06 | 260940 | -32.9 |  | -43.5 | 35.9 | 30.2 | 30.6 | 27.6 | 29 | 29.4667 |  | 27.1 | 28 | 25.5 | 27 | 26.8667
Russia |  | TIKSI | TIKSI, Russian Federation | 71.58N | 128.92E | 7 | 9.00 (YAK) | 82-06 | 218240 | -44.3 |  | -50.8 | 36.2 | 23.9 | 26.2 | 23.7 | 25 | 24.6 |  | 17.1 | 21.7 | 19.2 | 19 | 19.3333
Russia |  | TISUL | TISUL, Russian Federation | 55.75N | 88.32E | 211 | 7.00 (ASN) | 82-06 | 295570 | -39.2 |  | -49.8 | 38.3 | 29.9 | 31.2 | 29.7 | 30 | 30.2667 |  | 27.6 | 28.6 | 26.9 | 28 | 27.7
Russia |  | TIVJAKU | TIVJAKU, Russian Federation | 48.60N | 137.05E | 403 | 10.00 (ASV) | 82-06 | 317540 | -41 |  | -45.3 | 36.2 | 29.8 | 31.3 | 30.4 | 31 | 30.5 |  | 27.8 | 29.1 | 27.3 | 28 | 28.0667
Russia |  | TJUHTET | TJUHTET, Russian Federation | 56.53N | 89.32E | 205 | 7.00 (ASN) | 82-01 | 294560 | N/A |  | N/A | N/A | 27.9 | 31.3 | 28.4 | 29 | 29.2 |  | 25.7 | 29 | 26.1 | 27 | 26.9333
Russia |  | TJUKALINSK | TJUKALINSK, Russian Federation | 55.87N | 72.20E | 120 | 6.00 (ASR) | 83-06 | 285860 | -36.8 |  | -45.9 | 37.7 | 31.9 | 32.4 | 29.1 | 31 | 31.1333 |  | 29.6 | 29.7 | 27.2 | 29 | 28.8333
Russia |  | TJUMEN | TJUMEN, Russian Federation | 57.12N | 65.43E | 104 | 5.00 (EKT) | 82-06 | 283670 | -35.1 |  | -44.8 | 35.7 | 31.8 | 31.7 | 29.9 | 31 | 31.1333 |  | 29.4 | 29.3 | 26.9 | 29 | 28.5333
Russia |  | TOBOLSK | TOBOLSK, Russian Federation | 58.15N | 68.25E | 44 | 5.00 (EKT) | 82-06 | 282750 | -39.4 |  | -48.2 | 36.2 | 31.3 | 31.3 | 28.7 | 30 | 30.4333 |  | 28.8 | 29.3 | 26 | 28 | 28.0333
Russia |  | TOGUCHIN | TOGUCHIN, Russian Federation | 55.23N | 84.40E | 173 | 6.00 (ASR) | 82-06 | 296360 | -38.7 |  | -49.6 | 35.3 | 30.4 | 31.5 | 30.9 | 31 | 30.9333 |  | 27.8 | 29.4 | 27.8 | 28 | 28.3333
Russia |  | TOKO | TOKO, Russian Federation | 56.28N | 131.13E | 850 | 10.00 (ASV) | 82-06 | 311370 | -53.6 |  | -60.7 | 35.8 | 27.4 | 29.5 | 26.5 | 28 | 27.8 |  | 25.2 | 27.2 | 24 | 25 | 25.4667
Russia |  | TOMPA | TOMPA, Russian Federation | 55.12N | 109.75E | 465 | 8.00 (ASE) | 82-01 | 304390 | -35.6 |  | -44 | 32.7 | 24.6 | 26.7 | 25.5 | 26 | 25.6 |  | 21.6 | 23.1 | 22.8 | 23 | 22.5
Russia |  | TOMSK | TOMSK, Russian Federation | 56.50N | 84.92E | 139 | 7.00 (ASN) | 82-06 | 294300 | -39 |  | -50.4 | 35.1 | 29.8 | 30.6 | 29.4 | 30 | 29.9333 |  | 27.5 | 28.5 | 26.5 | 28 | 27.5
Russia |  | TOT`MA | TOT`MA, Russian Federation | 59.88N | 42.75E | 134 | 3.00 (RUS) | 82-06 | 270510 | -33.9 |  | -45.2 | 35 | 30.1 | 30.1 | 27.5 | 29 | 29.2333 |  | 27.1 | 27.7 | 24.5 | 26 | 26.4333
Russia |  | TROICKOE | TROICKOE, Russian Federation | 49.45N | 136.57E | 33 | 10.00 (ASV) | 82-06 | 316550 | -35.5 |  | -40.6 | 38.2 | 30.2 | 32 | 31.2 | 31 | 31.1333 |  | 28.1 | 29.8 | 28.2 | 29 | 28.7
Russia |  | TROICKO-PECHERSKOE | TROICKO-PECHERSKOE, Russian Federation | 62.70N | 56.20E | 139 | 3.00 (RUS) | 82-06 | 237110 | -40.3 |  | -48.3 | 35.2 | 30 | 31.1 | 27.4 | 30 | 29.5 |  | 27.2 | 29.2 | 23.9 | 27 | 26.7667
Russia |  | TROIZK | TROIZK, Russian Federation | 54.08N | 61.62E | 193 | 5.00 (EKT) | 82-06 | 287480 | -33.9 |  | -42.5 | 39.5 | 33.6 | 33.6 | 32.7 | 33 | 33.3 |  | 31.2 | 31.1 | 29.8 | 31 | 30.7
Russia |  | TRUBCEVSK | TRUBCEVSK, Russian Federation | 52.58N | 33.77E | 178 | 3.00 (RUS) | 82-06 | 269970 | -25.9 |  | -36.4 | 35.6 | 29.8 | 31.3 | 29.6 | 30 | 30.2333 |  | 27.5 | 28.7 | 27.3 | 28 | 27.8333
Russia |  | TUAPSE | TUAPSE, Russian Federation | 44.10N | 39.07E | 41 | 3.00 (RUS) | 82-06 | 370180 | -8 |  | -15.7 | 37.9 | 29.1 | 33.1 | 33.7 | 32 | 31.9667 |  | 27 | 31 | 31.2 | 30 | 29.7333
Russia |  | TULA | TULA, Russian Federation | 54.23N | 37.62E | 204 | 3.00 (RUS) | 90-06 | 277190 | -28.6 |  | -37.3 | 35.9 | 30.3 | 31.8 | 29.6 | 31 | 30.5667 |  | 28.2 | 29.5 | 27.3 | 28 | 28.3333
Russia |  | TULUN | TULUN, Russian Federation | 54.60N | 100.63E | 522 | 8.00 (ASE) | 82-06 | 305040 | -37 |  | -49 | 36.2 | 29.7 | 31.2 | 28.7 | 30 | 29.8667 |  | 27.1 | 29 | 26.1 | 27 | 27.4
Russia |  | TUMNIN | TUMNIN, Russian Federation | 49.67N | 140.12E | 58 | 10.00 (ASV) | 83-99 | 316830 | N/A |  | N/A | N/A | 32.2 | 30.9 | 30.7 | 31 | 31.2667 |  | 27.7 | 28.7 | 27.6 | 28 | 28
Russia |  | TUNGOKOCEN | TUNGOKOCEN, Russian Federation | 53.53N | 115.62E | 811 | 9.00 (YAK) | 82-06 | 306640 | N/A |  | N/A | N/A | 28 | 28.5 | 27.4 | 28 | 27.9667 |  | 25.7 | 26.5 | 24.7 | 26 | 25.6333
Russia |  | TUNKA | TUNKA, Russian Federation | 51.73N | 102.53E | 721 | 8.00 (ASE) | 82-06 | 308110 | -39 |  | -45.4 | 35.6 | 29.3 | 29.9 | 27.9 | 29 | 29.0333 |  | 26.3 | 27.4 | 25.5 | 26 | 26.4
Russia |  | TURA | TURA, Russian Federation | 64.27N | 100.23E | 168 | 7.00 (ASN) | 82-06 | 245070 | -51.2 |  | -58.1 | 33.9 | 30.3 | 31 | 27.3 | 30 | 29.5333 |  | 27.6 | 29 | 24.6 | 27 | 27.0667
Russia |  | TURINSK | TURINSK, Russian Federation | 58.05N | 63.68E | 71 | 5.00 (EKT) | 82-06 | 282550 | -35.5 |  | -44.4 | 38.8 | 31.8 | 31.8 | 30.3 | 31 | 31.3 |  | 29.4 | 29.5 | 26.3 | 28 | 28.4
Russia |  | TUROCAK | TUROCAK, Russian Federation | 52.27N | 87.17E | 327 | 6.00 (ASR) | 82-06 | 360610 | -37.8 |  | -47.9 | 38.2 | 31.6 | 33.1 | 32.7 | 32 | 32.4667 |  | 29.2 | 30.5 | 28.9 | 30 | 29.5333
Russia |  | TURUHANSK | TURUHANSK, Russian Federation | 65.78N | 87.93E | 38 | 7.00 (ASN) | 82-06 | 234720 | -48.9 |  | -58.6 | 35.3 | 30 | 29.1 | 27.5 | 29 | 28.8667 |  | 26.9 | 27.1 | 23.4 | 26 | 25.8
Russia |  | TVER | TVER, Russian Federation | 56.90N | 35.88E | 146 | 3.00 (RUS) | 82-06 | 274020 | -30 |  | -39.1 | 37.3 | 30.5 | 31.5 | 28.5 | 30 | 30.1667 |  | 27.8 | 28.9 | 26.2 | 28 | 27.6333
Russia |  | TYNDA | TYNDA, Russian Federation | 55.18N | 124.67E | 528 | 9.00 (YAK) | 82-06 | 304990 | -43.3 |  | -50.4 | 35.2 | 29.7 | 31.5 | 29 | 30 | 30.0667 |  | 27.6 | 29.2 | 26.2 | 28 | 27.6667
Russia |  | UAKIT | UAKIT, Russian Federation | 55.47N | 113.62E | 1097 | 8.00 (ASE) | 82-06 | 304550 | -40.8 |  | -48.2 | 32.9 | 25.8 | 27.6 | 26 | 26 | 26.4667 |  | 23.8 | 25.1 | 23 | 24 | 23.9667
Russia |  | UEGA | UEGA, Russian Federation | 60.72N | 142.78E | 398 | 10.00 (ASV) | 82-02 | 249820 | -45.1 |  | -51.7 | 34.2 | 28.5 | 30 | 25.2 | 28 | 27.9 |  | 25.5 | 26.5 | 23.1 | 25 | 25.0333
Russia |  | UFA | UFA, Russian Federation | 54.72N | 55.83E | 104 | 5.00 (EKT) | 82-06 | 287220 | -35.4 |  | -44.3 | 39.9 | 32.8 | 33 | 32.2 | 33 | 32.6667 |  | 30.2 | 30.9 | 28.8 | 30 | 29.9667
Russia |  | UHTA | UHTA, Russian Federation | 63.55N | 53.82E | 137 | 3.00 (RUS) | 82-06 | 236060 | -38.2 |  | -48.5 | 37 | 29.6 | 31.2 | 26.4 | 29 | 29.0667 |  | 26.9 | 28.5 | 23.3 | 26 | 26.2333
Russia |  | UJAR | UJAR, Russian Federation | 55.80N | 94.33E | 375 | 7.00 (ASN) | 82-01 | 295760 | N/A |  | N/A | N/A | 28.6 | 30.4 | 29.1 | 29 | 29.3667 |  | 26.5 | 28.2 | 26 | 27 | 26.9
Russia |  | ULAN-UDE | ULAN-UDE, Russian Federation | 51.83N | 107.60E | 515 | 8.00 (ASE) | 82-06 | 308230 | -38.1 |  | -46.6 | 40.3 | 33.2 | 33.9 | 31.3 | 33 | 32.8 |  | 30.4 | 30.9 | 28.8 | 30 | 30.0333
Russia |  | ULETY | ULETY, Russian Federation | 51.35N | 112.47E | 743 | 9.00 (YAK) | 82-06 | 308460 | -35 |  | -43.1 | 38 | 31.5 | 32.6 | 30.1 | 31 | 31.4 |  | 28.6 | 29.4 | 26.7 | 28 | 28.2333
Russia |  | ULYANOVSK | ULYANOVSK, Russian Federation | 54.32N | 48.33E | 127 | 3.00 (RUS) | 90-06 | 277860 | -31 |  | -40.4 | 38.7 | 32.6 | 32.6 | 32.1 | 32 | 32.4333 |  | 29.8 | 30.3 | 28.9 | 30 | 29.6667
Russia |  | UMBA | UMBA, Russian Federation | 66.68N | 34.35E | 40 | 3.00 (RUS) | 82-06 | 223240 | -30.6 |  | -41.7 | 29.6 | 24.2 | 25.1 | 23.1 | 24 | 24.1333 |  | 21.4 | 22.8 | 20.7 | 22 | 21.6333
Russia |  | UNAHA | UNAHA, Russian Federation | 55.03N | 126.80E | 448 | 9.00 (YAK) | 82-94 | 311990 | -46.4 |  | -50.4 | 33.7 | 29.5 | 30.3 | 27.6 | 29 | 29.1333 |  | 27.5 | 28.1 | 25.2 | 27 | 26.9333
Russia |  | URJUPINSK | URJUPINSK, Russian Federation | 50.80N | 42.00E | 110 | 3.00 (RUS) | 82-01 | 342400 | -27.5 |  | -37.8 | 41.9 | 34.1 | 35.6 | 33.6 | 34 | 34.4333 |  | 31.1 | 32.6 | 31.3 | 32 | 31.6667
Russia |  | URMI | URMI, Russian Federation | 49.40N | 133.23E | 198 | 10.00 (ASV) | 82-06 | 316240 | -39.7 |  | -44.9 | 38 | 31.4 | 31.6 | 30.9 | 31 | 31.3 |  | 28.9 | 29.2 | 28.4 | 29 | 28.8333
Russia |  | URUP | URUP, Russian Federation | 46.20N | 150.50E | 76 | 11.00 (MAG) | 82-97 | 321860 | -11.8 |  | -16.4 | 26.9 | 14.5 | 20.6 | 20.9 | 19 | 18.6667 |  | 11.1 | 15.4 | 18 | 15 | 14.8333
Russia |  | UST-BARGUZIN | UST-BARGUZIN, Russian Federation | 53.42N | 109.02E | 461 | 8.00 (ASE) | 82-06 | 306350 | -36.7 |  | -46 | 35.3 | 26.7 | 29.1 | 27.9 | 28 | 27.9 |  | 22.7 | 26 | 24.4 | 24 | 24.3667
Russia |  | UST-CILMA | UST-CILMA, Russian Federation | 65.43N | 52.27E | 68 | 3.00 (RUS) | 82-06 | 234050 | -39.3 |  | -50.8 | 34.8 | 27.9 | 30.2 | 25.4 | 28 | 27.8333 |  | 25.6 | 27.7 | 22.2 | 25 | 25.1667
Russia |  | UST-ILIMSK | UST-ILIMSK, Russian Federation | 58.20N | 102.75E | 401 | 8.00 (ASE) | 82-01 | 301170 | -40.5 |  | -51.4 | 35 | 29.8 | 32 | 27.7 | 30 | 29.8333 |  | 27.5 | 29.2 | 25.5 | 27 | 27.4
Russia |  | UST-ISIM | UST-ISIM, Russian Federation | 57.72N | 71.18W | 56 | 5.00 (EKT) | 82-06 | 283820 | -39.6 |  | -49.5 | 36.1 | 30.9 | 31.3 | 28.5 | 30 | 30.2333 |  | 28.8 | 28.7 | 25.8 | 28 | 27.7667
Russia |  | UST-JUDOMA | UST-JUDOMA, Russian Federation | 59.18N | 135.15E | 212 | 10.00 (ASV) | 82-06 | 310540 | -53.3 |  | -58 | 36.7 | 31 | 32.5 | 28.9 | 31 | 30.8 |  | 28.7 | 30.2 | 26.5 | 28 | 28.4667
Russia |  | UST-KAMCHATSK | UST-KAMCHATSK, Russian Federation | 56.22N | 162.47E | 30 | 12.00 (KAM) | 82-06 | 324080 | -33.8 |  | -39.9 | 30.8 | 22 | 24 | 21.5 | 23 | 22.5 |  | 18.2 | 20.5 | 19 | 19 | 19.2333
Russia |  | UST-KULOM | UST-KULOM, Russian Federation | 61.68N | 53.68E | 144 | 3.00 (RUS) | 82-06 | 238030 | -39.3 |  | -52.9 | 36.6 | 29.7 | 30.8 | 26.3 | 29 | 28.9333 |  | 27.4 | 29.2 | 23.7 | 27 | 26.7667
Russia |  | UST-KUT | UST-KUT, Russian Federation | 56.87N | 105.70E | 669 | 8.00 (ASE) | 82-00 | 303200 | -38.9 |  | -49.1 | 35.9 | 29.2 | 30.6 | 27.8 | 29 | 29.2 |  | 26 | 28.4 | 25.1 | 27 | 26.5
Russia |  | UST-MAJA | UST-MAJA, Russian Federation | 60.38N | 134.45E | 170 | 10.00 (ASV) | 82-06 | 249660 | -53.2 |  | -58 | 35.1 | 30 | 31.8 | 28.4 | 30 | 30.0667 |  | 27.7 | 29.8 | 25.9 | 28 | 27.8
Russia |  | UST-NJUKZHA | UST-NJUKZHA, Russian Federation | 56.58N | 121.48E | 426 | 9.00 (YAK) | 82-06 | 303850 | -45 |  | -51.6 | 36 | 29.6 | 32.1 | 29.5 | 30 | 30.4 |  | 27.5 | 29.6 | 26.9 | 28 | 28
Russia |  | UST-OLOJ | UST-OLOJ, Russian Federation | 66.55N | 159.42E | 127 | 12.00 (KAM) | 82-06 | 253250 | N/A |  | N/A | N/A | 28.6 | 29.1 | 25.2 | 28 | 27.6333 |  | 25.2 | 26.7 | 22 | 25 | 24.6333
Russia |  | USTORDYNSKIJ | USTORDYNSKIJ, Russian Federation | 52.82N | 104.77E | 526 | 8.00 (ASE) | 82-94 | 307130 | -39.2 |  | -46.7 | 36.8 | 31.4 | 30 | 29 | 30 | 30.1333 |  | 28.4 | 28.2 | 26.2 | 28 | 27.6
Russia |  | UST-UDA | UST-UDA, Russian Federation | 54.17N | 103.02E | 427 | 8.00 (ASE) | 82-98 | 305140 | -39.7 |  | -48.8 | 36.4 | 30.7 | 31.1 | 28.6 | 30 | 30.1333 |  | 27.5 | 29.3 | 26.2 | 28 | 27.6667
Russia |  | UST-UMALTA | UST-UMALTA, Russian Federation | 51.63N | 133.32E | 384 | 10.00 (ASV) | 82-06 | 314740 | -45.1 |  | -50.8 | 38 | 31 | 31.6 | 29.3 | 31 | 30.6333 |  | 28 | 29.4 | 26.7 | 28 | 28.0333
Russia |  | UST-USA | UST-USA, Russian Federation | 65.97N | 56.92E | 78 | 3.00 (RUS) | 82-06 | 234120 | -40.5 |  | -49.7 | 34.8 | 27.2 | 30.6 | 25 | 28 | 27.6 |  | 24.6 | 27.4 | 21.9 | 25 | 24.6333
Russia |  | UST-VOJAMPOLKA | UST-VOJAMPOLKA, Russian Federation | 58.50N | 159.17E | 7 | 12.00 (KAM) | 82-06 | 322520 | -35.7 |  | -40.4 | 26.1 | 17 | 20 | 19.6 | 19 | 18.8667 |  | 14 | 16.8 | 16.8 | 16 | 15.8667
Russia |  | USUGLI | USUGLI, Russian Federation | 52.65N | 115.17E | 646 | 9.00 (YAK) | 82-06 | 307640 | -43.7 |  | -50.6 | 37 | 30.5 | 31.1 | 29.7 | 30 | 30.4333 |  | 28 | 28.6 | 26.7 | 28 | 27.7667
Russia |  | UYBAT | UYBAT, Russian Federation | 53.72N | 90.37E | 525 | 7.00 (ASN) | 82-06 | 298640 | -34.4 |  | -43.3 | 35.5 | 30 | 31 | 29.1 | 30 | 30.0333 |  | 27.7 | 28.2 | 26.5 | 27 | 27.4667
Russia |  | UZUR | UZUR, Russian Federation | 55.30N | 89.82E | 387 | 7.00 (ASN) | 82-06 | 296530 | -37.9 |  | -49.1 | 35.6 | 29.1 | 29.6 | 28.6 | 29 | 29.1 |  | 26.5 | 27.4 | 25.7 | 27 | 26.5333
Russia |  | VANZIL-KYNAK | VANZIL-KYNAK, Russian Federation | 60.35N | 84.08E | 99 | 7.00 (ASN) | 82-06 | 239660 | -44.4 |  | -54.6 | 34.5 | 30.6 | 30.5 | 28.6 | 30 | 29.9 |  | 28 | 28.6 | 25.5 | 27 | 27.3667
Russia |  | VELIKIE LUKI | VELIKIE LUKI, Russian Federation | 56.35N | 30.62E | 106 | 3.00 (RUS) | 82-01 | 264770 | -28.1 |  | -39.2 | 34.8 | 28.9 | 30.4 | 28.1 | 29 | 29.1333 |  | 26.7 | 27.6 | 26.2 | 27 | 26.8333
Russia |  | VELSK | VELSK, Russian Federation | 61.08N | 42.07E | 91 | 3.00 (RUS) | 84-06 | 228670 | -35.5 |  | -45.2 | 36.9 | 31.4 | 31.3 | 28.2 | 30 | 30.3 |  | 28.6 | 28.2 | 25.2 | 27 | 27.3333
Russia |  | VERESCAGINO | VERESCAGINO, Russian Federation | 58.08N | 54.68E | 228 | 5.00 (EKT) | 82-06 | 282160 | -33.3 |  | -43.9 | 35.7 | 30.3 | 31 | 28.8 | 30 | 30.0333 |  | 28 | 29.3 | 25.9 | 28 | 27.7333
Russia |  | VERHNEE PENZINO | VERHNEE PENZINO, Russian Federation | 64.22N | 164.23E | 326 | 12.00 (KAM) | 82-06 | 255380 | -51.7 |  | -58.4 | 32.6 | 26.1 | 27.1 | 24.2 | 26 | 25.8 |  | 23.6 | 24.5 | 20.9 | 23 | 23
Russia |  | VERHNEIMBATSK | VERHNEIMBATSK, Russian Federation | 63.15N | 87.95E | 46 | 7.00 (ASN) | 82-06 | 236780 | N/A |  | N/A | N/A | 30 | 29.9 | 28.1 | 29 | 29.3333 |  | 27.3 | 27.9 | 24.4 | 27 | 26.5333
Russia |  | VERHNIJ BASKUNCAK | VERHNIJ BASKUNCAK, Russian Federation | 48.22N | 46.73E | 34 | 5.00 (EKT) | 82-06 | 345790 | -24.4 |  | -36.7 | 42.6 | 37.7 | 38 | 37.1 | 38 | 37.6 |  | 34.7 | 36 | 34.9 | 35 | 35.2
Russia |  | VERHNIJ UFALEJ | VERHNIJ UFALEJ, Russian Federation | 56.08N | 60.30E | 401 | 5.00 (EKT) | 83-06 | 285410 | -34.6 |  | -42.8 | 35.9 | 31 | 30.6 | 28.8 | 30 | 30.1333 |  | 28.3 | 28.2 | 25.9 | 27 | 27.4667
Russia |  | VERHNJAJA TOJMA | VERHNJAJA TOJMA, Russian Federation | 62.23N | 45.02E | 58 | 3.00 (RUS) | 82-02 | 227780 | -37.8 |  | -48 | 34.9 | 30.5 | 30.5 | 26.6 | 29 | 29.2 |  | 27.4 | 27.8 | 24.3 | 27 | 26.5
Russia |  | VERHNJAJA TOM | VERHNJAJA TOM, Russian Federation | 51.35N | 130.43E | 261 | 9.00 (YAK) | 82-98 | 314590 | -44.6 |  | -51.4 | 34.8 | 30.6 | 31.6 | 28.9 | 30 | 30.3667 |  | 28.6 | 29.6 | 26.6 | 28 | 28.2667
Russia |  | VERHOTUR`E | VERHOTUR`E, Russian Federation | 58.87N | 60.78E | 126 | 5.00 (EKT) | 82-06 | 281440 | -37.3 |  | -43.8 | 35.9 | 31.2 | 31.6 | 29.5 | 31 | 30.7667 |  | 28.8 | 29.2 | 25.7 | 28 | 27.9
Russia |  | VESELAJA GORKA | VESELAJA GORKA, Russian Federation | 52.28N | 135.80E | 201 | 10.00 (ASV) | 82-06 | 314180 | -34.4 |  | -39.9 | 36.6 | 31 | 31.9 | 30.7 | 31 | 31.2 |  | 28.3 | 29.3 | 27.5 | 28 | 28.3667
Russia |  | VESLJANA | VESLJANA, Russian Federation | 62.98N | 50.90E | 103 | 3.00 (RUS) | 82-06 | 237010 | -42.6 |  | -52.3 | 33.5 | 30.3 | 30.5 | 26.2 | 29 | 29 |  | 27.7 | 28.1 | 23.7 | 27 | 26.5
Russia |  | VIKULOVO | VIKULOVO, Russian Federation | 56.82N | 70.62E | 70 | 5.00 (EKT) | 82-06 | 284810 | -36.1 |  | -47.2 | 39.7 | 31.9 | 31.9 | 28.5 | 31 | 30.7667 |  | 29.9 | 29.4 | 25.9 | 28 | 28.4
Russia |  | VILJUJSK | VILJUJSK, Russian Federation | 63.77N | 121.62E | 111 | 9.00 (YAK) | 82-06 | 246410 | -51.1 |  | -58.9 | 38.2 | 31.4 | 33.7 | 29.5 | 32 | 31.5333 |  | 28.9 | 31.4 | 26.9 | 29 | 29.0667
Russia |  | VITIM | VITIM, Russian Federation | 59.45N | 112.58E | 190 | 9.00 (YAK) | 82-06 | 300540 | -50 |  | -59 | 38.9 | 31.2 | 33.1 | 29.6 | 31 | 31.3 |  | 28.7 | 30.3 | 26.4 | 28 | 28.4667
Russia |  | VJAZMA | VJAZMA, Russian Federation | 55.17N | 34.40E | 251 | 3.00 (RUS) | 82-06 | 266950 | -29.2 |  | -37.3 | 34.3 | 28.7 | 30.2 | 27.9 | 29 | 28.9333 |  | 26.4 | 27.5 | 25.6 | 27 | 26.5
Russia |  | VLADIMIR | VLADIMIR, Russian Federation | 56.12N | 40.35E | 170 | 3.00 (RUS) | 82-06 | 275320 | -29.2 |  | -39.7 | 35.3 | 30.4 | 30.3 | 28.6 | 30 | 29.7667 |  | 27.9 | 28.5 | 26.2 | 28 | 27.5333
Russia |  | VLADIVOSTOK | VLADIVOSTOK, Russian Federation | 43.12N | 131.93E | 183 | 10.00 (ASV) | 82-06 | 319600 | -27.2 |  | -37.9 | 36.4 | 28.2 | 30.8 | 30.8 | 30 | 29.9333 |  | 25 | 27.9 | 28.2 | 27 | 27.0333
Russia |  | VNUKOVO | VNUKOVO, Russian Federation | 55.58N | 37.25E | 214 | 3.00 (RUS) | 82-06 | 275185 | -27.1 |  | -35 | 35.5 | 29.8 | 30.9 | 28 | 30 | 29.5667 |  | 27.4 | 28.8 | 26 | 27 | 27.4
Russia |  | VOLCIHA | VOLCIHA, Russian Federation | 52.02N | 80.37E | 208 | 6.00 (ASR) | 82-06 | 360220 | -39 |  | -49.2 | 40.5 | 33.3 | 34.5 | 34.5 | 34 | 34.1 |  | 30.8 | 31.6 | 31.4 | 31 | 31.2667
Russia |  | VOLGOGRAD | VOLGOGRAD, Russian Federation | 48.78N | 44.37E | 134 | 3.00 (RUS) | 82-06 | 345600 | -24.2 |  | -34 | 41.5 | 35.5 | 36.2 | 35.8 | 36 | 35.8333 |  | 32.2 | 34 | 33.1 | 33 | 33.1
Russia |  | VOLOGDA | VOLOGDA, Russian Federation | 59.32N | 39.92E | 131 | 3.00 (RUS) | 82-06 | 270370 | -34.6 |  | -45.3 | 35.2 | 30 | 30.1 | 27.7 | 29 | 29.2667 |  | 27.2 | 28.1 | 24.8 | 27 | 26.7
Russia |  | VORKUTA | VORKUTA, Russian Federation | 67.48N | 64.02E | 172 | 3.00 (RUS) | 82-06 | 232260 | -42 |  | -49.9 | 34.5 | 25.1 | 30.1 | 22.9 | 26 | 26.0333 |  | 22 | 26.3 | 20.5 | 23 | 22.9333
Russia |  | VOROGOVO | VOROGOVO, Russian Federation | 61.03N | 89.63E | 49 | 7.00 (ASN) | 82-06 | 239730 | -45.8 |  | -57 | 35.7 | 30.5 | 31 | 28.6 | 30 | 30.0333 |  | 27.5 | 28.7 | 25.5 | 27 | 27.2333
Russia |  | VORONEZ | VORONEZ, Russian Federation | 51.65N | 39.25E | 104 | 3.00 (RUS) | 82-06 | 341220 | -26.3 |  | -37.8 | 37.1 | 31.1 | 30.9 | 31.7 | 31 | 31.2333 |  | 28.6 | 29 | 28.9 | 29 | 28.8333
Russia |  | VORONEZ | VORONEZ, Russian Federation | 51.70N | 39.22E | 149 | 3.00 (RUS) | 94-06 | 341230 | -25.3 |  | -34.6 | 39 | 31.4 | 34.4 | 32.7 | 33 | 32.8333 |  | 29.4 | 31.6 | 29.8 | 30 | 30.2667
Russia |  | VOZEGA | VOZEGA, Russian Federation | 60.47N | 40.20E | 202 | 3.00 (RUS) | 82-06 | 229540 | -31.9 |  | -43.8 | 34.7 | 29.3 | 29.7 | 26.3 | 28 | 28.4333 |  | 26.5 | 27.2 | 23.6 | 26 | 25.7667
Russia |  | VYBORG | VYBORG, Russian Federation | 60.72N | 28.73E | 13 | 3.00 (RUS) | 82-06 | 228920 | -26.9 |  | -37.9 | 33.3 | 28.2 | 28.9 | 26.9 | 28 | 28 |  | 25.2 | 26.8 | 25 | 26 | 25.6667
Russia |  | VYTEGRA | VYTEGRA, Russian Federation | 61.02N | 36.45E | 56 | 3.00 (RUS) | 82-00 | 228370 | -34.1 |  | -44.9 | 35.3 | 30.3 | 29.9 | 27 | 29 | 29.0667 |  | 27.4 | 27 | 24.3 | 26 | 26.2333
Russia |  | WLADIKAVKAZ | WLADIKAVKAZ, Russian Federation | 43.05N | 44.65E | 703 | 3.00 (RUS) | 82-06 | 372280 | -17 |  | -25 | 38.8 | 30.6 | 32.5 | 32.1 | 32 | 31.7333 |  | 27.7 | 30.1 | 29.6 | 29 | 29.1333
Russia |  | ZAMETCINO | ZAMETCINO, Russian Federation | 53.48N | 42.63E | 133 | 3.00 (RUS) | 82-06 | 278570 | -30.2 |  | -39.8 | 39 | 32.7 | 33.2 | 32.2 | 33 | 32.7 |  | 29.9 | 30.5 | 28.6 | 30 | 29.6667
Russia |  | ZAMOKTA | ZAMOKTA, Russian Federation | 52.77N | 109.97E | 1286 | 8.00 (ASE) | 82-06 | 307410 | -33 |  | -39.9 | 32.2 | 27.3 | 27.6 | 25.1 | 27 | 26.6667 |  | 24.2 | 24.7 | 22.6 | 24 | 23.8333
Russia |  | ZAVITAJA | ZAVITAJA, Russian Federation | 50.12N | 129.47E | 241 | 9.00 (YAK) | 82-06 | 315270 | -36.5 |  | -42.4 | 35 | 30.2 | 30.6 | 29.4 | 30 | 30.0667 |  | 28.2 | 28.7 | 27.3 | 28 | 28.0667
Russia |  | ZDVINSK | ZDVINSK, Russian Federation | 54.70N | 78.67E | 113 | 6.00 (ASR) | 82-06 | 297120 | -37.5 |  | -50.9 | 38 | 30.8 | 32.6 | 30.8 | 31 | 31.4 |  | 28.6 | 30.3 | 27.7 | 29 | 28.8667
Russia |  | ZEJA | ZEJA, Russian Federation | 53.70N | 127.30E | 229 | 9.00 (YAK) | 82-06 | 313000 | -37.3 |  | -43.3 | 37 | 31.1 | 32.7 | 29.8 | 31 | 31.2 |  | 29 | 30.3 | 27.2 | 29 | 28.8333
Russia |  | ZERDEVKA | ZERDEVKA, Russian Federation | 51.83N | 41.48E | 147 | 3.00 (RUS) | 90-06 | 340470 | -26.7 |  | -34.9 | 40.3 | 32.3 | 34 | 32.7 | 33 | 33 |  | 29.8 | 31.4 | 29.6 | 30 | 30.2667
Russia |  | ZHIGALOVO | ZHIGALOVO, Russian Federation | 54.80N | 105.22E | 426 | 8.00 (ASE) | 82-06 | 305210 | -44.5 |  | -54.2 | 41.8 | 30.9 | 32.7 | 30.2 | 31 | 31.2667 |  | 28.1 | 30.2 | 27.2 | 29 | 28.5
Russia |  | ZHIGANSK | ZHIGANSK, Russian Federation | 66.77N | 123.40E | 92 | 9.00 (YAK) | 82-06 | 243430 | -52.4 |  | -60.7 | 34.5 | 28.1 | 30.4 | 26 | 28 | 28.1667 |  | 24.8 | 28.2 | 23.4 | 25 | 25.4667
Russia |  | ZILAIR | ZILAIR, Russian Federation | 52.22N | 57.40E | 521 | 5.00 (EKT) | 83-06 | 350260 | -34.1 |  | -46.1 | 36 | 31.9 | 30.6 | 29.6 | 31 | 30.7 |  | 29.3 | 28.5 | 27.5 | 28 | 28.4333
Russia |  | ZILOVO | ZILOVO, Russian Federation | 53.07N | 117.48E | 708 | 9.00 (YAK) | 82-95 | 306690 | -37.7 |  | -45.6 | 35 | 28.9 | 29.9 | 27.6 | 29 | 28.8 |  | 26.6 | 27.1 | 25 | 26 | 26.2333
Russia |  | ZIMA | ZIMA, Russian Federation | 53.93N | 102.05E | 458 | 8.00 (ASE) | 82-06 | 306030 | -38.4 |  | -47.1 | 37.1 | 30.8 | 31.9 | 29.2 | 31 | 30.6333 |  | 28 | 29.7 | 26.9 | 28 | 28.2
Russia |  | ZIZGIN | ZIZGIN, Russian Federation | 65.20N | 36.82E | 17 | 3.00 (RUS) | 82-06 | 224380 | -23.5 |  | -36.1 | 28.7 | 22.6 | 22.9 | 19 | 22 | 21.5 |  | 19.5 | 20.2 | 16.8 | 19 | 18.8333
Russia |  | ZOHOVA ISLAND | ZOHOVA ISLAND, Russian Federation | 76.15N | 152.83E | 14 | 11.00 (MAG) | 82-93 | 213580 | -39.2 |  | -44.2 | 15.1 | 4.5 | 8.1 | 7.2 | 7 | 6.6 |  | 2.6 | 5.7 | 5.3 | 5 | 4.5333
Russia |  | ZOLOTOJ | ZOLOTOJ, Russian Federation | 47.32N | 138.98E | 26 | 10.00 (ASV) | 82-06 | 318290 | -24.8 |  | -33.7 | 31.2 | 20.7 | 23.4 | 25.7 | 23 | 23.2667 |  | 17.1 | 20.1 | 23.3 | 20 | 20.1667
Russia |  | ZURAVLEVKA | ZURAVLEVKA, Russian Federation | 44.75N | 134.47E | 170 | 10.00 (ASV) | 82-97 | 319420 | -39.2 |  | -47.7 | 38.5 | 30.3 | 32.9 | 33.3 | 32 | 32.1667 |  | 28.4 | 30.5 | 30.7 | 30 | 29.8667
Russia |  | ZYRJANKA | ZYRJANKA, Russian Federation | 65.73N | 150.90E | 43 | 11.00 (MAG) | 82-06 | 254000 | -50.5 |  | -55.8 | 36.7 | 30 | 31.7 | 27.4 | 30 | 29.7 |  | 27.3 | 29 | 24 | 27 | 26.7667
Saint Helena |  | ST. HELENA IS. | ST. HELENA IS., Saint Helena | 15.93S | 5.67W | 436 | 0.00 (GRW) | 82-06 | 619010 | 12.1 |  | 10 | 31.1 | 21.3 | 20.8 | 19.6 | 21 | 20.5667 |  | 20.3 | 19.3 | 18.6 | 19 | 19.4
Saint Helena |  | WIDE AWAKE FIELD (ASI) | WIDE AWAKE FIELD (ASI), Saint Helena | 7.97S | 14.40W | 79 | 0.00 (GRW) | 84-06 | 619020 | 19.4 |  | 15.1 | 32.1 | 28.9 | 28.1 | 27.2 | 28 | 28.0667 |  | 28.2 | 27.4 | 26.9 | 28 | 27.5
Saint Lucia |  | HEWANORRA INTL AIRP | HEWANORRA INTL AIRP, Saint Lucia | 13.75N | 60.95W | 10 | -4.00 (SAZ) | 83-06 | 789480 | 20 |  | 15.7 | 36.3 | 31.2 | 31.2 | 32 | 31 | 31.4667 |  | 31 | 30.8 | 31.2 | 31 | 31
Samoa |  | APIA | APIA, Samoa | 13.80S | 171.78W | 2 | -11.00 (PCM) | 82-06 | 917620 | N/A |  | N/A | N/A | 30.9 | 30.2 | 30.1 | 30 | 30.4 |  | 30.2 | 29.8 | 29.6 | 30 | 29.8667
Saudi Arabia |  | ABHA | ABHA, Saudi Arabia | 18.23N | 42.65E | 2093 | 3.00 (AFE) | 83-06 | 411120 | 2.4 |  | -2.1 | 35.2 | 31.7 | 31.9 | 31.2 | 32 | 31.6 |  | 30.8 | 30.8 | 30.4 | 31 | 30.6667
Saudi Arabia |  | AL-AHSA | AL-AHSA, Saudi Arabia | 25.30N | 49.48E | 178 | 3.00 (AFE) | 82-06 | 404200 | 3.5 |  | -0.8 | 50.7 | 47.2 | 48 | 47.2 | 47 | 47.4667 |  | 45.8 | 46.9 | 46.2 | 46 | 46.3
Saudi Arabia |  | AL-BAHA | AL-BAHA, Saudi Arabia | 20.30N | 41.65E | 1652 | 3.00 (AFE) | 83-06 | 410550 | 4.6 |  | 1.7 | 41.6 | 36.2 | 37.1 | 36.2 | 37 | 36.5 |  | 35.1 | 36 | 35.8 | 36 | 35.6333
Saudi Arabia |  | AL-JOUF | AL-JOUF, Saudi Arabia | 29.78N | 40.10E | 689 | 3.00 (AFE) | 82-06 | 403610 | -2.5 |  | -6.8 | 49.9 | 42.4 | 43 | 44 | 43 | 43.1333 |  | 40.8 | 41.2 | 42.2 | 41 | 41.4
Saudi Arabia |  | AL-MADINAH | AL-MADINAH, Saudi Arabia | 24.55N | 39.70E | 636 | 3.00 (AFE) | 82-06 | 404300 | 6.3 |  | 1.3 | 48.9 | 45.1 | 46.1 | 46.1 | 46 | 45.7667 |  | 44 | 45 | 45.1 | 45 | 44.7
Saudi Arabia |  | AL-QAISUMAH | AL-QAISUMAH, Saudi Arabia | 28.32N | 46.13E | 358 | 3.00 (AFE) | 82-06 | 403730 | 0.5 |  | -3.5 | 52.5 | 46.2 | 47.1 | 47.4 | 47 | 46.9 |  | 44.9 | 46 | 46.2 | 46 | 45.7
Saudi Arabia |  | AL-TAIF | AL-TAIF, Saudi Arabia | 21.48N | 40.55E | 1453 | 3.00 (AFE) | 83-06 | 410360 | 2.4 |  | -1.9 | 43.3 | 37.4 | 37.8 | 37.8 | 38 | 37.6667 |  | 36.4 | 36.5 | 36.3 | 36 | 36.4
Saudi Arabia |  | AL-WEJH | AL-WEJH, Saudi Arabia | 26.20N | 36.48E | 24 | 3.00 (AFE) | 82-06 | 404000 | 9.7 |  | 3.7 | 47 | 37.8 | 36 | 35.2 | 36 | 36.3333 |  | 34 | 34.1 | 34.1 | 34 | 34.0667
Saudi Arabia |  | ARAR | ARAR, Saudi Arabia | 30.90N | 41.13E | 549 | 3.00 (AFE) | 82-06 | 403570 | -1.9 |  | -7.1 | 48.3 | 42.2 | 44.1 | 44.5 | 44 | 43.6 |  | 40.7 | 42.8 | 42.9 | 42 | 42.1333
Saudi Arabia |  | BISHA | BISHA, Saudi Arabia | 19.98N | 42.63E | 1162 | 3.00 (AFE) | 83-06 | 410840 | N/A |  | N/A | N/A | 40.2 | 40.8 | 40.2 | 40 | 40.4 |  | 39.2 | 40 | 39.8 | 40 | 39.6667
Saudi Arabia |  | DHAHRAN | DHAHRAN, Saudi Arabia | 26.27N | 50.17E | 17 | 3.00 (AFE) | 82-06 | 404160 | 5.5 |  | 1.5 | 49.8 | 45.8 | 46.1 | 45.2 | 46 | 45.7 |  | 43.9 | 44.4 | 43.8 | 44 | 44.0333
Saudi Arabia |  | GASSIM | GASSIM, Saudi Arabia | 26.30N | 43.77E | 648 | 3.00 (AFE) | 82-06 | 404050 | 0.6 |  | -3.9 | 50.1 | 44.2 | 45.6 | 45.9 | 45 | 45.2333 |  | 43.1 | 44.2 | 44.6 | 44 | 43.9667
Saudi Arabia |  | GIZAN | GIZAN, Saudi Arabia | 16.88N | 42.58E | 7 | 3.00 (AFE) | 83-06 | 411400 | 17.8 |  | 12.1 | 44.4 | 39.2 | 39.1 | 39 | 39 | 39.1 |  | 38.1 | 38.1 | 37.9 | 38 | 38.0333
Saudi Arabia |  | GURIAT | GURIAT, Saudi Arabia | 31.40N | 37.28E | 504 | 3.00 (AFE) | 85-06 | 403600 | -2.9 |  | -7.9 | 47.2 | 41 | 42.2 | 42.9 | 42 | 42.0333 |  | 39.1 | 40 | 40.7 | 40 | 39.9333
Saudi Arabia |  | HAIL | HAIL, Saudi Arabia | 27.43N | 41.68E | 1002 | 3.00 (AFE) | 82-06 | 403940 | -3.4 |  | -9.5 | 47 | 41.2 | 42.2 | 42.9 | 42 | 42.1 |  | 40.1 | 41.1 | 41.9 | 41 | 41.0333
Saudi Arabia |  | JEDDAH (KING ABDUL AZIZ INTL) | JEDDAH (KING ABDUL AZIZ INTL), Saudi Arabia | 21.70N | 39.18E | 17 | 3.00 (AFE) | 83-06 | 410240 | 12.9 |  | 8.8 | 50.6 | 42.2 | 42.1 | 41.2 | 42 | 41.8333 |  | 39.8 | 40.2 | 39.8 | 40 | 39.9333
Saudi Arabia |  | KHAMIS MUSHAIT | KHAMIS MUSHAIT, Saudi Arabia | 18.30N | 42.80E | 2056 | 3.00 (AFE) | 83-06 | 411140 | 3.2 |  | -2.5 | 40.3 | 32.2 | 32.3 | 32.1 | 32 | 32.2 |  | 31.6 | 31.5 | 31.2 | 31 | 31.4333
Saudi Arabia |  | KING KHALED INT. AI | KING KHALED INT. AI, Saudi Arabia | 24.93N | 46.72E | 614 | 3.00 (AFE) | 84-06 | 404370 | 1.2 |  | -3 | 49.1 | 45 | 46 | 45.5 | 46 | 45.5 |  | 43.8 | 44.8 | 44.6 | 44 | 44.4
Saudi Arabia |  | MAKKAH | MAKKAH, Saudi Arabia | 21.43N | 39.77E | 240 | 3.00 (AFE) | 85-06 | 410300 | 12.7 |  | 6.7 | 50.3 | 46.8 | 45.8 | 45 | 46 | 45.8667 |  | 45.1 | 44.1 | 43.4 | 44 | 44.2
Saudi Arabia |  | NAJRAN | NAJRAN, Saudi Arabia | 17.62N | 44.42E | 1212 | 3.00 (AFE) | 83-06 | 411280 | 4.1 |  | -0.8 | 44.1 | 40.2 | 40.9 | 40.1 | 40 | 40.4 |  | 39.1 | 39.8 | 39.2 | 39 | 39.3667
Saudi Arabia |  | RAFHA | RAFHA, Saudi Arabia | 29.62N | 43.48E | 444 | 3.00 (AFE) | 82-06 | 403620 | -1.7 |  | -7.4 | 49.8 | 44.5 | 45.5 | 46.1 | 45 | 45.3667 |  | 42.8 | 44.1 | 44.9 | 44 | 43.9333
Saudi Arabia |  | RIYADH OBS. (O.A.P.) | RIYADH OBS. (O.A.P.), Saudi Arabia | 24.70N | 46.73E | 620 | 3.00 (AFE) | 82-06 | 404380 | 2.9 |  | -1.7 | 48 | 44.9 | 46 | 45.2 | 45 | 45.3667 |  | 43.8 | 44.3 | 44.2 | 44 | 44.1
Saudi Arabia |  | SHARORAH | SHARORAH, Saudi Arabia | 17.47N | 47.10E | 725 | 3.00 (AFE) | 83-06 | 411360 | 5 |  | -0.9 | 46.3 | 43.2 | 43.8 | 43.2 | 43 | 43.4 |  | 42.2 | 42.9 | 42.7 | 43 | 42.6
Saudi Arabia |  | TABUK | TABUK, Saudi Arabia | 28.38N | 36.60E | 768 | 3.00 (AFE) | 82-06 | 403750 | -0.8 |  | -3.7 | 45.5 | 41 | 42 | 42.7 | 42 | 41.9 |  | 39.2 | 40.2 | 41 | 40 | 40.1333
Saudi Arabia |  | TURAIF | TURAIF, Saudi Arabia | 31.68N | 38.73E | 852 | 3.00 (AFE) | 82-06 | 403560 | -3.8 |  | -7.9 | 45.7 | 39.2 | 41.2 | 42 | 41 | 40.8 |  | 37.2 | 39.2 | 40.1 | 39 | 38.8333
Saudi Arabia |  | YENBO | YENBO, Saudi Arabia | 24.13N | 38.07E | 10 | 3.00 (AFE) | 82-06 | 404390 | 8.7 |  | 5.5 | 50.9 | 45.2 | 45.2 | 45.7 | 45 | 45.3667 |  | 42.9 | 42.9 | 42.9 | 43 | 42.9
Senegal |  | DAKAR/YOFF | DAKAR/YOFF, Senegal | 14.73N | 17.50W | 24 | 0.00 (GRW) | 82-06 | 616410 | 14.7 |  | 10.7 | 42 | 30.8 | 31.2 | 31.2 | 31 | 31.0667 |  | 29.8 | 30.2 | 30.5 | 30 | 30.1667
Senegal |  | KAOLACK | KAOLACK, Senegal | 14.13N | 16.07W | 7 | 0.00 (GRW) | 82-06 | 616790 | 14.2 |  | 8.4 | 45.6 | 40.7 | 37.3 | 35.6 | 38 | 37.8667 |  | 38.4 | 35.7 | 34.4 | 36 | 36.1667
Senegal |  | LINGUERE | LINGUERE, Senegal | 15.38N | 15.12W | 21 | 0.00 (GRW) | 82-06 | 616270 | N/A |  | N/A | N/A | 43.5 | 39.8 | 37.1 | 40 | 40.1333 |  | 41.5 | 37.9 | 36 | 38 | 38.4667
Senegal |  | MATAM | MATAM, Senegal | 15.65N | 13.25W | 17 | 0.00 (GRW) | 82-06 | 616300 | N/A |  | N/A | N/A | 44.4 | 40.8 | 39 | 41 | 41.4 |  | 42.8 | 39.2 | 37.5 | 40 | 39.8333
Senegal |  | SAINT-LOUIS | SAINT-LOUIS, Senegal | 16.05N | 16.45W | 4 | 0.00 (GRW) | 82-06 | 616000 | 11.8 |  | 8.7 | 45.8 | 35.2 | 33.2 | 33.9 | 34 | 34.1 |  | 32 | 31.8 | 32.4 | 32 | 32.0667
Senegal |  | TAMBACOUNDA | TAMBACOUNDA, Senegal | 13.77N | 13.68W | 50 | 0.00 (GRW) | 82-06 | 616870 | 13.5 |  | 5.1 | 47.5 | 40.3 | 36.3 | 34.2 | 37 | 36.9333 |  | 39 | 34.7 | 32.9 | 36 | 35.5333
Senegal |  | ZIGUINCHOR | ZIGUINCHOR, Senegal | 12.55N | 16.27W | 23 | 0.00 (GRW) | 82-06 | 616950 | 13.2 |  | 7.5 | 42.5 | 36.7 | 33.9 | 33.4 | 35 | 34.6667 |  | 35 | 32.9 | 32.2 | 33 | 33.3667
Serbia |  | BANATSKI KARLOVAC | BANATSKI KARLOVAC, Serbia | 45.05N | 21.03E | 91 | 1.00 (EUW) | 93-06 | 131800 | -14.9 |  | -24.6 | 39.9 | 34.2 | 35 | 36 | 35 | 35.0667 |  | 32.2 | 32.9 | 33.5 | 33 | 32.8667
Serbia |  | BEOGRAD | BEOGRAD, Serbia | 44.80N | 20.47E | 132 | 1.00 (EUW) | 82-06 | 132740 | -11.6 |  | -17.8 | 41.5 | 34.2 | 35.3 | 36.5 | 35 | 35.3333 |  | 32.1 | 33.3 | 34.2 | 33 | 33.2
Serbia |  | BEOGRAD/SURCIN | BEOGRAD/SURCIN, Serbia | 44.82N | 20.28E | 99 | 1.00 (EUW) | 82-06 | 132720 | -15 |  | -26.6 | 41.9 | 34.1 | 35.9 | 36.8 | 36 | 35.6 |  | 31.9 | 33.2 | 34 | 33 | 33.0333
Serbia |  | CRNI VRH | CRNI VRH, Serbia | 44.12N | 21.95E | 1039 | 1.00 (EUW) | 82-06 | 132890 | -17.3 |  | -23.3 | 36.7 | 26.8 | 30.1 | 29.6 | 29 | 28.8333 |  | 24.5 | 26.8 | 27.2 | 26 | 26.1667
Serbia |  | CUPRIJA | CUPRIJA, Serbia | 43.93N | 21.38E | 125 | 1.00 (EUW) | 82-06 | 133840 | -16.7 |  | -26.6 | 44.2 | 34.6 | 37.1 | 37.4 | 36 | 36.3667 |  | 32.1 | 34.3 | 34.7 | 34 | 33.7
Serbia |  | DIMITROVGRAD | DIMITROVGRAD, Serbia | 43.02N | 22.75E | 450 | 1.00 (EUW) | 82-06 | 133970 | -17.2 |  | -27.7 | 40.9 | 32.3 | 35 | 35.2 | 34 | 34.1667 |  | 29.9 | 32.1 | 32.7 | 32 | 31.5667
Serbia |  | KIKINDA | KIKINDA, Serbia | 45.85N | 20.47E | 82 | 1.00 (EUW) | 82-06 | 131740 | -14.4 |  | -24.7 | 40.1 | 34.2 | 34.4 | 35.7 | 35 | 34.7667 |  | 31.6 | 32.8 | 33.4 | 33 | 32.6
Serbia |  | KOPAONIK | KOPAONIK, Serbia | 43.28N | 20.80E | 1713 | 1.00 (EUW) | 82-06 | 133780 | -18.6 |  | -25.9 | 28.6 | 21.7 | 24.7 | 24.3 | 24 | 23.5667 |  | 19.6 | 22.1 | 22 | 21 | 21.2333
Serbia |  | KRALJEVO | KRALJEVO, Serbia | 43.70N | 20.70E | 217 | 1.00 (EUW) | 82-06 | 133760 | -14.9 |  | -23.7 | 40.7 | 33.1 | 35.9 | 35.6 | 35 | 34.8667 |  | 30.8 | 32.7 | 32.9 | 32 | 32.1333
Serbia |  | KRUSEVAC | KRUSEVAC, Serbia | 43.57N | 21.35E | 167 | 1.00 (EUW) | 82-06 | 133830 | -16.1 |  | -25.4 | 42.9 | 34.1 | 36.3 | 37.1 | 36 | 35.8333 |  | 32.2 | 33.7 | 34.1 | 33 | 33.3333
Serbia |  | LESKOVAC | LESKOVAC, Serbia | 42.98N | 21.95E | 232 | 1.00 (EUW) | 82-06 | 133890 | -17.2 |  | -29.8 | 43.2 | 33.9 | 37 | 36.8 | 36 | 35.9 |  | 31.6 | 33.8 | 34.1 | 33 | 33.1667
Serbia |  | LOZNICA | LOZNICA, Serbia | 44.55N | 19.23E | 122 | 1.00 (EUW) | 82-06 | 132620 | -13.9 |  | -22.6 | 41 | 33.7 | 35 | 36.3 | 35 | 35 |  | 31.5 | 32.7 | 33.4 | 33 | 32.5333
Serbia |  | NEGOTIN | NEGOTIN, Serbia | 44.23N | 22.55E | 44 | 1.00 (EUW) | 82-06 | 132950 | -16.6 |  | -30.6 | 41.6 | 33.8 | 35.6 | 35.8 | 35 | 35.0667 |  | 31.3 | 33.4 | 33.7 | 33 | 32.8
Serbia |  | NIS | NIS, Serbia | 43.33N | 21.90E | 202 | 1.00 (EUW) | 82-06 | 133880 | -14.3 |  | -24.8 | 43.9 | 34.4 | 37.5 | 36.9 | 36 | 36.2667 |  | 31.9 | 34.5 | 34.4 | 34 | 33.6
Serbia |  | NOVI SAD RIMSKI SAN | NOVI SAD RIMSKI SAN, Serbia | 45.33N | 19.85E | 87 | 1.00 (EUW) | 86-06 | 131680 | -15.5 |  | -25.7 | 40.2 | 33.8 | 34.7 | 36 | 35 | 34.8333 |  | 31.6 | 32.7 | 33.4 | 33 | 32.5667
Serbia |  | PALIC | PALIC, Serbia | 46.10N | 19.77E | 105 | 1.00 (EUW) | 82-06 | 130670 | -15.3 |  | -25.6 | 40.9 | 33.8 | 33.7 | 35.2 | 34 | 34.2333 |  | 31.3 | 32.3 | 32.7 | 32 | 32.1
Serbia |  | PEC | PEC, Serbia | 42.67N | 20.30E | 499 | 1.00 (EUW) | 82-99 | 134730 | -12.9 |  | -25.1 | 39.6 | 31.1 | 34 | 33 | 33 | 32.7 |  | 28.4 | 31.2 | 31 | 30 | 30.2
Serbia |  | PLEVLJA | PLEVLJA, Serbia | 43.35N | 19.35E | 788 | 1.00 (EUW) | 82-06 | 133630 | N/A |  | N/A | N/A | 30.5 | 32.1 | 32.7 | 32 | 31.7667 |  | 28.1 | 29.9 | 30 | 29 | 29.3333
Serbia |  | PODGORICA | PODGORICA, Serbia | 42.35N | 19.25E | 44 | 1.00 (EUW) | 93-06 | 134624 | -5.9 |  | -10.3 | 42.3 | 36.1 | 37.2 | 38.6 | 37 | 37.3 |  | 34.1 | 36 | 36.2 | 35 | 35.4333
Serbia |  | PODGORICA/GOLUBOVCI | PODGORICA/GOLUBOVCI, Serbia | 42.37N | 19.25E | 33 | 1.00 (EUW) | 82-06 | 134620 | -6.5 |  | -11.9 | 41.5 | 34.4 | 37.1 | 37.5 | 36 | 36.3333 |  | 32.2 | 35.7 | 35.7 | 35 | 34.5333
Serbia |  | PRISTINA | PRISTINA, Serbia | 42.65N | 21.15E | 576 | 1.00 (EUW) | 82-99 | 134810 | -16 |  | -26.1 | 40.2 | 31.7 | 34.6 | 34.4 | 34 | 33.5667 |  | 29.8 | 31.9 | 32.2 | 31 | 31.3
Serbia |  | PRIZREN | PRIZREN, Serbia | 42.22N | 20.73E | 403 | 1.00 (EUW) | 82-99 | 134770 | -12.1 |  | -20.6 | 40.3 | 33.6 | 36.9 | 35.5 | 35 | 35.3333 |  | 31.1 | 33.8 | 33.2 | 33 | 32.7
Serbia |  | SJENICA | SJENICA, Serbia | 43.28N | 20.00E | 1039 | 1.00 (EUW) | 82-06 | 133690 | -23.1 |  | -39 | 36.9 | 28.1 | 30.8 | 30.8 | 30 | 29.9 |  | 26.1 | 28.2 | 28.1 | 27 | 27.4667
Serbia |  | SMEDEREVSKA PALANKA | SMEDEREVSKA PALANKA, Serbia | 44.37N | 20.95E | 122 | 1.00 (EUW) | 82-06 | 132790 | -15.8 |  | -26 | 43.1 | 33.8 | 35.9 | 36.7 | 35 | 35.4667 |  | 31.7 | 33.5 | 34 | 33 | 33.0667
Serbia |  | SOMBOR | SOMBOR, Serbia | 45.77N | 19.15E | 89 | 1.00 (EUW) | 82-06 | 131600 | -15.5 |  | -26.2 | 39.3 | 33.7 | 34.6 | 35.8 | 35 | 34.7 |  | 31.5 | 32.9 | 33.1 | 33 | 32.5
Serbia |  | SREMSKA MITROVICA | SREMSKA MITROVICA, Serbia | 45.10N | 19.55E | 83 | 1.00 (EUW) | 82-06 | 132660 | -15.5 |  | -25.3 | 40.3 | 33.4 | 34.3 | 35.3 | 34 | 34.3333 |  | 31.3 | 32.4 | 32.7 | 32 | 32.1333
Serbia |  | TIVAT | TIVAT, Serbia | 42.40N | 18.73E | 5 | 1.00 (EUW) | 82-06 | 134570 | -4.9 |  | -8.3 | 39.4 | 34 | 35.3 | 35.3 | 35 | 34.8667 |  | 31.9 | 33.8 | 33.8 | 33 | 33.1667
Serbia |  | VALJEVO | VALJEVO, Serbia | 44.32N | 19.92E | 177 | 1.00 (EUW) | 82-06 | 132690 | -15.3 |  | -23.6 | 41.9 | 33.3 | 34.9 | 36.2 | 35 | 34.8 |  | 31.5 | 32.8 | 33.5 | 33 | 32.6
Serbia |  | VELIKO GRADISTE | VELIKO GRADISTE, Serbia | 44.75N | 21.52E | 84 | 1.00 (EUW) | 82-06 | 132850 | -14.6 |  | -24.3 | 41.6 | 33.9 | 35.5 | 36.4 | 35 | 35.2667 |  | 31.3 | 33.1 | 33.7 | 33 | 32.7
Serbia |  | VRANJE | VRANJE, Serbia | 42.55N | 21.92E | 434 | 1.00 (EUW) | 82-06 | 134890 | -14.9 |  | -23.1 | 41.3 | 32.9 | 35.3 | 35.5 | 35 | 34.5667 |  | 30.5 | 32.9 | 33.1 | 32 | 32.1667
Serbia |  | VRSAC | VRSAC, Serbia | 45.15N | 21.32E | 85 | 1.00 (EUW) | 82-06 | 131830 | -15.9 |  | -27.6 | 40.4 | 33.2 | 34.4 | 35.7 | 34 | 34.4333 |  | 30.9 | 32.6 | 33.2 | 32 | 32.2333
Serbia |  | ZLATIBOR | ZLATIBOR, Serbia | 43.73N | 19.72E | 1029 | 1.00 (EUW) | 82-06 | 133670 | -16.6 |  | -22.6 | 35.2 | 28 | 30.7 | 30.7 | 30 | 29.8 |  | 26.3 | 28.1 | 28.2 | 28 | 27.5333
Serbia |  | ZRENJANIN | ZRENJANIN, Serbia | 45.37N | 20.42E | 82 | 1.00 (EUW) | 82-06 | 131730 | -15.5 |  | -26.3 | 40.3 | 34.3 | 34.6 | 35.7 | 35 | 34.8667 |  | 32.1 | 32.8 | 33.4 | 33 | 32.7667
Seychelles |  | SEYCHELLES INTERNAT | SEYCHELLES INTERNAT, Seychelles | 4.67S | 55.52E | 3 | 4.00 (ARN) | 82-06 | 639800 | 20.2 |  | 13.9 | 39.2 | 30.3 | 29.2 | 29.2 | 30 | 29.5667 |  | 29.8 | 28.8 | 28.8 | 29 | 29.1333
Singapore |  | SINGAPORE/CHANGI AI | SINGAPORE/CHANGI AI, Singapore | 1.37N | 103.98E | 16 | 7.00 (SEA) | 82-06 | 486980 | 21.8 |  | 20.3 | 37 | 33.2 | 32.5 | 32.8 | 33 | 32.8333 |  | 32.4 | 32 | 32 | 32 | 32.1333
Slovakia |  | BRATISLAVA-LETISKO | BRATISLAVA-LETISKO, Slovakia | 48.20N | 17.20E | 134 | 1.00 (EUW) | 82-06 | 118160 | -14.8 |  | -25.2 | 38.5 | 32.5 | 34.1 | 34.5 | 34 | 33.7 |  | 29.9 | 32 | 32 | 31 | 31.3
Slovakia |  | CHOPOK | CHOPOK, Slovakia | 48.98N | 19.60E | 2007 | 1.00 (EUW) | 82-06 | 119160 | -22.5 |  | -30.7 | 20.6 | 15.8 | 16.8 | 17.2 | 17 | 16.6 |  | 13.9 | 15.2 | 15.3 | 15 | 14.8
Slovakia |  | DUDINCE | DUDINCE, Slovakia | 48.17N | 18.87E | 140 | 1.00 (EUW) | 95-06 | 118800 | -20.5 |  | -28.3 | 38.4 | 33.6 | 33.8 | 34.2 | 34 | 33.8667 |  | 30.9 | 32.3 | 31.2 | 31 | 31.4667
Slovakia |  | HURBANOVO | HURBANOVO, Slovakia | 47.87N | 18.20E | 124 | 1.00 (EUW) | 82-06 | 118580 | -14.5 |  | -25 | 38.4 | 33 | 34 | 34.8 | 34 | 33.9333 |  | 30.3 | 32.1 | 32.1 | 32 | 31.5
Slovakia |  | KAMENICA NAD CIROCH | KAMENICA NAD CIROCH, Slovakia | 48.93N | 22.00E | 178 | 1.00 (EUW) | 95-06 | 119930 | -21.9 |  | -29.5 | 36.9 | 31.5 | 32.7 | 31.8 | 32 | 32 |  | 29.3 | 30.6 | 29.4 | 30 | 29.7667
Slovakia |  | KOSICE | KOSICE, Slovakia | 48.67N | 21.22E | 231 | 1.00 (EUW) | 82-06 | 119680 | -15.5 |  | -23.2 | 35.9 | 30.8 | 32 | 32.4 | 32 | 31.7333 |  | 28.1 | 30.1 | 29.7 | 29 | 29.3
Slovakia |  | LIESEK | LIESEK, Slovakia | 49.37N | 19.68E | 693 | 1.00 (EUW) | 95-06 | 119180 | -23.1 |  | -30.1 | 33.1 | 28.1 | 28.9 | 29.4 | 29 | 28.8 |  | 26 | 26.9 | 26 | 26 | 26.3
Slovakia |  | LOMNICKY STIT | LOMNICKY STIT, Slovakia | 49.20N | 20.22E | 2635 | 1.00 (EUW) | 82-06 | 119300 | -25.5 |  | -33 | 18.6 | 13.1 | 14.4 | 13.7 | 14 | 13.7333 |  | 11.3 | 12.4 | 12 | 12 | 11.9
Slovakia |  | LUCENEC | LUCENEC, Slovakia | 48.33N | 19.73E | 215 | 1.00 (EUW) | 86-06 | 119270 | -18.7 |  | -28.4 | 37.4 | 31.6 | 32.9 | 33.6 | 33 | 32.7 |  | 29.1 | 31 | 30.9 | 30 | 30.3333
Slovakia |  | MILHOSTOV | MILHOSTOV, Slovakia | 48.67N | 21.73E | 106 | 1.00 (EUW) | 89-06 | 119780 | -15.9 |  | -23 | 36.4 | 31.6 | 32.7 | 33.5 | 33 | 32.6 |  | 29 | 30.7 | 30.5 | 30 | 30.0667
Slovakia |  | NITRA | NITRA, Slovakia | 48.28N | 18.13E | 136 | 1.00 (EUW) | 88-06 | 118550 | -15.8 |  | -24.6 | 37.7 | 32.5 | 33.7 | 34.6 | 34 | 33.6 |  | 30 | 31.8 | 32 | 31 | 31.2667
Slovakia |  | PIESTANY | PIESTANY, Slovakia | 48.62N | 17.83E | 164 | 1.00 (EUW) | 82-06 | 118260 | -16.5 |  | -27.5 | 37.7 | 31.2 | 33.3 | 33.8 | 33 | 32.7667 |  | 28.8 | 31.1 | 31.1 | 30 | 30.3333
Slovakia |  | POPRAD/TATRY | POPRAD/TATRY, Slovakia | 49.07N | 20.25E | 696 | 1.00 (EUW) | 82-06 | 119340 | -22.3 |  | -30.6 | 34.4 | 28.1 | 29.8 | 30.2 | 29 | 29.3667 |  | 25.4 | 27.2 | 27.2 | 27 | 26.6
Slovakia |  | PRIEVIDZA | PRIEVIDZA, Slovakia | 48.77N | 18.60E | 261 | 1.00 (EUW) | 95-06 | 118670 | -19.6 |  | -26.9 | 37.2 | 31.5 | 33.3 | 32.9 | 33 | 32.5667 |  | 29.4 | 31.2 | 30.2 | 30 | 30.2667
Slovakia |  | SLIAC | SLIAC, Slovakia | 48.65N | 19.15E | 315 | 1.00 (EUW) | 82-06 | 119030 | -21 |  | -31.9 | 36.9 | 31.2 | 32.7 | 33.2 | 32 | 32.3667 |  | 28.6 | 30.5 | 30.2 | 30 | 29.7667
Slovakia |  | STRBSKE PLESO | STRBSKE PLESO, Slovakia | 49.12N | 20.08E | 1356 | 1.00 (EUW) | 95-06 | 119330 | -21.6 |  | -26.1 | 37.2 | 28 | 31.5 | 28.2 | 29 | 29.2333 |  | 24.8 | 28.2 | 25.1 | 26 | 26.0333
Slovakia |  | STROPKOV/TISINEC | STROPKOV/TISINEC, Slovakia | 49.22N | 21.65E | 217 | 1.00 (EUW) | 90-06 | 119760 | -20.8 |  | -29 | 34 | 30.1 | 31.3 | 30.3 | 31 | 30.5667 |  | 28 | 29.6 | 28.3 | 29 | 28.6333
Slovakia |  | TELGART | TELGART, Slovakia | 48.85N | 20.18E | 906 | 1.00 (EUW) | 96-06 | 119380 | -18.7 |  | -24.2 | 30.9 | 26.4 | 26.4 | 27.1 | 27 | 26.6333 |  | 24.2 | 25 | 24.4 | 25 | 24.5333
Slovakia |  | ZILINA/HRICOV | ZILINA/HRICOV, Slovakia | 49.23N | 18.62E | 311 | 1.00 (EUW) | 82-06 | 118410 | -19.4 |  | -28.5 | 35.4 | 30.4 | 32.1 | 32.3 | 32 | 31.6 |  | 28 | 29.8 | 29.5 | 29 | 29.1
Slovenia |  | KREDARICA | KREDARICA, Slovenia | 46.38N | 13.85E | 2515 | 1.00 (EUW) | 82-05 | 140080 | -21.8 |  | -29.1 | 18.4 | 14.3 | 15 | 16.1 | 15 | 15.1333 |  | 12.7 | 13.4 | 14.5 | 14 | 13.5333
Slovenia |  | LISCA | LISCA, Slovenia | 46.07N | 15.28E | 941 | 1.00 (EUW) | 96-06 | 140240 | -14.6 |  | -19.5 | 33.4 | 27.1 | 27.8 | 28.7 | 28 | 27.8667 |  | 25.2 | 25.5 | 26.5 | 26 | 25.7333
Slovenia |  | LJUBLJANA/BEZIGRAD | LJUBLJANA/BEZIGRAD, Slovenia | 46.07N | 14.52E | 298 | 1.00 (EUW) | 82-06 | 140150 | -12.6 |  | -18.5 | 37.9 | 32.3 | 33.2 | 33.5 | 33 | 33 |  | 30.3 | 31 | 31.4 | 31 | 30.9
Slovenia |  | LJUBLJANA/BRNIK | LJUBLJANA/BRNIK, Slovenia | 46.22N | 14.48E | 385 | 1.00 (EUW) | 82-06 | 130140 | -16.9 |  | -25.7 | 37 | 31.1 | 32.8 | 32.1 | 32 | 32 |  | 29 | 30.2 | 30.1 | 30 | 29.7667
Slovenia |  | MARIBOR | MARIBOR, Slovenia | 46.48N | 15.68E | 265 | 1.00 (EUW) | 82-95 | 130260 | -18.1 |  | -29.9 | 36.3 | 29.8 | 32 | 32.2 | 31 | 31.3333 |  | 27.7 | 30.1 | 30.2 | 29 | 29.3333
Slovenia |  | MURSKA SOBOTA | MURSKA SOBOTA, Slovenia | 46.65N | 16.18E | 188 | 1.00 (EUW) | 96-06 | 140310 | -17.4 |  | -28 | 39.7 | 32.8 | 32.6 | 34.2 | 33 | 33.2 |  | 30.9 | 30.9 | 31.6 | 31 | 31.1333
Slovenia |  | NOVA GORICA | NOVA GORICA, Slovenia | 45.90N | 13.63E | 56 | 1.00 (EUW) | 96-06 | 141060 | -8.7 |  | -13.4 | 39.2 | 34.3 | 34.7 | 35.1 | 35 | 34.7 |  | 31.8 | 32.8 | 33.3 | 33 | 32.6333
Slovenia |  | NOVO MESTO | NOVO MESTO, Slovenia | 45.80N | 15.18E | 213 | 1.00 (EUW) | 82-06 | 141210 | -15.2 |  | -19.9 | 39.5 | 32.7 | 33 | 34.2 | 33 | 33.3 |  | 30.7 | 30.7 | 31.5 | 31 | 30.9667
Slovenia |  | PORTOROZ | PORTOROZ, Slovenia | 45.52N | 13.57E | 95 | 1.00 (EUW) | 82-06 | 131050 | -6.8 |  | -12 | 38.6 | 32.9 | 33.7 | 34.1 | 34 | 33.5667 |  | 30.4 | 31.8 | 32.1 | 31 | 31.4333
Slovenia |  | SLAVONSKI BROD | SLAVONSKI BROD, Slovenia | 45.17N | 18.00E | 88 | 1.00 (EUW) | 82-91 | 131500 | -14.7 |  | -30.1 | 39.6 | 31.7 | 34.7 | 34 | 33 | 33.4667 |  | 29 | 32.5 | 31.4 | 31 | 30.9667
Solomon Islands |  | HONIARA/HENDERSON | HONIARA/HENDERSON, Solomon Islands | 9.42S | 160.05E | 9 | 11.00 (PCC) | 83-06 | 915200 | 17.8 |  | 10.4 | 42.3 | 31.9 | 31.9 | 31.8 | 32 | 31.8667 |  | 31 | 31.1 | 31 | 31 | 31.0333
South Africa |  | BETHLEHEM | BETHLEHEM, South Africa | 28.25S | 28.33E | 1678 | 2.00 (AFS) | 85-06 | 684610 | -6.9 |  | -10.4 | 34.8 | 20.8 | 21 | 23.4 | 22 | 21.7333 |  | 18.8 | 19.1 | 21.8 | 20 | 19.9
South Africa |  | BLOEMFONTEIN AIRPOR | BLOEMFONTEIN AIRPOR, South Africa | 29.10S | 26.30E | 1354 | 2.00 (AFS) | 82-06 | 684420 | -6.8 |  | -12 | 40 | 22 | 22.2 | 25.5 | 23 | 23.2333 |  | 20.1 | 20.2 | 23.9 | 21 | 21.4
South Africa |  | CALVINIA | CALVINIA, South Africa | 31.47S | 19.77E | 975 | 2.00 (AFS) | 94-06 | 686180 | -3.7 |  | -6.2 | 42.7 | 24.1 | 23.7 | 26.4 | 25 | 24.7333 |  | 22.6 | 21.9 | 24.1 | 23 | 22.8667
South Africa |  | CAPE COLUMBINE | CAPE COLUMBINE, South Africa | 32.83S | 17.85E | 67 | 2.00 (AFS) | 82-93 | 687120 | 6.6 |  | 4.1 | 36.1 | 21.7 | 22.1 | 22.9 | 22 | 22.2333 |  | 19.6 | 19.5 | 20.3 | 20 | 19.8
South Africa |  | CAPE TOWN INTNL. AI | CAPE TOWN INTNL. AI, South Africa | 33.97S | 18.60E | 42 | 2.00 (AFS) | 82-06 | 688160 | 1.2 |  | -1.3 | 40.1 | 25.8 | 24.9 | 26.6 | 26 | 25.7667 |  | 21.8 | 21.8 | 21.9 | 22 | 21.8333
South Africa |  | DE AAR | DE AAR, South Africa | 30.65S | 24.00E | 1287 | 2.00 (AFS) | 93-06 | 685380 | -3.8 |  | -7.7 | 40.4 | 21.5 | 22 | 25.1 | 23 | 22.8667 |  | 19.8 | 20 | 23.7 | 21 | 21.1667
South Africa |  | DURBAN INTNL. AIRPO | DURBAN INTNL. AIRPO, South Africa | 29.97S | 30.95E | 14 | 2.00 (AFS) | 82-06 | 685880 | 6.8 |  | 3 | 38 | 27.9 | 27.2 | 28.4 | 28 | 27.8333 |  | 25.1 | 24.6 | 25.3 | 25 | 25
South Africa |  | EAST LONDON | EAST LONDON, South Africa | 33.03S | 27.83E | 125 | 2.00 (AFS) | 82-06 | 688580 | 5.3 |  | 1.2 | 41.7 | 29.8 | 29.5 | 31.2 | 30 | 30.1667 |  | 26.2 | 26.1 | 25.9 | 26 | 26.0667
South Africa |  | GEORGE AIRPORT | GEORGE AIRPORT, South Africa | 34.02S | 22.38E | 190 | 2.00 (AFS) | 93-06 | 688280 | 3.4 |  | 1.2 | 42.5 | 28 | 28.1 | 29.5 | 29 | 28.5333 |  | 25.9 | 25.1 | 25.1 | 25 | 25.3667
South Africa |  | GOUGH ISLAND | GOUGH ISLAND, South Africa | 40.35S | 9.88W | 54 | 0.00 (GRW) | 82-06 | 689060 | 1.7 |  | -2.3 | 26.9 | 17 | 17 | 16.2 | 17 | 16.7333 |  | 15.8 | 15.6 | 14.7 | 15 | 15.3667
South Africa |  | JOHANNESBURG INTNL. | JOHANNESBURG INTNL., South Africa | 26.15S | 28.23E | 1720 | 2.00 (AFS) | 82-06 | 683680 | -2.4 |  | -7.3 | 33.7 | 21.1 | 21.1 | 24.2 | 22 | 22.1333 |  | 19 | 19.2 | 22.5 | 20 | 20.2333
South Africa |  | KIMBERLEY | KIMBERLEY, South Africa | 28.80S | 24.77E | 1196 | 2.00 (AFS) | 82-06 | 684380 | -5 |  | -8.9 | 40.7 | 23.7 | 24.4 | 27.2 | 25 | 25.1 |  | 21.9 | 22.2 | 25.6 | 23 | 23.2333
South Africa |  | LANGEBAANWEG | LANGEBAANWEG, South Africa | 32.97S | 18.17E | 32 | 2.00 (AFS) | 88-06 | 687140 | 2.6 |  | 0.7 | 44.7 | 26.8 | 26.4 | 28.1 | 27 | 27.1 |  | 24.1 | 23.3 | 23.9 | 24 | 23.7667
South Africa |  | MAFIKENG WO | MAFIKENG WO, South Africa | 25.82S | 25.55E | 1281 | 2.00 (AFS) | 96-06 | 682420 | N/A |  | N/A | N/A | 25.9 | 25.4 | 28.1 | 26 | 26.4667 |  | 23.3 | 23.6 | 26.6 | 25 | 24.5
South Africa |  | MARION ISLAND | MARION ISLAND, South Africa | 46.88S | 37.87E | 21 | 3.00 (AFE) | 82-06 | 689940 | -2.7 |  | -4.3 | 23 | 11.4 | 11 | 10.2 | 11 | 10.8667 |  | 9.9 | 9.4 | 9 | 9 | 9.4333
South Africa |  | MOSSEL BAY (CAPE ST BLAIZE) | MOSSEL BAY (CAPE ST BLAIZE), South Africa | 34.18S | 22.15E | 61 | 2.00 (AFS) | 82-97 | 689280 | 7.4 |  | 5.7 | 36.7 | 26.1 | 25.6 | 26.3 | 26 | 26 |  | 23.6 | 22.7 | 21.8 | 23 | 22.7
South Africa |  | PIETERSBURG | PIETERSBURG, South Africa | 23.87S | 29.45E | 1224 | 2.00 (AFS) | 82-06 | 681740 | 1.3 |  | -2.5 | 38.5 | 25.3 | 25.5 | 28.7 | 27 | 26.5 |  | 23.3 | 23.5 | 26.5 | 24 | 24.4333
South Africa |  | PORT ELIZABETH | PORT ELIZABETH, South Africa | 33.98S | 25.62E | 63 | 2.00 (AFS) | 82-06 | 688420 | 2.3 |  | -2 | 41 | 27.9 | 27.5 | 29.9 | 28 | 28.4333 |  | 24.9 | 24.5 | 24.7 | 25 | 24.7
South Africa |  | PRETORIA (IRENE) | PRETORIA (IRENE), South Africa | 25.92S | 28.22E | 1523 | 2.00 (AFS) | 94-06 | 682630 | -0.4 |  | -5.7 | 35.7 | 23.6 | 23.8 | 25.9 | 24 | 24.4333 |  | 21.2 | 21.3 | 24.1 | 22 | 22.2
South Africa |  | PRETORIA-EENDRACHT | PRETORIA-EENDRACHT, South Africa | 25.73S | 28.18E | 1326 | 2.00 (AFS) | 82-06 | 682620 | 0.8 |  | -2.8 | 38.6 | 23.3 | 23.9 | 27.5 | 25 | 24.9 |  | 21.9 | 22.3 | 25.8 | 23 | 23.3333
South Africa |  | SPRINGBOK | SPRINGBOK, South Africa | 29.67S | 17.90E | 1007 | 2.00 (AFS) | 87-06 | 685120 | 0.8 |  | -1.2 | 41.2 | 23.4 | 23.2 | 26.2 | 24 | 24.2667 |  | 21.9 | 21.6 | 24.4 | 23 | 22.6333
South Africa |  | UPINGTON | UPINGTON, South Africa | 28.40S | 21.27E | 836 | 2.00 (AFS) | 82-06 | 684240 | -2.2 |  | -6 | 44 | 26.8 | 27 | 30.2 | 28 | 28 |  | 25 | 25 | 28.7 | 26 | 26.2333
Spain |  | ALBACETE/LOS LLANOS | ALBACETE/LOS LLANOS, Spain | 38.95N | 1.85W | 704 | 1.00 (EUW) | 82-06 | 82800 | -8.2 |  | -17.5 | 41.8 | 36.1 | 38 | 37.1 | 37 | 37.0667 |  | 33.8 | 36.1 | 35.2 | 35 | 35.0333
Spain |  | ALICANTE/EL ALTET | ALICANTE/EL ALTET, Spain | 38.28N | 0.55W | 31 | 1.00 (EUW) | 82-06 | 83600 | 0.8 |  | -2.9 | 41.5 | 32.9 | 34.1 | 34.9 | 34 | 33.9667 |  | 30.6 | 32.2 | 32.9 | 32 | 31.9
Spain |  | ALMERIA/AEROPUERTO | ALMERIA/AEROPUERTO, Spain | 36.85N | 2.38W | 21 | 1.00 (EUW) | 82-06 | 84870 | 4.1 |  | -0.6 | 41 | 33.9 | 36.2 | 37.1 | 36 | 35.7333 |  | 31.8 | 34.1 | 34.2 | 33 | 33.3667
Spain |  | BARCELONA/AEROPUERT | BARCELONA/AEROPUERT, Spain | 41.28N | 2.07E | 6 | 1.00 (EUW) | 82-06 | 81810 | -0.8 |  | -6.1 | 36.5 | 30.3 | 31.8 | 32.2 | 31 | 31.4333 |  | 28 | 30.2 | 30.4 | 30 | 29.5333
Spain |  | BILBAO/SONDICA | BILBAO/SONDICA, Spain | 43.30N | 2.90W | 39 | 1.00 (EUW) | 94-06 | 80250 | N/A |  | N/A | N/A | 36.2 | 35 | 35.2 | 35 | 35.4667 |  | 31.2 | 30.8 | 31.2 | 31 | 31.0667
Spain |  | CACERES | CACERES, Spain | 39.47N | 6.33W | 405 | 1.00 (EUW) | 83-06 | 82610 | -2.2 |  | -5 | 43.3 | 37.1 | 39.5 | 39.5 | 39 | 38.7 |  | 35.2 | 37.9 | 37.6 | 37 | 36.9
Spain |  | CIUDAD REAL | CIUDAD REAL, Spain | 38.98N | 3.92W | 629 | 1.00 (EUW) | 82-06 | 83480 | -5.3 |  | -10 | 43.7 | 37.1 | 39 | 38.4 | 38 | 38.1667 |  | 34.9 | 37.4 | 36.5 | 36 | 36.2667
Spain |  | COIMBRA/CERNACHE | COIMBRA/CERNACHE, Spain | 40.15N | 8.47W | 179 | 0.00 (GMT) | 96-06 | 85480 | 0 |  | -2.9 | 42.2 | 35.7 | 36.1 | 37.4 | 36 | 36.4 |  | 31.7 | 33 | 33.8 | 33 | 32.8333
Spain |  | GERONA/COSTA BRAVA | GERONA/COSTA BRAVA, Spain | 41.90N | 2.77E | 129 | 1.00 (EUW) | 82-06 | 81840 | -5.2 |  | -9.6 | 40.9 | 34.1 | 35.9 | 36.1 | 35 | 35.3667 |  | 31.3 | 33.4 | 33.1 | 33 | 32.6
Spain |  | GRANADA/AEROPUERTO | GRANADA/AEROPUERTO, Spain | 37.18N | 3.78W | 570 | 1.00 (EUW) | 82-06 | 84190 | -6.2 |  | -13.2 | 43.2 | 37.6 | 40 | 39.1 | 39 | 38.9 |  | 35 | 38 | 37.1 | 37 | 36.7
Spain |  | IBIZA/ES CODOLA | IBIZA/ES CODOLA, Spain | 38.88N | 1.38E | 17 | 1.00 (EUW) | 82-06 | 83730 | 2.2 |  | -1.3 | 37.9 | 30.2 | 32.6 | 33.1 | 32 | 31.9667 |  | 28.9 | 31.1 | 31.9 | 31 | 30.6333
Spain |  | LA CORUNA | LA CORUNA, Spain | 43.37N | 8.42W | 67 | 1.00 (EUW) | 82-06 | 80010 | 1.7 |  | -3.3 | 35.3 | 27.4 | 27.9 | 27 | 27 | 27.4333 |  | 24.1 | 24.5 | 24.6 | 24 | 24.4
Spain |  | LAS PALMAS DE GRAN | LAS PALMAS DE GRAN, Spain | 27.93N | 15.38W | 47 | 0.00 (GMT) | 82-06 | 600300 | 11.7 |  | 8.8 | 40.2 | 28.8 | 32.2 | 32.2 | 31 | 31.0667 |  | 26.2 | 29 | 29.9 | 28 | 28.3667
Spain |  | LOGRONO/AGONCILLO | LOGRONO/AGONCILLO, Spain | 42.45N | 2.33W | 363 | 1.00 (EUW) | 82-06 | 80840 | -5.1 |  | -10.9 | 42.9 | 35.9 | 37.2 | 37.2 | 37 | 36.7667 |  | 33 | 35.1 | 34.2 | 34 | 34.1
Spain |  | MADRID/BARAJAS RS | MADRID/BARAJAS RS, Spain | 40.45N | 3.55W | 582 | 1.00 (EUW) | 82-06 | 82210 | -6.6 |  | -11.9 | 41.8 | 36.2 | 38.1 | 37.8 | 37 | 37.3667 |  | 34.1 | 36.5 | 36 | 36 | 35.5333
Spain |  | MADRID/TORREJON | MADRID/TORREJON, Spain | 40.48N | 3.45W | 611 | 1.00 (EUW) | 82-06 | 82270 | -6.9 |  | -13.5 | 42.4 | 36.8 | 38.1 | 38.2 | 38 | 37.7 |  | 34.2 | 36.9 | 36.2 | 36 | 35.7667
Spain |  | MALAGA/AEROPUERTO | MALAGA/AEROPUERTO, Spain | 36.67N | 4.48W | 7 | 1.00 (EUW) | 82-06 | 84820 | 1.3 |  | -3.1 | 44.1 | 35.2 | 38.2 | 37.7 | 37 | 37.0333 |  | 32.1 | 34.8 | 34.8 | 34 | 33.9
Spain |  | MENORCA/MAHON | MENORCA/MAHON, Spain | 39.87N | 4.23E | 86 | 1.00 (EUW) | 82-06 | 83140 | 1.9 |  | -3.2 | 38.7 | 31 | 33 | 33.2 | 32 | 32.4 |  | 28.9 | 31.1 | 31.2 | 30 | 30.4
Spain |  | MORON DE LA FRONTER | MORON DE LA FRONTER, Spain | 37.15N | 5.62W | 88 | 1.00 (EUW) | 94-06 | 83970 | -1.2 |  | -7.5 | 48.1 | 38.7 | 42 | 40.8 | 41 | 40.5 |  | 36 | 39.8 | 39 | 38 | 38.2667
Spain |  | MURCIA | MURCIA, Spain | 38.00N | 1.17W | 62 | 1.00 (EUW) | 92-06 | 84300 | -0.3 |  | -4.2 | 44.5 | 36.5 | 38.5 | 38 | 38 | 37.6667 |  | 34.1 | 35.7 | 35.7 | 35 | 35.1667
Spain |  | OVIEDO | OVIEDO, Spain | 43.35N | 5.87W | 339 | 1.00 (EUW) | 82-06 | 80150 | -2 |  | -5.7 | 37.8 | 29.1 | 29.5 | 29.5 | 29 | 29.3667 |  | 25.1 | 26.4 | 26 | 26 | 25.8333
Spain |  | PALMA DE MALLORCA/S | PALMA DE MALLORCA/S, Spain | 39.55N | 2.73E | 7 | 1.00 (EUW) | 82-06 | 83060 | -2.5 |  | -6 | 41.4 | 34.1 | 35.9 | 35.1 | 35 | 35.0333 |  | 31.2 | 33.5 | 33 | 33 | 32.5667
Spain |  | ROTA NAS | ROTA NAS, Spain | 36.65N | 6.35W | 27 | 1.00 (EUW) | 82-06 | 84490 | 1.1 |  | -3.7 | 43.9 | 33.9 | 36.2 | 36.8 | 36 | 35.6333 |  | 31.3 | 34.1 | 34 | 33 | 33.1333
Spain |  | SALAMANCA/MATACAN | SALAMANCA/MATACAN, Spain | 40.95N | 5.50W | 794 | 1.00 (EUW) | 82-06 | 82020 | -8 |  | -13.4 | 41.5 | 34 | 36 | 35.7 | 35 | 35.2333 |  | 31.8 | 34 | 33.5 | 33 | 33.1
Spain |  | SAN SEBASTIAN/IGUEL | SAN SEBASTIAN/IGUEL, Spain | 43.30N | 2.03W | 259 | 1.00 (EUW) | 82-06 | 80270 | -2.3 |  | -8.2 | 38.7 | 30.2 | 30.2 | 30 | 30 | 30.1333 |  | 26.6 | 26.7 | 26.9 | 27 | 26.7333
Spain |  | SANTANDER | SANTANDER, Spain | 43.48N | 3.80W | 59 | 1.00 (EUW) | 82-06 | 80230 | 1.5 |  | -2.4 | 38.2 | 26.4 | 27.8 | 27.1 | 27 | 27.1 |  | 22.9 | 24.9 | 24.8 | 24 | 24.2
Spain |  | SANTIAGO/LABACOLLA | SANTIAGO/LABACOLLA, Spain | 42.90N | 8.43W | 367 | 1.00 (EUW) | 82-06 | 80420 | -3.8 |  | -8.9 | 41.4 | 32.1 | 34 | 33.9 | 33 | 33.3333 |  | 28.3 | 30.2 | 30 | 30 | 29.5
Spain |  | SEVILLA/SAN PABLO | SEVILLA/SAN PABLO, Spain | 37.42N | 5.90W | 31 | 1.00 (EUW) | 82-06 | 83910 | -1.3 |  | -6 | 47.1 | 39.1 | 42.2 | 41.6 | 41 | 40.9667 |  | 37 | 40.1 | 39.4 | 39 | 38.8333
Spain |  | STA. CRUZ DE TENERI | STA. CRUZ DE TENERI, Spain | 28.45N | 16.25W | 36 | 0.00 (GMT) | 82-03 | 600200 | 11.2 |  | 5.7 | 39.1 | 29.9 | 33 | 33 | 32 | 31.9667 |  | 27.6 | 30.2 | 30.7 | 30 | 29.5
Spain |  | TENERIFE SUR | TENERIFE SUR, Spain | 28.05N | 16.57W | 77 | 0.00 (GMT) | 84-06 | 600250 | 11.5 |  | 8.6 | 46.1 | 29.9 | 34.6 | 35.9 | 33 | 33.4667 |  | 27.1 | 30.9 | 31.9 | 30 | 29.9667
Spain |  | VALENCIA/AEROPUERTO | VALENCIA/AEROPUERTO, Spain | 39.50N | 0.47W | 62 | 1.00 (EUW) | 82-06 | 82840 | -1.6 |  | -6 | 43.4 | 33.9 | 35.9 | 36 | 35 | 35.2667 |  | 31 | 32.8 | 33.1 | 32 | 32.3
Spain |  | VALLADOLID | VALLADOLID, Spain | 41.65N | 4.77W | 735 | 1.00 (EUW) | 82-06 | 81410 | -6.1 |  | -9.9 | 40.1 | 34.8 | 36.3 | 36.2 | 36 | 35.7667 |  | 32.3 | 34.6 | 34 | 34 | 33.6333
Spain |  | VIGO/PEINADOR | VIGO/PEINADOR, Spain | 42.23N | 8.63W | 255 | 1.00 (EUW) | 82-06 | 80450 | -1 |  | -4.7 | 39 | 31.1 | 33.1 | 33 | 32 | 32.4 |  | 28.9 | 30.5 | 30.2 | 30 | 29.8667
Spain |  | VITORIA | VITORIA, Spain | 42.88N | 2.72W | 510 | 1.00 (EUW) | 83-06 | 80800 | -7.8 |  | -14.1 | 42.7 | 35.1 | 35.5 | 37.9 | 36 | 36.1667 |  | 31.8 | 32.2 | 34 | 33 | 32.6667
Spain |  | ZARAGOZA (USAFB) | ZARAGOZA (USAFB), Spain | 41.67N | 1.05W | 263 | 1.00 (EUW) | 82-91 | 81605 | -3.4 |  | -10.1 | 44.1 | 35.9 | 39 | 38.1 | 38 | 37.6667 |  | 33.2 | 36.2 | 36 | 35 | 35.1333
Spain |  | ZARAGOZA/AEROPUERTO | ZARAGOZA/AEROPUERTO, Spain | 41.67N | 1.00W | 258 | 1.00 (EUW) | 82-06 | 81600 | -4.4 |  | -9.6 | 42.3 | 37.1 | 38.2 | 38 | 38 | 37.7667 |  | 34.5 | 36.2 | 35.8 | 36 | 35.5
Sri Lanka |  | KATUNAYAKE | KATUNAYAKE, Sri Lanka | 7.17N | 79.88E | 8 | 5.50 (IND) | 82-06 | 434500 | N/A |  | N/A | N/A | 31.9 | 31 | 31.2 | 31 | 31.3667 |  | 31.1 | 30.2 | 30.8 | 31 | 30.7
Suriname |  | ZANDERIJ | ZANDERIJ, Suriname | 5.45N | 55.20W | 15 | -3.00 (SAE) | 82-06 | 812250 | N/A |  | N/A | N/A | 33.1 | 33.7 | 34.2 | 34 | 33.6667 |  | 32.2 | 32.7 | 33.6 | 33 | 32.8333
Svalbard and Jan Mayen |  | BJORNOYA | BJORNOYA, Svalbard and Jan Mayen | 74.52N | 19.02E | 16 | 1.00 (EUW) | 82-06 | 10280 | -23.1 |  | -32.5 | 23.1 | 9.6 | 13.7 | 13.3 | 12 | 12.2 |  | 7.5 | 10.9 | 10.3 | 10 | 9.5667
Svalbard and Jan Mayen |  | HOPEN | HOPEN, Svalbard and Jan Mayen | 76.50N | 25.07E | 10 | 1.00 (EUW) | 82-06 | 10620 | -29.5 |  | -38.6 | 16.2 | 5.3 | 8.6 | 8.8 | 8 | 7.5667 |  | 4.3 | 7 | 7.2 | 6 | 6.1667
Svalbard and Jan Mayen |  | SVALBARD LUFTHAVN | SVALBARD LUFTHAVN, Svalbard and Jan Mayen | 78.25N | 15.47E | 29 | 1.00 (EUW) | 82-06 | 10080 | -31.7 |  | -43.8 | 21.1 | 10.2 | 15.1 | 12.8 | 13 | 12.7 |  | 8.2 | 12.4 | 11 | 11 | 10.5333
Sweden |  | ANGELHOLM | ANGELHOLM, Sweden | 56.30N | 12.85E | 20 | 1.00 (EUW) | 82-06 | 25635 | -14.6 |  | -27.7 | 34.4 | 26.8 | 29.2 | 28.1 | 28 | 28.0333 |  | 24.1 | 26.9 | 26 | 26 | 25.6667
Sweden |  | ARJEPLOG | ARJEPLOG, Sweden | 66.05N | 17.87E | 432 | 1.00 (EUW) | 82-06 | 21240 | -33.8 |  | -42.9 | 28.7 | 23.9 | 25.1 | 23.6 | 24 | 24.2 |  | 21.4 | 22.7 | 21.3 | 22 | 21.8
Sweden |  | ARVIKA | ARVIKA, Sweden | 59.67N | 12.58E | 75 | 1.00 (EUW) | 82-95 | 24040 | -22.5 |  | -36 | 34.9 | 28.3 | 29.9 | 30.2 | 29 | 29.4667 |  | 25.6 | 27.7 | 25.3 | 26 | 26.2
Sweden |  | BJUROKLUBB (LGT-H) | BJUROKLUBB (LGT-H), Sweden | 64.48N | 21.58E | 36 | 1.00 (EUW) | 82-95 | 22960 | -22.8 |  | -32.7 | 29.2 | 22.9 | 24.2 | 23.2 | 23 | 23.4333 |  | 20.1 | 21.7 | 20.7 | 21 | 20.8333
Sweden |  | BLOMSKOG | BLOMSKOG, Sweden | 59.22N | 12.08E | 171 | 1.00 (EUW) | 96-06 | 24080 | -21.3 |  | -26.3 | 31.3 | 24.5 | 27.1 | 26.5 | 26 | 26.0333 |  | 22.5 | 25.4 | 25 | 24 | 24.3
Sweden |  | BORLANGE | BORLANGE, Sweden | 60.43N | 15.52E | 150 | 1.00 (EUW) | 93-06 | 24350 | N/A |  | N/A | N/A | 26.2 | 28 | 27.7 | 27 | 27.3 |  | 24 | 26 | 26 | 25 | 25.3333
Sweden |  | EDSBYN | EDSBYN, Sweden | 61.37N | 15.72E | 185 | 1.00 (EUW) | 96-06 | 23380 | -28.4 |  | -37.3 | 33.1 | 25.7 | 27.8 | 27 | 27 | 26.8333 |  | 23.6 | 26.2 | 25 | 25 | 24.9333
Sweden |  | FALSTERBO | FALSTERBO, Sweden | 55.38N | 12.82E | 5 | 1.00 (EUW) | 82-06 | 26160 | -9.1 |  | -20.1 | 31.2 | 22.9 | 26 | 25.7 | 25 | 24.8667 |  | 21.2 | 24.2 | 24.3 | 23 | 23.2333
Sweden |  | FARO ISLAND | FARO ISLAND, Sweden | 57.90N | 19.17E | 8 | 1.00 (EUW) | 82-95 | 25880 | -8.3 |  | -16.5 | 31.4 | 22.9 | 26.5 | 25.9 | 25 | 25.1 |  | 20.7 | 23.9 | 23.6 | 23 | 22.7333
Sweden |  | FLODA | FLODA, Sweden | 59.05N | 16.40E | 33 | 1.00 (EUW) | 96-06 | 24760 | -22.5 |  | -30.2 | 33.2 | 26.7 | 29 | 27.8 | 28 | 27.8333 |  | 24.5 | 27.1 | 26.3 | 26 | 25.9667
Sweden |  | FOLKARNA | FOLKARNA, Sweden | 60.17N | 16.32E | 80 | 1.00 (EUW) | 82-94 | 24440 | N/A |  | N/A | N/A | 28.1 | 30.8 | 28.5 | 29 | 29.1333 |  | 25.3 | 27.5 | 25.2 | 26 | 26
Sweden |  | FRANSTA | FRANSTA, Sweden | 62.50N | 16.18E | 75 | 1.00 (EUW) | 82-95 | 23420 | -32.7 |  | -44.4 | 34.2 | 29.1 | 29.1 | 27.4 | 29 | 28.5333 |  | 25.2 | 26.8 | 23.5 | 25 | 25.1667
Sweden |  | GADDEDE | GADDEDE, Sweden | 64.50N | 14.17E | 330 | 1.00 (EUW) | 82-05 | 22220 | -30.7 |  | -44.1 | 31.6 | 25.2 | 26.4 | 25.3 | 26 | 25.6333 |  | 22.2 | 23.9 | 21.9 | 23 | 22.6667
Sweden |  | GALLIVARE | GALLIVARE, Sweden | 67.15N | 20.65E | 360 | 1.00 (EUW) | 82-06 | 20490 | -35.1 |  | -45.1 | 33 | 25.9 | 26.3 | 24.2 | 25 | 25.4667 |  | 22.2 | 24.2 | 22.8 | 23 | 23.0667
Sweden |  | GAVLE | GAVLE, Sweden | 60.72N | 17.17E | 16 | 1.00 (EUW) | 96-06 | 24530 | -22.8 |  | -30.6 | 33.8 | 25.9 | 28.2 | 27.6 | 27 | 27.2333 |  | 23.4 | 26 | 25.6 | 25 | 25
Sweden |  | GLADHAMMAR | GLADHAMMAR, Sweden | 57.78N | 16.60E | 9 | 1.00 (EUW) | 82-95 | 25760 | -18.3 |  | -30.6 | 36 | 26.9 | 30.8 | 29.7 | 29 | 29.1333 |  | 24.9 | 27.9 | 26.3 | 26 | 26.3667
Sweden |  | GOTEBORG | GOTEBORG, Sweden | 57.72N | 12.00E | 2 | 1.00 (EUW) | 96-06 | 25130 | -15.6 |  | -21.1 | 32 | 26.3 | 29.1 | 28.4 | 28 | 27.9333 |  | 24.2 | 26.8 | 26.8 | 26 | 25.9333
Sweden |  | GOTEBORG/LANDVETTER | GOTEBORG/LANDVETTER, Sweden | 57.67N | 12.30E | 169 | 1.00 (EUW) | 82-06 | 25260 | -16.3 |  | -26.7 | 33.6 | 26.9 | 28.7 | 28 | 28 | 27.8667 |  | 24.2 | 26.1 | 25.8 | 25 | 25.3667
Sweden |  | GOTEBORG/SAVE | GOTEBORG/SAVE, Sweden | 57.78N | 11.88E | 16 | 1.00 (EUW) | 82-06 | 25120 | -17.4 |  | -27.7 | 33.1 | 26.5 | 28.6 | 27.4 | 28 | 27.5 |  | 24 | 25.9 | 25.2 | 25 | 25.0333
Sweden |  | GOTSKA SANDON | GOTSKA SANDON, Sweden | 58.40N | 19.20E | 12 | 1.00 (EUW) | 82-06 | 25840 | -11 |  | -20.3 | 32 | 22.6 | 26.2 | 25.4 | 25 | 24.7333 |  | 20.2 | 24 | 23.8 | 23 | 22.6667
Sweden |  | GUNNARN | GUNNARN, Sweden | 65.02N | 17.68E | 283 | 1.00 (EUW) | 82-06 | 21280 | -34.6 |  | -43.2 | 32.8 | 27.2 | 27.2 | 25.4 | 27 | 26.6 |  | 23.9 | 24.5 | 23.1 | 24 | 23.8333
Sweden |  | HAGSHULT | HAGSHULT, Sweden | 57.30N | 14.13E | 169 | 1.00 (EUW) | 82-06 | 25560 | -19.9 |  | -28.9 | 35.3 | 27.9 | 29.8 | 28.5 | 29 | 28.7333 |  | 25.3 | 27.6 | 25.6 | 26 | 26.1667
Sweden |  | HALLANDS VADERO | HALLANDS VADERO, Sweden | 56.45N | 12.55E | 10 | 1.00 (EUW) | 96-06 | 26050 | -9.2 |  | -12.6 | 31.3 | 24 | 26.7 | 25.6 | 25 | 25.4333 |  | 21.8 | 24.4 | 24.2 | 23 | 23.4667
Sweden |  | HANO | HANO, Sweden | 56.02N | 14.85E | 60 | 1.00 (EUW) | 96-06 | 26280 | -10 |  | -13 | 30.6 | 22.3 | 26.1 | 25.1 | 25 | 24.5 |  | 20.5 | 23.8 | 23.7 | 23 | 22.6667
Sweden |  | HAPARANDA | HAPARANDA, Sweden | 65.83N | 24.15E | 6 | 1.00 (EUW) | 82-06 | 21960 | -29.2 |  | -38.5 | 30.8 | 26 | 25 | 24.5 | 25 | 25.1667 |  | 23.1 | 23.4 | 21.8 | 23 | 22.7667
Sweden |  | HARSTENA | HARSTENA, Sweden | 58.25N | 17.02E | 7 | 1.00 (EUW) | 82-96 | 25860 | -13.2 |  | -27.2 | 31.7 | 23.2 | 26.3 | 25.7 | 25 | 25.0667 |  | 21.1 | 24 | 23.5 | 23 | 22.8667
Sweden |  | HELSINGBORG | HELSINGBORG, Sweden | 56.03N | 12.77E | 44 | 1.00 (EUW) | 96-06 | 26110 | -15.2 |  | -23.4 | 31.4 | 26.4 | 28 | 27.3 | 27 | 27.2333 |  | 23.2 | 26.1 | 26.1 | 25 | 25.1333
Sweden |  | HOBURG | HOBURG, Sweden | 56.92N | 18.15E | 39 | 1.00 (EUW) | 82-06 | 26800 | -8.6 |  | -16.6 | 30.8 | 22.2 | 26 | 25.5 | 25 | 24.5667 |  | 20.5 | 24.2 | 23.8 | 23 | 22.8333
Sweden |  | HOLMOGADD | HOLMOGADD, Sweden | 63.60N | 20.75E | 6 | 1.00 (EUW) | 82-06 | 22880 | -18.8 |  | -30 | 25.9 | 20.5 | 22.5 | 22.2 | 22 | 21.7333 |  | 17.8 | 20.7 | 20.7 | 20 | 19.7333
Sweden |  | IDVATTNET | IDVATTNET, Sweden | 64.45N | 17.08E | 353 | 1.00 (EUW) | 83-95 | 22520 | -36.2 |  | -45.2 | 32 | 26.3 | 25.9 | 24.1 | 25 | 25.4333 |  | 22.5 | 23 | 20 | 22 | 21.8333
Sweden |  | JOKKMOKK (SWE-AFB) | JOKKMOKK (SWE-AFB), Sweden | 66.63N | 19.65E | 264 | 1.00 (EUW) | 82-98 | 21420 | -36.3 |  | -44.7 | 30.1 | 25.2 | 25.7 | 24.2 | 25 | 25.0333 |  | 22 | 23.1 | 21.7 | 22 | 22.2667
Sweden |  | JONKOPING/AXAMO | JONKOPING/AXAMO, Sweden | 57.75N | 14.08E | 224 | 1.00 (EUW) | 82-06 | 25500 | -22.3 |  | -33.6 | 34.7 | 27 | 29.2 | 28 | 28 | 28.0667 |  | 24.1 | 26.8 | 25.3 | 25 | 25.4
Sweden |  | JUNSELE | JUNSELE, Sweden | 63.68N | 16.95E | 217 | 1.00 (EUW) | 96-06 | 22440 | N/A |  | N/A | N/A | 26.8 | 27.3 | 27 | 27 | 27.0333 |  | 24 | 25.4 | 25.2 | 25 | 24.8667
Sweden |  | KALMAR | KALMAR, Sweden | 56.68N | 16.30E | 4 | 1.00 (EUW) | 96-06 | 26700 | -19.1 |  | -26.7 | 34.1 | 25.6 | 27.7 | 26.9 | 27 | 26.7333 |  | 22.8 | 25.8 | 25.4 | 25 | 24.6667
Sweden |  | KALMAR | KALMAR, Sweden | 56.73N | 16.30E | 16 | 1.00 (EUW) | 82-06 | 26720 | -17.3 |  | -29.2 | 36.2 | 26.9 | 29.9 | 27.9 | 28 | 28.2333 |  | 24 | 27.2 | 25.2 | 25 | 25.4667
Sweden |  | KARESUANDO | KARESUANDO, Sweden | 68.45N | 22.45E | 331 | 1.00 (EUW) | 96-06 | 20800 | -38.1 |  | -51.3 | 30.5 | 25.9 | 26.4 | 23.9 | 25 | 25.4 |  | 23.1 | 24.3 | 21.3 | 23 | 22.9
Sweden |  | KARLSBORG(SAFB) | KARLSBORG(SAFB), Sweden | 58.52N | 14.53E | 102 | 1.00 (EUW) | 82-93 | 25440 | -15.9 |  | -30.5 | 32.5 | 25.7 | 27.5 | 27.5 | 27 | 26.9 |  | 23.6 | 25.3 | 23.5 | 24 | 24.1333
Sweden |  | KARLSTAD FLYGPLATS | KARLSTAD FLYGPLATS, Sweden | 59.45N | 13.47E | 100 | 1.00 (EUW) | 82-06 | 24180 | -21 |  | -32 | 32.5 | 26.1 | 28 | 27.4 | 27 | 27.1667 |  | 24.1 | 26.1 | 25.1 | 25 | 25.1
Sweden |  | KATTERJAKK | KATTERJAKK, Sweden | 68.42N | 18.17E | 517 | 1.00 (EUW) | 82-06 | 20200 | -28.3 |  | -36.4 | 27 | 20.5 | 22.6 | 21.6 | 22 | 21.5667 |  | 17.9 | 20.3 | 18.9 | 19 | 19.0333
Sweden |  | KIRUNA | KIRUNA, Sweden | 67.82N | 20.33E | 447 | 1.00 (EUW) | 82-06 | 20440 | -32.5 |  | -40.8 | 28.4 | 23.9 | 25 | 22.4 | 24 | 23.7667 |  | 21.2 | 22.2 | 19.9 | 21 | 21.1
Sweden |  | KLIMPFJALL | KLIMPFJALL, Sweden | 65.07N | 14.80E | 560 | 1.00 (EUW) | 82-95 | 21080 | -32.1 |  | -42.5 | 30.3 | 22.8 | 23.2 | 22.2 | 23 | 22.7333 |  | 19.6 | 20.7 | 18.6 | 20 | 19.6333
Sweden |  | KRANGEDE | KRANGEDE, Sweden | 63.15N | 16.17E | 184 | 1.00 (EUW) | 96-06 | 22470 | -29.1 |  | -37.7 | 31.7 | 26.2 | 28.2 | 26.6 | 27 | 27 |  | 24.2 | 26 | 24.7 | 25 | 24.9667
Sweden |  | KUGGOREN | KUGGOREN, Sweden | 61.70N | 17.53E | 10 | 1.00 (EUW) | 96-06 | 23550 | -16.7 |  | -25 | 30.1 | 21.6 | 23.5 | 24 | 23 | 23.0333 |  | 18.7 | 22 | 22.1 | 21 | 20.9333
Sweden |  | KULLEN (LGT-H) | KULLEN (LGT-H), Sweden | 56.30N | 12.45E | 72 | 1.00 (EUW) | 82-95 | 26060 | -8.2 |  | -20.9 | 31.7 | 24.5 | 26.9 | 25.9 | 26 | 25.7667 |  | 22 | 24 | 23.1 | 23 | 23.0333
Sweden |  | KVIKKJOKK-ARRENJARK | KVIKKJOKK-ARRENJARK, Sweden | 66.88N | 17.75E | 315 | 1.00 (EUW) | 82-06 | 21200 | -36.3 |  | -45.6 | 29.7 | 24.4 | 25.2 | 23.9 | 25 | 24.5 |  | 21.8 | 23.2 | 21.4 | 22 | 22.1333
Sweden |  | LAINIO | LAINIO, Sweden | 67.77N | 22.35E | 325 | 1.00 (EUW) | 82-95 | 20860 | -33.9 |  | -43.4 | 28.6 | 24.2 | 25.2 | 23.2 | 24 | 24.2 |  | 21.8 | 22.2 | 19.8 | 21 | 21.2667
Sweden |  | LANDSORT | LANDSORT, Sweden | 58.75N | 17.87E | 32 | 1.00 (EUW) | 82-96 | 25820 | -11.8 |  | -24.6 | 28.4 | 20.9 | 24.2 | 23.9 | 23 | 23 |  | 19.5 | 22.1 | 22.1 | 21 | 21.2333
Sweden |  | LINKOPING/MALMSLATT | LINKOPING/MALMSLATT, Sweden | 58.40N | 15.53E | 93 | 1.00 (EUW) | 87-06 | 25620 | -19.8 |  | -31.1 | 36 | 27 | 29.7 | 27.5 | 28 | 28.0667 |  | 24.6 | 27.2 | 25.8 | 26 | 25.8667
Sweden |  | LJUNGBY | LJUNGBY, Sweden | 56.85N | 13.88E | 148 | 1.00 (EUW) | 82-06 | 26220 | N/A |  | N/A | N/A | 27.8 | 29 | 28.4 | 28 | 28.4 |  | 25.4 | 27 | 25.5 | 26 | 25.9667
Sweden |  | LJUNGBYHED | LJUNGBYHED, Sweden | 56.08N | 13.20E | 44 | 1.00 (EUW) | 82-06 | 20001 | -16.6 |  | -30.4 | 35 | 27.2 | 29.8 | 28.7 | 29 | 28.5667 |  | 24.6 | 27.4 | 26.1 | 26 | 26.0333
Sweden |  | LULEA-KALLAX | LULEA-KALLAX, Sweden | 65.55N | 22.13E | 17 | 1.00 (EUW) | 82-06 | 21860 | -29.8 |  | -39.5 | 32.3 | 25.4 | 26.2 | 24.2 | 25 | 25.2667 |  | 22.5 | 24 | 22.2 | 23 | 22.9
Sweden |  | MALILLA | MALILLA, Sweden | 57.40N | 15.82E | 98 | 1.00 (EUW) | 82-06 | 25660 | -22.1 |  | -33 | 36.8 | 27.9 | 31.3 | 29.3 | 30 | 29.5 |  | 25.2 | 28.7 | 27.2 | 27 | 27.0333
Sweden |  | MALMO/STURUP | MALMO/STURUP, Sweden | 55.55N | 13.37E | 106 | 1.00 (EUW) | 82-06 | 26360 | -15.3 |  | -27.9 | 32.4 | 26.1 | 28.2 | 27.2 | 27 | 27.1667 |  | 23.2 | 26.1 | 25.8 | 25 | 25.0333
Sweden |  | MALUNG | MALUNG, Sweden | 60.68N | 13.72E | 308 | 1.00 (EUW) | 82-06 | 24100 | -28.7 |  | -44 | 33.9 | 27.2 | 28.6 | 27.1 | 28 | 27.6333 |  | 24.3 | 26.3 | 24.7 | 25 | 25.1
Sweden |  | MASESKAR | MASESKAR, Sweden | 58.10N | 11.33E | 16 | 1.00 (EUW) | 96-06 | 25050 | N/A |  | N/A | N/A | 20 | 25.3 | 24.4 | 23 | 23.2333 |  | 18.6 | 23 | 23.4 | 22 | 21.6667
Sweden |  | NAIMAKKA | NAIMAKKA, Sweden | 68.68N | 21.53E | 403 | 1.00 (EUW) | 82-95 | 20600 | -37.9 |  | -44.8 | 28.5 | 23.3 | 23 | 22.8 | 23 | 23.0333 |  | 21 | 20.8 | 18.8 | 20 | 20.2
Sweden |  | NIDINGEN | NIDINGEN, Sweden | 57.30N | 11.90E | 2 | 1.00 (EUW) | 82-06 | 25180 | -9.4 |  | -21.6 | 31.4 | 22.5 | 24.6 | 24.7 | 24 | 23.9333 |  | 20.6 | 22.9 | 23.4 | 22 | 22.3
Sweden |  | NIKKALUOKTA | NIKKALUOKTA, Sweden | 67.85N | 19.03E | 468 | 1.00 (EUW) | 83-06 | 20360 | -38.6 |  | -46.8 | 27.6 | 23 | 23.9 | 22.4 | 23 | 23.1 |  | 20.3 | 21.9 | 20.5 | 21 | 20.9
Sweden |  | NORRKOPING/BRAVALLA | NORRKOPING/BRAVALLA, Sweden | 58.62N | 16.12E | 33 | 1.00 (EUW) | 82-93 | 25700 | -18.6 |  | -33.7 | 33.7 | 27.3 | 28.6 | 28.5 | 28 | 28.1333 |  | 25 | 26.7 | 25.4 | 26 | 25.7
Sweden |  | NORRKOPING/KUNGSANG | NORRKOPING/KUNGSANG, Sweden | 58.58N | 16.15E | 8 | 1.00 (EUW) | 82-06 | 25710 | -19.1 |  | -30.7 | 33.9 | 27.8 | 29.8 | 29 | 29 | 28.8667 |  | 25.1 | 27.2 | 26 | 26 | 26.1
Sweden |  | OLANDS NORRA UDDE | OLANDS NORRA UDDE, Sweden | 57.37N | 17.10E | 4 | 1.00 (EUW) | 82-95 | 25920 | -8.7 |  | -22.6 | 31.1 | 22.8 | 26.5 | 25.8 | 25 | 25.0333 |  | 21.1 | 24.2 | 23.1 | 23 | 22.8
Sweden |  | OLANDS SODRA UDDE | OLANDS SODRA UDDE, Sweden | 56.20N | 16.40E | 3 | 1.00 (EUW) | 96-06 | 26440 | -10.2 |  | -15.5 | 29.3 | 19.1 | 23.8 | 24 | 22 | 22.3 |  | 18 | 22.5 | 23.1 | 21 | 21.2
Sweden |  | OREBRO | OREBRO, Sweden | 59.23N | 15.05E | 55 | 1.00 (EUW) | 96-06 | 24320 | -21.3 |  | -30.8 | 32.7 | 26.6 | 29 | 27.8 | 28 | 27.8 |  | 24.6 | 27.5 | 26.2 | 26 | 26.1
Sweden |  | ORSKAR | ORSKAR, Sweden | 60.53N | 18.38E | 9 | 1.00 (EUW) | 96-06 | 24880 | -12.1 |  | -19.3 | 32.9 | 23.9 | 27.1 | 26.3 | 26 | 25.7667 |  | 21.9 | 24.8 | 24.2 | 24 | 23.6333
Sweden |  | OSBY | OSBY, Sweden | 56.37N | 13.95E | 85 | 1.00 (EUW) | 82-96 | 26260 | -15.7 |  | -29.5 | 35.9 | 27.8 | 30 | 28.7 | 29 | 28.8333 |  | 25.1 | 27 | 25.7 | 26 | 25.9333
Sweden |  | OSTERSUND FROSON | OSTERSUND FROSON, Sweden | 63.20N | 14.50E | 359 | 1.00 (EUW) | 82-06 | 22260 | -26.6 |  | -37.8 | 31 | 25.1 | 26.9 | 25.5 | 26 | 25.8333 |  | 22.2 | 24.2 | 23 | 23 | 23.1333
Sweden |  | OSTMARK | OSTMARK, Sweden | 60.35N | 12.65E | 310 | 1.00 (EUW) | 82-99 | 24000 | -23.5 |  | -39.3 | 32.8 | 27.2 | 28.5 | 27.7 | 28 | 27.8 |  | 24.3 | 26.1 | 24.3 | 25 | 24.9
Sweden |  | OVERKALIX SVARTBYN | OVERKALIX SVARTBYN, Sweden | 66.27N | 22.85E | 62 | 1.00 (EUW) | 96-06 | 21810 | -35.1 |  | -46.4 | 31.9 | 26.1 | 27.7 | 25.6 | 26 | 26.4667 |  | 23.8 | 26 | 23.5 | 24 | 24.4333
Sweden |  | PAJALA | PAJALA, Sweden | 67.22N | 23.40E | 168 | 1.00 (EUW) | 82-06 | 20960 | -34 |  | -43.2 | 29.5 | 26.4 | 26.7 | 24.6 | 26 | 25.9 |  | 23 | 25 | 22 | 23 | 23.3333
Sweden |  | PALKEM | PALKEM, Sweden | 66.38N | 21.63E | 261 | 1.00 (EUW) | 83-95 | 21640 | N/A |  | N/A | N/A | 25.5 | 23.7 | 23.8 | 24 | 24.3333 |  | 22.1 | 21.8 | 20.6 | 22 | 21.5
Sweden |  | PITE-RONNSKAR | PITE-RONNSKAR, Sweden | 65.03N | 21.57E | 4 | 1.00 (EUW) | 98-06 | 21760 | N/A |  | N/A | N/A | 20.2 | 23.2 | 22.5 | 22 | 21.9667 |  | 18.3 | 21.1 | 20.8 | 20 | 20.0667
Sweden |  | RANGEDALA | RANGEDALA, Sweden | 57.78N | 13.17E | 299 | 1.00 (EUW) | 96-06 | 25360 | -16.6 |  | -23.2 | 31.1 | 25.6 | 27.2 | 25.6 | 26 | 26.1333 |  | 23 | 25.1 | 24.5 | 24 | 24.2
Sweden |  | RITSEM | RITSEM, Sweden | 67.73N | 17.47E | 521 | 1.00 (EUW) | 82-97 | 20120 | -27.3 |  | -35.6 | 26.5 | 21.6 | 22.9 | 22.1 | 22 | 22.2 |  | 18.7 | 20.3 | 18.8 | 19 | 19.2667
Sweden |  | RONNEBY/KALLINGE | RONNEBY/KALLINGE, Sweden | 56.27N | 15.27E | 58 | 1.00 (EUW) | 82-06 | 26640 | -17.2 |  | -26.2 | 35.1 | 27 | 29.5 | 28.1 | 28 | 28.2 |  | 24.3 | 27.1 | 25.9 | 26 | 25.7667
Sweden |  | RORBACKSNAS | RORBACKSNAS, Sweden | 61.13N | 12.82E | 459 | 1.00 (EUW) | 82-95 | 23060 | N/A |  | N/A | N/A | 26.6 | 27.7 | 27.6 | 27 | 27.3 |  | 23.6 | 25.9 | 23.6 | 24 | 24.3667
Sweden |  | SARNA | SARNA, Sweden | 61.70N | 13.18E | 425 | 1.00 (EUW) | 82-99 | 23160 | -33.9 |  | -44.9 | 32.5 | 26.2 | 27 | 26.2 | 26 | 26.4667 |  | 22.8 | 24.7 | 23.5 | 24 | 23.6667
Sweden |  | SATENAS | SATENAS, Sweden | 58.43N | 12.72E | 54 | 1.00 (EUW) | 82-06 | 25200 | -18.1 |  | -28.6 | 32.1 | 25.1 | 27.5 | 26.9 | 27 | 26.5 |  | 22.9 | 25.5 | 24.8 | 24 | 24.4
Sweden |  | SINGO ISLAND | SINGO ISLAND, Sweden | 60.17N | 18.75E | 14 | 1.00 (EUW) | 82-95 | 24740 | -16.9 |  | -31.7 | 33.3 | 26.1 | 28.8 | 26.4 | 27 | 27.1 |  | 23.4 | 25.8 | 23 | 24 | 24.0667
Sweden |  | SKAGSUDDE | SKAGSUDDE, Sweden | 63.18N | 19.02E | 11 | 1.00 (EUW) | 96-06 | 22690 | -20.3 |  | -31 | 28.3 | 20.9 | 23.4 | 22.2 | 22 | 22.1667 |  | 18.3 | 21.7 | 21.2 | 20 | 20.4
Sweden |  | SKAVSTA | SKAVSTA, Sweden | 58.78N | 16.90E | 44 | 1.00 (EUW) | 94-06 | 24853 | -21.5 |  | -28.9 | 34.1 | 26.9 | 29.1 | 28.2 | 28 | 28.0667 |  | 24.1 | 27.1 | 26.9 | 26 | 26.0333
Sweden |  | SKILLINGE | SKILLINGE, Sweden | 55.48N | 14.32E | 5 | 1.00 (EUW) | 96-06 | 26250 | -12.2 |  | -16.5 | 29.9 | 23.1 | 26.8 | 25 | 25 | 24.9667 |  | 20.9 | 23.9 | 23 | 23 | 22.6
Sweden |  | SODERHAMN | SODERHAMN, Sweden | 61.25N | 17.10E | 28 | 1.00 (EUW) | 82-06 | 22861 | -21.5 |  | -31.1 | 35 | 27.4 | 29.7 | 27.1 | 28 | 28.0667 |  | 23.6 | 26.2 | 24 | 25 | 24.6
Sweden |  | STOCKHOLM/ARLANDA | STOCKHOLM/ARLANDA, Sweden | 59.65N | 17.95E | 61 | 1.00 (EUW) | 82-06 | 24600 | -19.5 |  | -31 | 34.8 | 27.2 | 30.1 | 28.8 | 29 | 28.7 |  | 25 | 27.9 | 26.8 | 27 | 26.5667
Sweden |  | STOCKHOLM/BROMMA | STOCKHOLM/BROMMA, Sweden | 59.37N | 17.90E | 14 | 1.00 (EUW) | 82-06 | 24640 | -19 |  | -30.2 | 34.8 | 26.9 | 30.1 | 28.6 | 29 | 28.5333 |  | 24.7 | 27.6 | 26.6 | 26 | 26.3
Sweden |  | STORLIEN | STORLIEN, Sweden | 63.30N | 12.12E | 644 | 1.00 (EUW) | 82-06 | 22060 | -24.8 |  | -36.8 | 29 | 22.8 | 24.4 | 23.6 | 24 | 23.6 |  | 20.2 | 21.9 | 20.7 | 21 | 20.9333
Sweden |  | SVEG | SVEG, Sweden | 62.02N | 14.37E | 363 | 1.00 (EUW) | 82-06 | 23240 | -31.4 |  | -45.9 | 33.6 | 27.6 | 28.2 | 26.8 | 28 | 27.5333 |  | 24 | 26.2 | 24 | 25 | 24.7333
Sweden |  | SVENSKA HOGARNA | SVENSKA HOGARNA, Sweden | 59.45N | 19.50E | 12 | 1.00 (EUW) | 82-06 | 24960 | -10.1 |  | -22.4 | 29.9 | 20.5 | 25.1 | 24.6 | 23 | 23.4 |  | 18.6 | 22.8 | 23 | 21 | 21.4667
Sweden |  | TANNAS | TANNAS, Sweden | 62.45N | 12.67E | 724 | 1.00 (EUW) | 96-06 | 23080 | -24.4 |  | -31.1 | 29.6 | 22.7 | 24.9 | 24.2 | 24 | 23.9333 |  | 20.4 | 22.6 | 21.8 | 22 | 21.6
Sweden |  | TIMRA/MIDLANDA | TIMRA/MIDLANDA, Sweden | 62.52N | 17.45E | 8 | 1.00 (EUW) | 82-06 | 23660 | -25.4 |  | -36.6 | 33.1 | 25.7 | 27.2 | 26.1 | 26 | 26.3333 |  | 22.7 | 24.8 | 23.8 | 24 | 23.7667
Sweden |  | UMEA | UMEA, Sweden | 63.80N | 20.28E | 8 | 1.00 (EUW) | 82-06 | 22860 | -27.4 |  | -37 | 32 | 25.1 | 27.2 | 25.2 | 26 | 25.8333 |  | 23 | 24.4 | 23.2 | 24 | 23.5333
Sweden |  | UNGSKAR | UNGSKAR, Sweden | 56.03N | 15.80E | 3 | 1.00 (EUW) | 82-95 | 26660 | -10.5 |  | -23.5 | 30.7 | 21.6 | 24.7 | 24 | 23 | 23.4333 |  | 19.7 | 22.7 | 22.4 | 22 | 21.6
Sweden |  | UPPSALA | UPPSALA, Sweden | 59.90N | 17.60E | 21 | 1.00 (EUW) | 82-06 | 24580 | -21.6 |  | -36.3 | 33.1 | 26.2 | 29.5 | 27.8 | 28 | 27.8333 |  | 24.2 | 27.1 | 25.9 | 26 | 25.7333
Sweden |  | VASTERAS/HASSLO AFB | VASTERAS/HASSLO AFB, Sweden | 59.58N | 16.63E | 31 | 1.00 (EUW) | 82-06 | 24460 | -20.3 |  | -33.2 | 34.4 | 27 | 29.8 | 28.7 | 29 | 28.5 |  | 25 | 27.1 | 26.1 | 26 | 26.0667
Sweden |  | VIDSEL | VIDSEL, Sweden | 65.88N | 20.15E | 182 | 1.00 (EUW) | 96-06 | 21540 | -35.1 |  | -43.1 | 34.3 | 27.1 | 28.5 | 26.4 | 27 | 27.3333 |  | 24.3 | 25.9 | 24.3 | 25 | 24.8333
Sweden |  | VILHELMINA | VILHELMINA, Sweden | 64.58N | 16.85E | 349 | 1.00 (EUW) | 96-06 | 22450 | -35.7 |  | -42.4 | 32.4 | 25.4 | 26.9 | 25.6 | 26 | 25.9667 |  | 23.2 | 24.7 | 23.7 | 24 | 23.8667
Sweden |  | VISBY | VISBY, Sweden | 57.67N | 18.35E | 47 | 1.00 (EUW) | 82-06 | 25900 | -14.2 |  | -25.1 | 33.1 | 24.9 | 27.9 | 27.2 | 27 | 26.6667 |  | 22.3 | 25.4 | 24.8 | 24 | 24.1667
Sweden |  | VUOGGATJALME | VUOGGATJALME, Sweden | 66.57N | 16.35E | 500 | 1.00 (EUW) | 82-95 | 21120 | -38 |  | -48 | 26.7 | 21.9 | 22.8 | 22.3 | 22 | 22.3333 |  | 19.5 | 20.6 | 18.3 | 19 | 19.4667
Switzerland |  | AIGLE | AIGLE, Switzerland | 46.33N | 6.92E | 383 | 1.00 (EUW) | 82-06 | 67120 | -11.8 |  | -23.6 | 34 | 29.1 | 29.9 | 29.9 | 30 | 29.6333 |  | 27 | 28.3 | 27.6 | 28 | 27.6333
Switzerland |  | ALTDORF | ALTDORF, Switzerland | 46.87N | 8.63E | 451 | 1.00 (EUW) | 82-06 | 66720 | -9.9 |  | -17.4 | 36.1 | 30.2 | 30.6 | 31.1 | 31 | 30.6333 |  | 27.5 | 28.4 | 27.9 | 28 | 27.9333
Switzerland |  | CHUR-EMS | CHUR-EMS, Switzerland | 46.87N | 9.53E | 556 | 1.00 (EUW) | 82-06 | 67860 | -12.5 |  | -20.5 | 38 | 31.4 | 33 | 32.8 | 32 | 32.4 |  | 28.7 | 29.9 | 29.2 | 29 | 29.2667
Switzerland |  | CIMETTA | CIMETTA, Switzerland | 46.20N | 8.80E | 1648 | 1.00 (EUW) | 82-06 | 67590 | -13 |  | -20.6 | 25.8 | 20.7 | 21.7 | 22.1 | 22 | 21.5 |  | 18.8 | 19.6 | 19.9 | 19 | 19.4333
Switzerland |  | COMPROVASCO | COMPROVASCO, Switzerland | 46.47N | 8.93E | 552 | 1.00 (EUW) | 89-06 | 67560 | -7.9 |  | -12.3 | 36.9 | 30.8 | 30.8 | 32.4 | 31 | 31.3333 |  | 28.1 | 28.5 | 28.7 | 28 | 28.4333
Switzerland |  | CORVATSCH | CORVATSCH, Switzerland | 46.42N | 9.82E | 3299 | 1.00 (EUW) | 82-06 | 67910 | -26 |  | -34.4 | 14 | 8.7 | 10.5 | 10.5 | 10 | 9.9 |  | 6.9 | 9 | 8.8 | 8 | 8.2333
Switzerland |  | DISENTIS | DISENTIS, Switzerland | 46.70N | 8.85E | 1180 | 1.00 (EUW) | 82-06 | 67820 | -15 |  | -24.2 | 32.1 | 27.3 | 27.9 | 28.1 | 28 | 27.7667 |  | 24.8 | 25.8 | 25.4 | 25 | 25.3333
Switzerland |  | FAHY | FAHY, Switzerland | 47.43N | 6.95E | 597 | 1.00 (EUW) | 82-06 | 66160 | -12.7 |  | -20.9 | 36.6 | 28.5 | 30.8 | 32.4 | 31 | 30.5667 |  | 26.1 | 28.1 | 28.1 | 27 | 27.4333
Switzerland |  | GENEVE-COINTRIN | GENEVE-COINTRIN, Switzerland | 46.25N | 6.13E | 416 | 1.00 (EUW) | 82-06 | 67000 | -9.2 |  | -17 | 38 | 31.9 | 33.3 | 33.7 | 33 | 32.9667 |  | 29.2 | 30.9 | 30.3 | 30 | 30.1333
Switzerland |  | GUETSCH | GUETSCH, Switzerland | 46.65N | 8.62E | 2284 | 1.00 (EUW) | 82-06 | 67500 | -19.4 |  | -29.9 | 23.9 | 17.8 | 19.4 | 19.2 | 19 | 18.8 |  | 15.3 | 16.7 | 16.8 | 16 | 16.2667
Switzerland |  | HOERNKI | HOERNKI, Switzerland | 47.37N | 8.95E | 1144 | 1.00 (EUW) | 94-06 | 66890 | -13.8 |  | -20.3 | 31.3 | 25.7 | 26.1 | 27.1 | 26 | 26.3 |  | 23.7 | 24.1 | 24.7 | 24 | 24.1667
Switzerland |  | INTERLAKEN | INTERLAKEN, Switzerland | 46.67N | 7.87E | 579 | 1.00 (EUW) | 82-06 | 67340 | -11.5 |  | -19.8 | 36.5 | 29.6 | 30.9 | 30.8 | 30 | 30.4333 |  | 27.1 | 28.5 | 27.7 | 28 | 27.7667
Switzerland |  | JUNGFRAUJOCH | JUNGFRAUJOCH, Switzerland | 46.55N | 7.98E | 3576 | 1.00 (EUW) | 82-06 | 67300 | -27.6 |  | -36.4 | 13.7 | 7.4 | 7.7 | 8.3 | 8 | 7.8 |  | 5.4 | 6.3 | 6.5 | 6 | 6.0667
Switzerland |  | LA CHAUX-DE-FONDS | LA CHAUX-DE-FONDS, Switzerland | 47.08N | 6.80E | 1019 | 1.00 (EUW) | 82-06 | 66120 | -18.9 |  | -32 | 32.8 | 26.8 | 28.3 | 28.7 | 28 | 27.9333 |  | 24.3 | 25.9 | 25.5 | 25 | 25.2333
Switzerland |  | LA DOLE | LA DOLE, Switzerland | 46.43N | 6.10E | 1675 | 1.00 (EUW) | 82-06 | 67020 | -15.2 |  | -25.6 | 29.6 | 21.8 | 23.6 | 23.8 | 23 | 23.0667 |  | 19.3 | 20.9 | 20.8 | 20 | 20.3333
Switzerland |  | LAEGERN | LAEGERN, Switzerland | 47.48N | 8.40E | 843 | 1.00 (EUW) | 82-06 | 66690 | -13 |  | -21.2 | 33 | 27 | 28.2 | 28.7 | 28 | 27.9667 |  | 24.7 | 26 | 26.1 | 26 | 25.6
Switzerland |  | LOCARNO-MAGADINO | LOCARNO-MAGADINO, Switzerland | 46.17N | 8.88E | 198 | 1.00 (EUW) | 82-06 | 67620 | -8.7 |  | -15.5 | 36.2 | 31.2 | 31.5 | 31.3 | 31 | 31.3333 |  | 29.1 | 29.8 | 29.3 | 29 | 29.4
Switzerland |  | LOCARNO-MONTI | LOCARNO-MONTI, Switzerland | 46.17N | 8.78E | 380 | 1.00 (EUW) | 82-06 | 67600 | -4.6 |  | -10.2 | 37 | 31.3 | 31.6 | 31.8 | 32 | 31.5667 |  | 28.8 | 29.6 | 29.3 | 29 | 29.2333
Switzerland |  | LUGANO | LUGANO, Switzerland | 46.00N | 8.97E | 276 | 1.00 (EUW) | 82-06 | 67700 | -6.3 |  | -11.5 | 37 | 31.2 | 31.8 | 32.1 | 32 | 31.7 |  | 29 | 30 | 29.9 | 30 | 29.6333
Switzerland |  | MONTANA | MONTANA, Switzerland | 46.32N | 7.48E | 1508 | 1.00 (EUW) | 82-06 | 67240 | -14.6 |  | -23.6 | 30.2 | 25.5 | 26.4 | 26.5 | 26 | 26.1333 |  | 22.9 | 24.4 | 23.9 | 24 | 23.7333
Switzerland |  | NAPF | NAPF, Switzerland | 47.00N | 7.93E | 1406 | 1.00 (EUW) | 87-06 | 66390 | -14 |  | -20.9 | 29.3 | 23.7 | 24 | 25.2 | 24 | 24.3 |  | 21.6 | 22.1 | 22.7 | 22 | 22.1333
Switzerland |  | NEUCHATEL | NEUCHATEL, Switzerland | 47.00N | 6.95E | 487 | 1.00 (EUW) | 82-06 | 66040 | -8.8 |  | -17 | 35.7 | 30 | 31.7 | 31.7 | 31 | 31.1333 |  | 27.5 | 29.5 | 28.7 | 29 | 28.5667
Switzerland |  | PAYERNE | PAYERNE, Switzerland | 46.82N | 6.95E | 491 | 1.00 (EUW) | 82-06 | 66100 | -11.1 |  | -19.5 | 36.8 | 30.4 | 32.1 | 32.2 | 32 | 31.5667 |  | 27.7 | 29.6 | 29 | 29 | 28.7667
Switzerland |  | PIOTTA | PIOTTA, Switzerland | 46.52N | 8.68E | 1016 | 1.00 (EUW) | 82-06 | 67530 | -12 |  | -18.6 | 37 | 28.2 | 29 | 29 | 29 | 28.7333 |  | 25.9 | 26.7 | 25.8 | 26 | 26.1333
Switzerland |  | PLAFFEIEN-OBERSCHRO | PLAFFEIEN-OBERSCHRO, Switzerland | 46.75N | 7.27E | 1041 | 1.00 (EUW) | 91-06 | 66280 | -13.4 |  | -18.9 | 31.4 | 26.2 | 26.8 | 27.7 | 27 | 26.9 |  | 24.2 | 24.8 | 25.1 | 25 | 24.7
Switzerland |  | ROBBIA | ROBBIA, Switzerland | 46.35N | 10.07E | 1078 | 1.00 (EUW) | 82-06 | 67940 | -14.4 |  | -19.8 | 32.9 | 27.8 | 27.7 | 28 | 28 | 27.8333 |  | 25 | 25.5 | 25.5 | 25 | 25.3333
Switzerland |  | SAENTIS | SAENTIS, Switzerland | 47.25N | 9.35E | 2500 | 1.00 (EUW) | 82-06 | 66800 | -21 |  | -31.2 | 29.7 | 14.6 | 17 | 16.2 | 16 | 15.9333 |  | 12.6 | 14.3 | 14.2 | 14 | 13.7
Switzerland |  | SAMEDAM-FLUGPLATZ | SAMEDAM-FLUGPLATZ, Switzerland | 46.53N | 9.88E | 1706 | 1.00 (EUW) | 82-06 | 67920 | -28.2 |  | -36.1 | 28.5 | 23.6 | 24.3 | 24.4 | 24 | 24.1 |  | 21.4 | 22.5 | 22.2 | 22 | 22.0333
Switzerland |  | SAN BERNARDINO | SAN BERNARDINO, Switzerland | 46.47N | 9.18E | 1638 | 1.00 (EUW) | 82-06 | 67830 | -17.1 |  | -26.1 | 27.9 | 22.4 | 23.1 | 23.7 | 23 | 23.0667 |  | 20.4 | 21.1 | 20.9 | 21 | 20.8
Switzerland |  | SION | SION, Switzerland | 46.22N | 7.33E | 481 | 1.00 (EUW) | 82-06 | 67200 | -10.9 |  | -18.8 | 37.7 | 31.6 | 32.4 | 32.9 | 32 | 32.3 |  | 29.2 | 30.3 | 29.5 | 30 | 29.6667
Switzerland |  | ST. GALLEN | ST. GALLEN, Switzerland | 47.43N | 9.40E | 791 | 1.00 (EUW) | 82-06 | 66810 | -13 |  | -22.4 | 33.6 | 27.4 | 29 | 28.7 | 28 | 28.3667 |  | 25.3 | 26.4 | 25.8 | 26 | 25.8333
Switzerland |  | STABIO | STABIO, Switzerland | 45.85N | 8.93E | 356 | 1.00 (EUW) | 82-06 | 67710 | -10.7 |  | -16.8 | 36.5 | 31.6 | 31.8 | 31.7 | 32 | 31.7 |  | 29.2 | 29.9 | 29.5 | 30 | 29.5333
Switzerland |  | WYNAU | WYNAU, Switzerland | 47.25N | 7.78E | 416 | 1.00 (EUW) | 82-06 | 66430 | -13 |  | -23.3 | 36.6 | 31 | 31.9 | 32.4 | 32 | 31.7667 |  | 28.2 | 29.4 | 28.8 | 29 | 28.8
Switzerland |  | ZUERICH METEOSCHWEI | ZUERICH METEOSCHWEI, Switzerland | 47.38N | 8.57E | 569 | 1.00 (EUW) | 82-06 | 66600 | -11 |  | -19.8 | 36.3 | 30.4 | 31.2 | 31.6 | 31 | 31.0667 |  | 27.7 | 28.8 | 28.4 | 28 | 28.3
Switzerland |  | ZURICH-KLOTEN | ZURICH-KLOTEN, Switzerland | 47.48N | 8.53E | 432 | 1.00 (EUW) | 82-06 | 66700 | -13.3 |  | -24.2 | 37.4 | 31.2 | 32.8 | 33.1 | 32 | 32.3667 |  | 28.8 | 30.1 | 29.8 | 30 | 29.5667
Syrian Arab Republic |  | ALEPPO INT. AEROPOR | ALEPPO INT. AEROPOR, Syrian Arab Republic | 36.18N | 37.20E | 384 | 2.00 (SYR) | 82-06 | 400070 | -4.1 |  | -7.8 | 47.9 | 39 | 41.3 | 41 | 40 | 40.4333 |  | 37 | 38.9 | 38.9 | 38 | 38.2667
Syrian Arab Republic |  | DAMASCUS INT. AIRPO | DAMASCUS INT. AIRPO, Syrian Arab Republic | 33.42N | 36.52E | 609 | 2.00 (SYR) | 82-06 | 400800 | -6.4 |  | -11.8 | 46.3 | 39.1 | 41.6 | 41 | 41 | 40.5667 |  | 37.2 | 39.2 | 39 | 38 | 38.4667
Syrian Arab Republic |  | DARAA | DARAA, Syrian Arab Republic | 32.60N | 36.10E | 543 | 2.00 (SYR) | 83-06 | 400950 | N/A |  | N/A | N/A | 37.1 | 37.6 | 36.4 | 37 | 37.0333 |  | 34.7 | 34.9 | 34.5 | 35 | 34.7
Syrian Arab Republic |  | DEIR EZZOR | DEIR EZZOR, Syrian Arab Republic | 35.32N | 40.15E | 212 | 2.00 (SYR) | 82-06 | 400450 | -3 |  | -6.2 | 48.8 | 42.3 | 44.8 | 43.7 | 44 | 43.6 |  | 40.6 | 43 | 41.9 | 42 | 41.8333
Syrian Arab Republic |  | HAMA | HAMA, Syrian Arab Republic | 35.12N | 36.75E | 303 | 2.00 (SYR) | 82-06 | 400300 | -3.3 |  | -10.5 | 46 | 39.6 | 41.2 | 40.9 | 41 | 40.5667 |  | 37.2 | 38.7 | 38.7 | 38 | 38.2
Syrian Arab Republic |  | LATTAKIA | LATTAKIA, Syrian Arab Republic | 35.53N | 35.77E | 7 | 2.00 (SYR) | 82-06 | 400220 | 0.4 |  | -5.4 | 43.2 | 33.9 | 33 | 32.9 | 33 | 33.2667 |  | 29.8 | 31 | 31.2 | 31 | 30.6667
Syrian Arab Republic |  | NABK | NABK, Syrian Arab Republic | 34.03N | 36.72E | 1333 | 2.00 (SYR) | 82-06 | 400830 | N/A |  | N/A | N/A | 31.9 | 34.2 | 33.4 | 33 | 33.1667 |  | 30.2 | 32.1 | 31.8 | 31 | 31.3667
Syrian Arab Republic |  | PALMYRA | PALMYRA, Syrian Arab Republic | 34.55N | 38.30E | 404 | 2.00 (SYR) | 82-06 | 400610 | -2.3 |  | -7.9 | 49.3 | 40.8 | 43.7 | 42.2 | 42 | 42.2333 |  | 38.7 | 41.4 | 40.5 | 40 | 40.2
Syrian Arab Republic |  | SAFITA | SAFITA, Syrian Arab Republic | 34.82N | 36.13E | 359 | 2.00 (SYR) | 82-06 | 400660 | 1 |  | -3.4 | 41.9 | 35 | 34.1 | 34.4 | 35 | 34.5 |  | 31.2 | 31.4 | 31.9 | 32 | 31.5
Taiwan |  | CHIANG KAI SHEK | CHIANG KAI SHEK, Taiwan, Province of China | 25.08N | 121.22E | 33 | 8.00 (CHN) | 82-06 | 466860 | 6.9 |  | 2.6 | 39.5 | 34.1 | 35.8 | 35.9 | 35 | 35.2667 |  | 33.1 | 34.2 | 34.1 | 34 | 33.8
Taiwan |  | CHIAYI | CHIAYI, Taiwan, Province of China | 23.50N | 120.45E | 28 | 8.00 (CHN) | 82-98 | 467480 | 6 |  | 1.2 | 38.2 | 34.4 | 34.6 | 33.7 | 34 | 34.2333 |  | 33.5 | 33.7 | 33 | 33 | 33.4
Taiwan |  | CHIAYI (TW-AFB) | CHIAYI (TW-AFB), Taiwan, Province of China | 23.47N | 120.38E | 25 | 8.00 (CHN) | 82-99 | 467460 | N/A |  | N/A | N/A | 34.8 | 34.9 | 34.2 | 35 | 34.6333 |  | 33.9 | 34 | 33.3 | 34 | 33.7333
Taiwan |  | CHIHHANG (TW-AFB) | CHIHHANG (TW-AFB), Taiwan, Province of China | 22.80N | 121.18E | 37 | 8.00 (CHN) | 82-99 | 467600 | N/A |  | N/A | N/A | 34.5 | 33.9 | 34 | 34 | 34.1333 |  | 33 | 33 | 32.9 | 33 | 32.9667
Taiwan |  | CHILUNG | CHILUNG, Taiwan, Province of China | 25.15N | 121.80E | 3 | 8.00 (CHN) | 82-98 | 466940 | 7.9 |  | 3.5 | 38.1 | 34.3 | 35.3 | 34.5 | 35 | 34.7 |  | 33.1 | 34 | 33.3 | 33 | 33.4667
Taiwan |  | CHINMEM/SHATOU(AFB) | CHINMEM/SHATOU(AFB), Taiwan, Province of China | 24.43N | 118.37E | 9 | 8.00 (CHN) | 82-99 | 467360 | 3.7 |  | -1.4 | 38.7 | 32.8 | 34.1 | 34.1 | 34 | 33.6667 |  | 31.8 | 33.1 | 33.1 | 33 | 32.6667
Taiwan |  | DONGSHA DAO | DONGSHA DAO, Taiwan, Province of China | 20.67N | 116.72E | 6 | 8.00 (CHN) | 82-06 | 597920 | 15.3 |  | 7.8 | 37.7 | 34.1 | 34.5 | 34.4 | 34 | 34.3333 |  | 33.1 | 33.6 | 33.1 | 33 | 33.2667
Taiwan |  | HENGCHUN | HENGCHUN, Taiwan, Province of China | 22.00N | 120.75E | 24 | 8.00 (CHN) | 82-06 | 595590 | 13.6 |  | 8.3 | 37.9 | 33 | 33.2 | 33.1 | 33 | 33.1 |  | 32.1 | 32.4 | 32.3 | 32 | 32.2667
Taiwan |  | HENGCHUN | HENGCHUN, Taiwan, Province of China | 21.93N | 120.83E | 13 | 8.00 (CHN) | 82-98 | 467520 | N/A |  | N/A | N/A | 33.8 | 33.9 | 33.6 | 34 | 33.7667 |  | 32.8 | 33 | 32.8 | 33 | 32.8667
Taiwan |  | HSINCHU (TW-AFB) | HSINCHU (TW-AFB), Taiwan, Province of China | 24.82N | 120.93E | 8 | 8.00 (CHN) | 82-99 | 467560 | N/A |  | N/A | N/A | 32.9 | 33.8 | 34.2 | 34 | 33.6333 |  | 32 | 33 | 33.2 | 33 | 32.7333
Taiwan |  | HSINCHU CITY | HSINCHU CITY, Taiwan, Province of China | 24.83N | 120.93E | 27 | 8.00 (CHN) | 82-98 | 467570 | 5.9 |  | -1.5 | 41.5 | 33.6 | 35.1 | 35 | 35 | 34.5667 |  | 32.7 | 33.9 | 33.8 | 33 | 33.4667
Taiwan |  | HUA-LIEN CITY | HUA-LIEN CITY, Taiwan, Province of China | 23.98N | 121.60E | 19 | 8.00 (CHN) | 82-98 | 466990 | 9.7 |  | 5.8 | 38.9 | 32.2 | 33.7 | 33.3 | 33 | 33.0667 |  | 31.5 | 32.5 | 32.2 | 32 | 32.0667
Taiwan |  | HULIEN AB (=593620) | HULIEN AB (=593620), Taiwan, Province of China | 24.03N | 121.62E | 16 | 8.00 (CHN) | 82-99 | 467630 | N/A |  | N/A | N/A | 33 | 33.7 | 34 | 34 | 33.5667 |  | 32 | 33 | 33 | 33 | 32.6667
Taiwan |  | ILAN CITY | ILAN CITY, Taiwan, Province of China | 24.75N | 121.78E | 7 | 8.00 (CHN) | 82-98 | 467080 | 8.2 |  | 3.7 | 40.8 | 32.9 | 34 | 34 | 34 | 33.6333 |  | 32.1 | 33.1 | 32.8 | 33 | 32.6667
Taiwan |  | KANGSHAN (TW-AFB) | KANGSHAN (TW-AFB), Taiwan, Province of China | 22.78N | 120.27E | 10 | 8.00 (CHN) | 82-99 | 467450 | N/A |  | N/A | N/A | 34 | 34.2 | 33.7 | 34 | 33.9667 |  | 33 | 33.2 | 32.8 | 33 | 33
Taiwan |  | KAOHSIUNG | KAOHSIUNG, Taiwan, Province of China | 22.63N | 120.28E | 29 | 8.00 (CHN) | 82-98 | 467440 | 10.1 |  | 6.1 | 40.9 | 33.2 | 34.4 | 33.2 | 34 | 33.6 |  | 32.4 | 33.1 | 32.4 | 33 | 32.6333
Taiwan |  | KAOHSIUNG INTL ARPT | KAOHSIUNG INTL ARPT, Taiwan, Province of China | 22.58N | 120.35E | 9 | 8.00 (CHN) | 82-06 | 467400 | 9.5 |  | 5.2 | 39.7 | 34.1 | 34.4 | 33.8 | 34 | 34.1 |  | 33.1 | 33.2 | 32.9 | 33 | 33.0667
Taiwan |  | LAN YU | LAN YU, Taiwan, Province of China | 22.03N | 121.55E | 325 | 8.00 (CHN) | 82-06 | 595670 | 12.9 |  | 9.6 | 42.2 | 30.2 | 30.6 | 30.4 | 30 | 30.4 |  | 29.1 | 29.6 | 29.4 | 29 | 29.3667
Taiwan |  | MAKUNG AB (=593450) | MAKUNG AB (=593450), Taiwan, Province of China | 23.58N | 119.62E | 31 | 8.00 (CHN) | 82-99 | 467340 | 8.2 |  | -0.5 | 41.4 | 32.4 | 33.1 | 33 | 33 | 32.8333 |  | 31.8 | 32.2 | 32.1 | 32 | 32.0333
Taiwan |  | MAZU | MAZU, Taiwan, Province of China | 26.17N | 119.93E | 91 | 8.00 (CHN) | 82-99 | 588490 | N/A |  | N/A | N/A | 31.4 | 32.6 | 32.2 | 32 | 32.0667 |  | 30 | 31.5 | 31.5 | 31 | 31
Taiwan |  | NANSHA DAO | NANSHA DAO, Taiwan, Province of China | 10.38N | 114.37E | 5 | 8.00 (CHN) | 96-06 | 599970 | 19.6 |  | 10.5 | 43.8 | 35.9 | 34.4 | 34.5 | 35 | 34.9333 |  | 34.2 | 33.3 | 33.1 | 34 | 33.5333
Taiwan |  | PENGHU ISLANDS | PENGHU ISLANDS, Taiwan, Province of China | 23.50N | 119.50E | 21 | 8.00 (CHN) | 82-98 | 467350 | 10.7 |  | 8.2 | 38.5 | 32.3 | 33.1 | 33 | 33 | 32.8 |  | 31.5 | 32.4 | 32.2 | 32 | 32.0333
Taiwan |  | PENGJIA YU | PENGJIA YU, Taiwan, Province of China | 25.63N | 122.07E | 102 | 8.00 (CHN) | 82-06 | 589740 | 6.8 |  | 0.9 | 37.5 | 31.5 | 32.7 | 32.7 | 32 | 32.3 |  | 30.7 | 31.9 | 31.9 | 32 | 31.5
Taiwan |  | PINGTUNG NORTH(AFB) | PINGTUNG NORTH(AFB), Taiwan, Province of China | 22.70N | 120.48E | 29 | 8.00 (CHN) | 82-99 | 467580 | N/A |  | N/A | N/A | 35.1 | 35.2 | 34.8 | 35 | 35.0333 |  | 34.2 | 34.2 | 33.9 | 34 | 34.1
Taiwan |  | PINGTUNG SOUTH(AFB) | PINGTUNG SOUTH(AFB), Taiwan, Province of China | 22.68N | 120.47E | 24 | 8.00 (CHN) | 82-99 | 467500 | N/A |  | N/A | N/A | 35.8 | 35.9 | 35.1 | 36 | 35.6 |  | 34.6 | 34.8 | 34.1 | 35 | 34.5
Taiwan |  | SUAO MET STATION | SUAO MET STATION, Taiwan, Province of China | 24.60N | 121.85E | 3 | 8.00 (CHN) | 85-98 | 467060 | 8.9 |  | 6 | 35.6 | 32.2 | 32.6 | 32.6 | 32 | 32.4667 |  | 31.5 | 31.9 | 31.7 | 32 | 31.7
Taiwan |  | SUNGSHAN/TAIPEI | SUNGSHAN/TAIPEI, Taiwan, Province of China | 25.07N | 121.55E | 6 | 8.00 (CHN) | 82-06 | 466960 | 6.4 |  | 1.2 | 40.5 | 35.1 | 36.4 | 35.9 | 36 | 35.8 |  | 34 | 35.1 | 34.2 | 34 | 34.4333
Taiwan |  | TAIBEI | TAIBEI, Taiwan, Province of China | 25.03N | 121.52E | 9 | 8.00 (CHN) | 82-06 | 589680 | 7.7 |  | 3.6 | 39.1 | 35.2 | 36.2 | 35.9 | 36 | 35.7667 |  | 34.1 | 35.1 | 34.5 | 35 | 34.5667
Taiwan |  | TAICHUNG (TW-AFB) | TAICHUNG (TW-AFB), Taiwan, Province of China | 24.18N | 120.65E | 112 | 8.00 (CHN) | 82-99 | 467510 | N/A |  | N/A | N/A | 34.9 | 35.2 | 35.2 | 35 | 35.1 |  | 33.8 | 34.2 | 34.2 | 34 | 34.0667
Taiwan |  | TAIDONG | TAIDONG, Taiwan, Province of China | 22.75N | 121.15E | 10 | 8.00 (CHN) | 82-06 | 595620 | 12.3 |  | 9.4 | 40.6 | 33.5 | 33.9 | 34.9 | 34 | 34.1 |  | 32.4 | 32.9 | 32.9 | 33 | 32.7333
Taiwan |  | TAINAN | TAINAN, Taiwan, Province of China | 23.00N | 120.22E | 14 | 8.00 (CHN) | 82-06 | 593580 | 8.8 |  | 4.9 | 38.3 | 34.1 | 34 | 33.8 | 34 | 33.9667 |  | 33.2 | 33.3 | 33.1 | 33 | 33.2
Taiwan |  | TAINAN (TW-AFB) | TAINAN (TW-AFB), Taiwan, Province of China | 22.95N | 120.20E | 19 | 8.00 (CHN) | 82-99 | 467430 | 5.3 |  | -3.8 | 39.5 | 34 | 34.2 | 33.9 | 34 | 34.0333 |  | 33.1 | 33.5 | 33 | 33 | 33.2
Taiwan |  | TAIZHONG | TAIZHONG, Taiwan, Province of China | 24.15N | 120.68E | 78 | 8.00 (CHN) | 82-06 | 591580 | 7.3 |  | 2.5 | 37.8 | 33.9 | 34.4 | 33.9 | 34 | 34.0667 |  | 33.1 | 33.5 | 33 | 33 | 33.2
Taiwan |  | TAOYUAN AB (=589650) | TAOYUAN AB (=589650), Taiwan, Province of China | 25.07N | 121.23E | 45 | 8.00 (CHN) | 82-99 | 466970 | N/A |  | N/A | N/A | 33.2 | 35 | 35.1 | 34 | 34.4333 |  | 32.6 | 33.9 | 33.8 | 33 | 33.4333
Taiwan |  | WU-CHI OBSERVATORY | WU-CHI OBSERVATORY, Taiwan, Province of China | 24.25N | 120.52E | 5 | 8.00 (CHN) | 82-98 | 467770 | 8.1 |  | 4.2 | 40.1 | 33.3 | 33.8 | 33.5 | 34 | 33.5333 |  | 32.5 | 32.8 | 32.7 | 33 | 32.6667
Taiwan |  | WUCHIA OBSERVATORY | WUCHIA OBSERVATORY, Taiwan, Province of China | 24.27N | 120.62E | 5 | 8.00 (CHN) | 82-99 | 467700 | 3.3 |  | -4.3 | 40.3 | 32.2 | 33.2 | 33.1 | 33 | 32.8333 |  | 31.8 | 32.3 | 32.1 | 32 | 32.0667
Tajikistan |  | DUSHANBE | DUSHANBE, Tajikistan | 38.55N | 68.78E | 800 | 5.00 (ASW) | 82-06 | 388360 | -10.7 |  | -19.5 | 42.9 | 38.1 | 39.3 | 38.6 | 39 | 38.6667 |  | 36.3 | 37.9 | 36.9 | 37 | 37.0333
Tajikistan |  | KHOROG | KHOROG, Tajikistan | 37.50N | 71.50E | 2077 | 5.00 (ASW) | 82-05 | 389540 | -20.3 |  | -26.8 | 37.8 | 31.9 | 33.6 | 33.8 | 33 | 33.1 |  | 29.5 | 32.3 | 32.1 | 31 | 31.3
Tajikistan |  | KHUDJAND | KHUDJAND, Tajikistan | 40.22N | 69.73E | 427 | 5.00 (ASW) | 82-95 | 385990 | -11.8 |  | -21.7 | 42.7 | 39.2 | 39 | 37 | 38 | 38.4 |  | 37.1 | 37.4 | 35.6 | 37 | 36.7
Tanzania |  | DAR ES SALAAM AIRPO | DAR ES SALAAM AIRPO, Tanzania, United Republic of | 6.87S | 39.20E | 53 | 3.00 (AFE) | 82-06 | 638940 | N/A |  | N/A | N/A | 30.3 | 30.2 | 30.8 | 30 | 30.4333 |  | 29.7 | 29.4 | 29.9 | 30 | 29.6667
Thailand |  | ARANYAPRATHET | ARANYAPRATHET, Thailand | 13.70N | 102.58E | 49 | 7.00 (SEA) | 82-06 | 484620 | 14.9 |  | 10.6 | 41.4 | 35.8 | 35 | 34.3 | 35 | 35.0333 |  | 34.7 | 33.9 | 33.3 | 34 | 33.9667
Thailand |  | BANGKOK METROPOLIS | BANGKOK METROPOLIS, Thailand | 13.73N | 100.57E | 4 | 7.00 (SEA) | 82-06 | 484550 | 16.8 |  | 10.7 | 40.1 | 35.2 | 34.9 | 34.4 | 35 | 34.8333 |  | 34.2 | 33.9 | 33.4 | 34 | 33.8333
Thailand |  | BHUMIBOL DAM | BHUMIBOL DAM, Thailand | 17.25N | 99.02E | 144 | 7.00 (SEA) | 83-06 | 483770 | 12.9 |  | 9.3 | 43.1 | 36.4 | 35.7 | 35.7 | 36 | 35.9333 |  | 35 | 34.3 | 34.4 | 35 | 34.5667
Thailand |  | BUA CHUM | BUA CHUM, Thailand | 15.27N | 101.18E | 50 | 7.00 (SEA) | 88-06 | 484180 | 12.9 |  | 8.4 | 42.7 | 36.5 | 35.8 | 35.2 | 36 | 35.8333 |  | 35.1 | 34.7 | 33.9 | 35 | 34.5667
Thailand |  | CHAIYAPHUM | CHAIYAPHUM, Thailand | 15.80N | 102.03E | 183 | 7.00 (SEA) | 83-06 | 484030 | 13 |  | 8.2 | 41.6 | 36 | 35.2 | 34.3 | 35 | 35.1667 |  | 34.7 | 34.1 | 33.1 | 34 | 33.9667
Thailand |  | CHANTHABURI | CHANTHABURI, Thailand | 12.60N | 102.12E | 4 | 7.00 (SEA) | 82-06 | 484800 | 17 |  | 13.1 | 38.6 | 33.2 | 33 | 32.7 | 33 | 32.9667 |  | 32.4 | 32.1 | 31.7 | 32 | 32.0667
Thailand |  | CHIANG MAI | CHIANG MAI, Thailand | 18.78N | 98.98E | 313 | 7.00 (SEA) | 82-06 | 483270 | 9.5 |  | 4.1 | 42.9 | 35.4 | 34.8 | 33.9 | 35 | 34.7 |  | 33.9 | 33.1 | 32.8 | 33 | 33.2667
Thailand |  | CHIANG RAI | CHIANG RAI, Thailand | 19.97N | 99.88E | 393 | 7.00 (SEA) | 82-06 | 483030 | 7.9 |  | 3.8 | 40.9 | 34.7 | 33.9 | 33.3 | 34 | 33.9667 |  | 33.2 | 32.6 | 32.1 | 33 | 32.6333
Thailand |  | CHON BURI | CHON BURI, Thailand | 13.37N | 100.98E | 2 | 7.00 (SEA) | 83-06 | 484590 | 17.5 |  | 12.4 | 39.7 | 35 | 34.7 | 34.2 | 35 | 34.6333 |  | 34.1 | 33.8 | 33.3 | 34 | 33.7333
Thailand |  | CHUMPHON | CHUMPHON, Thailand | 10.48N | 99.18E | 5 | 7.00 (SEA) | 82-06 | 485170 | 17.2 |  | 12.8 | 39.8 | 34.3 | 33.7 | 33.5 | 34 | 33.8333 |  | 33.3 | 32.9 | 32.6 | 33 | 32.9333
Thailand |  | DON MUANG | DON MUANG, Thailand | 13.92N | 100.60E | 12 | 7.00 (SEA) | 82-06 | 484560 | 16.8 |  | 11.5 | 41.2 | 37 | 36.1 | 35.9 | 36 | 36.3333 |  | 35.3 | 34.9 | 34.6 | 35 | 34.9333
Thailand |  | HAT YAI | HAT YAI, Thailand | 6.92N | 100.43E | 35 | 7.00 (SEA) | 82-06 | 485690 | 19.8 |  | 17.5 | 40.2 | 34.8 | 34.7 | 34.8 | 35 | 34.7667 |  | 33.9 | 33.8 | 33.8 | 34 | 33.8333
Thailand |  | HUA HIN | HUA HIN, Thailand | 12.58N | 99.95E | 6 | 7.00 (SEA) | 82-06 | 484750 | 18 |  | 12.6 | 39.8 | 35.1 | 35.3 | 34.9 | 35 | 35.1 |  | 34.1 | 34 | 33.7 | 34 | 33.9333
Thailand |  | KAM PAENG PHET | KAM PAENG PHET, Thailand | 16.48N | 99.53E | 81 | 7.00 (SEA) | 93-06 | 483800 | N/A |  | N/A | N/A | 36.6 | 35.7 | 34.9 | 36 | 35.7333 |  | 35 | 34.4 | 33.6 | 34 | 34.3333
Thailand |  | KANCHANABURI | KANCHANABURI, Thailand | 14.02N | 99.53E | 29 | 7.00 (SEA) | 83-06 | 484500 | 15.2 |  | 9.5 | 43.2 | 37.3 | 36.5 | 35.9 | 37 | 36.5667 |  | 35.4 | 35 | 34.4 | 35 | 34.9333
Thailand |  | KHLONG YAI | KHLONG YAI, Thailand | 11.77N | 102.88E | 4 | 7.00 (SEA) | 83-06 | 485010 | N/A |  | N/A | N/A | 32.7 | 32.1 | 32 | 32 | 32.2667 |  | 32.1 | 31.4 | 31.3 | 32 | 31.6
Thailand |  | KHON KAEN | KHON KAEN, Thailand | 16.43N | 102.83E | 166 | 7.00 (SEA) | 82-06 | 483810 | 11.4 |  | 6.5 | 43.3 | 36.3 | 35.3 | 34.5 | 35 | 35.3667 |  | 34.9 | 34 | 33.2 | 34 | 34.0333
Thailand |  | KO LANTA | KO LANTA, Thailand | 7.53N | 99.05E | 3 | 7.00 (SEA) | 83-06 | 485660 | 21.2 |  | 18.6 | 41.1 | 33.3 | 32.7 | 32.4 | 33 | 32.8 |  | 32.5 | 32 | 31.7 | 32 | 32.0667
Thailand |  | KO SAMUI | KO SAMUI, Thailand | 9.47N | 100.05E | 7 | 7.00 (SEA) | 83-06 | 485500 | 20.3 |  | 14.3 | 37.1 | 33.8 | 33.8 | 33.4 | 34 | 33.6667 |  | 33 | 32.9 | 32.6 | 33 | 32.8333
Thailand |  | KO SICHANG | KO SICHANG, Thailand | 13.17N | 100.80E | 26 | 7.00 (SEA) | 83-06 | 484600 | 19 |  | 17.3 | 42.5 | 33 | 32.7 | 32.2 | 33 | 32.6333 |  | 32.3 | 32 | 31.6 | 32 | 31.9667
Thailand |  | LAMPANG | LAMPANG, Thailand | 18.28N | 99.52E | 242 | 7.00 (SEA) | 82-06 | 483280 | 9.8 |  | 4.8 | 43 | 36.1 | 35.8 | 34.9 | 36 | 35.6 |  | 34.7 | 34.3 | 33.6 | 34 | 34.2
Thailand |  | LAMPHUN | LAMPHUN, Thailand | 18.57N | 99.03E | 298 | 7.00 (SEA) | 88-06 | 483290 | 9.5 |  | 4.5 | 43.2 | 36.3 | 35 | 34.5 | 35 | 35.2667 |  | 34.7 | 33.7 | 33.1 | 34 | 33.8333
Thailand |  | LOEI | LOEI, Thailand | 17.45N | 101.73E | 254 | 7.00 (SEA) | 82-06 | 483530 | 8.6 |  | 2.8 | 42.7 | 35.2 | 34.8 | 34.2 | 35 | 34.7333 |  | 34 | 33.5 | 33 | 34 | 33.5
Thailand |  | LOP BURI | LOP BURI, Thailand | 14.80N | 100.62E | 11 | 7.00 (SEA) | 83-06 | 484260 | 15.8 |  | 12 | 41.3 | 36.1 | 35.6 | 34.9 | 36 | 35.5333 |  | 34.9 | 34.5 | 33.8 | 34 | 34.4
Thailand |  | MAE HONG SON | MAE HONG SON, Thailand | 19.30N | 97.83E | 269 | 7.00 (SEA) | 82-06 | 483000 | 10.5 |  | 6.2 | 44.1 | 35.7 | 34.6 | 34.1 | 35 | 34.8 |  | 34.1 | 33.2 | 32.7 | 33 | 33.3333
Thailand |  | MAE SARIANG | MAE SARIANG, Thailand | 18.17N | 97.93E | 213 | 7.00 (SEA) | 82-06 | 483250 | 9 |  | 2.8 | 43.4 | 34.6 | 33.3 | 33.1 | 34 | 33.6667 |  | 33 | 31.9 | 31.8 | 32 | 32.2333
Thailand |  | MAE SOT | MAE SOT, Thailand | 16.67N | 98.55E | 197 | 7.00 (SEA) | 82-06 | 483750 | 10.3 |  | 5.3 | 42.9 | 33.3 | 32.3 | 32 | 33 | 32.5333 |  | 32 | 31.1 | 30.8 | 31 | 31.3
Thailand |  | MUKDAHAN | MUKDAHAN, Thailand | 16.53N | 104.72E | 139 | 7.00 (SEA) | 83-06 | 483830 | 11.2 |  | 6.5 | 41.8 | 35.5 | 34.5 | 33.9 | 35 | 34.6333 |  | 34.2 | 33.4 | 32.8 | 33 | 33.4667
Thailand |  | NAKHON PHANOM | NAKHON PHANOM, Thailand | 17.42N | 104.78E | 148 | 7.00 (SEA) | 83-06 | 483570 | 9.9 |  | 4.2 | 42.1 | 35.1 | 34.2 | 33.7 | 34 | 34.3333 |  | 33.7 | 33.1 | 32.5 | 33 | 33.1
Thailand |  | NAKHON RATCHASIMA | NAKHON RATCHASIMA, Thailand | 14.97N | 102.08E | 188 | 7.00 (SEA) | 82-06 | 484310 | 12.8 |  | 8.1 | 42.1 | 36.7 | 36 | 35.1 | 36 | 35.9333 |  | 35.5 | 34.9 | 34.1 | 35 | 34.8333
Thailand |  | NAKHON SAWAN | NAKHON SAWAN, Thailand | 15.80N | 100.17E | 35 | 7.00 (SEA) | 82-06 | 484000 | 13.4 |  | 7.6 | 42.4 | 37.1 | 36.5 | 35.3 | 36 | 36.3 |  | 35.7 | 35.1 | 34.2 | 35 | 35
Thailand |  | NAKHON SI THAMMARAT | NAKHON SI THAMMARAT, Thailand | 8.53N | 99.95E | 9 | 7.00 (SEA) | 83-06 | 485520 | 19.9 |  | 17 | 39.5 | 34.9 | 35.2 | 34.7 | 35 | 34.9333 |  | 34.1 | 34 | 33.8 | 34 | 33.9667
Thailand |  | NAN | NAN, Thailand | 18.77N | 100.77E | 201 | 7.00 (SEA) | 82-06 | 483310 | 9.4 |  | 4.2 | 42.7 | 36.1 | 35.2 | 34.6 | 35 | 35.3 |  | 34.5 | 33.9 | 33.2 | 34 | 33.8667
Thailand |  | NARATHIWAT | NARATHIWAT, Thailand | 6.42N | 101.82E | 5 | 7.00 (SEA) | 82-06 | 485830 | 20.5 |  | 17.7 | 39.1 | 34.3 | 34 | 34.1 | 34 | 34.1333 |  | 33.1 | 32.7 | 32.9 | 33 | 32.9
Thailand |  | NONG KHAI | NONG KHAI, Thailand | 17.87N | 102.72E | 175 | 7.00 (SEA) | 83-06 | 483520 | 11.1 |  | 6.1 | 42.2 | 35.6 | 34.7 | 34.1 | 35 | 34.8 |  | 34.4 | 33.5 | 33.1 | 34 | 33.6667
Thailand |  | PATTANI | PATTANI, Thailand | 6.78N | 101.15E | 9 | 7.00 (SEA) | 83-05 | 485800 | 19.7 |  | 15.8 | 41.2 | 34.3 | 34.4 | 34.1 | 34 | 34.2667 |  | 33.7 | 33.4 | 33.2 | 33 | 33.4333
Thailand |  | PHATTHAYA | PHATTHAYA, Thailand | 12.92N | 100.87E | 61 | 7.00 (SEA) | 95-06 | 484610 | N/A |  | N/A | N/A | 33.1 | 32.6 | 32.5 | 33 | 32.7333 |  | 32.3 | 31.8 | 31.7 | 32 | 31.9333
Thailand |  | PHAYAO | PHAYAO, Thailand | 19.13N | 99.90E | 399 | 7.00 (SEA) | 88-06 | 483100 | 8.1 |  | 1 | 41.6 | 35 | 34 | 33.5 | 34 | 34.1667 |  | 33.4 | 32.8 | 32.3 | 33 | 32.8333
Thailand |  | PHETCHABUN | PHETCHABUN, Thailand | 16.43N | 101.15E | 116 | 7.00 (SEA) | 82-06 | 483790 | 11.4 |  | 6 | 41.9 | 36.1 | 34.9 | 34.1 | 35 | 35.0333 |  | 34.5 | 33.6 | 32.8 | 34 | 33.6333
Thailand |  | PHETCHABURI | PHETCHABURI, Thailand | 13.15N | 100.07E | 4 | 7.00 (SEA) | 93-06 | 484650 | 16.1 |  | 10.4 | 37.2 | 34.5 | 34.8 | 34.1 | 34 | 34.4667 |  | 33.2 | 33.2 | 33 | 33 | 33.1333
Thailand |  | PHITSANULOK | PHITSANULOK, Thailand | 16.78N | 100.27E | 45 | 7.00 (SEA) | 82-06 | 483780 | 13.6 |  | 9 | 42.4 | 36.4 | 35.2 | 34.6 | 35 | 35.4 |  | 35 | 34.2 | 33.6 | 34 | 34.2667
Thailand |  | PHRAE | PHRAE, Thailand | 18.17N | 100.17E | 162 | 7.00 (SEA) | 83-06 | 483300 | 10.6 |  | 5.5 | 42.5 | 36.1 | 35.1 | 34.4 | 35 | 35.2 |  | 34.5 | 33.8 | 33.2 | 34 | 33.8333
Thailand |  | PHUKET | PHUKET, Thailand | 7.88N | 98.40E | 3 | 7.00 (SEA) | 83-06 | 485640 | 22.1 |  | 19.9 | 38 | 33.4 | 33 | 33.1 | 33 | 33.1667 |  | 32.7 | 32.4 | 32.4 | 33 | 32.5
Thailand |  | PHUKET AIRPORT | PHUKET AIRPORT, Thailand | 8.13N | 98.32E | 9 | 7.00 (SEA) | 82-06 | 485650 | 19.8 |  | 17.6 | 44 | 34.5 | 34.1 | 34 | 34 | 34.2 |  | 33 | 32.8 | 32.5 | 33 | 32.7667
Thailand |  | PRACHIN BURI | PRACHIN BURI, Thailand | 14.05N | 101.37E | 6 | 7.00 (SEA) | 83-06 | 484300 | 15.7 |  | 10.4 | 44.8 | 35.8 | 34.9 | 34.4 | 35 | 35.0333 |  | 34.7 | 34 | 33.3 | 34 | 34
Thailand |  | PRACHUAP KHIRIKHAN | PRACHUAP KHIRIKHAN, Thailand | 11.82N | 99.82E | 5 | 7.00 (SEA) | 82-06 | 485000 | 17 |  | 13.5 | 42.4 | 35.1 | 35 | 34.3 | 35 | 34.8 |  | 33.8 | 33.8 | 33 | 34 | 33.5333
Thailand |  | RANONG | RANONG, Thailand | 9.98N | 98.62E | 8 | 7.00 (SEA) | 82-06 | 485320 | 18.6 |  | 15.1 | 40.2 | 33.2 | 32.5 | 32.1 | 33 | 32.6 |  | 32.3 | 31.7 | 31.4 | 32 | 31.8
Thailand |  | RAYONG | RAYONG, Thailand | 12.63N | 101.35E | 5 | 7.00 (SEA) | 91-06 | 484780 | 16.9 |  | 13.3 | 40.5 | 35.6 | 35.3 | 34.8 | 35 | 35.2333 |  | 34.2 | 34 | 33.2 | 34 | 33.8
Thailand |  | ROI ET | ROI ET, Thailand | 16.05N | 103.68E | 142 | 7.00 (SEA) | 83-06 | 484050 | 12 |  | 7.3 | 42.2 | 35.7 | 34.7 | 33.8 | 35 | 34.7333 |  | 34.5 | 33.7 | 32.8 | 34 | 33.6667
Thailand |  | SAKON NAKHON | SAKON NAKHON, Thailand | 17.15N | 104.13E | 172 | 7.00 (SEA) | 82-06 | 483560 | 9.3 |  | 3.3 | 42.1 | 35.3 | 34.5 | 33.7 | 35 | 34.5 |  | 34 | 33.1 | 32.6 | 33 | 33.2333
Thailand |  | SATTAHIP | SATTAHIP, Thailand | 12.68N | 100.98E | 18 | 7.00 (SEA) | 82-06 | 484770 | 16.9 |  | 12.3 | 41.7 | 34.6 | 34.1 | 33.7 | 34 | 34.1333 |  | 33.5 | 33.2 | 32.8 | 33 | 33.1667
Thailand |  | SONGKHLA | SONGKHLA, Thailand | 7.20N | 100.62E | 9 | 7.00 (SEA) | 89-06 | 485680 | 21.7 |  | 18 | 39.4 | 34.6 | 34.6 | 34.8 | 35 | 34.6667 |  | 33.6 | 33.5 | 33.7 | 34 | 33.6
Thailand |  | SUPHAN BURI | SUPHAN BURI, Thailand | 14.47N | 100.13E | 8 | 7.00 (SEA) | 83-06 | 484250 | 15.6 |  | 10.6 | 42.5 | 36.4 | 35.9 | 35.6 | 36 | 35.9667 |  | 35.2 | 34.7 | 34.4 | 35 | 34.7667
Thailand |  | SURAT THANI | SURAT THANI, Thailand | 9.12N | 99.15E | 11 | 7.00 (SEA) | 82-06 | 485510 | 18.2 |  | 15.2 | 40.9 | 34.7 | 34.5 | 34.2 | 34 | 34.4667 |  | 33.8 | 33.5 | 33.1 | 33 | 33.4667
Thailand |  | SURIN | SURIN, Thailand | 14.88N | 103.50E | 147 | 7.00 (SEA) | 82-06 | 484320 | 12.7 |  | 7.9 | 41 | 35.5 | 34.7 | 33.7 | 35 | 34.6333 |  | 34.4 | 33.5 | 32.8 | 34 | 33.5667
Thailand |  | TAK | TAK, Thailand | 16.88N | 99.15E | 124 | 7.00 (SEA) | 83-06 | 483760 | 12.5 |  | 9.3 | 43.6 | 36.2 | 35.2 | 34.9 | 35 | 35.4333 |  | 34.2 | 33.8 | 33.4 | 34 | 33.8
Thailand |  | THA TUM | THA TUM, Thailand | 15.32N | 103.68E | 129 | 7.00 (SEA) | 88-06 | 484160 | 13.4 |  | 10.6 | 43.1 | 36 | 35.2 | 34.3 | 35 | 35.1667 |  | 35 | 34 | 33.2 | 34 | 34.0667
Thailand |  | THONG PHA PHUM | THONG PHA PHUM, Thailand | 14.75N | 98.63E | 99 | 7.00 (SEA) | 88-06 | 484210 | 12.5 |  | 7 | 42.5 | 34.6 | 33.9 | 33.7 | 34 | 34.0667 |  | 33 | 32.4 | 32.1 | 33 | 32.5
Thailand |  | TRANG | TRANG, Thailand | 7.52N | 99.62E | 16 | 7.00 (SEA) | 82-06 | 485670 | 19.3 |  | 16.2 | 39.7 | 34.2 | 33.5 | 33.5 | 34 | 33.7333 |  | 33.3 | 32.7 | 32.8 | 33 | 32.9333
Thailand |  | UBON RATCHATHANI | UBON RATCHATHANI, Thailand | 15.25N | 104.87E | 127 | 7.00 (SEA) | 82-06 | 484070 | 12.9 |  | 9.1 | 41.6 | 35.3 | 34.4 | 33.8 | 35 | 34.5 |  | 34.2 | 33.3 | 32.7 | 33 | 33.4
Thailand |  | UDON THANI | UDON THANI, Thailand | 17.38N | 102.80E | 182 | 7.00 (SEA) | 82-06 | 483540 | 10.6 |  | 5.5 | 42.6 | 36 | 35.2 | 34.3 | 35 | 35.1667 |  | 34.7 | 33.9 | 33.2 | 34 | 33.9333
Thailand |  | UTTARADIT | UTTARADIT, Thailand | 17.62N | 100.10E | 64 | 7.00 (SEA) | 82-06 | 483510 | 13.5 |  | 9.1 | 43.4 | 37.5 | 35.9 | 35.2 | 36 | 36.2 |  | 35.5 | 34.7 | 33.9 | 35 | 34.7
Togo |  | LOME | LOME, Togo | 6.17N | 1.25E | 25 | 0.00 (GRW) | 82-06 | 653870 | 18.6 |  | 13.7 | 41.1 | 32 | 30 | 29.6 | 31 | 30.5333 |  | 31 | 29.1 | 28.7 | 30 | 29.6
Tonga |  | FUAAMOTU | FUAAMOTU, Tonga | 21.23S | 175.15W | 41 | 13.00 (PCT) | 82-06 | 917920 | 11.8 |  | 8 | 35 | 27.2 | 27 | 26.7 | 27 | 26.9667 |  | 26.2 | 25.7 | 25.5 | 26 | 25.8
Tonga |  | HAAPAI | HAAPAI, Tonga | 19.80S | 174.35W | 3 | 13.00 (PCT) | 82-02 | 917840 | N/A |  | N/A | N/A | 27.8 | 28 | 27.2 | 28 | 27.6667 |  | 27.1 | 26.8 | 26.3 | 27 | 26.7333
Trinidad and Tobago |  | CROWN POINT AIRPORT | CROWN POINT AIRPORT, Trinidad and Tobago | 11.15N | 60.83W | 6 | -4.00 (SAZ) | 82-06 | 789620 | 20.6 |  | 16.6 | 33.5 | 31.6 | 31.2 | 31.7 | 32 | 31.5 |  | 31 | 30.7 | 31.1 | 31 | 30.9333
Trinidad and Tobago |  | PIARCO INT. AIRPORT | PIARCO INT. AIRPORT, Trinidad and Tobago | 10.62N | 61.35W | 15 | -4.00 (SAZ) | 82-06 | 789700 | 18.9 |  | 17.1 | 38.2 | 32.8 | 33 | 33.5 | 33 | 33.1 |  | 31.9 | 32.1 | 32.9 | 32 | 32.3
Tunisia |  | BIZERTE | BIZERTE, Tunisia | 37.25N | 9.80E | 3 | 1.00 (EUW) | 82-06 | 607140 | 0.8 |  | -1.6 | 47.8 | 38.6 | 40.1 | 39.9 | 40 | 39.5333 |  | 34.1 | 36.5 | 36.8 | 36 | 35.8
Tunisia |  | DJERBA MELLITA | DJERBA MELLITA, Tunisia | 33.87N | 10.77E | 4 | 1.00 (EUW) | 82-06 | 607690 | 3.8 |  | 0.2 | 48.6 | 40.8 | 41.2 | 41.1 | 41 | 41.0333 |  | 36.1 | 37.9 | 38 | 37 | 37.3333
Tunisia |  | GABES | GABES, Tunisia | 33.88N | 10.10E | 5 | 1.00 (EUW) | 82-06 | 607650 | 2.8 |  | -0.4 | 49.8 | 38.6 | 40.2 | 39.4 | 39 | 39.4 |  | 32.9 | 34.9 | 35.2 | 34 | 34.3333
Tunisia |  | GAFSA | GAFSA, Tunisia | 34.42N | 8.82E | 314 | 1.00 (EUW) | 82-06 | 607450 | -1.1 |  | -4 | 47.7 | 42.4 | 43.5 | 43.1 | 43 | 43 |  | 39.8 | 41.2 | 40.8 | 41 | 40.6
Tunisia |  | HABIB BOURGUIBA INT | HABIB BOURGUIBA INT, Tunisia | 35.75N | 10.75E | 3 | 1.00 (EUW) | 86-06 | 607403 | 3 |  | -0.1 | 50.3 | 38.1 | 40.6 | 41.2 | 40 | 39.9667 |  | 34.1 | 36.1 | 36.9 | 36 | 35.7
Tunisia |  | JENDOUBA | JENDOUBA, Tunisia | 36.48N | 8.80E | 144 | 1.00 (EUW) | 82-06 | 607250 | -0.6 |  | -3.3 | 48.7 | 42.2 | 43.8 | 43.7 | 43 | 43.2333 |  | 39.2 | 41.2 | 40.8 | 40 | 40.4
Tunisia |  | KAIROUAN | KAIROUAN, Tunisia | 35.67N | 10.10E | 68 | 1.00 (EUW) | 82-06 | 607350 | 1.8 |  | -1.8 | 49.1 | 43.4 | 44 | 43.8 | 44 | 43.7333 |  | 39 | 41.2 | 41 | 40 | 40.4
Tunisia |  | KELIBIA | KELIBIA, Tunisia | 36.85N | 11.08E | 30 | 1.00 (EUW) | 82-06 | 607200 | 3.6 |  | 0.3 | 43.2 | 32.1 | 34.8 | 34.6 | 34 | 33.8333 |  | 29.7 | 32 | 32.5 | 31 | 31.4
Tunisia |  | MONASTIR-SKANES | MONASTIR-SKANES, Tunisia | 35.67N | 10.75E | 3 | 1.00 (EUW) | 82-06 | 607400 | 2.9 |  | -0.1 | 49 | 38 | 40.2 | 40.7 | 40 | 39.6333 |  | 33.8 | 36.4 | 36.1 | 35 | 35.4333
Tunisia |  | SFAX EL-MAOU | SFAX EL-MAOU, Tunisia | 34.72N | 10.68E | 23 | 1.00 (EUW) | 82-06 | 607500 | 1.4 |  | -0.5 | 48.9 | 38.2 | 39.1 | 39.2 | 39 | 38.8333 |  | 34 | 35.9 | 36 | 35 | 35.3
Tunisia |  | TABARKA | TABARKA, Tunisia | 36.95N | 8.75E | 21 | 1.00 (EUW) | 82-06 | 607100 | 2 |  | -2.1 | 47.4 | 39.8 | 42.1 | 41.2 | 41 | 41.0333 |  | 35.9 | 38.7 | 38.1 | 38 | 37.5667
Tunisia |  | THALA | THALA, Tunisia | 35.55N | 8.68E | 1092 | 1.00 (EUW) | 82-06 | 607380 | -2.7 |  | -6.8 | 41.5 | 36.2 | 37.6 | 36.9 | 37 | 36.9 |  | 33.8 | 35.8 | 35.2 | 35 | 34.9333
Tunisia |  | TOZEUR | TOZEUR, Tunisia | 33.92N | 8.17E | 86 | 1.00 (EUW) | 82-06 | 607600 | 2.5 |  | -1.8 | 49.8 | 44.2 | 45.7 | 45 | 45 | 44.9667 |  | 41.9 | 43.3 | 42.8 | 43 | 42.6667
Tunisia |  | TUNIS-CARTHAGE | TUNIS-CARTHAGE, Tunisia | 36.83N | 10.23E | 4 | 1.00 (EUW) | 82-06 | 607150 | 2.2 |  | -0.9 | 49.1 | 39.2 | 40.9 | 40.5 | 40 | 40.2 |  | 35 | 37.1 | 37.2 | 36 | 36.4333
Turkey |  | ADANA | ADANA, Turkey | 36.98N | 35.30E | 20 | 2.00 (EUE) | 83-06 | 173520 | -1.5 |  | -6.3 | 44.3 | 37.8 | 37.1 | 38.8 | 38 | 37.9 |  | 34.8 | 35 | 35.9 | 35 | 35.2333
Turkey |  | ADANA/INCIRLIK AB | ADANA/INCIRLIK AB, Turkey | 37.00N | 35.43E | 73 | 2.00 (EUE) | 82-06 | 691464 | -2.7 |  | -7.3 | 44.3 | 37.8 | 37.9 | 38.5 | 38 | 38.0667 |  | 34.2 | 35.8 | 36 | 35 | 35.3333
Turkey |  | ADANA/INCIRLIK AFB | ADANA/INCIRLIK AFB, Turkey | 37.00N | 35.42E | 76 | 2.00 (EUE) | 82-06 | 173500 | -2.3 |  | -7.8 | 43.7 | 37.1 | 37.8 | 38.1 | 38 | 37.6667 |  | 34.2 | 35.2 | 35.2 | 35 | 34.8667
Turkey |  | AFYON | AFYON, Turkey | 38.75N | 30.53E | 1034 | 2.00 (EUE) | 82-06 | 171900 | -14.5 |  | -22.1 | 38.7 | 31.7 | 34.5 | 35.1 | 34 | 33.7667 |  | 29.5 | 32.5 | 32.8 | 32 | 31.6
Turkey |  | AKHISAR | AKHISAR, Turkey | 38.92N | 27.85E | 93 | 2.00 (EUE) | 82-06 | 171840 | -5.7 |  | -10.2 | 44 | 37.5 | 40.2 | 39 | 39 | 38.9 |  | 35.4 | 37.7 | 36.9 | 37 | 36.6667
Turkey |  | ANTALYA | ANTALYA, Turkey | 36.87N | 30.73E | 54 | 2.00 (EUE) | 82-06 | 173000 | -0.9 |  | -7 | 45 | 37.7 | 40.9 | 40.1 | 40 | 39.5667 |  | 35.1 | 38.2 | 37.7 | 37 | 37
Turkey |  | AYDIN | AYDIN, Turkey | 37.85N | 27.85E | 56 | 2.00 (EUE) | 83-06 | 172340 | -2.6 |  | -5.9 | 46.7 | 38.2 | 40.5 | 39 | 39 | 39.2333 |  | 36.2 | 38 | 37 | 37 | 37.0667
Turkey |  | BALIKESIR | BALIKESIR, Turkey | 39.62N | 27.92E | 102 | 2.00 (EUE) | 82-06 | 171500 | -9.1 |  | -16.8 | 43.8 | 35.9 | 38.9 | 37.7 | 38 | 37.5 |  | 33.5 | 35.8 | 34.9 | 35 | 34.7333
Turkey |  | BANDIRMA | BANDIRMA, Turkey | 40.32N | 27.97E | 42 | 2.00 (EUE) | 82-06 | 171150 | -6.8 |  | -13 | 43.5 | 33 | 34.3 | 33.8 | 34 | 33.7 |  | 30.2 | 31.3 | 30.9 | 31 | 30.8
Turkey |  | BODRUM | BODRUM, Turkey | 37.03N | 27.43E | 26 | 2.00 (EUE) | 82-06 | 172900 | -0.4 |  | -7.7 | 43.3 | 36.5 | 39.8 | 38.5 | 38 | 38.2667 |  | 34.5 | 36.6 | 36.2 | 36 | 35.7667
Turkey |  | BOLU | BOLU, Turkey | 40.73N | 31.60E | 743 | 2.00 (EUE) | 82-06 | 170700 | -14.5 |  | -23.4 | 40.3 | 31.1 | 33.8 | 33.7 | 33 | 32.8667 |  | 28.5 | 30.5 | 30.9 | 30 | 29.9667
Turkey |  | BURSA | BURSA, Turkey | 40.18N | 29.07E | 100 | 2.00 (EUE) | 82-06 | 171160 | -7.8 |  | -16.8 | 43 | 34.7 | 37.4 | 35.9 | 36 | 36 |  | 32.2 | 34.1 | 33.9 | 33 | 33.4
Turkey |  | CANAKKALE | CANAKKALE, Turkey | 40.13N | 26.40E | 6 | 2.00 (EUE) | 82-06 | 171120 | -5 |  | -10 | 39 | 32.3 | 34.6 | 34.1 | 34 | 33.6667 |  | 30.5 | 32.7 | 32.4 | 32 | 31.8667
Turkey |  | CORUM | CORUM, Turkey | 40.55N | 34.95E | 776 | 2.00 (EUE) | 82-06 | 170840 | -15.6 |  | -27.5 | 42.1 | 32.4 | 35.6 | 36.3 | 35 | 34.7667 |  | 29.8 | 33 | 33.2 | 32 | 32
Turkey |  | DALAMAN | DALAMAN, Turkey | 36.70N | 28.78E | 9 | 2.00 (EUE) | 91-06 | 172950 | -0.2 |  | -4.1 | 46.2 | 36.1 | 39.2 | 38.2 | 38 | 37.8333 |  | 33.1 | 36 | 34.9 | 35 | 34.6667
Turkey |  | DIKILI | DIKILI, Turkey | 39.07N | 26.88E | 3 | 2.00 (EUE) | 82-00 | 171800 | -3.8 |  | -8.7 | 40.3 | 32.6 | 35.6 | 35.1 | 34 | 34.4333 |  | 30.2 | 33.5 | 32.7 | 32 | 32.1333
Turkey |  | DIYARBAKIR | DIYARBAKIR, Turkey | 37.88N | 40.18E | 677 | 2.00 (EUE) | 82-06 | 172800 | -12.6 |  | -26 | 45.6 | 38.5 | 42.2 | 41.6 | 41 | 40.7667 |  | 37 | 40.8 | 40 | 39 | 39.2667
Turkey |  | EDIRNE | EDIRNE, Turkey | 41.67N | 26.57E | 51 | 2.00 (EUE) | 82-06 | 170500 | -10.3 |  | -18.5 | 42.6 | 34.5 | 37.3 | 36.6 | 36 | 36.1333 |  | 32.6 | 34.6 | 34.2 | 34 | 33.8
Turkey |  | ELAZIG | ELAZIG, Turkey | 38.60N | 39.28E | 881 | 2.00 (EUE) | 82-06 | 172020 | -14.3 |  | -24.1 | 43.7 | 36.1 | 40 | 39.2 | 38 | 38.4333 |  | 34.1 | 38.1 | 37.8 | 37 | 36.6667
Turkey |  | ERZINCAN | ERZINCAN, Turkey | 39.70N | 39.52E | 1154 | 2.00 (EUE) | 82-06 | 170920 | -18.6 |  | -31 | 40 | 32.2 | 36.1 | 36.3 | 35 | 34.8667 |  | 30.5 | 34.2 | 34.2 | 33 | 32.9667
Turkey |  | ERZURUM | ERZURUM, Turkey | 39.95N | 41.17E | 1758 | 2.00 (EUE) | 82-06 | 170960 | -32.7 |  | -42.4 | 38.1 | 27.6 | 32.2 | 32.9 | 31 | 30.9 |  | 25.8 | 29.9 | 30.4 | 29 | 28.7
Turkey |  | ESENBOGA | ESENBOGA, Turkey | 40.12N | 33.00E | 949 | 2.00 (EUE) | 82-06 | 171280 | -18 |  | -30.3 | 40.6 | 31.9 | 35.8 | 35.1 | 34 | 34.2667 |  | 29.8 | 33.2 | 33.1 | 32 | 32.0333
Turkey |  | ESKISEHIR | ESKISEHIR, Turkey | 39.78N | 30.57E | 786 | 2.00 (EUE) | 82-06 | 171240 | -14.7 |  | -24.3 | 40.1 | 32.9 | 35.2 | 35.2 | 34 | 34.4333 |  | 30.5 | 33 | 33.1 | 32 | 32.2
Turkey |  | ETIMESGUT | ETIMESGUT, Turkey | 39.95N | 32.68E | 806 | 2.00 (EUE) | 82-06 | 171290 | -13.5 |  | -21.2 | 41.6 | 33.2 | 36.8 | 36.2 | 35 | 35.4 |  | 31.1 | 34.1 | 34.2 | 33 | 33.1333
Turkey |  | GAZIANTEP | GAZIANTEP, Turkey | 37.08N | 37.37E | 701 | 2.00 (EUE) | 82-06 | 172600 | -7.1 |  | -11.8 | 44.7 | 37.4 | 41.1 | 40 | 40 | 39.5 |  | 35.9 | 39 | 38.7 | 38 | 37.8667
Turkey |  | GOKCEADA | GOKCEADA, Turkey | 40.18N | 25.90E | 72 | 2.00 (EUE) | 82-00 | 171100 | -3.9 |  | -9.4 | 39.6 | 32.5 | 35.2 | 32.6 | 33 | 33.4333 |  | 30.2 | 32.5 | 30.9 | 31 | 31.2
Turkey |  | GOLCUK/DUMLUPINAR | GOLCUK/DUMLUPINAR, Turkey | 40.67N | 29.83E | 18 | 2.00 (EUE) | 82-06 | 170670 | -3.7 |  | -10.3 | 42.6 | 33.3 | 34.2 | 34.6 | 34 | 34.0333 |  | 30.9 | 32 | 32.4 | 32 | 31.7667
Turkey |  | INEBOLU | INEBOLU, Turkey | 41.98N | 33.78E | 64 | 2.00 (EUE) | 82-06 | 170240 | -5.4 |  | -9.8 | 33.4 | 27.3 | 29.6 | 30 | 29 | 28.9667 |  | 25.7 | 27.9 | 28.5 | 27 | 27.3667
Turkey |  | ISKENDERUN | ISKENDERUN, Turkey | 36.58N | 36.17E | 4 | 2.00 (EUE) | 82-06 | 173700 | 3.4 |  | -1 | 40.1 | 31.7 | 33.1 | 33.6 | 33 | 32.8 |  | 29.8 | 31.7 | 32.1 | 31 | 31.2
Turkey |  | ISPARTA | ISPARTA, Turkey | 37.75N | 30.55E | 997 | 2.00 (EUE) | 82-06 | 172400 | -11.8 |  | -18.9 | 38.7 | 32.2 | 34.9 | 34.7 | 34 | 33.9333 |  | 30.2 | 33.2 | 33 | 32 | 32.1333
Turkey |  | ISTANBUL/ATATURK | ISTANBUL/ATATURK, Turkey | 40.97N | 28.82E | 37 | 2.00 (EUE) | 82-06 | 170600 | -5 |  | -13.3 | 39.5 | 31.1 | 33.2 | 33 | 32 | 32.4333 |  | 29.2 | 31.2 | 31.1 | 31 | 30.5
Turkey |  | IZMIR/A. MENDERES | IZMIR/A. MENDERES, Turkey | 38.27N | 27.15E | 120 | 2.00 (EUE) | 88-06 | 172190 | -5.5 |  | -9.8 | 44.4 | 37.1 | 40 | 39 | 39 | 38.7 |  | 35.1 | 37.1 | 36.9 | 36 | 36.3667
Turkey |  | IZMIR/CIGLI | IZMIR/CIGLI, Turkey | 38.52N | 27.02E | 5 | 2.00 (EUE) | 82-06 | 172180 | -4.1 |  | -7.5 | 45.4 | 37 | 39.2 | 37.9 | 38 | 38.0333 |  | 34.9 | 36.9 | 35.8 | 36 | 35.8667
Turkey |  | KAYSERI/ERKILET | KAYSERI/ERKILET, Turkey | 38.82N | 35.43E | 1054 | 2.00 (EUE) | 82-06 | 171950 | -19.1 |  | -29.9 | 40.9 | 32.9 | 36.1 | 35.9 | 35 | 34.9667 |  | 30.8 | 33.9 | 33.9 | 33 | 32.8667
Turkey |  | KONYA | KONYA, Turkey | 37.97N | 32.55E | 1031 | 2.00 (EUE) | 82-06 | 172440 | -16.2 |  | -26.5 | 40.1 | 33 | 36.1 | 35.4 | 35 | 34.8333 |  | 31 | 34.1 | 33.7 | 33 | 32.9333
Turkey |  | MALATYA/ERHAC | MALATYA/ERHAC, Turkey | 38.43N | 38.08E | 849 | 2.00 (EUE) | 82-06 | 172000 | -15.7 |  | -25.4 | 43.7 | 36.1 | 39.4 | 39.1 | 38 | 38.2 |  | 34.2 | 37.9 | 37.2 | 36 | 36.4333
Turkey |  | MERZIFON | MERZIFON, Turkey | 40.85N | 35.58E | 535 | 2.00 (EUE) | 82-06 | 170820 | -13.6 |  | -23.2 | 43 | 33 | 36.1 | 36.1 | 35 | 35.0667 |  | 29.9 | 32.8 | 33 | 32 | 31.9
Turkey |  | MUGLA | MUGLA, Turkey | 37.22N | 28.37E | 646 | 2.00 (EUE) | 82-06 | 172920 | -5.2 |  | -9.5 | 42 | 35.6 | 38.3 | 38 | 37 | 37.3 |  | 33.5 | 36.3 | 35.8 | 35 | 35.2
Turkey |  | SAMSUN | SAMSUN, Turkey | 41.28N | 36.30E | 4 | 2.00 (EUE) | 82-00 | 170300 | -2.6 |  | -7.4 | 36.7 | 27.3 | 29.1 | 29.5 | 29 | 28.6333 |  | 25.3 | 27.8 | 28 | 27 | 27.0333
Turkey |  | SILIFKE | SILIFKE, Turkey | 36.38N | 33.93E | 15 | 2.00 (EUE) | 82-06 | 173300 | 1.2 |  | -3.5 | 40.4 | 34.5 | 35.8 | 36.5 | 36 | 35.6 |  | 32 | 33.9 | 34.1 | 33 | 33.3333
Turkey |  | SINOP | SINOP, Turkey | 42.03N | 35.17E | 32 | 2.00 (EUE) | 82-06 | 170260 | -2.3 |  | -8.1 | 32.9 | 26.5 | 29 | 29.2 | 28 | 28.2333 |  | 25 | 27.6 | 28.2 | 27 | 26.9333
Turkey |  | SIVAS | SIVAS, Turkey | 39.75N | 37.02E | 1285 | 2.00 (EUE) | 82-06 | 170900 | -20.3 |  | -31.1 | 39.9 | 30.6 | 34.6 | 34.5 | 33 | 33.2333 |  | 28.3 | 32.2 | 32.3 | 31 | 30.9333
Turkey |  | TEKIRDAG | TEKIRDAG, Turkey | 40.98N | 27.55E | 3 | 2.00 (EUE) | 82-06 | 170560 | -7.1 |  | -12.2 | 38.8 | 29.4 | 31.3 | 31.5 | 31 | 30.7333 |  | 27.3 | 29.7 | 29.6 | 29 | 28.8667
Turkey |  | TRABZON | TRABZON, Turkey | 41.00N | 39.72E | 34 | 2.00 (EUE) | 82-06 | 170380 | -1.3 |  | -5.1 | 36.1 | 27.5 | 29 | 29.4 | 29 | 28.6333 |  | 26 | 28 | 28.4 | 27 | 27.4667
Turkey |  | USAK | USAK, Turkey | 38.68N | 29.40E | 919 | 2.00 (EUE) | 82-06 | 171880 | -10.2 |  | -15.9 | 40.2 | 32.5 | 35.4 | 35.3 | 34 | 34.4 |  | 30.5 | 33.5 | 33.5 | 33 | 32.5
Turkey |  | VAN | VAN, Turkey | 38.45N | 43.32E | 1662 | 2.00 (EUE) | 82-06 | 171700 | -16.2 |  | -23.9 | 36.7 | 27.8 | 30.9 | 31.1 | 30 | 29.9333 |  | 26.1 | 29.1 | 29.1 | 28 | 28.1
Turkey |  | ZONGULDAK | ZONGULDAK, Turkey | 41.45N | 31.80E | 137 | 2.00 (EUE) | 82-06 | 170220 | -3.3 |  | -8 | 37.8 | 29.4 | 30.4 | 29.6 | 30 | 29.8 |  | 26.8 | 27.5 | 27.4 | 27 | 27.2333
Turkmenistan |  | ASHGABAT KESHI | ASHGABAT KESHI, Turkmenistan | 37.92N | 58.33E | 312 | 5.00 (ASW) | 82-06 | 388800 | -9.1 |  | -16.6 | 46.9 | 41 | 42.1 | 41.9 | 42 | 41.6667 |  | 39.1 | 40.2 | 39.6 | 40 | 39.6333
Turkmenistan |  | BAJRAMALY | BAJRAMALY, Turkmenistan | 37.60N | 62.18E | 240 | 5.00 (ASW) | 82-06 | 388950 | -9.8 |  | -17.4 | 46.1 | 41.5 | 42.2 | 41.3 | 42 | 41.6667 |  | 39.8 | 40.6 | 39.6 | 40 | 40
Turkmenistan |  | BAKHERDEN | BAKHERDEN, Turkmenistan | 38.43N | 57.42E | 159 | 5.00 (ASW) | 85-06 | 387740 | -8.4 |  | -15.8 | 47.5 | 40.5 | 42 | 42 | 42 | 41.5 |  | 38.9 | 40 | 39.9 | 40 | 39.6
Turkmenistan |  | BYRDALYK | BYRDALYK, Turkmenistan | 38.47N | 64.37E | 212 | 5.00 (ASW) | 84-06 | 388060 | -11.4 |  | -23.4 | 49 | 41.1 | 41.9 | 40.6 | 41 | 41.2 |  | 39.3 | 40 | 39 | 39 | 39.4333
Turkmenistan |  | CARSANGA | CARSANGA, Turkmenistan | 37.52N | 66.02E | 265 | 5.00 (ASW) | 84-06 | 389150 | -8.5 |  | -17 | 47.7 | 42.2 | 43.4 | 41.8 | 42 | 42.4667 |  | 40.6 | 41.4 | 39.9 | 41 | 40.6333
Turkmenistan |  | CHARDZHEV | CHARDZHEV, Turkmenistan | 39.08N | 63.60E | 190 | 5.00 (ASW) | 82-06 | 386870 | -12.5 |  | -21 | 44.8 | 40.1 | 40.5 | 39 | 40 | 39.8667 |  | 38.1 | 38.6 | 37.5 | 38 | 38.0667
Turkmenistan |  | DASHKHOVUZ | DASHKHOVUZ, Turkmenistan | 41.75N | 59.82E | 82 | 5.00 (ASW) | 82-06 | 383920 | -17.9 |  | -28.5 | 45 | 41 | 41.6 | 40.5 | 41 | 41.0333 |  | 38.7 | 39.4 | 38.2 | 39 | 38.7667
Turkmenistan |  | EKEZHE | EKEZHE, Turkmenistan | 41.03N | 57.77E | 62 | 5.00 (ASW) | 82-06 | 383880 | -20.6 |  | -32.3 | 47.6 | 42.1 | 43.3 | 43.2 | 43 | 42.8667 |  | 40.3 | 41.6 | 41 | 41 | 40.9667
Turkmenistan |  | ERBENT | ERBENT, Turkmenistan | 39.32N | 58.60E | 87 | 5.00 (ASW) | 82-06 | 386560 | -12.9 |  | -24.2 | 47.2 | 42.5 | 43.7 | 43.3 | 43 | 43.1667 |  | 40.6 | 41.9 | 41.2 | 41 | 41.2333
Turkmenistan |  | ESENGYLY | ESENGYLY, Turkmenistan | 37.47N | 53.97E | -22 | 5.00 (ASW) | 82-06 | 387500 | -4.6 |  | -8.8 | 45.8 | 36.3 | 34.2 | 35.2 | 35 | 35.2333 |  | 32 | 32.4 | 33.2 | 33 | 32.5333
Turkmenistan |  | GAZANDZHYK | GAZANDZHYK, Turkmenistan | 39.25N | 55.52E | 31 | 5.00 (ASW) | 83-06 | 386470 | -8.8 |  | -18.9 | 48.9 | 41.2 | 42.5 | 42.9 | 42 | 42.2 |  | 39.1 | 40.8 | 40.3 | 40 | 40.0667
Turkmenistan |  | GYSHGY | GYSHGY, Turkmenistan | 35.28N | 62.35E | 625 | 5.00 (ASW) | 82-06 | 389870 | -13.4 |  | -22.7 | 44.4 | 39.8 | 40.4 | 39.3 | 40 | 39.8333 |  | 38 | 38.9 | 37.5 | 38 | 38.1333
Turkmenistan |  | GYZYLARBAT | GYZYLARBAT, Turkmenistan | 38.98N | 56.28E | 92 | 5.00 (ASW) | 82-06 | 387630 | -9.5 |  | -19.2 | 48.8 | 41.2 | 42.5 | 42.2 | 42 | 41.9667 |  | 39.2 | 40.8 | 40 | 40 | 40
Turkmenistan |  | KERKI | KERKI, Turkmenistan | 37.83N | 65.20E | 240 | 5.00 (ASW) | 82-06 | 389110 | -9.6 |  | -19.3 | 45.5 | 41.5 | 42.3 | 41.1 | 42 | 41.6333 |  | 39.7 | 40.5 | 39.3 | 40 | 39.8333
Turkmenistan |  | SARAGT | SARAGT, Turkmenistan | 36.53N | 61.22E | 275 | 5.00 (ASW) | 82-06 | 389740 | -9 |  | -17.3 | 46.8 | 42.2 | 42.1 | 41.5 | 42 | 41.9333 |  | 39.9 | 40.2 | 39.3 | 40 | 39.8
Turkmenistan |  | TEDZHEN | TEDZHEN, Turkmenistan | 37.38N | 60.52E | 186 | 5.00 (ASW) | 84-06 | 388860 | -8.7 |  | -17.9 | 44.8 | 41 | 41.7 | 41.2 | 41 | 41.3 |  | 39.1 | 39.8 | 39.3 | 39 | 39.4
Turkmenistan |  | TURKMENBASHI | TURKMENBASHI, Turkmenistan | 40.05N | 53.00E | 82 | 5.00 (ASW) | 82-06 | 385070 | -10.1 |  | -17.4 | 44.4 | 38 | 39.7 | 40 | 39 | 39.2333 |  | 35.9 | 38 | 37.5 | 37 | 37.1333
Turkmenistan |  | UCHADZHY | UCHADZHY, Turkmenistan | 38.08N | 62.80E | 185 | 5.00 (ASW) | 83-06 | 387990 | -13.4 |  | -25.6 | 47.9 | 43.4 | 44.8 | 43.2 | 44 | 43.8 |  | 41.7 | 42.7 | 41.5 | 42 | 41.9667
Tuvalu |  | FUNAFUTI NF | FUNAFUTI NF, Tuvalu | 8.53S | 179.22E | 2 | 12.00 (FJI) | 82-99 | 916430 | 22.7 |  | 19.7 | 44.3 | 31.7 | 31.2 | 31.3 | 31 | 31.4 |  | 31.1 | 30.7 | 30.8 | 31 | 30.8667
Ukraine |  | BORYSPIL | BORYSPIL, Ukraine | 50.33N | 30.97E | 122 | 2.00 (EUE) | 91-06 | 333470 | -23.8 |  | -33.9 | 38.3 | 30.8 | 33 | 33 | 32 | 32.2667 |  | 28.8 | 31 | 30.1 | 30 | 29.9667
Ukraine |  | CHERNIHIV | CHERNIHIV, Ukraine | 51.47N | 31.25E | 141 | 2.00 (EUE) | 82-06 | 331350 | -22.8 |  | -34.2 | 37.9 | 30.3 | 32.4 | 31.3 | 31 | 31.3333 |  | 28.1 | 30 | 28.9 | 29 | 29
Ukraine |  | CHERNIVTSI | CHERNIVTSI, Ukraine | 48.37N | 25.90E | 246 | 2.00 (EUE) | 82-06 | 336580 | -19.9 |  | -29.4 | 36.9 | 29.8 | 31.7 | 31.4 | 31 | 30.9667 |  | 27.7 | 29.1 | 28.8 | 29 | 28.5333
Ukraine |  | CHORNOMORSKE | CHORNOMORSKE, Ukraine | 45.52N | 32.70E | 10 | 2.00 (EUE) | 82-06 | 339240 | -12.6 |  | -20.9 | 38.5 | 28.5 | 31.9 | 30.9 | 30 | 30.4333 |  | 26.1 | 29.4 | 28.8 | 28 | 28.1
Ukraine |  | DNIPROPETROVSK | DNIPROPETROVSK, Ukraine | 48.37N | 35.08E | 143 | 2.00 (EUE) | 82-06 | 345040 | -20.3 |  | -30 | 41.5 | 32.3 | 35.6 | 33.7 | 34 | 33.8667 |  | 30 | 32.5 | 31.3 | 31 | 31.2667
Ukraine |  | DONETSK | DONETSK, Ukraine | 48.07N | 37.77E | 225 | 2.00 (EUE) | 82-06 | 345190 | -21.9 |  | -31.5 | 39.4 | 31.5 | 34.7 | 33.4 | 33 | 33.2 |  | 29.3 | 32 | 30.9 | 31 | 30.7333
Ukraine |  | HENICHESK | HENICHESK, Ukraine | 46.17N | 34.82E | 15 | 2.00 (EUE) | 82-04 | 339100 | -16.3 |  | -22.9 | 39.1 | 30.5 | 33.6 | 32.8 | 32 | 32.3 |  | 28.4 | 31 | 30.4 | 30 | 29.9333
Ukraine |  | IVANO-FRANKIVSK | IVANO-FRANKIVSK, Ukraine | 48.97N | 24.70E | 280 | 2.00 (EUE) | 82-06 | 335260 | -24.2 |  | -35.7 | 37.5 | 29.4 | 31.6 | 31.4 | 31 | 30.8 |  | 27.3 | 29.1 | 28.5 | 28 | 28.3
Ukraine |  | IZIUM | IZIUM, Ukraine | 49.18N | 37.30E | 78 | 2.00 (EUE) | 82-06 | 344150 | -25.9 |  | -37.7 | 40.7 | 32.1 | 35.2 | 33.9 | 34 | 33.7333 |  | 30.2 | 32.5 | 31.2 | 31 | 31.3
Ukraine |  | IZMAIL | IZMAIL, Ukraine | 45.37N | 28.85E | 30 | 2.00 (EUE) | 82-04 | 338890 | -16.2 |  | -24.2 | 40.9 | 32.1 | 34.5 | 34.3 | 34 | 33.6333 |  | 30.1 | 32.4 | 32.2 | 32 | 31.5667
Ukraine |  | KERCH | KERCH, Ukraine | 45.40N | 36.42E | 49 | 2.00 (EUE) | 82-06 | 339830 | -12.7 |  | -22.6 | 37.8 | 29.4 | 32.7 | 32.3 | 31 | 31.4667 |  | 27.7 | 31.1 | 30.4 | 30 | 29.7333
Ukraine |  | KHARKIV | KHARKIV, Ukraine | 49.97N | 36.13E | 155 | 2.00 (EUE) | 82-06 | 343000 | -21.9 |  | -32.6 | 39.5 | 31.1 | 34.2 | 32.9 | 33 | 32.7333 |  | 29.2 | 31.3 | 30.2 | 30 | 30.2333
Ukraine |  | KHERSON | KHERSON, Ukraine | 46.63N | 32.57E | 54 | 2.00 (EUE) | 82-06 | 339020 | -18.1 |  | -26.7 | 40.8 | 32.4 | 35.7 | 34.7 | 34 | 34.2667 |  | 30.1 | 33.3 | 32.5 | 32 | 31.9667
Ukraine |  | KHMELNYTSKYI | KHMELNYTSKYI, Ukraine | 49.43N | 26.98E | 350 | 2.00 (EUE) | 82-06 | 334290 | -20.7 |  | -31.1 | 34 | 28.3 | 30.2 | 30.2 | 30 | 29.5667 |  | 26.2 | 28.1 | 28 | 27 | 27.4333
Ukraine |  | KIROVOHRAD | KIROVOHRAD, Ukraine | 48.52N | 32.20E | 171 | 2.00 (EUE) | 82-06 | 337110 | -21.5 |  | -29.7 | 38.4 | 30.6 | 33.4 | 33.4 | 32 | 32.4667 |  | 28.7 | 31 | 30.7 | 30 | 30.1333
Ukraine |  | KONOTOP | KONOTOP, Ukraine | 51.23N | 33.20E | 149 | 2.00 (EUE) | 82-06 | 332610 | -23.1 |  | -33.3 | 37.7 | 30.5 | 32.3 | 31.6 | 31 | 31.4667 |  | 28.4 | 30 | 28.8 | 29 | 29.0667
Ukraine |  | KRYVYI RIH | KRYVYI RIH, Ukraine | 48.03N | 33.22E | 124 | 2.00 (EUE) | 82-06 | 337910 | -20.5 |  | -29.3 | 39.1 | 31.6 | 34.7 | 33.4 | 33 | 33.2333 |  | 29.6 | 32.2 | 31.5 | 31 | 31.1
Ukraine |  | KYIV | KYIV, Ukraine | 50.40N | 30.57E | 167 | 2.00 (EUE) | 82-06 | 333450 | -19.8 |  | -30.9 | 37.8 | 30 | 32.1 | 31.8 | 31 | 31.3 |  | 27.8 | 29.9 | 28.9 | 29 | 28.8667
Ukraine |  | LIUBASHIVKA | LIUBASHIVKA, Ukraine | 47.85N | 30.27E | 183 | 2.00 (EUE) | 82-06 | 337610 | -19.4 |  | -27.2 | 39.1 | 30.5 | 33.4 | 33.6 | 33 | 32.5 |  | 28.7 | 31.3 | 30.7 | 30 | 30.2333
Ukraine |  | LUBNY | LUBNY, Ukraine | 50.00N | 33.02E | 158 | 2.00 (EUE) | 82-06 | 333770 | -20.8 |  | -31 | 37.1 | 30.6 | 32.5 | 32 | 32 | 31.7 |  | 28.6 | 30.3 | 29.5 | 29 | 29.4667
Ukraine |  | LUHANSK | LUHANSK, Ukraine | 48.57N | 39.25E | 62 | 2.00 (EUE) | 82-06 | 345230 | -23.8 |  | -33.4 | 41.7 | 33.3 | 36.7 | 35.1 | 35 | 35.0333 |  | 30.9 | 33.6 | 32.2 | 32 | 32.2333
Ukraine |  | LVIV | LVIV, Ukraine | 49.82N | 23.95E | 323 | 2.00 (EUE) | 82-06 | 333930 | -20.9 |  | -32.2 | 35.2 | 29.2 | 30.8 | 30.6 | 30 | 30.2 |  | 26.8 | 28.2 | 27.7 | 28 | 27.5667
Ukraine |  | MARIUPOL | MARIUPOL, Ukraine | 47.03N | 37.50E | 70 | 2.00 (EUE) | 82-06 | 347120 | -17.8 |  | -27.7 | 37.1 | 29.8 | 32.7 | 32.2 | 32 | 31.5667 |  | 28.1 | 31.1 | 29.7 | 30 | 29.6333
Ukraine |  | MOHYLIV-PODILSKYI | MOHYLIV-PODILSKYI, Ukraine | 48.45N | 27.78E | 78 | 2.00 (EUE) | 82-06 | 336630 | -20 |  | -30.3 | 39.3 | 31.8 | 33.9 | 34.2 | 33 | 33.3 |  | 29.8 | 31.5 | 31.5 | 31 | 30.9333
Ukraine |  | MYRONIVKA | MYRONIVKA, Ukraine | 49.67N | 31.00E | 153 | 2.00 (EUE) | 82-06 | 334660 | -21.9 |  | -33.9 | 37.1 | 29.9 | 32.1 | 32.5 | 32 | 31.5 |  | 28 | 29.9 | 29.7 | 29 | 29.2
Ukraine |  | NIZHYN | NIZHYN, Ukraine | 51.05N | 31.90E | 126 | 2.00 (EUE) | 84-04 | 332460 | -22.8 |  | -31.9 | 36.4 | 30.1 | 32 | 31.5 | 31 | 31.2 |  | 28.3 | 29.9 | 29.3 | 29 | 29.1667
Ukraine |  | NOVA KAKHOVKA | NOVA KAKHOVKA, Ukraine | 46.78N | 33.37E | 25 | 2.00 (EUE) | 82-95 | 338690 | -17.1 |  | -26 | 38.5 | 30.7 | 33.4 | 32.7 | 32 | 32.2667 |  | 28.9 | 31.2 | 31.3 | 30 | 30.4667
Ukraine |  | ODESA | ODESA, Ukraine | 46.43N | 30.77E | 42 | 2.00 (EUE) | 82-06 | 338370 | -16.5 |  | -24.9 | 39.8 | 31.2 | 34.1 | 33.2 | 33 | 32.8333 |  | 29 | 31.8 | 31.1 | 31 | 30.6333
Ukraine |  | POLTAVA | POLTAVA, Ukraine | 49.60N | 34.55E | 160 | 2.00 (EUE) | 82-06 | 335060 | -22 |  | -32.7 | 38.1 | 30.6 | 33.4 | 32.5 | 32 | 32.1667 |  | 28.6 | 30.7 | 29.9 | 30 | 29.7333
Ukraine |  | RIVNE | RIVNE, Ukraine | 50.58N | 26.13E | 231 | 2.00 (EUE) | 82-06 | 333010 | -21.7 |  | -33.6 | 35.3 | 29.4 | 31.2 | 30.9 | 31 | 30.5 |  | 27.1 | 28.8 | 28.2 | 28 | 28.0333
Ukraine |  | SARNY | SARNY, Ukraine | 51.28N | 26.62E | 156 | 2.00 (EUE) | 82-06 | 330880 | -23.3 |  | -32.5 | 36.9 | 30.5 | 32 | 31.9 | 31 | 31.4667 |  | 28 | 29.8 | 29.1 | 29 | 28.9667
Ukraine |  | SHEPETIVKA | SHEPETIVKA, Ukraine | 50.17N | 27.03E | 278 | 2.00 (EUE) | 82-06 | 333170 | -21.8 |  | -31.8 | 34.9 | 28.8 | 30.5 | 30.5 | 30 | 29.9333 |  | 26.7 | 28.4 | 28.1 | 28 | 27.7333
Ukraine |  | SIMFEROPOL | SIMFEROPOL, Ukraine | 45.02N | 33.98E | 181 | 2.00 (EUE) | 82-06 | 339460 | -15.5 |  | -25 | 40.2 | 31.1 | 35.1 | 34.5 | 34 | 33.5667 |  | 28.9 | 32.9 | 32.1 | 31 | 31.3
Ukraine |  | SUMY | SUMY, Ukraine | 50.85N | 34.67E | 181 | 2.00 (EUE) | 82-06 | 332750 | -24.3 |  | -35.1 | 37.9 | 30.3 | 32.3 | 31.4 | 31 | 31.3333 |  | 28.3 | 29.8 | 28.9 | 29 | 29
Ukraine |  | SVITLOVODSK | SVITLOVODSK, Ukraine | 49.05N | 33.25E | 84 | 2.00 (EUE) | 95-06 | 336140 | -21 |  | -29.6 | 39.5 | 31.2 | 34 | 32.6 | 33 | 32.6 |  | 29.2 | 31.9 | 30 | 30 | 30.3667
Ukraine |  | TERNOPIL | TERNOPIL, Ukraine | 49.53N | 25.67E | 329 | 2.00 (EUE) | 82-06 | 334150 | -21.5 |  | -33 | 34.9 | 28.3 | 30.5 | 30.4 | 30 | 29.7333 |  | 26.4 | 28.2 | 27.8 | 27 | 27.4667
Ukraine |  | UMAN | UMAN, Ukraine | 48.77N | 30.23E | 216 | 2.00 (EUE) | 82-06 | 335870 | -20.8 |  | -31 | 37.1 | 29.9 | 32.1 | 32.4 | 31 | 31.4667 |  | 28 | 29.9 | 29.8 | 29 | 29.2333
Ukraine |  | UZHHOROD | UZHHOROD, Ukraine | 48.63N | 22.27E | 124 | 2.00 (EUE) | 82-06 | 336310 | -18.2 |  | -26.8 | 37.1 | 31.1 | 32.8 | 32.7 | 32 | 32.2 |  | 29 | 30.8 | 30.3 | 30 | 30.0333
Ukraine |  | VINNYTSIA | VINNYTSIA, Ukraine | 49.23N | 28.60E | 298 | 2.00 (EUE) | 82-06 | 335620 | -21.7 |  | -32.9 | 35.8 | 28.6 | 30.7 | 31.3 | 30 | 30.2 |  | 26.8 | 28.4 | 28.4 | 28 | 27.8667
Ukraine |  | VOLODYMYR-VOLYNSKYI | VOLODYMYR-VOLYNSKYI, Ukraine | 50.83N | 24.32E | 194 | 2.00 (EUE) | 82-06 | 331770 | -21.4 |  | -35.3 | 35.9 | 29.5 | 31.2 | 31 | 31 | 30.5667 |  | 27.2 | 29 | 28.2 | 28 | 28.1333
Ukraine |  | VOZNESENSK | VOZNESENSK, Ukraine | 47.57N | 31.33E | 34 | 2.00 (EUE) | 82-95 | 337770 | -18.6 |  | -28 | 40.8 | 31.6 | 34.1 | 35.2 | 34 | 33.6333 |  | 29.8 | 32 | 32.9 | 32 | 31.5667
Ukraine |  | YALTA | YALTA, Ukraine | 44.48N | 34.17E | 72 | 2.00 (EUE) | 82-04 | 339900 | -6.8 |  | -13.8 | 37.7 | 28.8 | 33 | 33.1 | 32 | 31.6333 |  | 27.2 | 31.1 | 30.8 | 30 | 29.7
Ukraine |  | ZAPORIZHZHIA | ZAPORIZHZHIA, Ukraine | 47.80N | 35.02E | 112 | 2.00 (EUE) | 82-06 | 346010 | -19.9 |  | -29.1 | 41 | 32.2 | 35.3 | 34.7 | 34 | 34.0667 |  | 29.9 | 32.9 | 32 | 32 | 31.6
Ukraine |  | ZHYTOMYR | ZHYTOMYR, Ukraine | 50.23N | 28.73E | 224 | 2.00 (EUE) | 82-06 | 333250 | -21.9 |  | -33.1 | 36.3 | 28.9 | 31 | 30.9 | 30 | 30.2667 |  | 27 | 28.7 | 28.3 | 28 | 28
United Arab Emirates |  | ABU DHABI BATEEN AI | ABU DHABI BATEEN AI, United Arab Emirates | 24.43N | 54.47E | 3 | 4.00 (ARN) | 83-01 | 412160 | 10.7 |  | 7.9 | 49.6 | 43.7 | 44.9 | 45 | 45 | 44.5333 |  | 41.3 | 42.9 | 43 | 42 | 42.4
United Arab Emirates |  | ABU DHABI INTER. AI | ABU DHABI INTER. AI, United Arab Emirates | 24.43N | 54.65E | 27 | 4.00 (ARN) | 83-06 | 412170 | 8.3 |  | 2.2 | 49.5 | 45.2 | 46.1 | 46.5 | 46 | 45.9333 |  | 43.3 | 44.7 | 44.9 | 44 | 44.3
United Arab Emirates |  | AL AIN INTERNATIONA | AL AIN INTERNATIONA, United Arab Emirates | 24.27N | 55.60E | 262 | 4.00 (ARN) | 94-06 | 412180 | 8.7 |  | 6.6 | 48.5 | 46.9 | 46.8 | 46.5 | 47 | 46.7333 |  | 45.8 | 45.8 | 45.6 | 46 | 45.7333
United Arab Emirates |  | DUBAI INTERNATIONAL | DUBAI INTERNATIONAL, United Arab Emirates | 25.25N | 55.33E | 5 | 4.00 (ARN) | 83-06 | 411940 | 10.6 |  | 7.1 | 47.9 | 43.2 | 44.2 | 44.2 | 44 | 43.8667 |  | 41.1 | 42.6 | 42.4 | 42 | 42.0333
United Arab Emirates |  | FUJAIRAH | FUJAIRAH, United Arab Emirates | 25.10N | 56.33E | 28 | 4.00 (ARN) | 95-06 | 411980 | 13.5 |  | 9.3 | 49.9 | 45.1 | 44.1 | 42.2 | 44 | 43.8 |  | 42.1 | 41.8 | 39.9 | 41 | 41.2667
United Arab Emirates |  | RAS AL KHAIMAH INTE | RAS AL KHAIMAH INTE, United Arab Emirates | 25.62N | 55.93E | 31 | 4.00 (ARN) | 83-06 | 411840 | 7 |  | 3.1 | 48.9 | 45.2 | 45.2 | 45.1 | 45 | 45.1667 |  | 43.8 | 44.1 | 43.7 | 44 | 43.8667
United Arab Emirates |  | SHARJAH INTER. AIRP | SHARJAH INTER. AIRP, United Arab Emirates | 25.33N | 55.52E | 33 | 4.00 (ARN) | 82-06 | 411960 | 6.8 |  | 1.6 | 49 | 44.8 | 45.7 | 45.4 | 45 | 45.3 |  | 42.9 | 43.9 | 43.7 | 44 | 43.5
United Kingdom |  | ABERDARON | ABERDARON, United Kingdom | 52.78N | 4.73W | 94 | 0.00 (GMT) | 94-06 | 34050 | -1.4 |  | -5.2 | 29.3 | 23.7 | 24.3 | 24.9 | 24 | 24.3 |  | 20.4 | 21.7 | 22.2 | 21 | 21.4333
United Kingdom |  | ABERDEEN/DYCE AIRPO | ABERDEEN/DYCE AIRPO, United Kingdom | 57.20N | 2.22W | 69 | 0.00 (GMT) | 82-06 | 30910 | -9.7 |  | -20.5 | 29.9 | 22.4 | 24.1 | 24.3 | 24 | 23.6 |  | 20.1 | 21.9 | 21.5 | 21 | 21.1667
United Kingdom |  | ABERPORTH | ABERPORTH, United Kingdom | 52.13N | 4.57W | 134 | 0.00 (GMT) | 82-06 | 35020 | -3.9 |  | -8.7 | 33.3 | 24.1 | 25.6 | 26.3 | 25 | 25.3333 |  | 20.3 | 22.1 | 21.9 | 21 | 21.4333
United Kingdom |  | ABOYNE | ABOYNE, United Kingdom | 57.08N | 2.83W | 140 | 0.00 (GMT) | 89-06 | 30800 | -11.5 |  | -26.4 | 30.3 | 24.6 | 25.8 | 26.9 | 26 | 25.7667 |  | 21.7 | 23.6 | 23.2 | 23 | 22.8333
United Kingdom |  | ALCONBURY RAF | ALCONBURY RAF, United Kingdom | 52.37N | 0.22W | 49 | 0.00 (GMT) | 83-94 | 35620 | N/A |  | N/A | N/A | 26.1 | 29.2 | 29.8 | 28 | 28.3667 |  | 23.8 | 26.9 | 26.8 | 26 | 25.8333
United Kingdom |  | ALTNAHARRA NO2 | ALTNAHARRA NO2, United Kingdom | 58.28N | 4.43W | 80 | 0.00 (GMT) | 93-06 | 30440 | -13.6 |  | -22.6 | 30.1 | 23.6 | 25.4 | 26 | 25 | 25 |  | 20.6 | 22.2 | 22.3 | 22 | 21.7
United Kingdom |  | ANDREWSFIELD | ANDREWSFIELD, United Kingdom | 51.88N | 0.45E | 87 | 0.00 (GMT) | 98-06 | 36840 | -5.1 |  | -7.7 | 36.3 | 27.2 | 29.2 | 30 | 29 | 28.8 |  | 24.2 | 27.1 | 27 | 26 | 26.1
United Kingdom |  | AONACH MOR | AONACH MOR, United Kingdom | 56.82N | 4.97W | 1130 | 0.00 (GMT) | 92-06 | 30410 | N/A |  | N/A | N/A | 15.2 | 17 | 18.4 | 17 | 16.8667 |  | 12.7 | 15 | 15.8 | 15 | 14.5
United Kingdom |  | AUGHTON | AUGHTON, United Kingdom | 53.55N | 2.92W | 56 | 0.00 (GMT) | 82-96 | 33220 | -4.9 |  | -10.8 | 33.5 | 26.3 | 27.3 | 28.1 | 27 | 27.2333 |  | 22.7 | 24.3 | 24 | 24 | 23.6667
United Kingdom |  | AULTBEA NO2 | AULTBEA NO2, United Kingdom | 57.87N | 5.63W | 10 | 0.00 (GMT) | 86-06 | 30340 | -3.2 |  | -6.8 | 30.4 | 21.6 | 23.9 | 24.3 | 23 | 23.2667 |  | 18.8 | 20.9 | 20.9 | 20 | 20.2
United Kingdom |  | AVIEMORE | AVIEMORE, United Kingdom | 57.20N | 3.83W | 228 | 0.00 (GMT) | 83-06 | 30630 | -13.3 |  | -25 | 32 | 25.3 | 26.4 | 26.5 | 26 | 26.0667 |  | 21.9 | 24 | 23.1 | 23 | 23
United Kingdom |  | BALLYKELLY | BALLYKELLY, United Kingdom | 55.07N | 7.02W | 5 | 0.00 (GMT) | 97-06 | 39080 | -4.8 |  | -9.1 | 30.8 | 21.7 | 26.4 | 23.1 | 24 | 23.7333 |  | 20.1 | 22.7 | 21.2 | 21 | 21.3333
United Kingdom |  | BALLYPATRICK FOREST | BALLYPATRICK FOREST, United Kingdom | 55.18N | 6.17W | 156 | 0.00 (GMT) | 87-06 | 39160 | -3.4 |  | -6.7 | 28 | 21.4 | 23.3 | 22.2 | 22 | 22.3 |  | 18.3 | 20.9 | 20.3 | 20 | 19.8333
United Kingdom |  | BALTASOUND NO.2 | BALTASOUND NO.2, United Kingdom | 60.75N | 0.85W | 15 | 0.00 (GMT) | 89-06 | 30020 | -6 |  | -11 | 24.7 | 17.1 | 18.9 | 19.5 | 19 | 18.5 |  | 14.9 | 17 | 17.3 | 16 | 16.4
United Kingdom |  | BANGOR HARBOUR | BANGOR HARBOUR, United Kingdom | 54.67N | 5.67W | 11 | 0.00 (GMT) | 92-06 | 39270 | -1.2 |  | -4.5 | 31.2 | 23.3 | 25.5 | 25.1 | 25 | 24.6333 |  | 20.9 | 23.2 | 22.6 | 22 | 22.2333
United Kingdom |  | BARRA | BARRA, United Kingdom | 57.03N | 7.45W | 3 | 0.00 (GMT) | 97-06 | 30350 | -1.9 |  | -10.3 | 26.3 | 19.1 | 20.7 | 21 | 20 | 20.2667 |  | 16.5 | 18.3 | 19.2 | 18 | 18
United Kingdom |  | BEDFORD | BEDFORD, United Kingdom | 52.22N | 0.48W | 84 | 0.00 (GMT) | 87-06 | 35600 | -5.4 |  | -8.9 | 36.9 | 27.3 | 30.2 | 30.5 | 29 | 29.3333 |  | 24.3 | 27.4 | 27.7 | 26 | 26.4667
United Kingdom |  | BELFAST/ALDERGROVE | BELFAST/ALDERGROVE, United Kingdom | 54.65N | 6.22W | 68 | 0.00 (GMT) | 82-06 | 39170 | -5.7 |  | -10.5 | 30.4 | 23.8 | 25.5 | 24.6 | 25 | 24.6333 |  | 21 | 23 | 21.9 | 22 | 21.9667
United Kingdom |  | BENBECULA ISLAND | BENBECULA ISLAND, United Kingdom | 57.47N | 7.37W | 6 | 0.00 (GMT) | 82-06 | 30220 | -4.7 |  | -9.8 | 28.5 | 21.8 | 22.3 | 21.6 | 22 | 21.9 |  | 18.4 | 19.6 | 18.2 | 19 | 18.7333
United Kingdom |  | BENSON | BENSON, United Kingdom | 51.62N | 1.08W | 57 | 0.00 (GMT) | 82-06 | 36580 | -8.7 |  | -12.6 | 35.7 | 28.3 | 30.2 | 30.3 | 30 | 29.6 |  | 25.2 | 27.9 | 27.7 | 27 | 26.9333
United Kingdom |  | BINGLEY NO.2 | BINGLEY NO.2, United Kingdom | 53.82N | 1.87W | 267 | 0.00 (GMT) | 82-06 | 33440 | -6.2 |  | -12.1 | 32.6 | 25.1 | 26.1 | 26.7 | 26 | 25.9667 |  | 21.8 | 23.9 | 23.1 | 23 | 22.9333
United Kingdom |  | BIRMINGHAM AIRPORT | BIRMINGHAM AIRPORT, United Kingdom | 52.45N | 1.73W | 99 | 0.00 (GMT) | 82-06 | 35340 | -8.7 |  | -17.1 | 36 | 27.1 | 29.7 | 29.5 | 29 | 28.7667 |  | 24.4 | 26.9 | 26.1 | 26 | 25.8
United Kingdom |  | BLACKPOOL AIRPORT | BLACKPOOL AIRPORT, United Kingdom | 53.77N | 3.03W | 10 | 0.00 (GMT) | 82-91 | 33180 | -6.8 |  | -12.5 | 34.8 | 24.7 | 26.7 | 27.1 | 26 | 26.1667 |  | 22.1 | 23.9 | 22.5 | 23 | 22.8333
United Kingdom |  | BOSCOMBE DOWN | BOSCOMBE DOWN, United Kingdom | 51.17N | 1.75W | 126 | 0.00 (GMT) | 82-06 | 37460 | -6.6 |  | -12.2 | 34.5 | 26.9 | 29.3 | 29.5 | 29 | 28.5667 |  | 24.3 | 26.8 | 26.5 | 26 | 25.8667
United Kingdom |  | BOULMER | BOULMER, United Kingdom | 55.42N | 1.60W | 27 | 0.00 (GMT) | 82-06 | 32400 | -5.3 |  | -12.5 | 27.9 | 21.4 | 23 | 22.8 | 22 | 22.4 |  | 19.1 | 20.7 | 20.6 | 20 | 20.1333
United Kingdom |  | BOURNEMOUTH/HURN | BOURNEMOUTH/HURN, United Kingdom | 50.78N | 1.83W | 10 | 0.00 (GMT) | 82-06 | 38620 | -7.9 |  | -12.1 | 34.9 | 26.7 | 28.7 | 29.1 | 28 | 28.1667 |  | 23.9 | 26.2 | 25.6 | 25 | 25.2333
United Kingdom |  | BRACKNELL/BEAUFORT | BRACKNELL/BEAUFORT, United Kingdom | 51.38N | 0.78W | 74 | 0.00 (GMT) | 92-03 | 37630 | -7.4 |  | -11.1 | 34.4 | 28 | 29.1 | 30.7 | 29 | 29.2667 |  | 24.9 | 26.2 | 27.8 | 26 | 26.3
United Kingdom |  | BRAWDY(RAF) | BRAWDY(RAF), United Kingdom | 51.88N | 5.12W | 111 | 0.00 (GMT) | 82-92 | 36030 | -5.6 |  | -12.1 | 32.2 | 23.3 | 25.5 | 26.1 | 25 | 24.9667 |  | 20.2 | 23.1 | 20.9 | 21 | 21.4
United Kingdom |  | BRIDLINGTON MRSC | BRIDLINGTON MRSC, United Kingdom | 54.10N | 0.17W | 19 | 0.00 (GMT) | 87-06 | 32920 | -4 |  | -9.8 | 30.9 | 23.5 | 24.5 | 24.1 | 24 | 24.0333 |  | 20.6 | 22 | 22 | 22 | 21.5333
United Kingdom |  | BRISTOL | BRISTOL, United Kingdom | 51.38N | 2.72W | 194 | 0.00 (GMT) | 86-06 | 37243 | -5.5 |  | -10.2 | 34.3 | 27 | 28.2 | 28.1 | 28 | 27.7667 |  | 24.1 | 25.9 | 24.8 | 25 | 24.9333
United Kingdom |  | BRISTOL WEA CENTER | BRISTOL WEA CENTER, United Kingdom | 51.47N | 2.60W | 11 | 0.00 (GMT) | 82-01 | 37260 | -4.7 |  | -11.1 | 34.7 | 27.7 | 29.1 | 29.6 | 29 | 28.8 |  | 24.9 | 26.8 | 26.2 | 26 | 25.9667
United Kingdom |  | BRIZE NORTON | BRIZE NORTON, United Kingdom | 51.75N | 1.58W | 81 | 0.00 (GMT) | 82-06 | 36490 | -6.9 |  | -12 | 35.7 | 27.6 | 30 | 29.6 | 29 | 29.0667 |  | 24.9 | 27.5 | 26.7 | 26 | 26.3667
United Kingdom |  | BUTT OF LEWIS (LH) | BUTT OF LEWIS (LH), United Kingdom | 58.52N | 6.27W | 23 | 0.00 (GMT) | 83-97 | 30250 | -2 |  | -4.8 | 25.5 | 18.1 | 19.7 | 19 | 19 | 18.9333 |  | 15.7 | 17.1 | 16.9 | 17 | 16.5667
United Kingdom |  | CAMBORNE | CAMBORNE, United Kingdom | 50.22N | 5.32W | 88 | 0.00 (GMT) | 82-06 | 38080 | -2.6 |  | -8.9 | 29.4 | 22.5 | 23.9 | 24 | 23 | 23.4667 |  | 19.7 | 21.7 | 21.4 | 21 | 20.9333
United Kingdom |  | CAPE WRATH (LGT-H) | CAPE WRATH (LGT-H), United Kingdom | 58.63N | 5.00W | 112 | 0.00 (GMT) | 82-97 | 30490 | -1.6 |  | -5.1 | 28.5 | 19.7 | 21.2 | 22.7 | 21 | 21.2 |  | 16.7 | 19.1 | 19.2 | 18 | 18.3333
United Kingdom |  | CAPEL CURIG | CAPEL CURIG, United Kingdom | 53.10N | 3.93W | 215 | 0.00 (GMT) | 94-06 | 33050 | -7.2 |  | -11.8 | 32.5 | 23.9 | 26.9 | 26.4 | 26 | 25.7333 |  | 20.7 | 23.9 | 23.9 | 23 | 22.8333
United Kingdom |  | CARDIFF WEATHER CEN | CARDIFF WEATHER CEN, United Kingdom | 51.48N | 3.18W | 52 | 0.00 (GMT) | 92-06 | 37170 | -3.1 |  | -5.4 | 32.8 | 27.2 | 28.2 | 29.6 | 28 | 28.3333 |  | 24.4 | 26 | 26.4 | 26 | 25.6
United Kingdom |  | CARDIFF-WALES ARPT | CARDIFF-WALES ARPT, United Kingdom | 51.40N | 3.35W | 67 | 0.00 (GMT) | 82-06 | 37150 | -5.3 |  | -9.8 | 33.7 | 25.7 | 27.9 | 27.5 | 27 | 27.0333 |  | 22.7 | 25.2 | 23.9 | 24 | 23.9333
United Kingdom |  | CARDINHAM | CARDINHAM, United Kingdom | 50.50N | 4.67W | 199 | 0.00 (GMT) | 87-06 | 38230 | -3.1 |  | -8.4 | 31.2 | 24.5 | 26 | 25.1 | 25 | 25.2 |  | 21.6 | 23.6 | 22.2 | 22 | 22.4667
United Kingdom |  | CARLISLE | CARLISLE, United Kingdom | 54.93N | 2.97W | 27 | 0.00 (GMT) | 88-06 | 32200 | -6.3 |  | -9.3 | 33.8 | 25.1 | 27.1 | 27.2 | 26 | 26.4667 |  | 21.5 | 23.9 | 23.6 | 23 | 23
United Kingdom |  | CELLARHEAD | CELLARHEAD, United Kingdom | 53.03N | 2.08W | 228 | 0.00 (GMT) | 82-97 | 33380 | -8.5 |  | -15.5 | 32.7 | 24.8 | 26.6 | 27.6 | 26 | 26.3333 |  | 22.1 | 24.4 | 23.6 | 23 | 23.3667
United Kingdom |  | CHARTERHALL | CHARTERHALL, United Kingdom | 55.70N | 2.38W | 111 | 0.00 (GMT) | 87-06 | 31580 | -7.2 |  | -14.1 | 33 | 23.4 | 26.6 | 26.8 | 26 | 25.6 |  | 20.9 | 23.9 | 23.2 | 23 | 22.6667
United Kingdom |  | CHIVENOR | CHIVENOR, United Kingdom | 51.08N | 4.15W | 6 | 0.00 (GMT) | 93-06 | 37070 | -4.1 |  | -5.8 | 32.8 | 26.5 | 28.2 | 28.2 | 28 | 27.6333 |  | 23 | 25 | 24.8 | 24 | 24.2667
United Kingdom |  | CHURCH LAWFORD | CHURCH LAWFORD, United Kingdom | 52.37N | 1.33W | 106 | 0.00 (GMT) | 83-06 | 35440 | -7.9 |  | -15.6 | 36.4 | 27.1 | 29.2 | 29.4 | 29 | 28.5667 |  | 24.2 | 26.8 | 26.4 | 26 | 25.8
United Kingdom |  | CILFYNYDD | CILFYNYDD, United Kingdom | 51.63N | 3.30W | 194 | 0.00 (GMT) | 82-96 | 36140 | -6.6 |  | -13.5 | 33.6 | 26.5 | 28.3 | 28.1 | 28 | 27.6333 |  | 23.8 | 26 | 24.8 | 25 | 24.8667
United Kingdom |  | COLLAFIRTH HILL | COLLAFIRTH HILL, United Kingdom | 60.53N | 1.38W | 57 | 0.00 (GMT) | 82-91 | 30040 | -5.2 |  | -7.1 | 24.6 | 18.5 | 18.6 | 19.1 | 19 | 18.7333 |  | 15.6 | 16.2 | 15.4 | 16 | 15.7333
United Kingdom |  | COLTISHALL | COLTISHALL, United Kingdom | 52.77N | 1.35E | 17 | 0.00 (GMT) | 82-06 | 34950 | -6.3 |  | -12.4 | 34.5 | 26.6 | 27.7 | 28.1 | 27 | 27.4667 |  | 23.2 | 25.2 | 25.5 | 25 | 24.6333
United Kingdom |  | CONINGSBY | CONINGSBY, United Kingdom | 53.08N | 0.17W | 6 | 0.00 (GMT) | 82-06 | 33910 | -6.5 |  | -13 | 34.8 | 27 | 28.6 | 29.3 | 28 | 28.3 |  | 24 | 26.1 | 26.3 | 25 | 25.4667
United Kingdom |  | CORSEWALL PT. (LH) | CORSEWALL PT. (LH), United Kingdom | 55.00N | 5.15W | 15 | 0.00 (GMT) | 82-90 | 31180 | -3.1 |  | -7.9 | 27.2 | 20.8 | 21.8 | 21.9 | 22 | 21.5 |  | 18.3 | 19.3 | 19 | 19 | 18.8667
United Kingdom |  | COTTESMORE | COTTESMORE, United Kingdom | 52.73N | 0.65W | 142 | 0.00 (GMT) | 93-06 | 34530 | -6.6 |  | -11 | 32.4 | 27.2 | 28.8 | 29.1 | 28 | 28.3667 |  | 23.8 | 26.4 | 26.4 | 26 | 25.5333
United Kingdom |  | CRANWELL | CRANWELL, United Kingdom | 53.03N | 0.50W | 62 | 0.00 (GMT) | 92-06 | 33790 | -6.2 |  | -10.8 | 34.7 | 27.5 | 28.9 | 29.4 | 29 | 28.6 |  | 24.1 | 26.4 | 26.5 | 26 | 25.6667
United Kingdom |  | CROSBY | CROSBY, United Kingdom | 53.50N | 3.07W | 9 | 0.00 (GMT) | 84-06 | 33160 | -6.3 |  | -11.4 | 34.4 | 26.1 | 27.9 | 27.7 | 27 | 27.2333 |  | 22.4 | 24.3 | 24.1 | 24 | 23.6
United Kingdom |  | CULDROSE | CULDROSE, United Kingdom | 50.08N | 5.25W | 84 | 0.00 (GMT) | 82-06 | 38090 | -3 |  | -8.7 | 30.2 | 22.5 | 24.7 | 24.1 | 24 | 23.7667 |  | 20.1 | 22.2 | 21.4 | 21 | 21.2333
United Kingdom |  | DISFORTH AIRFIELD | DISFORTH AIRFIELD, United Kingdom | 54.13N | 1.42W | 33 | 0.00 (GMT) | 92-06 | 32610 | -6.4 |  | -10 | 33.1 | 26.1 | 27.6 | 28.5 | 27 | 27.4 |  | 23.1 | 25.3 | 25.5 | 25 | 24.6333
United Kingdom |  | DONNA NOOK NO.2 | DONNA NOOK NO.2, United Kingdom | 53.48N | 0.08E | 11 | 0.00 (GMT) | 93-06 | 33850 | -4.8 |  | -10.9 | 32.1 | 24.8 | 25.7 | 24.5 | 25 | 25 |  | 22.1 | 23.2 | 22.8 | 23 | 22.7
United Kingdom |  | DRUMALBIN | DRUMALBIN, United Kingdom | 55.62N | 3.73W | 245 | 0.00 (GMT) | 91-06 | 31550 | -7.9 |  | -13.6 | 28.9 | 23 | 24.5 | 24.2 | 24 | 23.9 |  | 19.7 | 21.7 | 20.9 | 21 | 20.7667
United Kingdom |  | DUMFRIES/DRUNGANS | DUMFRIES/DRUNGANS, United Kingdom | 55.05N | 3.65W | 16 | 0.00 (GMT) | 82-04 | 31540 | -7.9 |  | -15.4 | 31.4 | 25.8 | 26.7 | 27.2 | 27 | 26.5667 |  | 22.5 | 24.3 | 23.9 | 24 | 23.5667
United Kingdom |  | DUNDRENNAN | DUNDRENNAN, United Kingdom | 54.80N | 4.00W | 113 | 0.00 (GMT) | 83-06 | 31530 | -3.7 |  | -6.8 | 30 | 23.2 | 24.6 | 22.1 | 23 | 23.3 |  | 19.9 | 21.9 | 19.9 | 21 | 20.5667
United Kingdom |  | DUNKESWELL AERODROM | DUNKESWELL AERODROM, United Kingdom | 50.87N | 3.23W | 253 | 0.00 (GMT) | 91-06 | 38400 | -5.4 |  | -8.1 | 31.1 | 24.1 | 26.3 | 26.7 | 26 | 25.7 |  | 21.8 | 23.8 | 23.9 | 23 | 23.1667
United Kingdom |  | EAST MIDLANDS | EAST MIDLANDS, United Kingdom | 52.83N | 1.32W | 96 | 0.00 (GMT) | 82-06 | 34185 | -6.6 |  | -14.5 | 35.4 | 27.2 | 29.2 | 29.2 | 29 | 28.5333 |  | 24.2 | 26.9 | 26.1 | 26 | 25.7333
United Kingdom |  | EDINBURGH AIRPORT | EDINBURGH AIRPORT, United Kingdom | 55.95N | 3.35W | 41 | 0.00 (GMT) | 82-06 | 31600 | -8.7 |  | -16.3 | 31 | 23.1 | 25.2 | 24.8 | 24 | 24.3667 |  | 20.8 | 22.7 | 22 | 22 | 21.8333
United Kingdom |  | EMLEY MOOR | EMLEY MOOR, United Kingdom | 53.62N | 1.67W | 259 | 0.00 (GMT) | 89-06 | 33450 | -5.1 |  | -8.8 | 32.8 | 24.9 | 26 | 26.9 | 26 | 25.9333 |  | 22 | 24.1 | 23.8 | 23 | 23.3
United Kingdom |  | ESKDALEMUIR | ESKDALEMUIR, United Kingdom | 55.32N | 3.20W | 242 | 0.00 (GMT) | 82-06 | 31620 | -10 |  | -17.9 | 30.9 | 24.2 | 26 | 25.5 | 25 | 25.2333 |  | 21.2 | 23.3 | 22.4 | 22 | 22.3
United Kingdom |  | EXETER AIRPORT | EXETER AIRPORT, United Kingdom | 50.73N | 3.42W | 30 | 0.00 (GMT) | 82-06 | 38390 | -5.6 |  | -10.4 | 34.6 | 25.6 | 28.4 | 28.1 | 27 | 27.3667 |  | 23.8 | 26.1 | 25.1 | 25 | 25
United Kingdom |  | FAIR ISLE | FAIR ISLE, United Kingdom | 59.53N | 1.63W | 57 | 0.00 (GMT) | 83-05 | 30080 | -2.5 |  | -5.4 | 21.4 | 15 | 16.7 | 17.2 | 16 | 16.3 |  | 13.4 | 15 | 15.7 | 15 | 14.7
United Kingdom |  | FAIRFORD RAF | FAIRFORD RAF, United Kingdom | 51.68N | 1.78W | 87 | 0.00 (GMT) | 82-06 | 36440 | -8.9 |  | -21.4 | 36 | 27.1 | 31.2 | 28.1 | 29 | 28.8 |  | 24.2 | 28.1 | 25.8 | 26 | 26.0333
United Kingdom |  | FARNBOROUGH | FARNBOROUGH, United Kingdom | 51.28N | 0.77W | 64 | 0.00 (GMT) | 88-06 | 37680 | -7.4 |  | -10 | 36.3 | 27.9 | 30.1 | 30.2 | 29 | 29.4 |  | 25.1 | 27.7 | 27.3 | 27 | 26.7
United Kingdom |  | FIFE NESS | FIFE NESS, United Kingdom | 56.30N | 2.58W | 12 | 0.00 (GMT) | 82-06 | 31740 | -3 |  | -7.7 | 27.7 | 20.4 | 22.5 | 21.6 | 22 | 21.5 |  | 18.4 | 19.9 | 19.8 | 19 | 19.3667
United Kingdom |  | FINNINGLEY(RAF) | FINNINGLEY(RAF), United Kingdom | 53.48N | 1.00W | 17 | 0.00 (GMT) | 82-95 | 33600 | -7.4 |  | -12.8 | 35.2 | 26.8 | 29.2 | 29.4 | 28 | 28.4667 |  | 24 | 26.4 | 25.8 | 25 | 25.4
United Kingdom |  | FOULA | FOULA, United Kingdom | 60.12N | 2.07W | 13 | 0.00 (GMT) | 84-06 | 30140 | -2.4 |  | -5.1 | 25.7 | 14.4 | 17.7 | 17.2 | 16 | 16.4333 |  | 13.1 | 15.5 | 15.7 | 15 | 14.7667
United Kingdom |  | FOYERS | FOYERS, United Kingdom | 57.27N | 4.48W | 21 | 0.00 (GMT) | 82-03 | 30570 | -5.5 |  | -11.8 | 30.1 | 22.7 | 24.8 | 25.3 | 24 | 24.2667 |  | 20 | 22 | 22.1 | 21 | 21.3667
United Kingdom |  | FYLINGDALES | FYLINGDALES, United Kingdom | 54.37N | 0.67W | 262 | 0.00 (GMT) | 82-06 | 32810 | -5.8 |  | -10.7 | 31.5 | 23.3 | 24.4 | 24.4 | 24 | 24.0333 |  | 20.6 | 22.3 | 21.8 | 22 | 21.5667
United Kingdom |  | GLASGOW AIRPORT | GLASGOW AIRPORT, United Kingdom | 55.87N | 4.43W | 8 | 0.00 (GMT) | 82-06 | 31400 | -9.4 |  | -18 | 31.1 | 25 | 26.4 | 26.1 | 26 | 25.8333 |  | 21.9 | 23.8 | 23 | 23 | 22.9
United Kingdom |  | GLEN OGLE | GLEN OGLE, United Kingdom | 56.42N | 4.32W | 564 | 0.00 (GMT) | 96-06 | 31480 | -6.6 |  | -8.5 | 25.6 | 17.7 | 20.7 | 21.1 | 20 | 19.8333 |  | 15.6 | 18.6 | 18.4 | 18 | 17.5333
United Kingdom |  | GLENANNE | GLENANNE, United Kingdom | 54.23N | 6.50W | 160 | 0.00 (GMT) | 85-06 | 39230 | -4.4 |  | -12.4 | 29.8 | 22.9 | 24.5 | 24.1 | 24 | 23.8333 |  | 20.4 | 22.1 | 21.1 | 21 | 21.2
United Kingdom |  | GRAVESEND-BROADNESS | GRAVESEND-BROADNESS, United Kingdom | 51.47N | 0.30E | 3 | 0.00 (GMT) | 97-06 | 37840 | N/A |  | N/A | N/A | 29.5 | 29.5 | 32.1 | 30 | 30.3667 |  | 25.9 | 27.7 | 29 | 28 | 27.5333
United Kingdom |  | GREAT DUN FELL | GREAT DUN FELL, United Kingdom | 54.68N | 2.45W | 847 | 0.00 (GMT) | 94-06 | 32270 | -8.8 |  | -14.7 | 31.4 | 18.2 | 20.7 | 20.4 | 20 | 19.7667 |  | 15.7 | 18.2 | 18.7 | 18 | 17.5333
United Kingdom |  | GREENOCK MRCC | GREENOCK MRCC, United Kingdom | 55.97N | 4.80W | 5 | 0.00 (GMT) | 87-06 | 31380 | -1.6 |  | -4 | 30 | 23.7 | 24.7 | 24.3 | 24 | 24.2333 |  | 20.4 | 22.3 | 21.5 | 21 | 21.4
United Kingdom |  | GWENNAP HEAD | GWENNAP HEAD, United Kingdom | 50.03N | 5.67W | 66 | 0.00 (GMT) | 82-92 | 38060 | -1.6 |  | -8 | 29.6 | 21.4 | 24.1 | 22.3 | 23 | 22.6 |  | 19 | 21.6 | 20.4 | 20 | 20.3333
United Kingdom |  | HAWARDEN | HAWARDEN, United Kingdom | 53.17N | 2.98W | 9 | 0.00 (GMT) | 86-06 | 33210 | -7.8 |  | -15.8 | 35.5 | 27 | 28.4 | 28.7 | 28 | 28.0333 |  | 23.2 | 25.5 | 24.8 | 25 | 24.5
United Kingdom |  | HEMSBY | HEMSBY, United Kingdom | 52.68N | 1.68E | 14 | 0.00 (GMT) | 82-01 | 34960 | -5 |  | -11.3 | 32.6 | 24.4 | 26.1 | 26 | 26 | 25.5 |  | 21.5 | 23.5 | 23.7 | 23 | 22.9
United Kingdom |  | HERSTMONCEUX | HERSTMONCEUX, United Kingdom | 50.87N | 0.33E | 18 | 0.00 (GMT) | 82-92 | 38840 | -7 |  | -17.2 | 34.6 | 25.5 | 27.7 | 28.5 | 27 | 27.2333 |  | 23 | 25 | 24.3 | 24 | 24.1
United Kingdom |  | HERSTMONCEUX | HERSTMONCEUX, United Kingdom | 50.90N | 0.32E | 52 | 0.00 (GMT) | 92-06 | 38820 | -4.8 |  | -8.1 | 34.5 | 26.9 | 29.4 | 29.2 | 29 | 28.5 |  | 24.1 | 26.1 | 26.5 | 26 | 25.5667
United Kingdom |  | HIGH WYCOMBE HQSTC | HIGH WYCOMBE HQSTC, United Kingdom | 51.68N | 0.80W | 205 | 0.00 (GMT) | 97-06 | 36600 | -4.5 |  | -6.1 | 35.9 | 27.1 | 29 | 29 | 28 | 28.3667 |  | 24.1 | 26.7 | 25.8 | 26 | 25.5333
United Kingdom |  | HILLSBOROUGH | HILLSBOROUGH, United Kingdom | 54.48N | 6.10W | 38 | 0.00 (GMT) | 82-03 | 39200 | -7.3 |  | -14 | 29.5 | 23.7 | 24.9 | 24.9 | 25 | 24.5 |  | 20.7 | 22.9 | 22.1 | 22 | 21.9
United Kingdom |  | HOLBEACH | HOLBEACH, United Kingdom | 52.87N | 0.15E | 2 | 0.00 (GMT) | 86-06 | 34690 | -5.2 |  | -7.7 | 34.7 | 26.9 | 27.5 | 28.7 | 28 | 27.7 |  | 23.8 | 25.2 | 25.3 | 25 | 24.7667
United Kingdom |  | HONINGTON | HONINGTON, United Kingdom | 52.33N | 0.77E | 53 | 0.00 (GMT) | 82-03 | 35860 | -7.3 |  | -15.4 | 35.6 | 26.6 | 28.8 | 29.1 | 28 | 28.1667 |  | 24 | 26.4 | 26.1 | 26 | 25.5
United Kingdom |  | HYSKEIR (LGT-H) | HYSKEIR (LGT-H), United Kingdom | 56.97N | 6.68W | 10 | 0.00 (GMT) | 86-95 | 30240 | N/A |  | N/A | N/A | 19.2 | 21.6 | 19.6 | 20 | 20.1333 |  | 17.4 | 18.7 | 17.6 | 18 | 17.9
United Kingdom |  | INVERBERVIE NO.2 | INVERBERVIE NO.2, United Kingdom | 56.85N | 2.27W | 134 | 0.00 (GMT) | 87-06 | 30880 | -3.5 |  | -6.2 | 27.3 | 19.8 | 21.3 | 20.9 | 21 | 20.6667 |  | 17.6 | 19.2 | 19 | 19 | 18.6
United Kingdom |  | INVERGORDON HARBOUR | INVERGORDON HARBOUR, United Kingdom | 57.68N | 4.17W | 3 | 0.00 (GMT) | 84-01 | 30580 | -4.9 |  | -11.5 | 28.4 | 21.8 | 23.1 | 22.7 | 23 | 22.5333 |  | 19.3 | 20.5 | 21 | 20 | 20.2667
United Kingdom |  | ISLE OF PORTLAND | ISLE OF PORTLAND, United Kingdom | 50.52N | 2.45W | 52 | 0.00 (GMT) | 94-06 | 38570 | -1.7 |  | -5.8 | 31 | 21.5 | 24.1 | 24.1 | 23 | 23.2333 |  | 18.7 | 21.5 | 22 | 21 | 20.7333
United Kingdom |  | KENLEY AIRFIELD | KENLEY AIRFIELD, United Kingdom | 51.30N | 0.08W | 170 | 0.00 (GMT) | 88-06 | 37810 | -4.6 |  | -7.3 | 35.8 | 27.1 | 28.7 | 29.3 | 28 | 28.3667 |  | 24.4 | 26.7 | 26.8 | 26 | 25.9667
United Kingdom |  | KESWICK | KESWICK, United Kingdom | 54.62N | 3.17W | 81 | 0.00 (GMT) | 84-06 | 32120 | -7.5 |  | -11.4 | 31.5 | 25.6 | 26.9 | 27 | 27 | 26.5 |  | 22.6 | 24.3 | 23.5 | 23 | 23.4667
United Kingdom |  | KINLOSS | KINLOSS, United Kingdom | 57.65N | 3.57W | 5 | 0.00 (GMT) | 82-06 | 30660 | -8 |  | -15 | 32.1 | 23.8 | 25.5 | 25.8 | 25 | 25.0333 |  | 20.6 | 22.7 | 22.3 | 22 | 21.8667
United Kingdom |  | KIRKWALL AIRPORT | KIRKWALL AIRPORT, United Kingdom | 58.95N | 2.90W | 26 | 0.00 (GMT) | 82-06 | 30170 | -3.6 |  | -6.6 | 25.2 | 18.5 | 20.3 | 20.7 | 20 | 19.8333 |  | 16.5 | 18.3 | 18.2 | 18 | 17.6667
United Kingdom |  | LAKENHEATH RAF | LAKENHEATH RAF, United Kingdom | 52.40N | 0.57E | 10 | 0.00 (GMT) | 82-95 | 35833 | -8.1 |  | -14.9 | 34.4 | 27.8 | 29.9 | 29.9 | 29 | 29.2 |  | 25.2 | 27.1 | 26.2 | 26 | 26.1667
United Kingdom |  | LAKENHEATH RAF | LAKENHEATH RAF, United Kingdom | 52.42N | 0.57E | 10 | 0.00 (GMT) | 82-06 | 35830 | N/A |  | N/A | N/A | 28.9 | 28.9 | 30.1 | 29 | 29.3 |  | 25.9 | 26.2 | 28 | 27 | 26.7
United Kingdom |  | LANGDON BAY | LANGDON BAY, United Kingdom | 51.13N | 1.35E | 117 | 0.00 (GMT) | 82-06 | 37960 | -4.2 |  | -11.4 | 33.2 | 24.1 | 26.2 | 26.2 | 26 | 25.5 |  | 21.3 | 23.2 | 23.6 | 23 | 22.7
United Kingdom |  | LARKHILL | LARKHILL, United Kingdom | 51.20N | 1.80W | 133 | 0.00 (GMT) | 95-06 | 37430 | -6.6 |  | -10.7 | 34.1 | 26.8 | 29 | 29.5 | 28 | 28.4333 |  | 24.2 | 26.7 | 26.9 | 26 | 25.9333
United Kingdom |  | LARNE | LARNE, United Kingdom | 54.85N | 5.80W | 3 | 0.00 (GMT) | 82-03 | 39280 | -1.4 |  | -5.3 | 28.4 | 20.9 | 22.6 | 22.4 | 22 | 21.9667 |  | 18.8 | 20.6 | 20.4 | 20 | 19.9333
United Kingdom |  | LECONFIELD | LECONFIELD, United Kingdom | 53.87N | 0.43W | 7 | 0.00 (GMT) | 84-06 | 33820 | -7.2 |  | -14.1 | 33.4 | 25.8 | 27.2 | 27.7 | 27 | 26.9 |  | 22.7 | 25 | 24.8 | 24 | 24.1667
United Kingdom |  | LEEDS BRADFORD | LEEDS BRADFORD, United Kingdom | 53.87N | 1.65W | 213 | 0.00 (GMT) | 95-06 | 33463 | -5.2 |  | -8.1 | 31.7 | 25.2 | 26.9 | 27.1 | 26 | 26.4 |  | 22 | 24.2 | 24.2 | 23 | 23.4667
United Kingdom |  | LEEDS WEATHER CTR | LEEDS WEATHER CTR, United Kingdom | 53.80N | 1.55W | 47 | 0.00 (GMT) | 88-03 | 33470 | -4.4 |  | -9 | 34.8 | 27.2 | 28.2 | 29.8 | 28 | 28.4 |  | 24 | 25.8 | 26.4 | 25 | 25.4
United Kingdom |  | LEEMING | LEEMING, United Kingdom | 54.30N | 1.53W | 32 | 0.00 (GMT) | 82-06 | 32570 | -7.9 |  | -14 | 32.9 | 25.7 | 27.5 | 28.2 | 27 | 27.1333 |  | 23 | 25.3 | 24.7 | 24 | 24.3333
United Kingdom |  | LERWICK | LERWICK, United Kingdom | 60.13N | 1.18W | 84 | 0.00 (GMT) | 82-06 | 30050 | -4.4 |  | -7.5 | 23.7 | 17.2 | 17.8 | 18.7 | 18 | 17.9 |  | 14.3 | 16 | 16.4 | 16 | 15.5667
United Kingdom |  | LEUCHARS | LEUCHARS, United Kingdom | 56.40N | 2.87W | 10 | 0.00 (GMT) | 82-06 | 31710 | -7.2 |  | -14.3 | 31.8 | 22.9 | 24.7 | 24.6 | 24 | 24.0667 |  | 20.6 | 22.2 | 21.7 | 22 | 21.5
United Kingdom |  | LINTON-ON-OUSE | LINTON-ON-OUSE, United Kingdom | 54.05N | 1.25W | 14 | 0.00 (GMT) | 93-06 | 32660 | -7 |  | -11.6 | 33.2 | 26.7 | 27.8 | 28.9 | 28 | 27.8 |  | 23.4 | 25.8 | 25.9 | 25 | 25.0333
United Kingdom |  | LISCOMBE | LISCOMBE, United Kingdom | 51.08N | 3.60W | 347 | 0.00 (GMT) | 93-06 | 37100 | N/A |  | N/A | N/A | 23.5 | 25.6 | 26.5 | 25 | 25.2 |  | 21.2 | 23.4 | 23.6 | 23 | 22.7333
United Kingdom |  | LITTLE RISSINGTON | LITTLE RISSINGTON, United Kingdom | 51.87N | 1.68W | 210 | 0.00 (GMT) | 84-06 | 36470 | -6.5 |  | -13.3 | 35 | 25.6 | 28.5 | 27.9 | 27 | 27.3333 |  | 22.9 | 25.6 | 24.9 | 24 | 24.4667
United Kingdom |  | LIVERPOOL | LIVERPOOL, United Kingdom | 53.33N | 2.85W | 25 | 0.00 (GMT) | 82-06 | 33233 | -5.8 |  | -11.2 | 34.9 | 26.9 | 28.8 | 28.1 | 28 | 27.9333 |  | 23.2 | 25.9 | 24.8 | 25 | 24.6333
United Kingdom |  | LOCH GLASCARNOCH | LOCH GLASCARNOCH, United Kingdom | 57.72N | 4.88W | 264 | 0.00 (GMT) | 92-06 | 30310 | -11.3 |  | -19.7 | 29.3 | 23.5 | 23.7 | 24.5 | 24 | 23.9 |  | 19.9 | 21 | 20.9 | 21 | 20.6
United Kingdom |  | LOFTUS SAMOS | LOFTUS SAMOS, United Kingdom | 54.57N | 0.87W | 159 | 0.00 (GMT) | 96-06 | 32750 | -3.9 |  | -6.3 | 30.9 | 24.1 | 25 | 26 | 25 | 25.0333 |  | 21.1 | 23 | 23 | 22 | 22.3667
United Kingdom |  | LONDON WEA CENTER | LONDON WEA CENTER, United Kingdom | 51.52N | 0.12W | 23 | 0.00 (GMT) | 82-92 | 37780 | -3.2 |  | -11.3 | 36.6 | 27.5 | 30.6 | 29.6 | 29 | 29.2333 |  | 25 | 27.7 | 26.6 | 26 | 26.4333
United Kingdom |  | LONDON WEATHER CENT | LONDON WEATHER CENT, United Kingdom | 51.52N | 0.10W | 43 | 0.00 (GMT) | 92-06 | 37790 | -2.3 |  | -5.4 | 37.3 | 29.9 | 30.6 | 31.1 | 31 | 30.5333 |  | 26.6 | 28.2 | 28.4 | 28 | 27.7333
United Kingdom |  | LONDON/GATWICK ARPT | LONDON/GATWICK ARPT, United Kingdom | 51.15N | 0.18W | 62 | 0.00 (GMT) | 82-06 | 37760 | -7.6 |  | -14.4 | 36.7 | 27.9 | 30 | 30.5 | 29 | 29.4667 |  | 25.2 | 27.3 | 27.1 | 27 | 26.5333
United Kingdom |  | LONDON/HEATHROW AIR | LONDON/HEATHROW AIR, United Kingdom | 51.48N | 0.45W | 25 | 0.00 (GMT) | 82-06 | 37720 | -5.4 |  | -10.2 | 37.5 | 29.2 | 31.1 | 31.4 | 31 | 30.5667 |  | 26.2 | 28.6 | 28 | 28 | 27.6
United Kingdom |  | LOSSIEMOUTH | LOSSIEMOUTH, United Kingdom | 57.72N | 3.32W | 6 | 0.00 (GMT) | 82-06 | 30680 | -8.3 |  | -15.6 | 30.8 | 23.3 | 25.2 | 25.2 | 25 | 24.5667 |  | 20.1 | 22 | 22 | 21 | 21.3667
United Kingdom |  | LOUGH FEA | LOUGH FEA, United Kingdom | 54.72N | 6.82W | 227 | 0.00 (GMT) | 94-06 | 39110 | -5.6 |  | -8.5 | 29.4 | 21.8 | 24.2 | 24.2 | 23 | 23.4 |  | 19.2 | 21.7 | 21.8 | 21 | 20.9
United Kingdom |  | LUNDY ISL (LGT-H) | LUNDY ISL (LGT-H), United Kingdom | 51.17N | 4.65W | 43 | 0.00 (GMT) | 82-94 | 37020 | -0.8 |  | -7.3 | 30 | 20.4 | 22.9 | 22.5 | 22 | 21.9333 |  | 18.6 | 21.1 | 20.2 | 20 | 19.9667
United Kingdom |  | LUTON | LUTON, United Kingdom | 51.87N | 0.37W | 164 | 0.00 (GMT) | 82-06 | 36733 | -5.9 |  | -11.8 | 36.6 | 27 | 29.8 | 29.9 | 29 | 28.9 |  | 24.1 | 26.9 | 26.8 | 26 | 25.9333
United Kingdom |  | LYNEHAM | LYNEHAM, United Kingdom | 51.50N | 1.98W | 147 | 0.00 (GMT) | 82-06 | 37400 | -7.1 |  | -14.3 | 35 | 26.5 | 29 | 28.8 | 28 | 28.1 |  | 24.1 | 26.4 | 25.6 | 25 | 25.3667
United Kingdom |  | MACHRIHANISH | MACHRIHANISH, United Kingdom | 55.43N | 5.70W | 10 | 0.00 (GMT) | 83-06 | 31110 | -5.6 |  | -9.3 | 30.8 | 21.9 | 23.7 | 23.6 | 23 | 23.0667 |  | 18.9 | 21 | 20.9 | 20 | 20.2667
United Kingdom |  | MADLEY | MADLEY, United Kingdom | 52.03N | 2.85W | 78 | 0.00 (GMT) | 84-97 | 35210 | -8.8 |  | -17.3 | 34.4 | 26.7 | 26.9 | 27.6 | 27 | 27.0667 |  | 23.8 | 25.3 | 24.5 | 25 | 24.5333
United Kingdom |  | MANCHESTER AIRPORT | MANCHESTER AIRPORT, United Kingdom | 53.35N | 2.28W | 69 | 0.00 (GMT) | 82-06 | 33340 | -6.6 |  | -11.6 | 34.3 | 26.8 | 28.5 | 28.7 | 28 | 28 |  | 23.7 | 26.1 | 25.3 | 25 | 25.0333
United Kingdom |  | MANSTON | MANSTON, United Kingdom | 51.35N | 1.37E | 44 | 0.00 (GMT) | 82-06 | 37970 | -5.2 |  | -11.9 | 33.9 | 25.8 | 28 | 28 | 27 | 27.2667 |  | 23.2 | 25.3 | 25.4 | 25 | 24.6333
United Kingdom |  | MARHAM | MARHAM, United Kingdom | 52.65N | 0.57E | 21 | 0.00 (GMT) | 82-06 | 34820 | -7.3 |  | -13.5 | 35.7 | 27.2 | 29.4 | 29.5 | 29 | 28.7 |  | 24.4 | 26.8 | 26.7 | 26 | 25.9667
United Kingdom |  | MIDDLE WALLOP | MIDDLE WALLOP, United Kingdom | 51.15N | 1.57W | 91 | 0.00 (GMT) | 94-06 | 37490 | -6.3 |  | -10.3 | 35.8 | 27.4 | 29.4 | 30.4 | 29 | 29.0667 |  | 24.7 | 27.1 | 27.3 | 26 | 26.3667
United Kingdom |  | MILDENHALL RAF | MILDENHALL RAF, United Kingdom | 52.37N | 0.48E | 10 | 0.00 (GMT) | 82-95 | 35773 | -6.8 |  | -13.5 | 35.6 | 27.9 | 30.1 | 30 | 29 | 29.3333 |  | 25.8 | 27.8 | 27.1 | 27 | 26.9
United Kingdom |  | MILFORD HAVEN | MILFORD HAVEN, United Kingdom | 51.70N | 5.05W | 32 | 0.00 (GMT) | 82-06 | 36040 | -3.1 |  | -8.2 | 30.4 | 23 | 25.4 | 25.1 | 25 | 24.5 |  | 20.9 | 23.1 | 22.1 | 22 | 22.0333
United Kingdom |  | MUCKLE FLUGGA | MUCKLE FLUGGA, United Kingdom | 60.85N | 0.88W | 53 | 0.00 (GMT) | 82-95 | 30010 | -1.9 |  | -5.1 | 24.5 | 17.6 | 18.7 | 18.6 | 18 | 18.3 |  | 15.2 | 16.7 | 16.1 | 16 | 16
United Kingdom |  | MUCKLE HOLM | MUCKLE HOLM, United Kingdom | 60.58N | 1.27W | 20 | 0.00 (GMT) | 82-04 | 30070 | -2.5 |  | -9.4 | 21.6 | 15.3 | 16.5 | 16.9 | 16 | 16.2333 |  | 13.3 | 15 | 15.6 | 15 | 14.6333
United Kingdom |  | MUMBLES | MUMBLES, United Kingdom | 51.57N | 3.98W | 32 | 0.00 (GMT) | 82-06 | 36090 | -2.4 |  | -7.9 | 31 | 23.5 | 25.5 | 25.2 | 25 | 24.7333 |  | 21.3 | 23.4 | 22.9 | 23 | 22.5333
United Kingdom |  | NEWCASTLE | NEWCASTLE, United Kingdom | 55.03N | 1.68W | 83 | 0.00 (GMT) | 82-06 | 32433 | -8 |  | -15.5 | 32.1 | 24 | 25.2 | 26.1 | 25 | 25.1 |  | 21.2 | 23.1 | 22.9 | 22 | 22.4
United Kingdom |  | NEWCASTLE WEATHER C | NEWCASTLE WEATHER C, United Kingdom | 54.98N | 1.60W | 52 | 0.00 (GMT) | 82-05 | 32460 | -5.4 |  | -12.1 | 31.1 | 24 | 25.2 | 26.2 | 25 | 25.1333 |  | 21.4 | 23 | 23 | 22 | 22.4667
United Kingdom |  | NEWHAVEN (LGT-H) | NEWHAVEN (LGT-H), United Kingdom | 50.78N | 0.05E | 5 | 0.00 (GMT) | 82-00 | 38800 | -3.9 |  | -12.1 | 30.7 | 24.5 | 26 | 26.6 | 26 | 25.7 |  | 21.1 | 23.8 | 23.7 | 23 | 22.8667
United Kingdom |  | NORTH RONA | NORTH RONA, United Kingdom | 59.12N | 5.82W | 103 | 0.00 (GMT) | 92-06 | 30110 | -1.9 |  | -5.3 | 27.2 | 15.5 | 18.1 | 18.9 | 18 | 17.5 |  | 13.7 | 15.9 | 16.5 | 15 | 15.3667
United Kingdom |  | NORTHOLT | NORTHOLT, United Kingdom | 51.55N | 0.42W | 39 | 0.00 (GMT) | 82-06 | 36720 | -7.2 |  | -13.2 | 37.2 | 29.1 | 30.8 | 31.4 | 30 | 30.4333 |  | 26.1 | 28.2 | 28.4 | 28 | 27.5667
United Kingdom |  | NORWICH WEA CNTRE | NORWICH WEA CNTRE, United Kingdom | 52.63N | 1.32E | 18 | 0.00 (GMT) | 87-03 | 34920 | -4.1 |  | -9.8 | 35 | 26.4 | 28.2 | 28.7 | 28 | 27.7667 |  | 23.8 | 25.9 | 26.3 | 25 | 25.3333
United Kingdom |  | NOTTINGHAM/WATNALL | NOTTINGHAM/WATNALL, United Kingdom | 53.00N | 1.25W | 117 | 0.00 (GMT) | 82-06 | 33540 | -6.1 |  | -12.5 | 35 | 27.2 | 29.1 | 29.2 | 29 | 28.5 |  | 24.2 | 26.5 | 25.8 | 26 | 25.5
United Kingdom |  | OBAN | OBAN, United Kingdom | 56.42N | 5.47W | 4 | 0.00 (GMT) | 82-00 | 31140 | -5.4 |  | -11.2 | 30.4 | 25 | 25.4 | 25 | 25 | 25.1333 |  | 21.4 | 22.8 | 22.4 | 22 | 22.2
United Kingdom |  | ODIHAM | ODIHAM, United Kingdom | 51.23N | 0.95W | 118 | 0.00 (GMT) | 82-06 | 37610 | -6.4 |  | -9.2 | 35.9 | 27.3 | 29.3 | 30.5 | 29 | 29.0333 |  | 24.6 | 26.9 | 26.9 | 26 | 26.1333
United Kingdom |  | ORSAY (LGT-H) | ORSAY (LGT-H), United Kingdom | 55.67N | 6.50W | 23 | 0.00 (GMT) | 84-98 | 31020 | -1.7 |  | -6 | 25.7 | 19.6 | 20.5 | 19.7 | 20 | 19.9333 |  | 16.7 | 17.4 | 17.9 | 17 | 17.3333
United Kingdom |  | PEMBREY SANDS | PEMBREY SANDS, United Kingdom | 51.72N | 4.37W | 6 | 0.00 (GMT) | 93-06 | 36050 | -5.9 |  | -9.1 | 32.6 | 24.6 | 26.4 | 27 | 26 | 26 |  | 21.6 | 23.1 | 23.2 | 23 | 22.6333
United Kingdom |  | PENDENNIS POINT | PENDENNIS POINT, United Kingdom | 50.15N | 5.07W | 42 | 0.00 (GMT) | 84-06 | 38100 | -0.7 |  | -6 | 29.2 | 21.9 | 24.1 | 24.1 | 23 | 23.3667 |  | 19.9 | 21.9 | 21.8 | 21 | 21.2
United Kingdom |  | PENDINE (AUT) | PENDINE (AUT), United Kingdom | 51.75N | 4.52W | 5 | 0.00 (GMT) | 88-99 | 36080 | -4.3 |  | -7.8 | 30.6 | 23.2 | 25.9 | 27.5 | 26 | 25.5333 |  | 21.2 | 23.7 | 24.1 | 23 | 23
United Kingdom |  | PERSHORE | PERSHORE, United Kingdom | 52.15N | 2.03W | 31 | 0.00 (GMT) | 82-06 | 35290 | -7.2 |  | -9.8 | 35.9 | 27.3 | 29.9 | 29.2 | 29 | 28.8 |  | 24.7 | 27.2 | 26.1 | 26 | 26
United Kingdom |  | PETERHEAD HARBOUR | PETERHEAD HARBOUR, United Kingdom | 57.50N | 1.77W | 15 | 0.00 (GMT) | 82-06 | 30920 | -2.5 |  | -6.6 | 24.8 | 17.8 | 19.7 | 19.6 | 19 | 19.0333 |  | 16.1 | 17.7 | 17.9 | 17 | 17.2333
United Kingdom |  | PLYMOUTH MOUNT BATT | PLYMOUTH MOUNT BATT, United Kingdom | 50.35N | 4.12W | 50 | 0.00 (GMT) | 82-06 | 38270 | -3.1 |  | -7.1 | 32.6 | 24.5 | 26 | 26.7 | 26 | 25.7333 |  | 21.8 | 23.8 | 23.3 | 23 | 22.9667
United Kingdom |  | PORTGLENONE | PORTGLENONE, United Kingdom | 54.87N | 6.45W | 65 | 0.00 (GMT) | 94-06 | 39150 | -5.4 |  | -10.7 | 29 | 23.9 | 24.9 | 25 | 25 | 24.6 |  | 20.7 | 22.6 | 22.5 | 22 | 21.9333
United Kingdom |  | PORTLAND HELIPORT | PORTLAND HELIPORT, United Kingdom | 50.57N | 2.45W | 3 | 0.00 (GMT) | 88-99 | 38580 | -2.2 |  | -8.6 | 31.7 | 23.5 | 24.4 | 25.7 | 25 | 24.5333 |  | 21 | 22.3 | 23.3 | 22 | 22.2
United Kingdom |  | PRESTWICK RNAS | PRESTWICK RNAS, United Kingdom | 55.52N | 4.58W | 27 | 0.00 (GMT) | 93-06 | 31360 | -6.2 |  | -12.2 | 32.4 | 24.6 | 26.3 | 26.2 | 26 | 25.7 |  | 20.4 | 22.4 | 22.9 | 22 | 21.9
United Kingdom |  | PRESTWICK(CIV/NAVY) | PRESTWICK(CIV/NAVY), United Kingdom | 55.50N | 4.58W | 20 | 0.00 (GMT) | 82-06 | 31350 | -7.1 |  | -14.4 | 32.5 | 25 | 26 | 26.1 | 26 | 25.7 |  | 21 | 23 | 22.5 | 22 | 22.1667
United Kingdom |  | REDESDALE CAMP | REDESDALE CAMP, United Kingdom | 55.28N | 2.28W | 212 | 0.00 (GMT) | 83-06 | 32300 | -10.3 |  | -17.1 | 30.7 | 23.6 | 25.7 | 25.5 | 25 | 24.9333 |  | 20.9 | 23.3 | 22.2 | 22 | 22.1333
United Kingdom |  | RHYL | RHYL, United Kingdom | 53.25N | 3.50W | 76 | 0.00 (GMT) | 86-06 | 33130 | -4.7 |  | -10.4 | 33.6 | 24.7 | 27.1 | 27.3 | 26 | 26.3667 |  | 21.4 | 23.6 | 23.6 | 23 | 22.8667
United Kingdom |  | SCILLY: ST MARYS AI | SCILLY: ST MARYS AI, United Kingdom | 49.92N | 6.30W | 30 | 0.00 (GMT) | 86-06 | 38030 | 1 |  | -6 | 25.3 | 20.2 | 21.6 | 21.5 | 21 | 21.1 |  | 18.6 | 20.2 | 20.2 | 20 | 19.6667
United Kingdom |  | SELLA NESS | SELLA NESS, United Kingdom | 60.45N | 1.27W | 7 | 0.00 (GMT) | 82-04 | 30060 | -3.8 |  | -8.1 | 26 | 18.3 | 20.1 | 20.8 | 20 | 19.7333 |  | 15.5 | 17.7 | 18.3 | 17 | 17.1667
United Kingdom |  | SENNYBRIDGE | SENNYBRIDGE, United Kingdom | 52.07N | 3.62W | 307 | 0.00 (GMT) | 84-06 | 35070 | -9.7 |  | -16.5 | 31.1 | 23.6 | 25.7 | 26.2 | 25 | 25.1667 |  | 21.1 | 23.2 | 22.9 | 22 | 22.4
United Kingdom |  | SHAP | SHAP, United Kingdom | 54.50N | 2.68W | 255 | 0.00 (GMT) | 82-06 | 32250 | -9.7 |  | -16.2 | 31.1 | 23.1 | 25.5 | 25.6 | 25 | 24.7333 |  | 20.7 | 23 | 23 | 22 | 22.2333
United Kingdom |  | SHAWBURY | SHAWBURY, United Kingdom | 52.80N | 2.67W | 72 | 0.00 (GMT) | 82-06 | 34140 | -9 |  | -16.7 | 34.8 | 26.6 | 28.6 | 28.5 | 28 | 27.9 |  | 23.5 | 26.2 | 24.9 | 25 | 24.8667
United Kingdom |  | SHEERNESS | SHEERNESS, United Kingdom | 51.45N | 0.75E | 25 | 0.00 (GMT) | 83-06 | 37910 | -2.6 |  | -9.3 | 33.3 | 25.2 | 26.6 | 27.1 | 26 | 26.3 |  | 22.5 | 24.2 | 24.3 | 24 | 23.6667
United Kingdom |  | SHOBDON | SHOBDON, United Kingdom | 52.25N | 2.88W | 99 | 0.00 (GMT) | 92-06 | 35200 | -7.1 |  | -13.9 | 35.2 | 27 | 28.8 | 28.8 | 28 | 28.2 |  | 24 | 26.2 | 25.9 | 25 | 25.3667
United Kingdom |  | SHOEBURYNESS | SHOEBURYNESS, United Kingdom | 51.55N | 0.83E | 3 | 0.00 (GMT) | 92-06 | 36930 | -4.5 |  | -7.8 | 32.8 | 25.8 | 27.5 | 28.2 | 27 | 27.1667 |  | 23.3 | 25.3 | 25.3 | 25 | 24.6333
United Kingdom |  | SHOREHAM AIRPORT | SHOREHAM AIRPORT, United Kingdom | 50.83N | 0.28W | 2 | 0.00 (GMT) | 99-06 | 38760 | -5.5 |  | -7.8 | 32.7 | 25.6 | 26.5 | 27 | 26 | 26.3667 |  | 22.6 | 24.6 | 23.9 | 24 | 23.7
United Kingdom |  | SKYE/LUSA | SKYE/LUSA, United Kingdom | 57.25N | 5.80W | 18 | 0.00 (GMT) | 98-06 | 30370 | N/A |  | N/A | N/A | 23.2 | 23.7 | 25.4 | 24 | 24.1 |  | 19.1 | 20.4 | 21.3 | 20 | 20.2667
United Kingdom |  | SOLENT M.R.S.C. | SOLENT M.R.S.C., United Kingdom | 50.80N | 1.22W | 13 | 0.00 (GMT) | 86-06 | 38740 | -4.2 |  | -9.5 | 32.8 | 26.1 | 27.8 | 28 | 27 | 27.3 |  | 23.3 | 25.4 | 24.8 | 25 | 24.5
United Kingdom |  | SOUTHAMPTON WX CNTR | SOUTHAMPTON WX CNTR, United Kingdom | 50.90N | 1.40W | 9 | 0.00 (GMT) | 82-01 | 38650 | -4.7 |  | -10.2 | 34.4 | 26.7 | 28.7 | 28.6 | 28 | 28 |  | 24.2 | 26.3 | 25.7 | 25 | 25.4
United Kingdom |  | SOUTHEND | SOUTHEND, United Kingdom | 51.57N | 0.68E | 15 | 0.00 (GMT) | 82-06 | 36913 | -5.7 |  | -12.2 | 35.2 | 27.1 | 28.9 | 29.2 | 28 | 28.4 |  | 24.1 | 26.2 | 26.2 | 26 | 25.5
United Kingdom |  | SPADEADAM | SPADEADAM, United Kingdom | 55.05N | 2.55W | 286 | 0.00 (GMT) | 92-06 | 32240 | -7.7 |  | -12.4 | 30.9 | 23 | 25.2 | 25.5 | 25 | 24.5667 |  | 20.1 | 22.6 | 22.4 | 22 | 21.7
United Kingdom |  | ST ANGELO | ST ANGELO, United Kingdom | 54.40N | 7.65W | 47 | 0.00 (GMT) | 85-06 | 39030 | -6 |  | -10.1 | 31.1 | 24.9 | 25.3 | 25 | 25 | 25.0667 |  | 21.6 | 22.9 | 21.7 | 22 | 22.0667
United Kingdom |  | ST BEES HEAD NO.2 | ST BEES HEAD NO.2, United Kingdom | 54.52N | 3.60W | 123 | 0.00 (GMT) | 84-06 | 32100 | -3.6 |  | -8.4 | 31.4 | 23.2 | 24.9 | 25 | 24 | 24.3667 |  | 19.9 | 21.7 | 21.5 | 21 | 21.0333
United Kingdom |  | ST. CATHERINES POIN | ST. CATHERINES POIN, United Kingdom | 50.58N | 1.30W | 24 | 0.00 (GMT) | 82-06 | 38660 | -2.9 |  | -9.2 | 29.8 | 22.9 | 25 | 25.3 | 24 | 24.4 |  | 20.6 | 22.7 | 23.2 | 22 | 22.1667
United Kingdom |  | ST. MAWGAN | ST. MAWGAN, United Kingdom | 50.43N | 5.00W | 103 | 0.00 (GMT) | 82-06 | 38170 | -3.4 |  | -8.8 | 31.6 | 24.3 | 26.2 | 25.8 | 25 | 25.4333 |  | 21.1 | 23.4 | 22.6 | 22 | 22.3667
United Kingdom |  | STANSTED AIRPORT | STANSTED AIRPORT, United Kingdom | 51.88N | 0.23E | 106 | 0.00 (GMT) | 82-06 | 36830 | -6.9 |  | -13.7 | 36.4 | 27.1 | 29.7 | 29.9 | 29 | 28.9 |  | 24.3 | 27 | 26.9 | 26 | 26.0667
United Kingdom |  | STORNOWAY | STORNOWAY, United Kingdom | 58.22N | 6.32W | 15 | 0.00 (GMT) | 82-06 | 30260 | -4 |  | -8 | 27.2 | 19 | 20.7 | 21 | 20 | 20.2333 |  | 16.4 | 18.5 | 18.4 | 18 | 17.7667
United Kingdom |  | STRATHALLEN AIRFIEL | STRATHALLEN AIRFIEL, United Kingdom | 56.32N | 3.73W | 35 | 0.00 (GMT) | 89-06 | 31440 | -9.4 |  | -14.1 | 30.1 | 23.7 | 25.7 | 25.3 | 25 | 24.9 |  | 21 | 23.4 | 22.7 | 22 | 22.3667
United Kingdom |  | SULE SKERRY | SULE SKERRY, United Kingdom | 59.08N | 4.40W | 12 | 0.00 (GMT) | 82-06 | 30100 | -0.5 |  | -4.4 | 23.5 | 15.3 | 17.2 | 18.4 | 17 | 16.9667 |  | 14.1 | 16.1 | 17 | 16 | 15.7333
United Kingdom |  | SUMBURGH (CAPE) | SUMBURGH (CAPE), United Kingdom | 59.88N | 1.30W | 5 | 0.00 (GMT) | 82-06 | 30030 | -3.5 |  | -6.2 | 21.7 | 16 | 17.3 | 17.7 | 17 | 17 |  | 14.2 | 16.1 | 16.1 | 15 | 15.4667
United Kingdom |  | TAIN RANGE | TAIN RANGE, United Kingdom | 57.82N | 3.97W | 4 | 0.00 (GMT) | 89-06 | 30620 | -8.2 |  | -16.4 | 29.8 | 21.7 | 23.1 | 23.9 | 23 | 22.9 |  | 19.4 | 20.7 | 21.4 | 21 | 20.5
United Kingdom |  | THAMES TOWER (AUT) | THAMES TOWER (AUT), United Kingdom | 51.67N | 1.10E | 8 | 0.00 (GMT) | 82-99 | 36950 | N/A |  | N/A | N/A | 20.4 | 22.8 | 23.2 | 22 | 22.1333 |  | 19 | 21.5 | 21.9 | 21 | 20.8
United Kingdom |  | THORNEY ISLAND | THORNEY ISLAND, United Kingdom | 50.82N | 0.92W | 3 | 0.00 (GMT) | 84-06 | 38720 | -5 |  | -9 | 33.6 | 26.3 | 28 | 28.1 | 27 | 27.4667 |  | 23.5 | 25.1 | 25 | 25 | 24.5333
United Kingdom |  | TIREE | TIREE, United Kingdom | 56.50N | 6.88W | 12 | 0.00 (GMT) | 82-06 | 31000 | -3 |  | -9.6 | 27.8 | 19.8 | 21.4 | 21.3 | 21 | 20.8333 |  | 16.9 | 18.4 | 18.5 | 18 | 17.9333
United Kingdom |  | TRAWSGOED | TRAWSGOED, United Kingdom | 52.35N | 3.95W | 62 | 0.00 (GMT) | 83-06 | 35030 | -6.8 |  | -12.2 | 35.9 | 26.4 | 27.1 | 27 | 27 | 26.8333 |  | 22.8 | 24.3 | 23 | 23 | 23.3667
United Kingdom |  | TULLOCH BRIDGE | TULLOCH BRIDGE, United Kingdom | 56.87N | 4.70W | 236 | 0.00 (GMT) | 83-06 | 30470 | -10.6 |  | -16.7 | 29.1 | 25.1 | 24.8 | 24.3 | 25 | 24.7333 |  | 21.2 | 22.1 | 20.6 | 21 | 21.3
United Kingdom |  | TYNEMOUTH | TYNEMOUTH, United Kingdom | 55.02N | 1.42W | 30 | 0.00 (GMT) | 82-99 | 32620 | -4.5 |  | -10.5 | 31.7 | 20.4 | 23.2 | 22.8 | 22 | 22.1333 |  | 18.4 | 21.1 | 20.6 | 20 | 20.0333
United Kingdom |  | UPPER HEYFORD RAF | UPPER HEYFORD RAF, United Kingdom | 51.93N | 1.25W | 134 | 0.00 (GMT) | 82-93 | 36553 | -7.5 |  | -17 | 35.9 | 26 | 29 | 27.9 | 28 | 27.6333 |  | 23.9 | 26.2 | 24.9 | 25 | 25
United Kingdom |  | VALLEY | VALLEY, United Kingdom | 53.25N | 4.53W | 10 | 0.00 (GMT) | 82-06 | 33020 | -3.8 |  | -8.5 | 34.1 | 24.6 | 26.4 | 26.4 | 26 | 25.8 |  | 21 | 23.4 | 22.4 | 22 | 22.2667
United Kingdom |  | WADDINGTON | WADDINGTON, United Kingdom | 53.17N | 0.52W | 68 | 0.00 (GMT) | 82-06 | 33770 | -6.3 |  | -13.5 | 34.4 | 26.6 | 28.5 | 28.8 | 28 | 27.9667 |  | 23.8 | 26 | 25.8 | 25 | 25.2
United Kingdom |  | WAINFLEET | WAINFLEET, United Kingdom | 53.08N | 0.27E | 5 | 0.00 (GMT) | 84-06 | 33920 | -5.7 |  | -12.8 | 32.7 | 25.4 | 26.1 | 26.5 | 26 | 26 |  | 22.2 | 23.6 | 24.4 | 23 | 23.4
United Kingdom |  | WALNEY ISLAND | WALNEY ISLAND, United Kingdom | 54.12N | 3.25W | 14 | 0.00 (GMT) | 83-06 | 32140 | -3.5 |  | -7.7 | 32.1 | 24.3 | 26.5 | 26.3 | 26 | 25.7 |  | 21 | 23.2 | 22.8 | 22 | 22.3333
United Kingdom |  | WALTON-ON-NAZE | WALTON-ON-NAZE, United Kingdom | 51.85N | 1.28E | 5 | 0.00 (GMT) | 90-06 | 36960 | -3.8 |  | -6.8 | 29.9 | 23.5 | 24.7 | 25.1 | 24 | 24.4333 |  | 21 | 23 | 23.4 | 22 | 22.4667
United Kingdom |  | WARCOP RANGE | WARCOP RANGE, United Kingdom | 54.57N | 2.42W | 227 | 0.00 (GMT) | 83-06 | 32260 | -7 |  | -10.6 | 31.1 | 23.9 | 25.7 | 26.1 | 25 | 25.2333 |  | 21.3 | 23.4 | 23.3 | 23 | 22.6667
United Kingdom |  | WATTISHAM | WATTISHAM, United Kingdom | 52.12N | 0.97E | 89 | 0.00 (GMT) | 82-06 | 35900 | -6.7 |  | -13.1 | 34.9 | 26.2 | 28.7 | 28.8 | 28 | 27.9 |  | 23.7 | 26.3 | 26.3 | 25 | 25.4333
United Kingdom |  | WEST FREUGH | WEST FREUGH, United Kingdom | 54.85N | 4.95W | 10 | 0.00 (GMT) | 83-06 | 31320 | -6 |  | -11.7 | 30.6 | 22.6 | 24.9 | 23.4 | 24 | 23.6333 |  | 19.4 | 21.8 | 20.6 | 21 | 20.6
United Kingdom |  | WEYBOURNE | WEYBOURNE, United Kingdom | 52.95N | 1.13E | 20 | 0.00 (GMT) | 86-06 | 34880 | -4.2 |  | -10.4 | 33.1 | 26.5 | 27.3 | 27.5 | 27 | 27.1 |  | 22.7 | 23.8 | 24.2 | 24 | 23.5667
United Kingdom |  | WICK | WICK, United Kingdom | 58.45N | 3.08W | 36 | 0.00 (GMT) | 82-06 | 30750 | -6.8 |  | -12.2 | 25 | 18.4 | 20 | 20.3 | 20 | 19.5667 |  | 16.2 | 18 | 18.2 | 17 | 17.4667
United Kingdom |  | WITTERING | WITTERING, United Kingdom | 52.62N | 0.47W | 73 | 0.00 (GMT) | 82-06 | 34620 | -6.1 |  | -9.9 | 34.1 | 27.5 | 29.6 | 29.7 | 29 | 28.9333 |  | 24.4 | 27 | 27.2 | 26 | 26.2
United Kingdom |  | WYTON(RAF) | WYTON(RAF), United Kingdom | 52.35N | 0.12W | 41 | 0.00 (GMT) | 82-95 | 35660 | -7 |  | -15.1 | 35.8 | 26.7 | 29.3 | 28.4 | 28 | 28.1333 |  | 24.2 | 26.8 | 25.7 | 26 | 25.5667
United Kingdom |  | YEOVILTON | YEOVILTON, United Kingdom | 51.00N | 2.63W | 20 | 0.00 (GMT) | 82-06 | 38530 | -7.9 |  | -13.9 | 35.9 | 26.5 | 29.5 | 29.1 | 28 | 28.3667 |  | 24.2 | 26.6 | 25.6 | 25 | 25.4667
United_States | Alabama | ANNISTON METROPOLITAN AP | ANNISTON METROPOLITAN AP, AL, USA | 33.59N | 85.86W | 183 | -6.00 (NAC) | 82-06 | 722287 | -11.3 | -11 | -19.8 | 40.6 | 35.2 | 36.5 | 36.9 | 36 | 36.2 | 37 | 33.3 | 34.8 | 34.6 | 34 | 34.2333 | 34 | 1 | United_StatesAlabamaANNISTON METROPOLITAN AP
United_States | Alabama | AUBURN-OPELIKA APT | AUBURN-OPELIKA APT, AL, USA | 32.62N | 85.43W | 236 | -6.00 (NAC) | 92-06 | 722284 | -8.9 | -9 | -15.4 | 40.1 | 34.1 | 36.2 | 36 | 35 | 35.4333 | 36 | 32.7 | 34.1 | 33 | 33 | 33.2667 | 33 | 2 | United_StatesAlabamaAUBURN-OPELIKA APT
United_States | Alabama | BIRMINGHAM MUNICIPAL AP | BIRMINGHAM MUNICIPAL AP, AL, USA | 33.56N | 86.75W | 192 | -6.00 (NAC) | 82-06 | 722280 | -11.8 | -12 | -21.4 | 41 | 35.2 | 36.7 | 37.1 | 36 | 36.3333 | 37 | 33.4 | 34.9 | 34.9 | 34 | 34.4 | 34 | 3 | United_StatesAlabamaBIRMINGHAM MUNICIPAL AP
United_States | Alabama | CAIRNS AAF/OZARK | CAIRNS AAF/OZARK, AL, USA | 31.28N | 85.72W | 91 | -6.00 (NAC) | 82-06 | 722269 | -7.5 | -8 | -15.5 | 40.4 | 37.2 | 37.2 | 36.2 | 37 | 36.8667 | 37 | 34.8 | 35.2 | 34.8 | 35 | 34.9333 | 35 | 4 | United_StatesAlabamaCAIRNS AAF/OZARK
United_States | Alabama | CENTREVILLE WSMO | CENTREVILLE WSMO, AL, USA | 32.90N | 87.25W | 138 | -6.00 (NAC) | 84-94 | 722290 | -11.1 | -11 | -23.1 | 38 | 35.1 | 35.9 | 35.7 | 36 | 35.5667 | 36 | 33.5 | 34.2 | 34 | 34 | 33.9 | 34 | 5 | United_StatesAlabamaCENTREVILLE WSMO
United_States | Alabama | DAUPHIN ISLAND | DAUPHIN ISLAND, AL, USA | 30.25N | 88.08W | 9 | -6.00 (NAC) | 89-06 | 994420 | -2.1 | -2 | -9.5 | 35.6 | 30.8 | 31.8 | 32.4 | 32 | 31.6667 | 32 | 30 | 31 | 31.1 | 31 | 30.7 | 31 | 6 | United_StatesAlabamaDAUPHIN ISLAND
United_States | Alabama | DOTHAN MUNICIPAL | DOTHAN MUNICIPAL, AL, USA | 31.32N | 85.45W | 98 | -6.00 (NAC) | 82-06 | 722268 | -7.5 | -8 | -16.4 | 40.7 | 36.8 | 37.2 | 36.6 | 37 | 36.8667 | 37 | 34.7 | 35.1 | 34.7 | 35 | 34.8333 | 35 | 7 | United_StatesAlabamaDOTHAN MUNICIPAL
United_States | Alabama | GADSEN MUNI (AWOS) | GADSEN MUNI (AWOS), AL, USA | 33.97N | 86.08W | 173 | -6.00 (NAC) | 92-06 | 722285 | -11.6 | -12 | -18.1 | 41.1 | 34.1 | 36.2 | 36.4 | 36 | 35.5667 | 36 | 32.7 | 34.1 | 34 | 34 | 33.6 | 34 | 8 | United_StatesAlabamaGADSEN MUNI (AWOS)
United_States | Alabama | HUNTSVILLE INTL/JONES FIELD | HUNTSVILLE INTL/JONES FIELD, AL, USA | 34.64N | 86.79W | 196 | -6.00 (NAC) | 82-06 | 723230 | -12.9 | -13 | -23.8 | 41 | 35.1 | 36.2 | 36.7 | 36 | 36 | 36 | 33.2 | 34.6 | 34.7 | 34 | 34.1667 | 34 | 9 | United_StatesAlabamaHUNTSVILLE INTL/JONES FIELD
United_States | Alabama | MAXWELL AFB/MONTGOM | MAXWELL AFB/MONTGOM, AL, USA | 32.38N | 86.37W | 53 | -6.00 (NAC) | 85-99 | 722265 | -5.8 | -6 | -10.3 | 40.3 | 37.2 | 37.7 | 37.5 | 37 | 37.4667 | 38 | 35.4 | 36.2 | 35.8 | 36 | 35.8 | 36 | 10 | United_StatesAlabamaMAXWELL AFB/MONTGOM
United_States | Alabama | MOBILE REGIONAL AP | MOBILE REGIONAL AP, AL, USA | 30.69N | 88.25W | 67 | -6.00 (NAC) | 82-06 | 722230 | -7.2 | -7 | -16.5 | 39.3 | 34.7 | 35.7 | 35.5 | 35 | 35.3 | 36 | 33.3 | 34.1 | 34 | 34 | 33.8 | 34 | 11 | United_StatesAlabamaMOBILE REGIONAL AP
United_States | Alabama | MONTGOMERY DANNELLY FIELD | MONTGOMERY DANNELLY FIELD, AL, USA | 32.30N | 86.39W | 62 | -6.00 (NAC) | 82-06 | 722260 | -9.3 | -9 | -17.7 | 41 | 36.3 | 37.1 | 37.4 | 37 | 36.9333 | 37 | 34.5 | 35.5 | 35.6 | 35 | 35.2 | 35 | 12 | United_StatesAlabamaMONTGOMERY DANNELLY FIELD
United_States | Alabama | MUSCLE SHOALS REGIONAL AP | MUSCLE SHOALS REGIONAL AP, AL, USA | 34.75N | 87.61W | 171 | -6.00 (NAC) | 82-06 | 723235 | -12.3 | -12 | -23.9 | 41.6 | 35.2 | 36.9 | 37.3 | 36 | 36.4667 | 37 | 33.6 | 35.2 | 35.4 | 35 | 34.7333 | 35 | 13 | United_StatesAlabamaMUSCLE SHOALS REGIONAL AP
United_States | Alabama | TUSCALOOSA MUNICIPAL AP | TUSCALOOSA MUNICIPAL AP, AL, USA | 33.21N | 87.62W | 57 | -6.00 (NAC) | 82-06 | 722286 | -11.1 | -11 | -20.7 | 39.4 | 35.7 | 37 | 37.3 | 37 | 36.6667 | 37 | 34 | 35.2 | 35.4 | 35 | 34.8667 | 35 | 14 | United_StatesAlabamaTUSCALOOSA MUNICIPAL AP
United_States | Alaska | ADAK NAS | ADAK NAS, AK, USA | 51.88N | 176.65W | 6 | -10.00 (NAH) | 82-06 | 704540 | -11.1 | -11 | -15.5 | 24.5 | 13.7 | 17.2 | 18 | 16 | 16.3 | 17 | 11.3 | 14.7 | 15.8 | 14 | 13.9333 | 14 | 15 | United_StatesAlaskaADAK NAS
United_States | Alaska | AMBLER | AMBLER, AK, USA | 67.10N | 157.85W | 88 | -9.00 (NAK) | 92-06 | 701718 | N/A | N/A | N/A | N/A | 27.4 | 27.1 | 25.2 | 27 | 26.5667 | 27 | 24.7 | 24.9 | 22 | 24 | 23.8667 | 24 | 16 | United_StatesAlaskaAMBLER
United_States | Alaska | ANAKTUVUK PASS | ANAKTUVUK PASS, AK, USA | 68.13N | 151.73W | 657 | -9.00 (NAK) | 85-06 | 701625 | N/A | N/A | N/A | N/A | 23.7 | 24 | 22.7 | 23 | 23.4667 | 24 | 21.3 | 21.7 | 18.6 | 21 | 20.5333 | 21 | 17 | United_StatesAlaskaANAKTUVUK PASS
United_States | Alaska | ANCHORAGE INTL AP | ANCHORAGE INTL AP, AK, USA | 61.18N | 149.99W | 40 | -9.00 (NAK) | 82-06 | 702730 | -25.6 | -26 | -33.7 | 28.6 | 23.4 | 24.2 | 23.2 | 24 | 23.6 | 24 | 21.1 | 22.1 | 20.8 | 21 | 21.3333 | 21 | 18 | United_StatesAlaskaANCHORAGE INTL AP
United_States | Alaska | ANCHORAGE MERRILL FIELD | ANCHORAGE MERRILL FIELD, AK, USA | 61.22N | 149.86W | 42 | -9.00 (NAK) | 82-06 | 702735 | -26.4 | -26 | -34.1 | 29.3 | 24.2 | 25.2 | 24 | 24 | 24.4667 | 25 | 22.2 | 22.8 | 22 | 22 | 22.3333 | 22 | 19 | United_StatesAlaskaANCHORAGE MERRILL FIELD
United_States | Alaska | ANCHORAGE/ELMENDORF | ANCHORAGE/ELMENDORF, AK, USA | 61.25N | 149.80W | 59 | -9.00 (NAK) | 82-06 | 702720 | -29 | -29 | -37.9 | 31.1 | 24.8 | 26.2 | 25.2 | 25 | 25.4 | 26 | 22.5 | 23.3 | 22.5 | 23 | 22.7667 | 23 | 20 | United_StatesAlaskaANCHORAGE/ELMENDORF
United_States | Alaska | ANNETTE ISLAND AP | ANNETTE ISLAND AP, AK, USA | 55.04N | 131.57W | 34 | -9.00 (NAK) | 82-06 | 703980 | -12.6 | -13 | -20.9 | 34.2 | 27.9 | 24.6 | 25.4 | 26 | 25.9667 | 25 | 22.3 | 21.9 | 21.8 | 22 | 22 | 22 | 21 | United_StatesAlaskaANNETTE ISLAND AP
United_States | Alaska | ANVIK | ANVIK, AK, USA | 62.65N | 160.18W | 99 | -9.00 (NAK) | 95-06 | 702075 | -34.4 | -34 | -44.9 | 29.1 | 24.9 | 24.2 | 25.8 | 25 | 24.9667 | 24 | 22.8 | 22.8 | 21 | 22 | 22.2 | 22 | 22 | United_StatesAlaskaANVIK
United_States | Alaska | BARROW W POST-W ROGERS ARPT | BARROW W POST-W ROGERS ARPT, AK, USA | 71.29N | 156.76W | 4 | -9.00 (NAK) | 82-06 | 700260 | -42.6 | -43 | -49.3 | 25.7 | 15.2 | 18.2 | 16.8 | 17 | 16.7333 | 18 | 11.4 | 14.8 | 13.6 | 13 | 13.2667 | 13 | 23 | United_StatesAlaskaBARROW W POST-W ROGERS ARPT
United_States | Alaska | BARTER ISLAND (DEW) | BARTER ISLAND (DEW), AK, USA | 70.13N | 143.63W | 12 | -9.00 (NAK) | 82-99 | 700860 | N/A | N/A | N/A | N/A | 13.7 | 15.7 | 28.5 | 19 | 19.3 | 16 | 8.9 | 12.8 | 17.4 | 13 | 13.0333 | 13 | 24 | United_StatesAlaskaBARTER ISLAND (DEW)
United_States | Alaska | BETHEL AIRPORT | BETHEL AIRPORT, AK, USA | 60.79N | 161.83W | 46 | -9.00 (NAK) | 82-06 | 702190 | -34.7 | -35 | -43.6 | 31.8 | 25.5 | 25.1 | 24.1 | 25 | 24.9 | 25 | 21.8 | 22.5 | 20.5 | 22 | 21.6 | 22 | 25 | United_StatesAlaskaBETHEL AIRPORT
United_States | Alaska | BETTLES FIELD | BETTLES FIELD, AK, USA | 66.92N | 151.51W | 196 | -9.00 (NAK) | 82-06 | 701740 | -47.6 | -48 | -53.2 | 34.1 | 29.2 | 28.8 | 26.2 | 28 | 28.0667 | 29 | 26.4 | 26.4 | 22.7 | 25 | 25.1667 | 25 | 26 | United_StatesAlaskaBETTLES FIELD
United_States | Alaska | BIG DELTA ALLEN AAF | BIG DELTA ALLEN AAF, AK, USA | 64.00N | 145.72W | 388 | -9.00 (NAK) | 82-06 | 702670 | -42.2 | -42 | -52.2 | 32.5 | 27.9 | 27.9 | 27.7 | 28 | 27.8333 | 28 | 25.4 | 25.5 | 24.5 | 25 | 25.1333 | 25 | 27 | United_StatesAlaskaBIG DELTA ALLEN AAF
United_States | Alaska | CAPE LISBURNE(AWOS) | CAPE LISBURNE(AWOS), AK, USA | 68.88N | 166.13W | 3 | -9.00 (NAK) | 82-06 | 701040 | N/A | N/A | N/A | N/A | 15.3 | 16.7 | 17.2 | 16 | 16.4 | 17 | 11.8 | 15 | 14.7 | 14 | 13.8333 | 14 | 28 | United_StatesAlaskaCAPE LISBURNE(AWOS)
United_States | Alaska | CAPE NEWENHAM AFS | CAPE NEWENHAM AFS, AK, USA | 58.65N | 162.07W | 161 | -9.00 (NAK) | 82-06 | 703050 | N/A | N/A | N/A | N/A | 18.7 | 18 | 18 | 18 | 18.2333 | 18 | 15.6 | 16.2 | 16.2 | 16 | 16 | 16 | 29 | United_StatesAlaskaCAPE NEWENHAM AFS
United_States | Alaska | CAPE ROMANZOFF AWOS | CAPE ROMANZOFF AWOS, AK, USA | 61.78N | 166.03W | 123 | -9.00 (NAK) | 82-06 | 702120 | N/A | N/A | N/A | N/A | 21.3 | 19.9 | 21.1 | 21 | 20.7667 | 20 | 17.2 | 17.4 | 18 | 18 | 17.5333 | 18 | 30 | United_StatesAlaskaCAPE ROMANZOFF AWOS
United_States | Alaska | COLD BAY ARPT | COLD BAY ARPT, AK, USA | 55.21N | 162.72W | 31 | -9.00 (NAK) | 82-06 | 703160 | -16.4 | -16 | -24.2 | 24.3 | 15.8 | 17 | 17.7 | 17 | 16.8333 | 17 | 13.1 | 15 | 15.7 | 15 | 14.6 | 15 | 31 | United_StatesAlaskaCOLD BAY ARPT
United_States | Alaska | CORDOVA | CORDOVA, AK, USA | 60.49N | 145.45W | 15 | -9.00 (NAK) | 82-06 | 702960 | -22.4 | -22 | -31.2 | 31.4 | 24.3 | 24.3 | 24.4 | 24 | 24.3333 | 24 | 20.9 | 20.9 | 21 | 21 | 20.9333 | 21 | 32 | United_StatesAlaskaCORDOVA
United_States | Alaska | DEADHORSE | DEADHORSE, AK, USA | 70.19N | 148.48W | 18 | -9.00 (NAK) | 82-06 | 700637 | -44.7 | -45 | -51.8 | 29.4 | 20.2 | 22.9 | 21.8 | 22 | 21.6333 | 23 | 17.2 | 20 | 17.9 | 18 | 18.3667 | 18 | 33 | United_StatesAlaskaDEADHORSE
United_States | Alaska | DILLINGHAM MUNI | DILLINGHAM MUNI, AK, USA | 59.05N | 158.52W | 29 | -9.00 (NAK) | 82-06 | 703210 | -32.6 | -33 | -45 | 30.7 | 22.8 | 23.9 | 22.7 | 23 | 23.1333 | 24 | 19.9 | 21.4 | 20.2 | 21 | 20.5 | 21 | 34 | United_StatesAlaskaDILLINGHAM MUNI
United_States | Alaska | DUTCH HARBOR | DUTCH HARBOR, AK, USA | 53.90N | 166.55W | 4 | -9.00 (NAK) | 92-06 | 704890 | -9.8 | -10 | -19.2 | 24.3 | 15.9 | 19 | 19.9 | 18 | 18.2667 | 19 | 12.6 | 17 | 17.6 | 16 | 15.7333 | 16 | 35 | United_StatesAlaskaDUTCH HARBOR
United_States | Alaska | FAIRBANKS INTL ARPT | FAIRBANKS INTL ARPT, AK, USA | 64.82N | 147.86W | 138 | -9.00 (NAK) | 82-06 | 702610 | -42.8 | -43 | -51.2 | 35.6 | 30 | 29.7 | 27.6 | 29 | 29.1 | 30 | 27.5 | 27.4 | 24.5 | 26 | 26.4667 | 26 | 36 | United_StatesAlaskaFAIRBANKS INTL ARPT
United_States | Alaska | FAIRBANKS/EIELSON A | FAIRBANKS/EIELSON A, AK, USA | 64.65N | 147.07W | 167 | -9.00 (NAK) | 82-00 | 702650 | -43.6 | -44 | -52.7 | 36.2 | 30 | 29.8 | 28 | 29 | 29.2667 | 30 | 27.6 | 27.4 | 24.2 | 26 | 26.4 | 26 | 37 | United_StatesAlaskaFAIRBANKS/EIELSON A
United_States | Alaska | FIVE FINGER ISLAND | FIVE FINGER ISLAND, AK, USA | 57.27N | 133.63W | 21 | -9.00 (NAK) | 85-06 | 994080 | -9 | -9 | -15.7 | 25.3 | 20 | 20.4 | 20.2 | 20 | 20.2 | 20 | 17.7 | 18.4 | 18.2 | 18 | 18.1 | 18 | 38 | United_StatesAlaskaFIVE FINGER ISLAND
United_States | Alaska | FORT YUKON | FORT YUKON, AK, USA | 66.57N | 145.27W | 138 | -9.00 (NAK) | 82-06 | 701940 | -48.6 | -49 | -57 | 35.6 | 28.2 | 29.4 | 27.5 | 28 | 28.3667 | 29 | 26 | 26.9 | 24.3 | 26 | 25.7333 | 26 | 39 | United_StatesAlaskaFORT YUKON
United_States | Alaska | FT. RICHARDSON/BRYA | FT. RICHARDSON/BRYA, AK, USA | 61.27N | 149.65W | 115 | -9.00 (NAK) | 82-94 | 702700 | -30.9 | -31 | -41 | 29.7 | 25.1 | 26.2 | 24.2 | 25 | 25.1667 | 26 | 22.7 | 23.6 | 21.8 | 23 | 22.7 | 23 | 40 | United_StatesAlaskaFT. RICHARDSON/BRYA
United_States | Alaska | GALENA A. | GALENA A., AK, USA | 64.73N | 156.93W | 49 | -9.00 (NAK) | 82-06 | 702220 | -45.5 | -46 | -56.8 | 32.1 | 27.7 | 28 | 26.4 | 27 | 27.3667 | 28 | 25.4 | 26 | 22.6 | 25 | 24.6667 | 25 | 41 | United_StatesAlaskaGALENA A.
United_States | Alaska | GULKANA INTERMEDIATE FIELD | GULKANA INTERMEDIATE FIELD, AK, USA | 62.16N | 145.46W | 481 | -9.00 (NAK) | 82-06 | 702710 | -40.7 | -41 | -48.8 | 32.7 | 27.9 | 27.3 | 27.5 | 28 | 27.5667 | 27 | 24.7 | 25.1 | 24.5 | 25 | 24.7667 | 25 | 42 | United_StatesAlaskaGULKANA INTERMEDIATE FIELD
United_States | Alaska | HOMER ARPT | HOMER ARPT, AK, USA | 59.65N | 151.48W | 22 | -9.00 (NAK) | 82-06 | 703410 | -20.4 | -20 | -29.3 | 27 | 19 | 21.1 | 20.3 | 20 | 20.1333 | 21 | 16.9 | 18.5 | 18.4 | 18 | 17.9333 | 18 | 43 | United_StatesAlaskaHOMER ARPT
United_States | Alaska | HOOPER BAY | HOOPER BAY, AK, USA | 61.52N | 166.13W | 6 | -9.00 (NAK) | 92-06 | 702186 | N/A | N/A | N/A | N/A | 22 | 19.2 | 20.1 | 20 | 20.4333 | 19 | 17.1 | 17.3 | 17.2 | 17 | 17.2 | 17 | 44 | United_StatesAlaskaHOOPER BAY
United_States | Alaska | ILIAMNA ARPT | ILIAMNA ARPT, AK, USA | 59.75N | 154.92W | 49 | -9.00 (NAK) | 82-06 | 703400 | -29.1 | -29 | -39.1 | 31.4 | 23.1 | 25.6 | 23.7 | 24 | 24.1333 | 26 | 20 | 21.9 | 20.7 | 21 | 20.8667 | 21 | 45 | United_StatesAlaskaILIAMNA ARPT
United_States | Alaska | INDIAN MTN AFS AWOS | INDIAN MTN AFS AWOS, AK, USA | 66.00N | 153.70W | 372 | -9.00 (NAK) | 82-06 | 701730 | N/A | N/A | N/A | N/A | 27.5 | 26.8 | 25.1 | 26 | 26.4667 | 27 | 25.1 | 25 | 21.6 | 24 | 23.9 | 24 | 46 | United_StatesAlaskaINDIAN MTN AFS AWOS
United_States | Alaska | JUNEAU INT'L ARPT | JUNEAU INT'L ARPT, AK, USA | 58.36N | 134.58W | 7 | -9.00 (NAK) | 82-06 | 703810 | -18 | -18 | -24.8 | 30.7 | 26.2 | 25.6 | 24.5 | 25 | 25.4333 | 26 | 22.7 | 22.8 | 22.1 | 23 | 22.5333 | 23 | 47 | United_StatesAlaskaJUNEAU INT'L ARPT
United_States | Alaska | KAKE SEAPLANE BASE | KAKE SEAPLANE BASE, AK, USA | 56.97N | 133.95W | 0 | -9.00 (NAK) | 93-06 | 703855 | -13.9 | -14 | -18.5 | 30.1 | 23 | 22.2 | 22.9 | 23 | 22.7 | 22 | 20 | 19.7 | 20.3 | 20 | 20 | 20 | 48 | United_StatesAlaskaKAKE SEAPLANE BASE
United_States | Alaska | KENAI MUNICIPAL AP | KENAI MUNICIPAL AP, AK, USA | 60.58N | 151.24W | 28 | -9.00 (NAK) | 82-06 | 702590 | -32.9 | -33 | -41.6 | 29.4 | 22.9 | 23.9 | 22.9 | 23 | 23.2333 | 24 | 19.9 | 20.6 | 20.3 | 20 | 20.2667 | 20 | 49 | United_StatesAlaskaKENAI MUNICIPAL AP
United_States | Alaska | KETCHIKAN INTL AP | KETCHIKAN INTL AP, AK, USA | 55.36N | 131.71W | 29 | -9.00 (NAK) | 82-06 | 703950 | -14.4 | -14 | -21.6 | 29.7 | 23.9 | 23.8 | 23.8 | 24 | 23.8333 | 24 | 21 | 21.7 | 21.6 | 21 | 21.4333 | 21 | 50 | United_StatesAlaskaKETCHIKAN INTL AP
United_States | Alaska | KING SALMON ARPT | KING SALMON ARPT, AK, USA | 58.68N | 156.65W | 15 | -9.00 (NAK) | 82-06 | 703260 | -34.3 | -34 | -46.8 | 31.1 | 24.2 | 25.3 | 24.1 | 25 | 24.5333 | 25 | 21 | 22.4 | 21.1 | 22 | 21.5 | 22 | 51 | United_StatesAlaskaKING SALMON ARPT
United_States | Alaska | KLAWOCK | KLAWOCK, AK, USA | 55.58N | 133.08W | 15 | -9.00 (NAK) | 97-06 | 703894 | -11.6 | -12 | -15.1 | 37 | 27.8 | 21.9 | 25.7 | 25 | 25.1333 | 22 | 20.7 | 19.3 | 21.7 | 21 | 20.5667 | 21 | 52 | United_StatesAlaskaKLAWOCK
United_States | Alaska | KODIAK AIRPORT | KODIAK AIRPORT, AK, USA | 57.75N | 152.49W | 34 | -9.00 (NAK) | 82-06 | 703500 | -17 | -17 | -25.5 | 29.4 | 22 | 24.2 | 22.8 | 23 | 23 | 24 | 18.2 | 20.5 | 20.2 | 20 | 19.6333 | 20 | 53 | United_StatesAlaskaKODIAK AIRPORT
United_States | Alaska | KOTZEBUE RALPH WEIN MEMORIAL | KOTZEBUE RALPH WEIN MEMORIAL, AK, USA | 66.89N | 162.60W | 5 | -9.00 (NAK) | 82-06 | 701330 | -38.9 | -39 | -47.7 | 30.7 | 23.1 | 22.8 | 21.1 | 22 | 22.3333 | 23 | 18.6 | 20.3 | 18.2 | 19 | 19.0333 | 19 | 54 | United_StatesAlaskaKOTZEBUE RALPH WEIN MEMORIAL
United_States | Alaska | LAKE HOOD SEAPLANE | LAKE HOOD SEAPLANE, AK, USA | 61.18N | 149.96W | 40 | -9.00 (NAK) | 94-06 | 702725 | -24.4 | -24 | -32.8 | 32.6 | 24.1 | 26.3 | 25.3 | 25 | 25.2333 | 26 | 22.6 | 23.8 | 22.7 | 23 | 23.0333 | 23 | 55 | United_StatesAlaskaLAKE HOOD SEAPLANE
United_States | Alaska | MCGRATH ARPT | MCGRATH ARPT, AK, USA | 62.95N | 155.60W | 103 | -9.00 (NAK) | 82-06 | 702310 | -45.5 | -46 | -52.9 | 32.2 | 28 | 27.9 | 26.3 | 27 | 27.4 | 28 | 25.4 | 26 | 22.9 | 25 | 24.7667 | 25 | 56 | United_StatesAlaskaMCGRATH ARPT
United_States | Alaska | MCKINLEY PARK | MCKINLEY PARK, AK, USA | 63.73N | 148.92W | 524 | -9.00 (NAK) | 95-06 | 702645 | N/A | N/A | N/A | N/A | 26.3 | 25.8 | 26.1 | 26 | 26.0667 | 26 | 23 | 22.7 | 22.9 | 23 | 22.8667 | 23 | 57 | United_StatesAlaskaMCKINLEY PARK
United_States | Alaska | MEKORYUK | MEKORYUK, AK, USA | 60.37N | 166.27W | 15 | -9.00 (NAK) | 92-06 | 702185 | -28.8 | -29 | -33.2 | 27.3 | 16.4 | 17.9 | 18.7 | 18 | 17.6667 | 18 | 13.9 | 16 | 16.2 | 15 | 15.3667 | 15 | 58 | United_StatesAlaskaMEKORYUK
United_States | Alaska | MIDDLETON ISL. AMOS | MIDDLETON ISL. AMOS, AK, USA | 59.43N | 146.33W | 37 | -9.00 (NAK) | 82-06 | 703430 | -9 | -9 | -17.4 | 25.1 | 17.3 | 19.6 | 20.2 | 19 | 19.0333 | 20 | 15.1 | 17.6 | 17.7 | 17 | 16.8 | 17 | 59 | United_StatesAlaskaMIDDLETON ISL. AMOS
United_States | Alaska | MINCHUMINA | MINCHUMINA, AK, USA | 63.90N | 152.27W | 213 | -9.00 (NAK) | 93-06 | 702460 | N/A | N/A | N/A | N/A | 27.2 | 26.4 | 26.9 | 27 | 26.8333 | 26 | 24.3 | 24.4 | 23.7 | 24 | 24.1333 | 24 | 60 | United_StatesAlaskaMINCHUMINA
United_States | Alaska | NENANA MUNICIPAL AP | NENANA MUNICIPAL AP, AK, USA | 64.55N | 149.07W | 110 | -9.00 (NAK) | 82-06 | 702600 | -46.3 | -46 | -55.5 | 35.7 | 29 | 29.8 | 27.2 | 29 | 28.6667 | 30 | 26.7 | 27.2 | 24.2 | 26 | 26.0333 | 26 | 61 | United_StatesAlaskaNENANA MUNICIPAL AP
United_States | Alaska | NOME MUNICIPAL ARPT | NOME MUNICIPAL ARPT, AK, USA | 64.51N | 165.44W | 7 | -9.00 (NAK) | 82-06 | 702000 | -35.8 | -36 | -45.2 | 30.6 | 23.4 | 23.9 | 20.7 | 23 | 22.6667 | 24 | 20.3 | 20.4 | 18 | 20 | 19.5667 | 20 | 62 | United_StatesAlaskaNOME MUNICIPAL ARPT
United_States | Alaska | NORTHWAY AIRPORT | NORTHWAY AIRPORT, AK, USA | 62.96N | 141.95W | 525 | -9.00 (NAK) | 82-06 | 702910 | -47.4 | -47 | -56.3 | 32.2 | 28.5 | 28 | 27.4 | 28 | 27.9667 | 28 | 25.2 | 25.5 | 23.7 | 25 | 24.8 | 25 | 63 | United_StatesAlaskaNORTHWAY AIRPORT
United_States | Alaska | PALMER MUNICIPAL | PALMER MUNICIPAL, AK, USA | 61.60N | 149.09W | 76 | -9.00 (NAK) | 97-06 | 702740 | -27.9 | -28 | -39.7 | 31.1 | 24.9 | 26.4 | 25.9 | 26 | 25.7333 | 26 | 22.7 | 23.5 | 23.2 | 23 | 23.1333 | 23 | 64 | United_StatesAlaskaPALMER MUNICIPAL
United_States | Alaska | PETERSBURG | PETERSBURG, AK, USA | 56.82N | 132.97W | 33 | -9.00 (NAK) | 92-06 | 703860 | -15.8 | -16 | -20.8 | 30.7 | 23.9 | 22.7 | 22.9 | 23 | 23.1667 | 23 | 21 | 20.3 | 20.5 | 21 | 20.6 | 21 | 65 | United_StatesAlaskaPETERSBURG
United_States | Alaska | POINT HOPE (AWOS) | POINT HOPE (AWOS), AK, USA | 68.35N | 166.80W | 4 | -9.00 (NAK) | 92-06 | 701043 | N/A | N/A | N/A | N/A | 16.2 | 17.7 | 16.3 | 17 | 16.7333 | 18 | 12.4 | 16.1 | 13.7 | 14 | 14.0667 | 14 | 66 | United_StatesAlaskaPOINT HOPE (AWOS)
United_States | Alaska | PORT HEIDEN | PORT HEIDEN, AK, USA | 56.95N | 158.62W | 29 | -9.00 (NAK) | 82-06 | 703330 | -24 | -24 | -35.5 | 26.1 | 17.9 | 20.9 | 21.3 | 20 | 20.0333 | 21 | 15.9 | 17.7 | 18.4 | 17 | 17.3333 | 17 | 67 | United_StatesAlaskaPORT HEIDEN
United_States | Alaska | SAINT MARY`S (AWOS) | SAINT MARY`S (AWOS), AK, USA | 62.07N | 163.30W | 95 | -9.00 (NAK) | 90-06 | 702005 | -34.4 | -34 | -42.8 | 31.3 | 23 | 24 | 23 | 23 | 23.3333 | 24 | 21.1 | 21.3 | 19.1 | 21 | 20.5 | 21 | 68 | United_StatesAlaskaSAINT MARY`S (AWOS)
United_States | Alaska | SAND POINT | SAND POINT, AK, USA | 55.32N | 160.52W | 7 | -9.00 (NAK) | 94-06 | 703165 | -11.7 | -12 | -17.4 | 20.6 | 17.1 | 17.5 | 17.5 | 17 | 17.3667 | 18 | 13.9 | 16.1 | 16.3 | 15 | 15.4333 | 15 | 69 | United_StatesAlaskaSAND POINT
United_States | Alaska | SEWARD | SEWARD, AK, USA | 60.12N | 149.45W | 18 | -9.00 (NAK) | 82-06 | 702770 | -17.3 | -17 | -26.8 | 32.6 | 23.3 | 26 | 22.8 | 24 | 24.0333 | 26 | 19.3 | 21.5 | 20.4 | 20 | 20.4 | 20 | 70 | United_StatesAlaskaSEWARD
United_States | Alaska | SHEMYA AFB | SHEMYA AFB, AK, USA | 52.72N | 174.12E | 31 | -10.00 (NAH) | 82-95 | 704140 | -7.6 | -8 | -10.6 | 18.5 | 10.5 | 13.4 | 14.1 | 13 | 12.6667 | 13 | 9.2 | 11.7 | 12.9 | 11 | 11.2667 | 11 | 71 | United_StatesAlaskaSHEMYA AFB
United_States | Alaska | SHISHMAREF (AWOS) | SHISHMAREF (AWOS), AK, USA | 66.27N | 166.05W | 2 | -9.00 (NAK) | 90-06 | 701195 | N/A | N/A | N/A | N/A | 16 | 18.7 | 17.1 | 17 | 17.2667 | 19 | 12.7 | 16.2 | 14.8 | 15 | 14.5667 | 15 | 72 | United_StatesAlaskaSHISHMAREF (AWOS)
United_States | Alaska | SITKA JAPONSKI AP | SITKA JAPONSKI AP, AK, USA | 57.05N | 135.36W | 20 | -9.00 (NAK) | 82-06 | 703710 | -10.8 | -11 | -17.1 | 29.4 | 20.8 | 20.1 | 22.9 | 21 | 21.2667 | 20 | 17.6 | 17.9 | 19.3 | 18 | 18.2667 | 18 | 73 | United_StatesAlaskaSITKA JAPONSKI AP
United_States | Alaska | SKAGWAY AIRPORT | SKAGWAY AIRPORT, AK, USA | 59.46N | 135.31W | 13 | -9.00 (NAK) | 96-06 | 703620 | -17.5 | -18 | -23.7 | 33.4 | 24.8 | 24 | 25.4 | 25 | 24.7333 | 24 | 22 | 21.2 | 21.8 | 22 | 21.6667 | 22 | 74 | United_StatesAlaskaSKAGWAY AIRPORT
United_States | Alaska | SOLDOTNA | SOLDOTNA, AK, USA | 60.47N | 151.03W | 34 | -9.00 (NAK) | 92-06 | 702595 | -32.7 | -33 | -42.8 | 28.3 | 23.7 | 25 | 23.3 | 24 | 24 | 25 | 21.1 | 22.3 | 21.2 | 22 | 21.5333 | 22 | 75 | United_StatesAlaskaSOLDOTNA
United_States | Alaska | SPARREVOHN AFS | SPARREVOHN AFS, AK, USA | 61.10N | 155.57W | 484 | -9.00 (NAK) | 82-06 | 702350 | -35 | -35 | -38.7 | 31.8 | 24.2 | 24.3 | 25.3 | 25 | 24.6 | 24 | 21.2 | 22 | 21.6 | 22 | 21.6 | 22 | 76 | United_StatesAlaskaSPARREVOHN AFS
United_States | Alaska | ST PAUL ISLAND ARPT | ST PAUL ISLAND ARPT, AK, USA | 57.16N | 170.22W | 9 | -9.00 (NAK) | 82-06 | 703080 | -18.1 | -18 | -26.8 | 18.9 | 12.6 | 14.2 | 13.9 | 14 | 13.5667 | 14 | 10.3 | 12.7 | 12.6 | 12 | 11.8667 | 12 | 77 | United_StatesAlaskaST PAUL ISLAND ARPT
United_States | Alaska | TALKEETNA STATE ARPT | TALKEETNA STATE ARPT, AK, USA | 62.32N | 150.09W | 109 | -9.00 (NAK) | 82-06 | 702510 | -35.1 | -35 | -45.1 | 33 | 27.6 | 28 | 27.1 | 28 | 27.5667 | 28 | 24.7 | 25.4 | 23.2 | 24 | 24.4333 | 24 | 78 | United_StatesAlaskaTALKEETNA STATE ARPT
United_States | Alaska | TATALINA LRRS | TATALINA LRRS, AK, USA | 62.88N | 155.97W | 301 | -9.00 (NAK) | 82-06 | 702315 | N/A | N/A | N/A | N/A | 26.3 | 27.1 | 26.1 | 27 | 26.5 | 27 | 24.1 | 24.7 | 22.7 | 24 | 23.8333 | 24 | 79 | United_StatesAlaskaTATALINA LRRS
United_States | Alaska | TIN CITY AFS (AWOS) | TIN CITY AFS (AWOS), AK, USA | 65.57N | 167.92W | 83 | -9.00 (NAK) | 82-06 | 701170 | N/A | N/A | N/A | N/A | 18.9 | 20.2 | 16.5 | 19 | 18.5333 | 20 | 14.9 | 16.8 | 14 | 15 | 15.2333 | 15 | 80 | United_StatesAlaskaTIN CITY AFS (AWOS)
United_States | Alaska | TOGIAC VILLAGE AWOS | TOGIAC VILLAGE AWOS, AK, USA | 59.05N | 160.40W | 6 | -9.00 (NAK) | 92-06 | 703606 | -31.2 | -31 | -39.4 | 28.9 | 22.9 | 22.4 | 20.3 | 22 | 21.8667 | 22 | 19.1 | 19.9 | 17.9 | 19 | 18.9667 | 19 | 81 | United_StatesAlaskaTOGIAC VILLAGE AWOS
United_States | Alaska | UNALAKLEET FIELD | UNALAKLEET FIELD, AK, USA | 63.88N | 160.80W | 6 | -9.00 (NAK) | 83-06 | 702070 | N/A | N/A | N/A | N/A | 24.9 | 24.8 | 22.3 | 24 | 24 | 25 | 19.6 | 21.6 | 19.1 | 20 | 20.1 | 20 | 82 | United_StatesAlaskaUNALAKLEET FIELD
United_States | Alaska | VALDEZ PIONEER FIEL | VALDEZ PIONEER FIEL, AK, USA | 61.13N | 146.25W | 38 | -9.00 (NAK) | 96-06 | 702756 | -20.8 | -21 | -27.1 | 29.9 | 23 | 22.9 | 24 | 23 | 23.3 | 23 | 20.9 | 19.9 | 20.9 | 21 | 20.5667 | 21 | 83 | United_StatesAlaskaVALDEZ PIONEER FIEL
United_States | Alaska | VALDEZ WSO | VALDEZ WSO, AK, USA | 61.13N | 146.35W | 11 | -9.00 (NAK) | 82-05 | 702750 | -17.1 | -17 | -23.4 | 30.8 | 23 | 24.6 | 23.4 | 24 | 23.6667 | 25 | 20.5 | 20.8 | 20.2 | 21 | 20.5 | 21 | 84 | United_StatesAlaskaVALDEZ WSO
United_States | Alaska | WHITTIER | WHITTIER, AK, USA | 60.77N | 148.68W | 9 | -9.00 (NAK) | 87-06 | 702757 | -16.3 | -16 | -26.2 | 28.2 | 22.5 | 23.8 | 22.7 | 23 | 23 | 24 | 20.8 | 21.9 | 20.7 | 21 | 21.1333 | 21 | 85 | United_StatesAlaskaWHITTIER
United_States | Alaska | WRANGELL | WRANGELL, AK, USA | 56.48N | 132.37W | 13 | -9.00 (NAK) | 92-06 | 703870 | -13.4 | -13 | -18.2 | 30 | 24.1 | 23.2 | 23.7 | 24 | 23.6667 | 23 | 21.2 | 21.2 | 21.1 | 21 | 21.1667 | 21 | 86 | United_StatesAlaskaWRANGELL
United_States | Alaska | YAKUTAT STATE ARPT | YAKUTAT STATE ARPT, AK, USA | 59.51N | 139.63W | 9 | -9.00 (NAK) | 82-06 | 703610 | -20 | -20 | -28.4 | 32.1 | 23.2 | 21.7 | 22.5 | 22 | 22.4667 | 22 | 18.3 | 18.4 | 19.4 | 19 | 18.7 | 19 | 87 | United_StatesAlaskaYAKUTAT STATE ARPT
United_States | Arizona | CASA GRANDA (AWOS) | CASA GRANDA (AWOS), AZ, USA | 32.95N | 111.77W | 446 | -7.00 (NAZ) | 92-06 | 722748 | -3.6 | -4 | -6.6 | 48.7 | 43.4 | 44.4 | 43 | 44 | 43.6 | 44 | 42.1 | 42.7 | 41.9 | 42 | 42.2333 | 42 | 88 | United_StatesArizonaCASA GRANDA (AWOS)
United_States | Arizona | DAVIS-MONTHAN AFB | DAVIS-MONTHAN AFB, AZ, USA | 32.17N | 110.88W | 809 | -7.00 (NAZ) | 82-06 | 722745 | -2.5 | -3 | -5.9 | 46.7 | 42.5 | 42.3 | 40.8 | 42 | 41.8667 | 42 | 40.9 | 40.8 | 38.7 | 40 | 40.1333 | 40 | 89 | United_StatesArizonaDAVIS-MONTHAN AFB
United_States | Arizona | DOUGLAS BISBEE-DOUGLAS INTL A | DOUGLAS BISBEE-DOUGLAS INTL A, AZ, USA | 31.47N | 109.60W | 1250 | -7.00 (NAZ) | 86-06 | 722735 | -9.1 | -9 | -13 | 43.1 | 39.4 | 39 | 36.6 | 38 | 38.3333 | 39 | 37.8 | 37.4 | 34.8 | 37 | 36.6667 | 37 | 90 | United_StatesArizonaDOUGLAS BISBEE-DOUGLAS INTL A
United_States | Arizona | FLAGSTAFF AIRPORT | FLAGSTAFF AIRPORT, AZ, USA | 35.13N | 111.67W | 2135 | -7.00 (NAZ) | 82-06 | 723750 | -21.4 | -21 | -30.3 | 35.8 | 31.4 | 31.9 | 30.3 | 31 | 31.2 | 32 | 29.3 | 30.1 | 28.3 | 29 | 29.2333 | 29 | 91 | United_StatesArizonaFLAGSTAFF AIRPORT
United_States | Arizona | GRAND CANYON NATL P | GRAND CANYON NATL P, AZ, USA | 35.95N | 112.13W | 2065 | -7.00 (NAZ) | 93-06 | 723783 | -22.3 | -22 | -29.9 | 38.1 | 32.7 | 33.9 | 32.4 | 33 | 33 | 34 | 31.3 | 32.5 | 31.1 | 32 | 31.6333 | 32 | 92 | United_StatesArizonaGRAND CANYON NATL P
United_States | Arizona | KINGMAN (AMOS) | KINGMAN (AMOS), AZ, USA | 35.26N | 113.94W | 1050 | -7.00 (NAZ) | 82-06 | 723700 | -8 | -8 | -14 | 45.3 | 39.1 | 41.2 | 39.1 | 40 | 39.8 | 41 | 37.4 | 38.9 | 37.6 | 38 | 37.9667 | 38 | 93 | United_StatesArizonaKINGMAN (AMOS)
United_States | Arizona | LUKE AFB/PHOENIX | LUKE AFB/PHOENIX, AZ, USA | 33.53N | 112.38W | 331 | -7.00 (NAZ) | 82-06 | 722785 | -1 | -1 | -6.2 | 51 | 46.1 | 45.9 | 44.8 | 46 | 45.6 | 46 | 43.3 | 43.9 | 42.9 | 43 | 43.3667 | 43 | 94 | United_StatesArizonaLUKE AFB/PHOENIX
United_States | Arizona | NOGALES INTL | NOGALES INTL, AZ, USA | 31.42N | 110.85W | 1236 | -7.00 (NAZ) | 89-06 | 722728 | -6.3 | -6 | -10.6 | 44 | 39.8 | 39.4 | 37.4 | 39 | 38.8667 | 39 | 37.8 | 37.8 | 35.2 | 37 | 36.9333 | 37 | 95 | United_StatesArizonaNOGALES INTL
United_States | Arizona | PAGE MUNI (AMOS) | PAGE MUNI (AMOS), AZ, USA | 36.93N | 111.45W | 1304 | -7.00 (NAZ) | 82-06 | 723710 | -8.5 | -9 | -17.5 | 44.6 | 38.3 | 40.2 | 38 | 39 | 38.8333 | 40 | 36.9 | 38.2 | 36.3 | 37 | 37.1333 | 37 | 96 | United_StatesArizonaPAGE MUNI (AMOS)
United_States | Arizona | PHOENIX SKY HARBOR INTL AP | PHOENIX SKY HARBOR INTL AP, AZ, USA | 33.44N | 111.99W | 337 | -7.00 (NAZ) | 82-06 | 722780 | 1.3 | 1 | -2.5 | 49.8 | 45.1 | 45.4 | 44 | 45 | 44.8333 | 45 | 42.9 | 43.7 | 42.5 | 43 | 43.0333 | 43 | 97 | United_StatesArizonaPHOENIX SKY HARBOR INTL AP
United_States | Arizona | PRESCOTT LOVE FIELD | PRESCOTT LOVE FIELD, AZ, USA | 34.65N | 112.42W | 1540 | -7.00 (NAZ) | 82-06 | 723723 | -12.3 | -12 | -21.1 | 41 | 36.3 | 37.1 | 35.2 | 36 | 36.2 | 37 | 33.9 | 35.1 | 33.1 | 34 | 34.0333 | 34 | 98 | United_StatesArizonaPRESCOTT LOVE FIELD
United_States | Arizona | SAFFORD (AMOS) | SAFFORD (AMOS), AZ, USA | 32.82N | 109.68W | 950 | -7.00 (NAZ) | 83-06 | 722747 | -7.3 | -7 | -11.7 | 46 | 42.4 | 42.3 | 39.9 | 42 | 41.5333 | 42 | 40.3 | 40.3 | 37.8 | 39 | 39.4667 | 39 | 99 | United_StatesArizonaSAFFORD (AMOS)
United_States | Arizona | TUCSON INTERNATIONAL AP | TUCSON INTERNATIONAL AP, AZ, USA | 32.13N | 110.96W | 779 | -7.00 (NAZ) | 82-06 | 722740 | -3.1 | -3 | -7.9 | 47.4 | 43.5 | 42.7 | 41 | 42 | 42.4 | 43 | 41.2 | 41.2 | 39.1 | 41 | 40.5 | 41 | 100 | United_StatesArizonaTUCSON INTERNATIONAL AP
United_States | Arizona | WINSLOW MUNICIPAL AP | WINSLOW MUNICIPAL AP, AZ, USA | 35.02N | 110.72W | 1488 | -7.00 (NAZ) | 82-06 | 723740 | -15.4 | -15 | -23.1 | 43.9 | 37.2 | 38.8 | 36.6 | 38 | 37.5333 | 39 | 35.6 | 37 | 34.7 | 36 | 35.7667 | 36 | 101 | United_StatesArizonaWINSLOW MUNICIPAL AP
United_States | Arizona | YUMA INTL AIRPORT | YUMA INTL AIRPORT, AZ, USA | 32.65N | 114.60W | 63 | -7.00 (NAZ) | 82-06 | 722800 | 2.2 | 2 | -0.6 | 50.3 | 45.1 | 45.5 | 45 | 45 | 45.2 | 46 | 42.9 | 43.7 | 43.3 | 43 | 43.3 | 43 | 102 | United_StatesArizonaYUMA INTL AIRPORT
United_States | Arizona | YUMA MCAS | YUMA MCAS, AZ, USA | 32.65N | 114.62W | 65 | -7.00 (NAZ) | 82-06 | 699604 | 2.3 | 2 | -0.9 | 50.8 | 45 | 45.7 | 45 | 45 | 45.2333 | 46 | 42.8 | 43.9 | 43.3 | 43 | 43.3333 | 43 | 103 | United_StatesArizonaYUMA MCAS
United_States | Arkansas | BATESVILLE (AWOS) | BATESVILLE (AWOS), AR, USA | 35.73N | 91.65W | 141 | -6.00 (NAC) | 92-06 | 723448 | -12.8 | -13 | -18 | 42.5 | 35.2 | 37.6 | 38.7 | 37 | 37.1667 | 38 | 33.7 | 36.2 | 36.4 | 35 | 35.4333 | 35 | 104 | United_StatesArkansasBATESVILLE (AWOS)
United_States | Arkansas | BENTONVILLE (AWOS) | BENTONVILLE (AWOS), AR, USA | 36.35N | 94.22W | 395 | -6.00 (NAC) | 92-06 | 723444 | -16.2 | -16 | -23.8 | 41.1 | 33 | 36.3 | 37.1 | 35 | 35.4667 | 36 | 31.9 | 34.1 | 35 | 34 | 33.6667 | 34 | 105 | United_StatesArkansasBENTONVILLE (AWOS)
United_States | Arkansas | EAKER AFB | EAKER AFB, AR, USA | 35.97N | 89.95W | 80 | -6.00 (NAC) | 82-92 | 723408 | -14.9 | -15 | -28 | 43.7 | 37.3 | 38.6 | 37.2 | 38 | 37.7 | 39 | 35.3 | 36.3 | 35.5 | 36 | 35.7 | 36 | 106 | United_StatesArkansasEAKER AFB
United_States | Arkansas | EL DORADO GOODWIN FIELD | EL DORADO GOODWIN FIELD, AR, USA | 33.22N | 92.81W | 87 | -6.00 (NAC) | 91-06 | 723419 | -9.2 | -9 | -14 | 44.9 | 35.1 | 37.9 | 39.8 | 38 | 37.6 | 38 | 33.8 | 36.3 | 37.5 | 36 | 35.8667 | 36 | 107 | United_StatesArkansasEL DORADO GOODWIN FIELD
United_States | Arkansas | FAYETTEVILLE DRAKE FIELD | FAYETTEVILLE DRAKE FIELD, AR, USA | 36.01N | 94.17W | 384 | -6.00 (NAC) | 82-06 | 723445 | -17.2 | -17 | -29.2 | 42.3 | 33.7 | 37.1 | 37 | 36 | 35.9333 | 37 | 32.3 | 35 | 35.5 | 34 | 34.2667 | 34 | 108 | United_StatesArkansasFAYETTEVILLE DRAKE FIELD
United_States | Arkansas | FLIPPIN (AWOS) | FLIPPIN (AWOS), AR, USA | 36.30N | 92.47W | 350 | -6.00 (NAC) | 92-06 | 723447 | -14.9 | -15 | -19.4 | 43.8 | 34.9 | 37.8 | 38.6 | 37 | 37.1 | 38 | 33 | 36.3 | 36.3 | 35 | 35.2 | 35 | 109 | United_StatesArkansasFLIPPIN (AWOS)
United_States | Arkansas | FORT SMITH REGIONAL AP | FORT SMITH REGIONAL AP, AR, USA | 35.33N | 94.37W | 141 | -6.00 (NAC) | 82-06 | 723440 | -12.6 | -13 | -21.9 | 44.5 | 36.1 | 39.2 | 39.2 | 38 | 38.1667 | 39 | 33.9 | 37.1 | 37.5 | 36 | 36.1667 | 36 | 110 | United_StatesArkansasFORT SMITH REGIONAL AP
United_States | Arkansas | HARRISON FAA AP | HARRISON FAA AP, AR, USA | 36.26N | 93.16W | 422 | -6.00 (NAC) | 88-06 | 723446 | -15.4 | -15 | -23.1 | 41.5 | 33.6 | 36.4 | 36.9 | 36 | 35.6333 | 36 | 32.1 | 34.5 | 34.8 | 34 | 33.8 | 34 | 111 | United_StatesArkansasHARRISON FAA AP
United_States | Arkansas | JONESBORO MUNI | JONESBORO MUNI, AR, USA | 35.83N | 90.63W | 82 | -6.00 (NAC) | 82-06 | 723407 | -14.6 | -15 | -25.9 | 41.8 | 36.2 | 37.3 | 37.2 | 37 | 36.9 | 37 | 34.3 | 35.7 | 35.5 | 35 | 35.1667 | 35 | 112 | United_StatesArkansasJONESBORO MUNI
United_States | Arkansas | LITTLE ROCK ADAMS FIELD | LITTLE ROCK ADAMS FIELD, AR, USA | 34.75N | 92.23W | 78 | -6.00 (NAC) | 82-06 | 723403 | -11.3 | -11 | -20.6 | 44 | 36.1 | 38.6 | 38.9 | 38 | 37.8667 | 39 | 34.1 | 36.4 | 36.9 | 36 | 35.8 | 36 | 113 | United_StatesArkansasLITTLE ROCK ADAMS FIELD
United_States | Arkansas | LITTLE ROCK AFB | LITTLE ROCK AFB, AR, USA | 34.92N | 92.15W | 103 | -6.00 (NAC) | 82-06 | 723405 | -13.4 | -13 | -22.1 | 44 | 37.2 | 39.9 | 39.8 | 39 | 38.9667 | 40 | 34.7 | 37.4 | 37.4 | 37 | 36.5 | 37 | 114 | United_StatesArkansasLITTLE ROCK AFB
United_States | Arkansas | LITTLE ROCK/ADAMS F | LITTLE ROCK/ADAMS F, AR, USA | 34.83N | 92.25W | 351 | -6.00 (NAC) | 82-06 | 723400 | -11.7 | -12 | -21.7 | 42.1 | 34.1 | 37 | 37.3 | 36 | 36.1333 | 37 | 32.7 | 35.1 | 35.3 | 34 | 34.3667 | 34 | 115 | United_StatesArkansasLITTLE ROCK/ADAMS F
United_States | Arkansas | PINE BLUFF FAA AP | PINE BLUFF FAA AP, AR, USA | 34.18N | 91.94W | 65 | -6.00 (NAC) | 88-06 | 723417 | -8.7 | -9 | -16.4 | 41.6 | 35.9 | 37.8 | 37.5 | 37 | 37.0667 | 38 | 34.4 | 36.3 | 36.1 | 36 | 35.6 | 36 | 116 | United_StatesArkansasPINE BLUFF FAA AP
United_States | Arkansas | ROGERS (AWOS) | ROGERS (AWOS), AR, USA | 36.37N | 94.10W | 415 | -6.00 (NAC) | 92-06 | 723449 | -15.3 | -15 | -20.1 | 40.9 | 32.8 | 36.3 | 37.1 | 35 | 35.4 | 36 | 31.2 | 33.9 | 34.8 | 33 | 33.3 | 33 | 117 | United_StatesArkansasROGERS (AWOS)
United_States | Arkansas | SILOAM SPRING(AWOS) | SILOAM SPRING(AWOS), AR, USA | 36.18N | 94.48W | 364 | -6.00 (NAC) | 92-06 | 723443 | -15.4 | -15 | -23.9 | 41.8 | 33.5 | 37 | 37.6 | 36 | 36.0333 | 37 | 31.5 | 34.9 | 36 | 34 | 34.1333 | 34 | 118 | United_StatesArkansasSILOAM SPRING(AWOS)
United_States | Arkansas | STUTTGART (AWOS) | STUTTGART (AWOS), AR, USA | 34.60N | 91.57W | 68 | -6.00 (NAC) | 92-06 | 723416 | -8.7 | -9 | -13.5 | 41.2 | 36.1 | 37.2 | 37.4 | 37 | 36.9 | 37 | 33.9 | 35.8 | 36 | 35 | 35.2333 | 35 | 119 | United_StatesArkansasSTUTTGART (AWOS)
United_States | Arkansas | TEXARKANA WEBB FIELD | TEXARKANA WEBB FIELD, AR, USA | 33.45N | 94.01W | 122 | -6.00 (NAC) | 82-06 | 723418 | -9.2 | -9 | -17.5 | 43.2 | 36 | 38.6 | 38.6 | 38 | 37.7333 | 39 | 34.1 | 36.7 | 37.2 | 36 | 36 | 36 | 120 | United_StatesArkansasTEXARKANA WEBB FIELD
United_States | Arkansas | WALNUT RIDGE (AWOS) | WALNUT RIDGE (AWOS), AR, USA | 36.13N | 90.92W | 83 | -6.00 (NAC) | 92-06 | 723406 | -13.2 | -13 | -18.9 | 42.6 | 35.3 | 37.2 | 36.3 | 36 | 36.2667 | 37 | 33.8 | 35.2 | 34.1 | 34 | 34.3667 | 34 | 121 | United_StatesArkansasWALNUT RIDGE (AWOS)
United_States | California | ALAMEDA NAS | ALAMEDA NAS, CA, USA | 37.73N | 122.32W | 4 | -8.00 (NAP) | 82-96 | 745060 | 2.8 | 3 | -2.7 | 40.4 | 31.1 | 30.1 | 29.1 | 30 | 30.1 | 30 | 26.2 | 26 | 25.7 | 26 | 25.9667 | 26 | 122 | United_StatesCaliforniaALAMEDA NAS
United_States | California | ARCATA AIRPORT | ARCATA AIRPORT, CA, USA | 40.98N | 124.11W | 64 | -8.00 (NAP) | 82-06 | 725945 | -2.5 | -3 | -6.8 | 33.9 | 21.4 | 21.2 | 21.5 | 21 | 21.3667 | 21 | 18.3 | 19 | 19.8 | 19 | 19.0333 | 19 | 123 | United_StatesCaliforniaARCATA AIRPORT
United_States | California | BAKERSFIELD MEADOWS FIELD | BAKERSFIELD MEADOWS FIELD, CA, USA | 35.43N | 119.06W | 150 | -8.00 (NAP) | 82-06 | 723840 | -2.2 | -2 | -7.9 | 44.5 | 39.7 | 41.5 | 41 | 41 | 40.7333 | 42 | 37.9 | 39.6 | 39.2 | 39 | 38.9 | 39 | 124 | United_StatesCaliforniaBAKERSFIELD MEADOWS FIELD
United_States | California | BEALE AFB/MARYSVILE | BEALE AFB/MARYSVILE, CA, USA | 39.13N | 121.43W | 38 | -8.00 (NAP) | 82-02 | 724837 | -2.6 | -3 | -7.4 | 44.9 | 39 | 40.7 | 40 | 40 | 39.9 | 41 | 37 | 38 | 37.8 | 38 | 37.6 | 38 | 125 | United_StatesCaliforniaBEALE AFB/MARYSVILE
United_States | California | BISHOP AIRPORT | BISHOP AIRPORT, CA, USA | 37.37N | 118.36W | 1263 | -8.00 (NAP) | 82-06 | 724800 | -13.4 | -13 | -22.4 | 43.1 | 38.5 | 40.3 | 39.2 | 39 | 39.3333 | 40 | 36.8 | 38.8 | 37.7 | 38 | 37.7667 | 38 | 126 | United_StatesCaliforniaBISHOP AIRPORT
United_States | California | BLUE CANYON AP | BLUE CANYON AP, CA, USA | 39.29N | 120.71W | 1610 | -8.00 (NAP) | 82-06 | 725845 | -8.4 | -8 | -14.9 | 35.7 | 28.6 | 30.8 | 30.1 | 30 | 29.8333 | 31 | 26.3 | 28.5 | 28.4 | 28 | 27.7333 | 28 | 127 | United_StatesCaliforniaBLUE CANYON AP
United_States | California | BLYTHE RIVERSIDE CO ARPT | BLYTHE RIVERSIDE CO ARPT, CA, USA | 33.62N | 114.72W | 120 | -8.00 (NAP) | 88-06 | 747188 | -0.9 | -1 | -5.3 | 51.8 | 45.9 | 47.2 | 46 | 46 | 46.3667 | 47 | 43.7 | 45.1 | 44.2 | 44 | 44.3333 | 44 | 128 | United_StatesCaliforniaBLYTHE RIVERSIDE CO ARPT
United_States | California | BURBANK-GLENDALE-PASSADENA AP | BURBANK-GLENDALE-PASSADENA AP, CA, USA | 34.20N | 118.36W | 223 | -8.00 (NAP) | 82-06 | 722880 | 1 | 1 | -4.3 | 46 | 36.8 | 38.2 | 38.7 | 38 | 37.9 | 38 | 33 | 35 | 36.1 | 35 | 34.7 | 35 | 129 | United_StatesCaliforniaBURBANK-GLENDALE-PASSADENA AP
United_States | California | CAMARILLO (AWOS) | CAMARILLO (AWOS), CA, USA | 34.22N | 119.08W | 23 | -8.00 (NAP) | 92-06 | 723926 | 1.1 | 1 | -1.6 | 40.8 | 27.4 | 28 | 30 | 28 | 28.4667 | 28 | 25.1 | 27.1 | 27.6 | 27 | 26.6 | 27 | 130 | United_StatesCaliforniaCAMARILLO (AWOS)
United_States | California | CAMP PENDLETON MCAS | CAMP PENDLETON MCAS, CA, USA | 33.30N | 117.35W | 24 | -8.00 (NAP) | 85-06 | 722926 | -2.4 | -2 | -7.1 | 44 | 32.3 | 32.3 | 34 | 33 | 32.8667 | 32 | 27.6 | 29.4 | 31 | 29 | 29.3333 | 29 | 131 | United_StatesCaliforniaCAMP PENDLETON MCAS
United_States | California | CARLSBAD/PALOMAR | CARLSBAD/PALOMAR, CA, USA | 33.13N | 117.28W | 100 | -8.00 (NAP) | 98-06 | 722927 | 3.8 | 4 | 1.1 | 40.1 | 26.1 | 27.9 | 28 | 27 | 27.3333 | 28 | 22.9 | 26.3 | 26.3 | 25 | 25.1667 | 25 | 132 | United_StatesCaliforniaCARLSBAD/PALOMAR
United_States | California | CASTLE AFB/MERCED | CASTLE AFB/MERCED, CA, USA | 37.38N | 120.57W | 60 | -8.00 (NAP) | 82-93 | 724810 | -2.8 | -3 | -6.8 | 44 | 37.9 | 40.1 | 39.4 | 39 | 39.1333 | 40 | 36 | 37.6 | 37.1 | 37 | 36.9 | 37 | 133 | United_StatesCaliforniaCASTLE AFB/MERCED
United_States | California | CRESCENT CITY FAA AI | CRESCENT CITY FAA AI, CA, USA | 41.78N | 124.24W | 17 | -8.00 (NAP) | 92-06 | 725946 | -1.2 | -1 | -10.7 | 31.7 | 18 | 19.2 | 21 | 19 | 19.4 | 19 | 17.4 | 18 | 19 | 18 | 18.1333 | 18 | 134 | United_StatesCaliforniaCRESCENT CITY FAA AI
United_States | California | DAGGETT BARSTOW-DAGGETT AP | DAGGETT BARSTOW-DAGGETT AP, CA, USA | 34.85N | 116.79W | 588 | -8.00 (NAP) | 88-06 | 723815 | -5 | -5 | -11.5 | 48.9 | 42.7 | 44.9 | 43.7 | 44 | 43.7667 | 45 | 41.1 | 43 | 42.3 | 42 | 42.1333 | 42 | 135 | United_StatesCaliforniaDAGGETT BARSTOW-DAGGETT AP
United_States | California | EDWARDS AFB | EDWARDS AFB, CA, USA | 34.90N | 117.88W | 706 | -8.00 (NAP) | 91-06 | 723810 | -9.5 | -10 | -16.8 | 46.2 | 41.3 | 42.9 | 42.5 | 42 | 42.2333 | 43 | 38.8 | 40.9 | 41.1 | 40 | 40.2667 | 40 | 136 | United_StatesCaliforniaEDWARDS AFB
United_States | California | EL TORO MCAS | EL TORO MCAS, CA, USA | 33.68N | 117.73W | 117 | -8.00 (NAP) | 82-98 | 690140 | 2.6 | 3 | -2 | 44.6 | 32.9 | 34 | 35.3 | 34 | 34.0667 | 34 | 29.1 | 30.7 | 32.6 | 31 | 30.8 | 31 | 137 | United_StatesCaliforniaEL TORO MCAS
United_States | California | EUREKA | EUREKA, CA, USA | 40.80N | 124.17W | 18 | -8.00 (NAP) | 82-06 | 725940 | -0.9 | -1 | -3.1 | 34.2 | 18.7 | 19.4 | 20.8 | 20 | 19.6333 | 19 | 17.4 | 18.2 | 19.2 | 18 | 18.2667 | 18 | 138 | United_StatesCaliforniaEUREKA
United_States | California | FRESNO YOSEMITE INTL AP | FRESNO YOSEMITE INTL AP, CA, USA | 36.78N | 119.72W | 100 | -8.00 (NAP) | 82-06 | 723890 | -1.9 | -2 | -7.6 | 44.8 | 40.2 | 41.9 | 40.9 | 41 | 41 | 42 | 38.3 | 40.1 | 39.2 | 39 | 39.2 | 39 | 139 | United_StatesCaliforniaFRESNO YOSEMITE INTL AP
United_States | California | FULLERTON MUNICIPAL | FULLERTON MUNICIPAL, CA, USA | 33.87N | 117.98W | 29 | -8.00 (NAP) | 98-06 | 722976 | 2.2 | 2 | -0.4 | 43.6 | 32.8 | 34 | 35 | 34 | 33.9333 | 34 | 29 | 32.3 | 32.7 | 31 | 31.3333 | 31 | 140 | United_StatesCaliforniaFULLERTON MUNICIPAL
United_States | California | GEORGE AFB | GEORGE AFB, CA, USA | 34.58N | 117.38W | 876 | -8.00 (NAP) | 82-05 | 723825 | -5.5 | -6 | -11.1 | 44.9 | 37.9 | 41.5 | 38.8 | 39 | 39.4 | 42 | 36.4 | 39 | 37.5 | 38 | 37.6333 | 38 | 141 | United_StatesCaliforniaGEORGE AFB
United_States | California | HAYWARD AIR TERM | HAYWARD AIR TERM, CA, USA | 37.66N | 122.12W | 14 | -8.00 (NAP) | 98-06 | 724935 | 1 | 1 | -1.6 | 42.8 | 33.6 | 33.1 | 32 | 33 | 32.9 | 33 | 28.1 | 28.5 | 27.2 | 28 | 27.9333 | 28 | 142 | United_StatesCaliforniaHAYWARD AIR TERM
United_States | California | IMPERIAL | IMPERIAL, CA, USA | 32.83N | 115.58W | -17 | -8.00 (NAP) | 88-06 | 747185 | -0.9 | -1 | -5.8 | 51.4 | 44.6 | 46.3 | 45.6 | 46 | 45.5 | 46 | 42.8 | 44 | 43.7 | 44 | 43.5 | 44 | 143 | United_StatesCaliforniaIMPERIAL
United_States | California | JACK NORTHROP FLD H | JACK NORTHROP FLD H, CA, USA | 33.92N | 118.33W | 21 | -8.00 (NAP) | 98-06 | 722956 | 3.9 | 4 | -1.9 | 40.6 | 27.7 | 30.8 | 28.9 | 29 | 29.1333 | 31 | 24.1 | 27.7 | 27.3 | 26 | 26.3667 | 26 | 144 | United_StatesCaliforniaJACK NORTHROP FLD H
United_States | California | LANCASTER GEN WM FOX FIELD | LANCASTER GEN WM FOX FIELD, CA, USA | 34.74N | 118.22W | 713 | -8.00 (NAP) | 82-06 | 723816 | -9 | -9 | -14.9 | 45 | 38.9 | 41.7 | 40.9 | 41 | 40.5 | 42 | 37 | 39.4 | 38.9 | 38 | 38.4333 | 38 | 145 | United_StatesCaliforniaLANCASTER GEN WM FOX FIELD
United_States | California | LEMOORE REEVES NAS | LEMOORE REEVES NAS, CA, USA | 36.33N | 119.95W | 71 | -8.00 (NAP) | 82-06 | 747020 | -3.4 | -3 | -9.8 | 47.1 | 40.6 | 41.2 | 40.9 | 41 | 40.9 | 41 | 38.5 | 39.4 | 38.9 | 39 | 38.9333 | 39 | 146 | United_StatesCaliforniaLEMOORE REEVES NAS
United_States | California | LIVERMORE MUNICIPAL | LIVERMORE MUNICIPAL, CA, USA | 37.69N | 121.82W | 121 | -8.00 (NAP) | 98-06 | 724927 | -2.8 | -3 | -4.5 | 45.6 | 37.9 | 41.3 | 38.5 | 39 | 39.2333 | 41 | 34.6 | 37.2 | 35.9 | 36 | 35.9 | 36 | 147 | United_StatesCaliforniaLIVERMORE MUNICIPAL
United_States | California | LOMPOC (AWOS) | LOMPOC (AWOS), CA, USA | 34.67N | 120.47W | 27 | -8.00 (NAP) | 92-06 | 722895 | -2.2 | -2 | -4.8 | 49.8 | 27.4 | 26 | 26.3 | 27 | 26.5667 | 26 | 23 | 23 | 23.7 | 23 | 23.2333 | 23 | 148 | United_StatesCaliforniaLOMPOC (AWOS)
United_States | California | LONG BEACH DAUGHERTY FLD | LONG BEACH DAUGHERTY FLD, CA, USA | 33.83N | 118.16W | 12 | -8.00 (NAP) | 82-06 | 722970 | 2.3 | 2 | -1.5 | 44.7 | 32.2 | 33.1 | 35 | 33 | 33.4333 | 33 | 28 | 30.4 | 31.7 | 30 | 30.0333 | 30 | 149 | United_StatesCaliforniaLONG BEACH DAUGHERTY FLD
United_States | California | LOS ANGELES INTL ARPT | LOS ANGELES INTL ARPT, CA, USA | 33.94N | 118.41W | 99 | -8.00 (NAP) | 82-06 | 722950 | 4.4 | 4 | 0.7 | 40.9 | 26.4 | 28.1 | 29.5 | 28 | 28 | 28 | 23.8 | 26 | 26.9 | 26 | 25.5667 | 26 | 150 | United_StatesCaliforniaLOS ANGELES INTL ARPT
United_States | California | MARCH AFB/RIVERSIDE | MARCH AFB/RIVERSIDE, CA, USA | 33.88N | 117.27W | 462 | -8.00 (NAP) | 82-06 | 722860 | -1.8 | -2 | -6.2 | 45.6 | 38.1 | 39.9 | 40.2 | 39 | 39.4 | 40 | 35.6 | 37.4 | 37.9 | 37 | 36.9667 | 37 | 151 | United_StatesCaliforniaMARCH AFB/RIVERSIDE
United_States | California | MCCLELLAN AFB | MCCLELLAN AFB, CA, USA | 38.67N | 121.40W | 25 | -8.00 (NAP) | 82-00 | 724836 | -2.7 | -3 | -9.7 | 44.8 | 39.4 | 41 | 41.1 | 41 | 40.5 | 41 | 37.3 | 38.7 | 38.7 | 38 | 38.2333 | 38 | 152 | United_StatesCaliforniaMCCLELLAN AFB
United_States | California | MODESTO CITY-COUNTY AP | MODESTO CITY-COUNTY AP, CA, USA | 37.63N | 120.95W | 30 | -8.00 (NAP) | 86-06 | 724926 | -2.3 | -2 | -4.6 | 45.8 | 39.4 | 42 | 39 | 40 | 40.1333 | 42 | 36.9 | 39 | 37.3 | 38 | 37.7333 | 38 | 153 | United_StatesCaliforniaMODESTO CITY-COUNTY AP
United_States | California | MONTAGUE SISKIYOU COUNTY AP | MONTAGUE SISKIYOU COUNTY AP, CA, USA | 41.78N | 122.47W | 805 | -8.00 (NAP) | 90-06 | 725955 | N/A | N/A | N/A | N/A | 35.1 | 37.9 | 37.3 | 37 | 36.7667 | 38 | 32 | 36.3 | 35.1 | 34 | 34.4667 | 34 | 154 | United_StatesCaliforniaMONTAGUE SISKIYOU COUNTY AP
United_States | California | MONTEREY PENINSULA | MONTEREY PENINSULA, CA, USA | 36.58N | 121.85W | 50 | -8.00 (NAP) | 88-06 | 724915 | 1 | 1 | -0.4 | 39 | 27.3 | 23.8 | 24.7 | 25 | 25.2667 | 24 | 22.3 | 22 | 22.2 | 22 | 22.1667 | 22 | 155 | United_StatesCaliforniaMONTEREY PENINSULA
United_States | California | MOUNT SHASTA | MOUNT SHASTA, CA, USA | 41.33N | 122.33W | 1078 | -8.00 (NAP) | 82-06 | 725957 | -12 | -12 | -21.4 | 38.9 | 31.8 | 34.9 | 34.6 | 34 | 33.7667 | 35 | 29.1 | 32.7 | 32.4 | 31 | 31.4 | 31 | 156 | United_StatesCaliforniaMOUNT SHASTA
United_States | California | MOUNTAIN VIEW MOFFETT FLD NAS | MOUNTAIN VIEW MOFFETT FLD NAS, CA, USA | 37.42N | 122.05W | 10 | -8.00 (NAP) | 82-06 | 745090 | -0.2 | 0 | -5.3 | 40.4 | 33.6 | 33.1 | 32.4 | 33 | 33.0333 | 33 | 28.6 | 29 | 28.5 | 29 | 28.7 | 29 | 157 | United_StatesCaliforniaMOUNTAIN VIEW MOFFETT FLD NAS
United_States | California | NAPA CO. AIRPORT | NAPA CO. AIRPORT, CA, USA | 38.21N | 122.28W | 17 | -8.00 (NAP) | 98-06 | 724955 | -4.2 | -4 | -6.7 | 44 | 35.2 | 35.2 | 34.7 | 35 | 35.0333 | 35 | 31 | 30.7 | 30.3 | 31 | 30.6667 | 31 | 158 | United_StatesCaliforniaNAPA CO. AIRPORT
United_States | California | NORTON AFB/SAN BERN | NORTON AFB/SAN BERN, CA, USA | 34.10N | 117.23W | 353 | -8.00 (NAP) | 82-93 | 722866 | -1.6 | -2 | -5.6 | 46.2 | 39.5 | 41 | 41 | 41 | 40.5 | 41 | 37 | 38.7 | 38.7 | 38 | 38.1333 | 38 | 159 | United_StatesCaliforniaNORTON AFB/SAN BERN
United_States | California | OAKLAND METROPOLITAN ARPT | OAKLAND METROPOLITAN ARPT, CA, USA | 37.76N | 122.22W | 27 | -8.00 (NAP) | 82-06 | 724930 | 0.8 | 1 | -3.8 | 39 | 29.2 | 29.4 | 28.9 | 29 | 29.1667 | 29 | 24.6 | 25.4 | 25 | 25 | 25 | 25 | 160 | United_StatesCaliforniaOAKLAND METROPOLITAN ARPT
United_States | California | ONTARIO | ONTARIO, CA, USA | 34.07N | 117.65W | 304 | -8.00 (NAP) | 82-01 | 722865 | -0.8 | -1 | -5.9 | 45.9 | 38.6 | 39.3 | 40.2 | 39 | 39.3667 | 39 | 35.1 | 36.9 | 37.8 | 37 | 36.6 | 37 | 161 | United_StatesCaliforniaONTARIO
United_States | California | PALM SPRINGS INTL | PALM SPRINGS INTL, CA, USA | 33.83N | 116.50W | 145 | -8.00 (NAP) | 98-06 | 722868 | 2.6 | 3 | -0.1 | 51.4 | 44 | 47.4 | 46.1 | 46 | 45.8333 | 47 | 42.7 | 44.9 | 43.7 | 44 | 43.7667 | 44 | 162 | United_StatesCaliforniaPALM SPRINGS INTL
United_States | California | PALM SPRINGS THERMAL AP | PALM SPRINGS THERMAL AP, CA, USA | 33.63N | 116.16W | -36 | -8.00 (NAP) | 82-06 | 747187 | -4.6 | -5 | -10 | 53.5 | 45.6 | 47.3 | 46 | 46 | 46.3 | 47 | 42.9 | 44.1 | 43.7 | 44 | 43.5667 | 44 | 163 | United_StatesCaliforniaPALM SPRINGS THERMAL AP
United_States | California | PASO ROBLES MUNICIPAL ARPT | PASO ROBLES MUNICIPAL ARPT, CA, USA | 35.67N | 120.63W | 249 | -8.00 (NAP) | 82-06 | 723965 | -5.6 | -6 | -11.5 | 46.8 | 39.6 | 41.6 | 41.5 | 41 | 40.9 | 42 | 36.5 | 38.6 | 38.7 | 38 | 37.9333 | 38 | 164 | United_StatesCaliforniaPASO ROBLES MUNICIPAL ARPT
United_States | California | POINT ARENA | POINT ARENA, CA, USA | 38.95N | 123.73W | 19 | -8.00 (NAP) | 85-06 | 994120 | 1.5 | 2 | -3 | 28.2 | 15.7 | 16.5 | 17.5 | 17 | 16.5667 | 17 | 14.8 | 15.3 | 16.2 | 15 | 15.4333 | 15 | 165 | United_StatesCaliforniaPOINT ARENA
United_States | California | POINT ARGUELLO | POINT ARGUELLO, CA, USA | 34.57N | 120.63W | 34 | -8.00 (NAP) | 85-06 | 994210 | 5.4 | 5 | 0.3 | 28.3 | 18 | 20.8 | 18.8 | 19 | 19.2 | 21 | 16.5 | 18.5 | 17.5 | 18 | 17.5 | 18 | 166 | United_StatesCaliforniaPOINT ARGUELLO
United_States | California | POINT MUGU NF | POINT MUGU NF, CA, USA | 34.12N | 119.12W | 4 | -8.00 (NAP) | 82-06 | 723910 | 2 | 2 | -2.2 | 40.7 | 24.5 | 26.4 | 27.3 | 26 | 26.0667 | 26 | 22.8 | 24.5 | 25.4 | 24 | 24.2333 | 24 | 167 | United_StatesCaliforniaPOINT MUGU NF
United_States | California | PORTERVILLE (AWOS) | PORTERVILLE (AWOS), CA, USA | 36.03N | 119.07W | 135 | -8.00 (NAP) | 92-06 | 723895 | -2.3 | -2 | -5.1 | 43.9 | 39.1 | 40.9 | 39.1 | 40 | 39.7 | 41 | 37.5 | 38 | 37.7 | 38 | 37.7333 | 38 | 168 | United_StatesCaliforniaPORTERVILLE (AWOS)
United_States | California | PT.PIEDRAS BLANCA | PT.PIEDRAS BLANCA, CA, USA | 35.67N | 121.29W | 21 | -8.00 (NAP) | 82-05 | 723900 | 3.4 | 3 | -2.1 | 35.7 | 23.8 | 21.2 | 22.8 | 23 | 22.6 | 21 | 20 | 18.9 | 21.1 | 20 | 20 | 20 | 169 | United_StatesCaliforniaPT.PIEDRAS BLANCA
United_States | California | RED BLUFF MUNICIPAL ARPT | RED BLUFF MUNICIPAL ARPT, CA, USA | 40.15N | 122.25W | 108 | -8.00 (NAP) | 82-06 | 725910 | -3.7 | -4 | -8.3 | 47.7 | 41.2 | 43.6 | 42.3 | 42 | 42.3667 | 44 | 38.2 | 40.9 | 39.8 | 40 | 39.6333 | 40 | 170 | United_StatesCaliforniaRED BLUFF MUNICIPAL ARPT
United_States | California | REDDING MUNICIPAL ARPT | REDDING MUNICIPAL ARPT, CA, USA | 40.52N | 122.31W | 153 | -8.00 (NAP) | 86-06 | 725920 | -4.4 | -4 | -8.6 | 49.1 | 41.3 | 44 | 42.8 | 43 | 42.7 | 44 | 38.4 | 41.3 | 40.5 | 40 | 40.0667 | 40 | 171 | United_StatesCaliforniaREDDING MUNICIPAL ARPT
United_States | California | RIVERSIDE MUNI | RIVERSIDE MUNI, CA, USA | 33.95N | 117.43W | 256 | -8.00 (NAP) | 98-06 | 722869 | -0.9 | -1 | -4.1 | 46 | 37.2 | 38.7 | 39.1 | 38 | 38.3333 | 39 | 34.1 | 37.2 | 37.5 | 36 | 36.2667 | 36 | 172 | United_StatesCaliforniaRIVERSIDE MUNI
United_States | California | SACRAMENTO EXECUTIVE ARPT | SACRAMENTO EXECUTIVE ARPT, CA, USA | 38.51N | 121.49W | 8 | -8.00 (NAP) | 82-06 | 724830 | -2.6 | -3 | -7.1 | 45.3 | 38.6 | 40.6 | 40.2 | 40 | 39.8 | 41 | 36.2 | 37.9 | 37.3 | 37 | 37.1333 | 37 | 173 | United_StatesCaliforniaSACRAMENTO EXECUTIVE ARPT
United_States | California | SACRAMENTO MATHER AIRPORT | SACRAMENTO MATHER AIRPORT, CA, USA | 38.55N | 121.29W | 29 | -8.00 (NAP) | 82-06 | 724833 | -3.2 | -3 | -9.3 | 46.5 | 38.8 | 42.2 | 40.1 | 40 | 40.3667 | 42 | 36.4 | 38.9 | 37.7 | 38 | 37.6667 | 38 | 174 | United_StatesCaliforniaSACRAMENTO MATHER AIRPORT
United_States | California | SACRAMENTO METROPOLITAN AP | SACRAMENTO METROPOLITAN AP, CA, USA | 38.70N | 121.59W | 10 | -8.00 (NAP) | 82-06 | 724839 | -2.7 | -3 | -9.1 | 44.8 | 38.9 | 41.1 | 40.5 | 40 | 40.1667 | 41 | 36.7 | 38 | 37.7 | 37 | 37.4667 | 37 | 175 | United_StatesCaliforniaSACRAMENTO METROPOLITAN AP
United_States | California | SALINAS MUNICIPAL AP | SALINAS MUNICIPAL AP, CA, USA | 36.66N | 121.61W | 24 | -8.00 (NAP) | 82-06 | 724917 | -1.2 | -1 | -4.7 | 41 | 29.1 | 28.5 | 27.9 | 29 | 28.5 | 29 | 24.4 | 24.6 | 24.5 | 25 | 24.5 | 25 | 176 | United_StatesCaliforniaSALINAS MUNICIPAL AP
United_States | California | SAN DIEGO LINDBERGH FIELD | SAN DIEGO LINDBERGH FIELD, CA, USA | 32.74N | 117.17W | 9 | -8.00 (NAP) | 82-06 | 722900 | 5 | 5 | 1.5 | 41.4 | 27.3 | 29.2 | 29.7 | 29 | 28.7333 | 29 | 24.1 | 27 | 27.7 | 26 | 26.2667 | 26 | 177 | United_StatesCaliforniaSAN DIEGO LINDBERGH FIELD
United_States | California | SAN DIEGO MIRAMAR NAS | SAN DIEGO MIRAMAR NAS, CA, USA | 32.87N | 117.15W | 146 | -8.00 (NAP) | 89-04 | 722930 | 1.2 | 1 | -6.4 | 40.7 | 32 | 32 | 33.9 | 33 | 32.6333 | 32 | 28.3 | 29.2 | 31.3 | 30 | 29.6 | 30 | 178 | United_StatesCaliforniaSAN DIEGO MIRAMAR NAS
United_States | California | SAN DIEGO NORTH ISLAND NAS | SAN DIEGO NORTH ISLAND NAS, CA, USA | 32.70N | 117.20W | 8 | -8.00 (NAP) | 82-06 | 722906 | 4.4 | 4 | 1.6 | 42 | 26.3 | 27.7 | 28.8 | 28 | 27.6 | 28 | 23.2 | 25.9 | 26.6 | 25 | 25.2333 | 25 | 179 | United_StatesCaliforniaSAN DIEGO NORTH ISLAND NAS
United_States | California | SAN DIEGO/BROWN FLD | SAN DIEGO/BROWN FLD, CA, USA | 32.57N | 116.98W | 159 | -8.00 (NAP) | 97-06 | 722904 | 1.6 | 2 | -1.2 | 44.1 | 29.1 | 31.1 | 32.4 | 31 | 30.8667 | 31 | 26.1 | 28.6 | 29 | 28 | 27.9 | 28 | 180 | United_StatesCaliforniaSAN DIEGO/BROWN FLD
United_States | California | SAN DIEGO/MONTGOMER | SAN DIEGO/MONTGOMER, CA, USA | 32.82N | 117.13W | 129 | -8.00 (NAP) | 82-06 | 722903 | 2.8 | 3 | 0.5 | 41.7 | 31 | 32.3 | 32.7 | 32 | 32 | 32 | 26.3 | 28.9 | 29.3 | 28 | 28.1667 | 28 | 181 | United_StatesCaliforniaSAN DIEGO/MONTGOMER
United_States | California | SAN FRANCISCO INTL AP | SAN FRANCISCO INTL AP, CA, USA | 37.62N | 122.40W | 6 | -8.00 (NAP) | 82-06 | 724940 | 1.8 | 2 | -1.9 | 40.5 | 31.5 | 29.4 | 29.2 | 30 | 30.0333 | 29 | 25.6 | 25.3 | 25 | 25 | 25.3 | 25 | 182 | United_StatesCaliforniaSAN FRANCISCO INTL AP
United_States | California | SAN JOSE INTL AP | SAN JOSE INTL AP, CA, USA | 37.36N | 121.93W | 15 | -8.00 (NAP) | 82-06 | 724945 | 0 | 0 | -5 | 42.1 | 35.2 | 36 | 34.8 | 35 | 35.3333 | 36 | 31.7 | 32.3 | 32 | 32 | 32 | 32 | 183 | United_StatesCaliforniaSAN JOSE INTL AP
United_States | California | SAN LUIS CO RGNL | SAN LUIS CO RGNL, CA, USA | 35.23N | 120.63W | 66 | -8.00 (NAP) | 85-06 | 722897 | -1.5 | -2 | -5.8 | 43.4 | 31.6 | 32 | 31.5 | 32 | 31.7 | 32 | 27.6 | 28.2 | 28.2 | 28 | 28 | 28 | 184 | United_StatesCaliforniaSAN LUIS CO RGNL
United_States | California | SANDBERG | SANDBERG, CA, USA | 34.74N | 118.72W | 1379 | -8.00 (NAP) | 82-06 | 723830 | -5.2 | -5 | -12.1 | 39.1 | 33.6 | 35.2 | 35 | 35 | 34.6 | 35 | 30.8 | 33.1 | 33 | 32 | 32.3 | 32 | 185 | United_StatesCaliforniaSANDBERG
United_States | California | SANTA BARBARA MUNICIPAL AP | SANTA BARBARA MUNICIPAL AP, CA, USA | 34.43N | 119.84W | 6 | -8.00 (NAP) | 82-06 | 723925 | -1 | -1 | -5.7 | 43.4 | 27.6 | 28.8 | 28.9 | 28 | 28.4333 | 29 | 24.3 | 25.8 | 26.4 | 26 | 25.5 | 26 | 186 | United_StatesCaliforniaSANTA BARBARA MUNICIPAL AP
United_States | California | SANTA MARIA PUBLIC ARPT | SANTA MARIA PUBLIC ARPT, CA, USA | 34.92N | 120.47W | 73 | -8.00 (NAP) | 82-06 | 723940 | -2.6 | -3 | -6.9 | 41.9 | 28.4 | 29.2 | 28.4 | 29 | 28.6667 | 29 | 24.1 | 25.9 | 25.4 | 25 | 25.1333 | 25 | 187 | United_StatesCaliforniaSANTA MARIA PUBLIC ARPT
United_States | California | SANTA ROSA (AWOS) | SANTA ROSA (AWOS), CA, USA | 38.51N | 122.81W | 45 | -8.00 (NAP) | 98-06 | 724957 | -3 | -3 | -4.3 | 44 | 37.5 | 37.8 | 36.3 | 37 | 37.2 | 38 | 33.3 | 33.8 | 33.5 | 34 | 33.5333 | 34 | 188 | United_StatesCaliforniaSANTA ROSA (AWOS)
United_States | California | STOCKTON METROPOLITAN ARPT | STOCKTON METROPOLITAN ARPT, CA, USA | 37.89N | 121.24W | 8 | -8.00 (NAP) | 82-06 | 724920 | -3 | -3 | -7.8 | 45.4 | 39.2 | 41.1 | 39.9 | 40 | 40.0667 | 41 | 36.7 | 38.4 | 37.7 | 38 | 37.6 | 38 | 189 | United_StatesCaliforniaSTOCKTON METROPOLITAN ARPT
United_States | California | TRAVIS AFB/FAIRFLD | TRAVIS AFB/FAIRFLD, CA, USA | 38.27N | 121.93W | 18 | -8.00 (NAP) | 82-06 | 745160 | -3 | -3 | -9.2 | 46 | 38.7 | 40 | 38.9 | 39 | 39.2 | 40 | 35.5 | 36.9 | 36 | 36 | 36.1333 | 36 | 190 | United_StatesCaliforniaTRAVIS AFB/FAIRFLD
United_States | California | TRUCKEE-TAHOE | TRUCKEE-TAHOE, CA, USA | 39.32N | 120.13W | 1798 | -8.00 (NAP) | 94-06 | 725846 | N/A | N/A | N/A | N/A | 30.9 | 33.6 | 32.4 | 32 | 32.3 | 34 | 27.9 | 32.3 | 31 | 30 | 30.4 | 30 | 191 | United_StatesCaliforniaTRUCKEE-TAHOE
United_States | California | TUSTIN MCAF | TUSTIN MCAF, CA, USA | 33.70N | 117.83W | 17 | -8.00 (NAP) | 82-97 | 690160 | 1.6 | 2 | -1.8 | 46.2 | 33.8 | 34 | 35.6 | 34 | 34.4667 | 34 | 29.5 | 31.4 | 33 | 31 | 31.3 | 31 | 192 | United_StatesCaliforniaTUSTIN MCAF
United_States | California | UKIAH MUNICIPAL AP | UKIAH MUNICIPAL AP, CA, USA | 39.13N | 123.20W | 191 | -8.00 (NAP) | 92-06 | 725905 | -3.3 | -3 | -7.7 | 47 | 37.7 | 41.2 | 41.2 | 40 | 40.0333 | 41 | 35 | 37.6 | 37.8 | 37 | 36.8 | 37 | 193 | United_StatesCaliforniaUKIAH MUNICIPAL AP
United_States | California | VISALIA MUNI (AWOS) | VISALIA MUNI (AWOS), CA, USA | 36.32N | 119.40W | 89 | -8.00 (NAP) | 92-06 | 723896 | -2.8 | -3 | -7.7 | 42.5 | 38.8 | 39.1 | 38.8 | 39 | 38.9 | 39 | 37.3 | 37.6 | 37.3 | 37 | 37.4 | 37 | 194 | United_StatesCaliforniaVISALIA MUNI (AWOS)
United_States | Colorado | AKRON WASHINGTON CO AP | AKRON WASHINGTON CO AP, CO, USA | 40.17N | 103.23W | 1409 | -7.00 (NAM) | 88-06 | 724698 | -23.2 | -23 | -34.2 | 41.6 | 36.2 | 37.5 | 35.3 | 36 | 36.3333 | 38 | 33.3 | 35.5 | 33.3 | 34 | 34.0333 | 34 | 195 | United_StatesColoradoAKRON WASHINGTON CO AP
United_States | Colorado | ALAMOSA SAN LUIS VALLEY RGNL | ALAMOSA SAN LUIS VALLEY RGNL, CO, USA | 37.44N | 105.87W | 2299 | -7.00 (NAM) | 82-06 | 724620 | -29.8 | -30 | -40.5 | 35.1 | 30.8 | 31.8 | 29.8 | 31 | 30.8 | 32 | 28.8 | 30.1 | 28.2 | 29 | 29.0333 | 29 | 196 | United_StatesColoradoALAMOSA SAN LUIS VALLEY RGNL
United_States | Colorado | ASPEN PITKIN CO SAR | ASPEN PITKIN CO SAR, CO, USA | 39.22N | 106.87W | 2444 | -7.00 (NAM) | 98-06 | 724676 | -24 | -24 | -30.6 | 34.8 | 29 | 32 | 29.1 | 30 | 30.0333 | 32 | 27.5 | 30.2 | 27.7 | 28 | 28.4667 | 28 | 197 | United_StatesColoradoASPEN PITKIN CO SAR
United_States | Colorado | BUCKLEY ANGB/DENVER | BUCKLEY ANGB/DENVER, CO, USA | 39.72N | 104.75W | 1726 | -7.00 (NAM) | 82-06 | 724695 | -22.3 | -22 | -31.9 | 40.4 | 34.8 | 36.4 | 34.8 | 35 | 35.3333 | 36 | 32.5 | 34.7 | 32.6 | 33 | 33.2667 | 33 | 198 | United_StatesColoradoBUCKLEY ANGB/DENVER
United_States | Colorado | COLORADO SPRINGS MUNI AP | COLORADO SPRINGS MUNI AP, CO, USA | 38.81N | 104.71W | 1881 | -7.00 (NAM) | 82-06 | 724660 | -22.6 | -23 | -33.5 | 37.8 | 33.3 | 34.7 | 32.7 | 34 | 33.5667 | 35 | 31.3 | 33 | 30.9 | 32 | 31.7333 | 32 | 199 | United_StatesColoradoCOLORADO SPRINGS MUNI AP
United_States | Colorado | CORTEZ/MONTEZUMA CO | CORTEZ/MONTEZUMA CO, CO, USA | 37.30N | 108.63W | 1803 | -7.00 (NAM) | 96-06 | 724767 | -19 | -19 | -22.9 | 39.9 | 34.1 | 37.2 | 34.1 | 35 | 35.1333 | 37 | 32.8 | 35.2 | 32.7 | 34 | 33.5667 | 34 | 200 | United_StatesColoradoCORTEZ/MONTEZUMA CO
United_States | Colorado | CRAIG-MOFFAT | CRAIG-MOFFAT, CO, USA | 40.50N | 107.53W | 1915 | -7.00 (NAM) | 82-06 | 725700 | -31.2 | -31 | -46.7 | 38.3 | 32.5 | 34.9 | 32.7 | 33 | 33.3667 | 35 | 30.2 | 32.8 | 31.2 | 31 | 31.4 | 31 | 201 | United_StatesColoradoCRAIG-MOFFAT
United_States | Colorado | DENVER INTL AP | DENVER INTL AP, CO, USA | 39.83N | 104.66W | 1655 | -7.00 (NAM) | 94-06 | 725650 | -22.7 | -23 | -29.9 | 40.5 | 34.6 | 37.3 | 35.2 | 36 | 35.7 | 37 | 32.8 | 35.5 | 33.6 | 34 | 33.9667 | 34 | 202 | United_StatesColoradoDENVER INTL AP
United_States | Colorado | DENVER STAPLETON INT'L ARPT | DENVER STAPLETON INT'L ARPT, CO, USA | 39.77N | 104.87W | 1611 | -7.00 (NAM) | 82-95 | 724690 | -24.6 | -25 | -35.1 | 40.7 | 36.1 | 36.4 | 34.8 | 36 | 35.7667 | 36 | 33.3 | 34.6 | 32.9 | 34 | 33.6 | 34 | 203 | United_StatesColoradoDENVER STAPLETON INT'L ARPT
United_States | Colorado | DENVER/CENTENNIAL | DENVER/CENTENNIAL, CO, USA | 39.57N | 104.85W | 1793 | -7.00 (NAM) | 83-06 | 724666 | -22.9 | -23 | -32.8 | 39.2 | 34 | 36.1 | 33.8 | 35 | 34.6333 | 36 | 32.2 | 33.8 | 32.2 | 33 | 32.7333 | 33 | 204 | United_StatesColoradoDENVER/CENTENNIAL
United_States | Colorado | DURANGO/LA PLATA CO | DURANGO/LA PLATA CO, CO, USA | 37.15N | 107.75W | 2038 | -7.00 (NAM) | 96-06 | 724625 | -20.7 | -21 | -28 | 38.4 | 32.7 | 34.1 | 32.7 | 33 | 33.1667 | 34 | 31.3 | 32.8 | 31.2 | 32 | 31.7667 | 32 | 205 | United_StatesColoradoDURANGO/LA PLATA CO
United_States | Colorado | EAGLE COUNTY AP | EAGLE COUNTY AP, CO, USA | 39.64N | 106.92W | 1992 | -7.00 (NAM) | 82-06 | 724675 | -27.7 | -28 | -37.2 | 37.2 | 31.4 | 33 | 31.6 | 32 | 32 | 33 | 29.3 | 32.1 | 29.9 | 30 | 30.4333 | 30 | 206 | United_StatesColoradoEAGLE COUNTY AP
United_States | Colorado | FORT COLLINS (AWOS) | FORT COLLINS (AWOS), CO, USA | 40.45N | 105.02W | 1529 | -7.00 (NAM) | 92-06 | 724769 | -22.5 | -23 | -31 | 41.2 | 35.9 | 37.6 | 34.9 | 36 | 36.1333 | 38 | 32.7 | 35.7 | 32.7 | 34 | 33.7 | 34 | 207 | United_StatesColoradoFORT COLLINS (AWOS)
United_States | Colorado | FORT COLLINS(SAWRS) | FORT COLLINS(SAWRS), CO, USA | 40.58N | 105.08W | 1525 | -7.00 (NAM) | 82-94 | 724697 | -23 | -23 | -35.5 | 37.7 | 33.8 | 34.4 | 32.9 | 34 | 33.7 | 34 | 31.3 | 32.4 | 31.1 | 32 | 31.6 | 32 | 208 | United_StatesColoradoFORT COLLINS(SAWRS)
United_States | Colorado | GRAND JUNCTION WALKER FIELD | GRAND JUNCTION WALKER FIELD, CO, USA | 39.13N | 108.54W | 1475 | -7.00 (NAM) | 82-06 | 724760 | -17.2 | -17 | -28.4 | 42 | 37.5 | 38.6 | 36.5 | 38 | 37.5333 | 39 | 35 | 37 | 34.9 | 36 | 35.6333 | 36 | 209 | United_StatesColoradoGRAND JUNCTION WALKER FIELD
United_States | Colorado | GREELEY/WELD (AWOS) | GREELEY/WELD (AWOS), CO, USA | 40.43N | 104.63W | 1420 | -7.00 (NAM) | 92-06 | 724768 | -26.9 | -27 | -35.4 | 41.8 | 36.4 | 37.9 | 36 | 37 | 36.7667 | 38 | 33.8 | 36.3 | 33.6 | 35 | 34.5667 | 35 | 210 | United_StatesColoradoGREELEY/WELD (AWOS)
United_States | Colorado | GUNNISON CO. (AWOS) | GUNNISON CO. (AWOS), CO, USA | 38.53N | 106.93W | 2339 | -7.00 (NAM) | 92-06 | 724677 | -31.1 | -31 | -40.6 | 33.7 | 28.2 | 31.1 | 27.9 | 29 | 29.0667 | 31 | 27.2 | 28.9 | 26.9 | 28 | 27.6667 | 28 | 211 | United_StatesColoradoGUNNISON CO. (AWOS)
United_States | Colorado | HAYDEN/YAMPA (AWOS) | HAYDEN/YAMPA (AWOS), CO, USA | 40.48N | 107.22W | 2012 | -7.00 (NAM) | 92-06 | 725715 | -24.6 | -25 | -32.3 | 37.7 | 31.1 | 32.9 | 32 | 32 | 32 | 33 | 28.7 | 32.1 | 29.8 | 30 | 30.2 | 30 | 212 | United_StatesColoradoHAYDEN/YAMPA (AWOS)
United_States | Colorado | LA JUNTA MUNICIPAL AP | LA JUNTA MUNICIPAL AP, CO, USA | 38.05N | 103.53W | 1285 | -7.00 (NAM) | 83-06 | 724635 | -21 | -21 | -33.4 | 44.1 | 38.9 | 39.5 | 38.5 | 39 | 38.9667 | 40 | 36.8 | 38 | 36.7 | 37 | 37.1667 | 37 | 213 | United_StatesColoradoLA JUNTA MUNICIPAL AP
United_States | Colorado | LAMAR MUNICIPAL | LAMAR MUNICIPAL, CO, USA | 38.07N | 102.68W | 1129 | -7.00 (NAM) | 95-06 | 724636 | -21.8 | -22 | -33.9 | 43.8 | 38.7 | 40.1 | 37.9 | 39 | 38.9 | 40 | 36.4 | 38 | 37 | 37 | 37.1333 | 37 | 214 | United_StatesColoradoLAMAR MUNICIPAL
United_States | Colorado | LIMON | LIMON, CO, USA | 39.19N | 103.72W | 1635 | -7.00 (NAM) | 82-06 | 724665 | -24.7 | -25 | -33.7 | 39.9 | 34 | 36.3 | 33.8 | 35 | 34.7 | 36 | 32.1 | 33.9 | 32 | 33 | 32.6667 | 33 | 215 | United_StatesColoradoLIMON
United_States | Colorado | MONTROSE CO. ARPT | MONTROSE CO. ARPT, CO, USA | 38.50N | 107.90W | 1755 | -7.00 (NAM) | 93-06 | 724765 | -18.5 | -19 | -26.4 | 38.5 | 35.2 | 37 | 34.2 | 35 | 35.4667 | 37 | 32.9 | 35.1 | 32.7 | 34 | 33.5667 | 34 | 216 | United_StatesColoradoMONTROSE CO. ARPT
United_States | Colorado | PUEBLO MEMORIAL AP | PUEBLO MEMORIAL AP, CO, USA | 38.29N | 104.50W | 1439 | -7.00 (NAM) | 82-06 | 724640 | -23.8 | -24 | -34.7 | 41.7 | 37.8 | 39.3 | 37.2 | 38 | 38.1 | 39 | 35.9 | 37.5 | 35.4 | 36 | 36.2667 | 36 | 217 | United_StatesColoradoPUEBLO MEMORIAL AP
United_States | Colorado | RIFLE/GARFIELD RGNL | RIFLE/GARFIELD RGNL, CO, USA | 39.53N | 107.72W | 1691 | -7.00 (NAM) | 97-06 | 725717 | -22 | -22 | -30.3 | 40.1 | 35.9 | 37.7 | 36 | 37 | 36.5333 | 38 | 33.6 | 36.4 | 33 | 34 | 34.3333 | 34 | 218 | United_StatesColoradoRIFLE/GARFIELD RGNL
United_States | Colorado | TRINIDAD LAS ANIMAS COUNTY AP | TRINIDAD LAS ANIMAS COUNTY AP, CO, USA | 37.26N | 104.34W | 1751 | -7.00 (NAM) | 82-06 | 724645 | -22.6 | -23 | -33.1 | 39.7 | 35.4 | 35.9 | 34.1 | 35 | 35.1333 | 36 | 33.1 | 34.1 | 32.6 | 33 | 33.2667 | 33 | 219 | United_StatesColoradoTRINIDAD LAS ANIMAS COUNTY AP
United_States | Connecticut | BRIDGEPORT SIKORSKY MEMORIAL | BRIDGEPORT SIKORSKY MEMORIAL, CT, USA | 41.18N | 73.15W | 5 | -5.00 (NAE) | 89-06 | 725040 | -14.3 | -14 | -22.1 | 40.6 | 31.5 | 33.3 | 32.8 | 33 | 32.5333 | 33 | 29.2 | 31.2 | 30.4 | 30 | 30.2667 | 30 | 220 | United_StatesConnecticutBRIDGEPORT SIKORSKY MEMORIAL
United_States | Connecticut | HARTFORD BRADLEY INTL AP | HARTFORD BRADLEY INTL AP, CT, USA | 41.94N | 72.68W | 55 | -5.00 (NAE) | 82-06 | 725080 | -19.7 | -20 | -28.4 | 39.5 | 34 | 35.4 | 34.7 | 35 | 34.7 | 35 | 31.9 | 33.2 | 32.2 | 32 | 32.4333 | 32 | 221 | United_StatesConnecticutHARTFORD BRADLEY INTL AP
United_States | Connecticut | HARTFORD BRAINARD FD | HARTFORD BRAINARD FD, CT, USA | 41.74N | 72.65W | 6 | -5.00 (NAE) | 83-06 | 725087 | N/A | N/A | N/A | N/A | 33.9 | 35.8 | 34.1 | 35 | 34.6 | 36 | 31.5 | 32.7 | 31.9 | 32 | 32.0333 | 32 | 222 | United_StatesConnecticutHARTFORD BRAINARD FD
United_States | Connecticut | OXFORD (AWOS) | OXFORD (AWOS), CT, USA | 41.48N | 73.13W | 222 | -5.00 (NAE) | 92-06 | 725029 | -19 | -19 | -25.7 | 37.6 | 31.3 | 32.9 | 32.5 | 32 | 32.2333 | 33 | 29 | 31 | 29.7 | 30 | 29.9 | 30 | 223 | United_StatesConnecticutOXFORD (AWOS)
United_States | Connecticut | WILLIMANTIC (ASOS) | WILLIMANTIC (ASOS), CT, USA | 41.73N | 72.18W | 76 | -5.00 (NAE) | 97-06 | 725084 | -19 | -19 | -24.9 | 38.4 | 32.7 | 34 | 33 | 33 | 33.2333 | 34 | 31.2 | 32.2 | 31.1 | 32 | 31.5 | 32 | 224 | United_StatesConnecticutWILLIMANTIC (ASOS)
United_States | Delaware | DOVER AFB | DOVER AFB, DE, USA | 39.13N | 75.47W | 7 | -5.00 (NAE) | 82-06 | 724088 | -13.4 | -13 | -22 | 40.3 | 34.2 | 36 | 34.7 | 35 | 34.9667 | 36 | 32.3 | 33.9 | 32.5 | 33 | 32.9 | 33 | 225 | United_StatesDelawareDOVER AFB
United_States | Delaware | GEORGETOWN/SUSSEX | GEORGETOWN/SUSSEX, DE, USA | 38.68N | 75.37W | 16 | -5.00 (NAE) | 97-06 | 724093 | -11.4 | -11 | -18.1 | 39.8 | 33.7 | 35.9 | 34.9 | 35 | 34.8333 | 36 | 32.4 | 33.6 | 32.9 | 33 | 32.9667 | 33 | 226 | United_StatesDelawareGEORGETOWN/SUSSEX
United_States | Delaware | WILMINGTON NEW CASTLE CNTY AP | WILMINGTON NEW CASTLE CNTY AP, DE, USA | 39.67N | 75.60W | 24 | -5.00 (NAE) | 82-06 | 724089 | -15.3 | -15 | -27 | 39.8 | 33.9 | 35.7 | 34.5 | 35 | 34.7 | 36 | 31.8 | 33.7 | 32.4 | 33 | 32.6333 | 33 | 227 | United_StatesDelawareWILMINGTON NEW CASTLE CNTY AP
United_States | Florida | APALACHICOLA MUNI AP | APALACHICOLA MUNI AP, FL, USA | 29.73N | 85.03W | 6 | -5.00 (NAE) | 82-06 | 722200 | -4.6 | -5 | -14.5 | 38.7 | 33.5 | 34.6 | 34.4 | 34 | 34.1667 | 35 | 32.3 | 33 | 33 | 33 | 32.7667 | 33 | 228 | United_StatesFloridaAPALACHICOLA MUNI AP
United_States | Florida | CAPE SAN BLAS | CAPE SAN BLAS, FL, USA | 29.67N | 85.37W | 2 | -6.00 (NAC) | 85-04 | 994360 | -1.8 | -2 | -10.2 | 34.7 | 30 | 30.7 | 31.4 | 31 | 30.7 | 31 | 29.2 | 30 | 30.5 | 30 | 29.9 | 30 | 229 | United_StatesFloridaCAPE SAN BLAS
United_States | Florida | CECIL FIELD | CECIL FIELD, FL, USA | 30.22N | 81.87W | 27 | -5.00 (NAE) | 82-98 | 722067 | -5.6 | -6 | -15 | 40.4 | 37.4 | 36.9 | 36.3 | 37 | 36.8667 | 37 | 35.7 | 35.5 | 35 | 35 | 35.4 | 35 | 230 | United_StatesFloridaCECIL FIELD
United_States | Florida | CRESTVIEW BOB SIKES AP | CRESTVIEW BOB SIKES AP, FL, USA | 30.78N | 86.52W | 56 | -6.00 (NAC) | 82-06 | 722215 | -8.7 | -9 | -15.7 | 40.8 | 36.7 | 37 | 36.2 | 37 | 36.6333 | 37 | 34.7 | 35.1 | 34.3 | 35 | 34.7 | 35 | 231 | United_StatesFloridaCRESTVIEW BOB SIKES AP
United_States | Florida | CROSS CITY AIRPORT | CROSS CITY AIRPORT, FL, USA | 29.55N | 83.11W | 13 | -5.00 (NAE) | 82-06 | 722120 | -6.2 | -6 | -10.5 | 39.2 | 35.7 | 35.9 | 35.6 | 36 | 35.7333 | 36 | 33.6 | 34.1 | 34.1 | 34 | 33.9333 | 34 | 232 | United_StatesFloridaCROSS CITY AIRPORT
United_States | Florida | DAYTONA BEACH INTL AP | DAYTONA BEACH INTL AP, FL, USA | 29.18N | 81.06W | 13 | -5.00 (NAE) | 82-06 | 722056 | -2.3 | -2 | -9.5 | 38.7 | 35.5 | 35.1 | 34.5 | 35 | 35.0333 | 35 | 33.1 | 33.5 | 33.2 | 33 | 33.2667 | 33 | 233 | United_StatesFloridaDAYTONA BEACH INTL AP
United_States | Florida | DESTIN FT. WALTON | DESTIN FT. WALTON, FL, USA | 30.40N | 86.47W | 7 | -6.00 (NAC) | 97-06 | 722069 | N/A | N/A | N/A | N/A | 32.5 | 34.1 | 33.9 | 34 | 33.5 | 34 | 31.3 | 32.7 | 32.7 | 32 | 32.2333 | 32 | 234 | United_StatesFloridaDESTIN FT. WALTON
United_States | Florida | EGLIN AFB/VALPARAIS | EGLIN AFB/VALPARAIS, FL, USA | 30.48N | 86.53W | 20 | -6.00 (NAC) | 82-06 | 722210 | -6.3 | -6 | -14.8 | 39.4 | 33.9 | 35.6 | 34.8 | 35 | 34.7667 | 36 | 32.4 | 33.7 | 33 | 33 | 33.0333 | 33 | 235 | United_StatesFloridaEGLIN AFB/VALPARAIS
United_States | Florida | FORT LAUDERDALE HOLLYWOOD INT | FORT LAUDERDALE HOLLYWOOD INT, FL, USA | 26.07N | 80.15W | 3 | -5.00 (NAE) | 82-06 | 722025 | 4.5 | 5 | -3.1 | 40.2 | 34.3 | 34.1 | 34.1 | 34 | 34.1667 | 34 | 32.7 | 32.9 | 32.9 | 33 | 32.8333 | 33 | 236 | United_StatesFloridaFORT LAUDERDALE HOLLYWOOD INT
United_States | Florida | FORT MYERS PAGE FIELD | FORT MYERS PAGE FIELD, FL, USA | 26.59N | 81.86W | 6 | -5.00 (NAE) | 82-06 | 722106 | 1.5 | 2 | -4.4 | 38 | 35.1 | 35.1 | 35.1 | 35 | 35.1 | 35 | 33.9 | 34.1 | 34 | 34 | 34 | 34 | 237 | United_StatesFloridaFORT MYERS PAGE FIELD
United_States | Florida | GAINESVILLE REGIONAL AP | GAINESVILLE REGIONAL AP, FL, USA | 29.69N | 82.27W | 50 | -5.00 (NAE) | 82-06 | 722146 | -5.2 | -5 | -12 | 40.9 | 35.9 | 35.2 | 35 | 35 | 35.3667 | 35 | 34 | 34 | 33.7 | 34 | 33.9 | 34 | 238 | United_StatesFloridaGAINESVILLE REGIONAL AP
United_States | Florida | HOMESTEAD AFB | HOMESTEAD AFB, FL, USA | 25.48N | 80.38W | 5 | -5.00 (NAE) | 82-06 | 722026 | 4.6 | 5 | -2 | 37.2 | 33.6 | 34 | 33.7 | 34 | 33.7667 | 34 | 32.4 | 32.7 | 32.7 | 33 | 32.6 | 33 | 239 | United_StatesFloridaHOMESTEAD AFB
United_States | Florida | HURLBURT FIELD (AF) | HURLBURT FIELD (AF), FL, USA | 30.43N | 86.68W | 12 | -6.00 (NAC) | 83-06 | 747770 | -5.2 | -5 | -11.7 | 39 | 33.9 | 35.1 | 34.9 | 35 | 34.6333 | 35 | 32.4 | 33.2 | 33.1 | 33 | 32.9 | 33 | 240 | United_StatesFloridaHURLBURT FIELD (AF)
United_States | Florida | JACKSONVILLE INTL ARPT | JACKSONVILLE INTL ARPT, FL, USA | 30.49N | 81.69W | 10 | -5.00 (NAE) | 82-06 | 722060 | -5.3 | -5 | -12.7 | 39.8 | 36.3 | 36.2 | 35.4 | 36 | 35.9667 | 36 | 34.4 | 34.7 | 34.1 | 34 | 34.4 | 34 | 241 | United_StatesFloridaJACKSONVILLE INTL ARPT
United_States | Florida | JACKSONVILLE NAS | JACKSONVILLE NAS, FL, USA | 30.23N | 81.68W | 7 | -5.00 (NAE) | 82-06 | 722065 | -3.7 | -4 | -13 | 40.9 | 37.4 | 36.9 | 36.6 | 37 | 36.9667 | 37 | 34.8 | 35.1 | 34.7 | 35 | 34.8667 | 35 | 242 | United_StatesFloridaJACKSONVILLE NAS
United_States | Florida | JACKSONVILLE/CRAIG | JACKSONVILLE/CRAIG, FL, USA | 30.34N | 81.52W | 13 | -5.00 (NAE) | 82-06 | 722068 | -4.1 | -4 | -12.2 | 38.8 | 36.2 | 35.8 | 35.1 | 36 | 35.7 | 36 | 33.7 | 34.1 | 33.5 | 34 | 33.7667 | 34 | 243 | United_StatesFloridaJACKSONVILLE/CRAIG
United_States | Florida | KEY WEST INTL ARPT | KEY WEST INTL ARPT, FL, USA | 24.55N | 81.75W | 6 | -5.00 (NAE) | 82-06 | 722010 | 10 | 10 | 4.4 | 35.2 | 32.6 | 33 | 33.3 | 33 | 32.9667 | 33 | 31.8 | 32.4 | 32.6 | 32 | 32.2667 | 32 | 244 | United_StatesFloridaKEY WEST INTL ARPT
United_States | Florida | KEY WEST NAS | KEY WEST NAS, FL, USA | 24.58N | 81.68W | 7 | -5.00 (NAE) | 82-06 | 722015 | 10.3 | 10 | 5.1 | 36.3 | 32.5 | 32.8 | 32.9 | 33 | 32.7333 | 33 | 31.9 | 32.3 | 32.4 | 32 | 32.2 | 32 | 245 | United_StatesFloridaKEY WEST NAS
United_States | Florida | MACDILL AFB/TAMPA | MACDILL AFB/TAMPA, FL, USA | 27.85N | 82.52W | 8 | -5.00 (NAE) | 82-06 | 747880 | 0.8 | 1 | -6.5 | 38 | 34.2 | 34.9 | 34.6 | 35 | 34.5667 | 35 | 33.3 | 33.7 | 33.6 | 34 | 33.5333 | 34 | 246 | United_StatesFloridaMACDILL AFB/TAMPA
United_States | Florida | MARATHON AIRPORT | MARATHON AIRPORT, FL, USA | 24.73N | 81.05W | 2 | -5.00 (NAE) | 95-06 | 722016 | N/A | N/A | N/A | N/A | 33 | 33.9 | 33.9 | 34 | 33.6 | 34 | 32.7 | 32.9 | 33 | 33 | 32.8667 | 33 | 247 | United_StatesFloridaMARATHON AIRPORT
United_States | Florida | MAYPORT NS | MAYPORT NS, FL, USA | 30.40N | 81.42W | 4 | -5.00 (NAE) | 84-06 | 722066 | -2.8 | -3 | -13.4 | 40.7 | 36.3 | 36.5 | 35.8 | 36 | 36.2 | 37 | 34.1 | 34.8 | 33.8 | 34 | 34.2333 | 34 | 248 | United_StatesFloridaMAYPORT NS
United_States | Florida | MELBOURNE REGIONAL AP | MELBOURNE REGIONAL AP, FL, USA | 28.10N | 80.65W | 8 | -5.00 (NAE) | 82-06 | 722040 | -0.3 | 0 | -8.8 | 39 | 35 | 35.2 | 34.4 | 35 | 34.8667 | 35 | 33 | 33.5 | 33 | 33 | 33.1667 | 33 | 249 | United_StatesFloridaMELBOURNE REGIONAL AP
United_States | Florida | MIAMI INTL AP | MIAMI INTL AP, FL, USA | 25.82N | 80.30W | 9 | -5.00 (NAE) | 82-06 | 722020 | 5.1 | 5 | -2.9 | 37.4 | 33.8 | 34.2 | 34.1 | 34 | 34.0333 | 34 | 32.6 | 33 | 33 | 33 | 32.8667 | 33 | 250 | United_StatesFloridaMIAMI INTL AP
United_States | Florida | MIAMI/KENDALL-TAMIA | MIAMI/KENDALL-TAMIA, FL, USA | 25.65N | 80.43W | 3 | -5.00 (NAE) | 83-06 | 722029 | 4.1 | 4 | -3.2 | 40.1 | 34.1 | 34.1 | 34.2 | 34 | 34.1333 | 34 | 32.9 | 33.2 | 33.4 | 33 | 33.1667 | 33 | 251 | United_StatesFloridaMIAMI/KENDALL-TAMIA
United_States | Florida | MOLASSES REEF | MOLASSES REEF, FL, USA | 25.02N | 80.38W | 11 | -5.00 (NAE) | 89-06 | 994430 | 8.8 | 9 | 1 | 32.1 | 29.9 | 30.6 | 30.6 | 30 | 30.3667 | 31 | 29.5 | 30 | 30.2 | 30 | 29.9 | 30 | 252 | United_StatesFloridaMOLASSES REEF
United_States | Florida | NAPLES MUNICIPAL | NAPLES MUNICIPAL, FL, USA | 26.15N | 81.78W | 7 | -5.00 (NAE) | 92-06 | 722038 | 2.8 | 3 | -1.4 | 36.9 | 33.1 | 33.5 | 33.2 | 33 | 33.2667 | 34 | 32.3 | 32.5 | 32.5 | 32 | 32.4333 | 32 | 253 | United_StatesFloridaNAPLES MUNICIPAL
United_States | Florida | NASA SHUTTLE FCLTY | NASA SHUTTLE FCLTY, FL, USA | 28.62N | 80.72W | 3 | -5.00 (NAE) | 82-06 | 747946 | -0.4 | 0 | -8 | 38.5 | 34.5 | 34.4 | 34.3 | 34 | 34.4 | 34 | 32.7 | 33.1 | 32.9 | 33 | 32.9 | 33 | 254 | United_StatesFloridaNASA SHUTTLE FCLTY
United_States | Florida | OCALA MUNI (AWOS) | OCALA MUNI (AWOS), FL, USA | 29.17N | 82.22W | 27 | -5.00 (NAE) | 92-06 | 722055 | -5.5 | -6 | -10 | 38.1 | 36.1 | 34.9 | 34.7 | 35 | 35.2333 | 35 | 33.9 | 33.8 | 33.7 | 34 | 33.8 | 34 | 255 | United_StatesFloridaOCALA MUNI (AWOS)
United_States | Florida | ORLANDO EXECUTIVE AP | ORLANDO EXECUTIVE AP, FL, USA | 28.55N | 81.33W | 34 | -5.00 (NAE) | 88-06 | 722053 | 0.9 | 1 | -5.4 | 38.9 | 36.3 | 35.2 | 35 | 36 | 35.5 | 35 | 34.1 | 34.1 | 34 | 34 | 34.0667 | 34 | 256 | United_StatesFloridaORLANDO EXECUTIVE AP
United_States | Florida | ORLANDO INTL ARPT | ORLANDO INTL ARPT, FL, USA | 28.43N | 81.33W | 32 | -5.00 (NAE) | 82-06 | 722050 | -0.9 | -1 | -9.1 | 38.1 | 35.5 | 35.1 | 35 | 35 | 35.2 | 35 | 34 | 34.1 | 33.9 | 34 | 34 | 34 | 257 | United_StatesFloridaORLANDO INTL ARPT
United_States | Florida | ORLANDO SANFORD AIRPORT | ORLANDO SANFORD AIRPORT, FL, USA | 28.78N | 81.24W | 17 | -5.00 (NAE) | 92-06 | 722057 | 0.6 | 1 | -4.3 | 39.3 | 37 | 36.2 | 36 | 36 | 36.4 | 36 | 34.6 | 34.3 | 34.1 | 34 | 34.3333 | 34 | 258 | United_StatesFloridaORLANDO SANFORD AIRPORT
United_States | Florida | PANAMA CITY BAY CO | PANAMA CITY BAY CO, FL, USA | 30.20N | 85.68W | 6 | -6.00 (NAC) | 98-06 | 722245 | -3.5 | -4 | -8.9 | 40 | 33.8 | 36.2 | 34.2 | 35 | 34.7333 | 36 | 32.6 | 33.8 | 33 | 33 | 33.1333 | 33 | 259 | United_StatesFloridaPANAMA CITY BAY CO
United_States | Florida | PENSACOLA FOREST SHERMAN NAS | PENSACOLA FOREST SHERMAN NAS, FL, USA | 30.35N | 87.32W | 9 | -6.00 (NAC) | 82-06 | 722225 | -6.2 | -6 | -15.7 | 41.2 | 34.2 | 36.2 | 35.4 | 35 | 35.2667 | 36 | 32.9 | 34.2 | 33.7 | 34 | 33.6 | 34 | 260 | United_StatesFloridaPENSACOLA FOREST SHERMAN NAS
United_States | Florida | PENSACOLA REGIONAL AP | PENSACOLA REGIONAL AP, FL, USA | 30.47N | 87.19W | 36 | -6.00 (NAC) | 82-06 | 722223 | -5.5 | -6 | -13.7 | 40.5 | 35.2 | 36.4 | 35.3 | 36 | 35.6333 | 36 | 33.3 | 34.4 | 33.7 | 34 | 33.8 | 34 | 261 | United_StatesFloridaPENSACOLA REGIONAL AP
United_States | Florida | SARASOTA BRADENTON | SARASOTA BRADENTON, FL, USA | 27.38N | 82.55W | 10 | -5.00 (NAE) | 82-06 | 722115 | 0 | 0 | -6.5 | 39 | 34 | 34.5 | 34.3 | 34 | 34.2667 | 35 | 32.7 | 33 | 33.3 | 33 | 33 | 33 | 262 | United_StatesFloridaSARASOTA BRADENTON
United_States | Florida | SOMBRERO KEY | SOMBRERO KEY, FL, USA | 24.62N | 81.10W | 37 | -5.00 (NAE) | 89-06 | 994450 | 10.9 | 11 | 6 | 33.5 | 30.8 | 31.5 | 31.9 | 31 | 31.4 | 32 | 30.1 | 30.8 | 31.2 | 31 | 30.7 | 31 | 263 | United_StatesFloridaSOMBRERO KEY
United_States | Florida | SOUTHWEST FLORIDA I | SOUTHWEST FLORIDA I, FL, USA | 26.53N | 81.75W | 9 | -5.00 (NAE) | 88-06 | 722108 | 0.9 | 1 | -6 | 38 | 35.3 | 35.1 | 35.1 | 35 | 35.1667 | 35 | 34.1 | 34 | 34 | 34 | 34.0333 | 34 | 264 | United_StatesFloridaSOUTHWEST FLORIDA I
United_States | Florida | ST AUGSUTINE ARPT | ST AUGSUTINE ARPT, FL, USA | 29.97N | 81.33W | 3 | -5.00 (NAE) | 97-06 | 722212 | N/A | N/A | N/A | N/A | 36.2 | 35.2 | 33.9 | 35 | 35.1 | 35 | 33 | 32.9 | 32.6 | 33 | 32.8333 | 33 | 265 | United_StatesFloridaST AUGSUTINE ARPT
United_States | Florida | ST PETERSBURG CLEAR | ST PETERSBURG CLEAR, FL, USA | 27.90N | 82.68W | 3 | -5.00 (NAE) | 82-06 | 722116 | 1.1 | 1 | -6.1 | 38.3 | 34.9 | 35.1 | 34.7 | 35 | 34.9 | 35 | 33.4 | 33.8 | 33.7 | 34 | 33.6333 | 34 | 266 | United_StatesFloridaST PETERSBURG CLEAR
United_States | Florida | ST. AUGUSTINE | ST. AUGUSTINE, FL, USA | 29.87N | 81.27W | 9 | -5.00 (NAE) | 89-06 | 994410 | -0.2 | 0 | -6.7 | 38.2 | 34.1 | 33.9 | 34 | 34 | 34 | 34 | 30.9 | 31.8 | 31.3 | 31 | 31.3333 | 31 | 267 | United_StatesFloridaST. AUGUSTINE
United_States | Florida | TALLAHASSEE REGIONAL AP | TALLAHASSEE REGIONAL AP, FL, USA | 30.39N | 84.35W | 21 | -5.00 (NAE) | 82-06 | 722140 | -7.5 | -8 | -13.2 | 40.5 | 36.7 | 36.9 | 36.2 | 37 | 36.6 | 37 | 34.7 | 35.1 | 34.8 | 35 | 34.8667 | 35 | 268 | United_StatesFloridaTALLAHASSEE REGIONAL AP
United_States | Florida | TAMPA INTERNATIONAL AP | TAMPA INTERNATIONAL AP, FL, USA | 27.96N | 82.54W | 3 | -5.00 (NAE) | 82-06 | 722110 | -0.7 | -1 | -8.3 | 37.1 | 34.4 | 34.2 | 34.2 | 34 | 34.2667 | 34 | 33.1 | 33.3 | 33.4 | 33 | 33.2667 | 33 | 269 | United_StatesFloridaTAMPA INTERNATIONAL AP
United_States | Florida | TYNDALL AFB | TYNDALL AFB, FL, USA | 30.07N | 85.58W | 7 | -6.00 (NAC) | 82-04 | 747750 | -4.5 | -5 | -12.4 | 39.7 | 32.8 | 34.5 | 34 | 34 | 33.7667 | 35 | 31.7 | 32.7 | 32.8 | 32 | 32.4 | 32 | 270 | United_StatesFloridaTYNDALL AFB
United_States | Florida | VENICE PIER | VENICE PIER, FL, USA | 27.07N | 82.45W | 5 | -5.00 (NAE) | 86-06 | 994220 | 1.4 | 1 | -4.3 | 34.1 | 30.7 | 32.1 | 31.9 | 32 | 31.5667 | 32 | 29.6 | 30.5 | 30.8 | 30 | 30.3 | 30 | 271 | United_StatesFloridaVENICE PIER
United_States | Florida | VERO BEACH MUNICIPAL ARPT | VERO BEACH MUNICIPAL ARPT, FL, USA | 27.66N | 80.42W | 9 | -5.00 (NAE) | 82-06 | 722045 | 0.1 | 0 | -7.8 | 38.1 | 34 | 34.8 | 33.9 | 34 | 34.2333 | 35 | 32.6 | 33 | 32.9 | 33 | 32.8333 | 33 | 272 | United_StatesFloridaVERO BEACH MUNICIPAL ARPT
United_States | Florida | WEST PALM BEACH INTL ARPT | WEST PALM BEACH INTL ARPT, FL, USA | 26.69N | 80.10W | 6 | -5.00 (NAE) | 82-06 | 722030 | 2.7 | 3 | -4.7 | 37.1 | 33.7 | 34 | 34 | 34 | 33.9 | 34 | 32.3 | 32.7 | 32.9 | 33 | 32.6333 | 33 | 273 | United_StatesFloridaWEST PALM BEACH INTL ARPT
United_States | Florida | WHITING FIELD NAAS | WHITING FIELD NAAS, FL, USA | 30.72N | 87.02W | 61 | -6.00 (NAC) | 82-98 | 722226 | -7.4 | -7 | -17 | 39.4 | 35.7 | 35.9 | 36.1 | 36 | 35.9 | 36 | 34.1 | 34.7 | 34.6 | 34 | 34.4667 | 34 | 274 | United_StatesFloridaWHITING FIELD NAAS
United_States | Georgia | ALBANY DOUGHERTY COUNTY AP | ALBANY DOUGHERTY COUNTY AP, GA, USA | 31.54N | 84.19W | 59 | -5.00 (NAE) | 82-06 | 722160 | -7.7 | -8 | -16.6 | 41 | 37.1 | 37.3 | 36.9 | 37 | 37.1 | 37 | 35.4 | 35.9 | 35.3 | 36 | 35.5333 | 36 | 275 | United_StatesGeorgiaALBANY DOUGHERTY COUNTY AP
United_States | Georgia | ATHENS BEN EPPS AP | ATHENS BEN EPPS AP, GA, USA | 33.95N | 83.33W | 244 | -5.00 (NAE) | 82-06 | 723110 | -10.5 | -11 | -20.4 | 42 | 35.9 | 37.2 | 36.8 | 37 | 36.6333 | 37 | 33.9 | 35.4 | 34.5 | 35 | 34.6 | 35 | 276 | United_StatesGeorgiaATHENS BEN EPPS AP
United_States | Georgia | ATLANTA (NEXRAD) | ATLANTA (NEXRAD), GA, USA | 33.37N | 84.55W | 296 | -5.00 (NAE) | 96-06 | 722197 | -10.6 | -11 | -14.7 | 39.2 | 34 | 36 | 36 | 35 | 35.3333 | 36 | 32.7 | 33.7 | 33.7 | 33 | 33.3667 | 33 | 277 | United_StatesGeorgiaATLANTA (NEXRAD)
United_States | Georgia | ATLANTA HARTSFIELD INTL AP | ATLANTA HARTSFIELD INTL AP, GA, USA | 33.64N | 84.43W | 313 | -5.00 (NAE) | 82-06 | 722190 | -11.2 | -11 | -22.1 | 40.6 | 34.9 | 36.6 | 35.7 | 36 | 35.7333 | 37 | 33.2 | 34.8 | 33.8 | 34 | 33.9333 | 34 | 278 | United_StatesGeorgiaATLANTA HARTSFIELD INTL AP
United_States | Georgia | AUGUSTA BUSH FIELD | AUGUSTA BUSH FIELD, GA, USA | 33.37N | 81.97W | 45 | -5.00 (NAE) | 82-06 | 722180 | -9.6 | -10 | -17.7 | 42.8 | 37.4 | 38.1 | 37.7 | 38 | 37.7333 | 38 | 35.2 | 36.3 | 35.5 | 36 | 35.6667 | 36 | 279 | United_StatesGeorgiaAUGUSTA BUSH FIELD
United_States | Georgia | AUGUSTA\DANIEL FLD | AUGUSTA\DANIEL FLD, GA, USA | 33.47N | 82.03W | 128 | -5.00 (NAE) | 97-06 | 722181 | -6.2 | -6 | -12.2 | 42.2 | 37.1 | 37.3 | 37.4 | 37 | 37.2667 | 37 | 34.1 | 36 | 35.1 | 35 | 35.0667 | 35 | 280 | United_StatesGeorgiaAUGUSTA\DANIEL FLD
United_States | Georgia | BRUNSWICK MALCOLM MCKINNON AP | BRUNSWICK MALCOLM MCKINNON AP, GA, USA | 31.25N | 81.39W | 7 | -5.00 (NAE) | 82-06 | 722137 | -5.2 | -5 | -14.7 | 38.9 | 34.6 | 35.6 | 35.2 | 35 | 35.1333 | 36 | 32.7 | 33.8 | 33.1 | 33 | 33.2 | 33 | 281 | United_StatesGeorgiaBRUNSWICK MALCOLM MCKINNON AP
United_States | Georgia | COLUMBUS METROPOLITAN ARPT | COLUMBUS METROPOLITAN ARPT, GA, USA | 32.52N | 84.94W | 120 | -5.00 (NAE) | 82-06 | 722255 | -8.6 | -9 | -17.7 | 41.1 | 36.3 | 37.4 | 37.2 | 37 | 36.9667 | 37 | 34.6 | 36 | 35.3 | 35 | 35.3 | 35 | 282 | United_StatesGeorgiaCOLUMBUS METROPOLITAN ARPT
United_States | Georgia | DEKALB PEACHTREE | DEKALB PEACHTREE, GA, USA | 33.87N | 84.30W | 313 | -5.00 (NAE) | 98-06 | 722196 | -9.2 | -9 | -14.6 | 41 | 34.2 | 36.1 | 36.3 | 36 | 35.5333 | 36 | 32.9 | 34 | 34 | 34 | 33.6333 | 34 | 283 | United_StatesGeorgiaDEKALB PEACHTREE
United_States | Georgia | DOBBINS AFB/MARIETT | DOBBINS AFB/MARIETT, GA, USA | 33.92N | 84.52W | 330 | -5.00 (NAE) | 82-05 | 722270 | -11.5 | -12 | -21.1 | 41.4 | 34.6 | 36.1 | 36.5 | 36 | 35.7333 | 36 | 32.7 | 34.5 | 33.8 | 34 | 33.6667 | 34 | 284 | United_StatesGeorgiaDOBBINS AFB/MARIETT
United_States | Georgia | FORT BENNING | FORT BENNING, GA, USA | 32.33N | 85.00W | 88 | -5.00 (NAE) | 82-06 | 722250 | -9.7 | -10 | -17.3 | 42.4 | 37.4 | 37.8 | 37.2 | 37 | 37.4667 | 38 | 35.2 | 36.1 | 35.2 | 36 | 35.5 | 36 | 285 | United_StatesGeorgiaFORT BENNING
United_States | Georgia | FULTON CO ARPT BROW | FULTON CO ARPT BROW, GA, USA | 33.77N | 84.52W | 263 | -5.00 (NAE) | 82-06 | 722195 | -11.1 | -11 | -21.4 | 40.6 | 34.7 | 36.4 | 36.1 | 36 | 35.7333 | 36 | 33 | 34.6 | 34 | 34 | 33.8667 | 34 | 286 | United_StatesGeorgiaFULTON CO ARPT BROW
United_States | Georgia | GAINESVILLE\LEE GIL | GAINESVILLE\LEE GIL, GA, USA | 34.27N | 83.83W | 389 | -5.00 (NAE) | 97-06 | 722185 | -8.4 | -8 | -14.5 | 39.8 | 33.7 | 34.8 | 35.1 | 35 | 34.5333 | 35 | 32.4 | 32.9 | 32.9 | 33 | 32.7333 | 33 | 287 | United_StatesGeorgiaGAINESVILLE\LEE GIL
United_States | Georgia | HUNTER AAF | HUNTER AAF, GA, USA | 32.00N | 81.13W | 13 | -5.00 (NAE) | 82-06 | 747804 | -5.2 | -5 | -11.1 | 41.2 | 36.8 | 37.5 | 36.2 | 37 | 36.8333 | 38 | 34.5 | 35.7 | 34.5 | 35 | 34.9 | 35 | 288 | United_StatesGeorgiaHUNTER AAF
United_States | Georgia | MACON MIDDLE GA REGIONAL AP | MACON MIDDLE GA REGIONAL AP, GA, USA | 32.69N | 83.65W | 110 | -5.00 (NAE) | 82-06 | 722170 | -9.4 | -9 | -18.9 | 41.9 | 37 | 37.8 | 37.4 | 37 | 37.4 | 38 | 34.9 | 36.1 | 35.4 | 35 | 35.4667 | 35 | 289 | United_StatesGeorgiaMACON MIDDLE GA REGIONAL AP
United_States | Georgia | MOODY AFB/VALDOSTA | MOODY AFB/VALDOSTA, GA, USA | 30.97N | 83.20W | 71 | -5.00 (NAE) | 82-00 | 747810 | -6.7 | -7 | -19.4 | 41 | 37.3 | 36.8 | 36.2 | 37 | 36.7667 | 37 | 35.2 | 35.3 | 34.7 | 35 | 35.0667 | 35 | 290 | United_StatesGeorgiaMOODY AFB/VALDOSTA
United_States | Georgia | ROME R B RUSSELL AP | ROME R B RUSSELL AP, GA, USA | 34.35N | 85.16W | 196 | -5.00 (NAE) | 82-06 | 723200 | -11.3 | -11 | -22.1 | 41.8 | 36.2 | 37.7 | 37.2 | 37 | 37.0333 | 38 | 34 | 36 | 35.1 | 35 | 35.0333 | 35 | 291 | United_StatesGeorgiaROME R B RUSSELL AP
United_States | Georgia | SAVANNAH INTL AP | SAVANNAH INTL AP, GA, USA | 32.12N | 81.20W | 16 | -5.00 (NAE) | 82-06 | 722070 | -6.8 | -7 | -15.1 | 41.1 | 36.6 | 37.3 | 36.1 | 37 | 36.6667 | 37 | 34.4 | 35.6 | 34.5 | 35 | 34.8333 | 35 | 292 | United_StatesGeorgiaSAVANNAH INTL AP
United_States | Georgia | VALDOSTA WB AIRPORT | VALDOSTA WB AIRPORT, GA, USA | 30.78N | 83.28W | 60 | -5.00 (NAE) | 82-06 | 722166 | -7 | -7 | -15.8 | 41.6 | 37.4 | 37 | 36.4 | 37 | 36.9333 | 37 | 34.9 | 35.1 | 34.9 | 35 | 34.9667 | 35 | 293 | United_StatesGeorgiaVALDOSTA WB AIRPORT
United_States | Georgia | WARNER ROBINS AFB | WARNER ROBINS AFB, GA, USA | 32.63N | 83.60W | 92 | -5.00 (NAE) | 82-06 | 722175 | -8.4 | -8 | -16.7 | 42.6 | 37.5 | 37.9 | 37.5 | 38 | 37.6333 | 38 | 35.3 | 36.3 | 35.8 | 36 | 35.8 | 36 | 294 | United_StatesGeorgiaWARNER ROBINS AFB
United_States | Georgia | WAYCROSS WARE CO AP | WAYCROSS WARE CO AP, GA, USA | 31.25N | 82.40W | 43 | -5.00 (NAE) | 83-06 | 722130 | -6.4 | -6 | -20.9 | 42.1 | 36.7 | 37.8 | 36.2 | 37 | 36.9 | 38 | 34.8 | 35.9 | 34.9 | 35 | 35.2 | 35 | 295 | United_StatesGeorgiaWAYCROSS WARE CO AP
United_States | Hawaii | BARBERS POINT NAS | BARBERS POINT NAS, HI, USA | 21.30N | 158.07W | 10 | -10.00 (PCH) | 82-99 | 911780 | 12.7 | 13 | 10.2 | 37 | 32.6 | 33.6 | 33.3 | 33 | 33.1667 | 34 | 31.8 | 32.4 | 32.4 | 32 | 32.2 | 32 | 296 | United_StatesHawaiiBARBERS POINT NAS
United_States | Hawaii | HILO INTERNATIONAL AP | HILO INTERNATIONAL AP, HI, USA | 19.72N | 155.05W | 11 | -10.00 (PCH) | 82-06 | 912850 | 14.7 | 15 | 12.3 | 33.7 | 29.4 | 29.9 | 30.2 | 30 | 29.8333 | 30 | 28.5 | 29 | 29.4 | 29 | 28.9667 | 29 | 297 | United_StatesHawaiiHILO INTERNATIONAL AP
United_States | Hawaii | HONOLULU INTL ARPT | HONOLULU INTL ARPT, HI, USA | 21.33N | 157.94W | 5 | -10.00 (PCH) | 82-06 | 911820 | 14.2 | 14 | 11 | 35.5 | 31.7 | 32.3 | 32.9 | 32 | 32.3 | 32 | 31 | 31.7 | 32.2 | 32 | 31.6333 | 32 | 298 | United_StatesHawaiiHONOLULU INTL ARPT
United_States | Hawaii | KAHULUI AIRPORT | KAHULUI AIRPORT, HI, USA | 20.90N | 156.43W | 15 | -10.00 (PCH) | 82-06 | 911900 | 12.7 | 13 | 10.3 | 36.1 | 31.7 | 32.3 | 32.7 | 32 | 32.2333 | 32 | 30.6 | 31.2 | 31.7 | 31 | 31.1667 | 31 | 299 | United_StatesHawaiiKAHULUI AIRPORT
United_States | Hawaii | KANEOHE BAY MCAS | KANEOHE BAY MCAS, HI, USA | 21.45N | 157.77W | 6 | -10.00 (PCH) | 82-06 | 911760 | 16.3 | 16 | 10.5 | 33.7 | 28.9 | 29.6 | 30.2 | 30 | 29.5667 | 30 | 28.2 | 28.9 | 29.3 | 29 | 28.8 | 29 | 300 | United_StatesHawaiiKANEOHE BAY MCAS
United_States | Hawaii | KONA INTL AT KEAHOL | KONA INTL AT KEAHOL, HI, USA | 19.73N | 156.03W | 15 | -10.00 (PCH) | 89-06 | 911975 | 14.4 | 14 | 2.8 | 34.7 | 30.5 | 31.3 | 32 | 31 | 31.2667 | 31 | 29.1 | 30.2 | 31.2 | 30 | 30.1667 | 30 | 301 | United_StatesHawaiiKONA INTL AT KEAHOL
United_States | Hawaii | LIHUE AIRPORT | LIHUE AIRPORT, HI, USA | 21.98N | 159.34W | 45 | -10.00 (PCH) | 82-06 | 911650 | 13.7 | 14 | 10.7 | 32.7 | 29.4 | 29.6 | 30.3 | 30 | 29.7667 | 30 | 28.6 | 29.1 | 29.5 | 29 | 29.0667 | 29 | 302 | United_StatesHawaiiLIHUE AIRPORT
United_States | Hawaii | MOLOKAI (AMOS) | MOLOKAI (AMOS), HI, USA | 21.15N | 157.10W | 137 | -10.00 (PCH) | 82-06 | 911860 | 12.8 | 13 | 9.9 | 38.3 | 30.5 | 31.2 | 31.6 | 31 | 31.1 | 31 | 29.3 | 30 | 30.6 | 30 | 29.9667 | 30 | 303 | United_StatesHawaiiMOLOKAI (AMOS)
United_States | Idaho | BOISE AIR TERMINAL | BOISE AIR TERMINAL, ID, USA | 43.57N | 116.22W | 874 | -7.00 (NAM) | 82-06 | 726810 | -17.2 | -17 | -33.2 | 43.7 | 36.7 | 39.4 | 38.5 | 38 | 38.2 | 39 | 34.1 | 37.2 | 36.2 | 36 | 35.8333 | 36 | 304 | United_StatesIdahoBOISE AIR TERMINAL
United_States | Idaho | BURLEY MUNICIPAL ARPT | BURLEY MUNICIPAL ARPT, ID, USA | 42.54N | 113.77W | 1267 | -7.00 (NAM) | 82-06 | 725867 | -20.3 | -20 | -33.9 | 42.8 | 34.4 | 37.2 | 36.4 | 36 | 36 | 37 | 31.6 | 34.7 | 34.1 | 33 | 33.4667 | 33 | 305 | United_StatesIdahoBURLEY MUNICIPAL ARPT
United_States | Idaho | CALDWELL (AWOS) | CALDWELL (AWOS), ID, USA | 43.63N | 116.63W | 740 | -7.00 (NAM) | 92-06 | 726813 | -13.4 | -13 | -23 | 43.6 | 35.2 | 38.8 | 37.4 | 37 | 37.1333 | 39 | 32.5 | 37 | 35.2 | 35 | 34.9 | 35 | 306 | United_StatesIdahoCALDWELL (AWOS)
United_States | Idaho | CHALLIS | CHALLIS, ID, USA | 44.52N | 114.22W | 1546 | -7.00 (NAM) | 83-06 | 722142 | -29.3 | -29 | -39.6 | 41.1 | 33.4 | 36.1 | 34.2 | 35 | 34.5667 | 36 | 31 | 33.7 | 32.3 | 32 | 32.3333 | 32 | 307 | United_StatesIdahoCHALLIS
United_States | Idaho | COEUR D`ALENE(AWOS) | COEUR D`ALENE(AWOS), ID, USA | 47.77N | 116.82W | 707 | -8.00 (NAP) | 90-06 | 727834 | -17.7 | -18 | -29 | 41.6 | 32.2 | 36.4 | 35.3 | 35 | 34.6333 | 36 | 28.6 | 33.6 | 33.3 | 32 | 31.8333 | 32 | 308 | United_StatesIdahoCOEUR D`ALENE(AWOS)
United_States | Idaho | ELK CITY (RAMOS) | ELK CITY (RAMOS), ID, USA | 45.82N | 115.43W | 1249 | -8.00 (NAP) | 83-06 | 725784 | -15.4 | -15 | -25.9 | 42 | 35.9 | 37.5 | 38 | 37 | 37.1333 | 38 | 31.4 | 35.1 | 34.1 | 34 | 33.5333 | 34 | 309 | United_StatesIdahoELK CITY (RAMOS)
United_States | Idaho | IDAHO FALLS FANNING FIELD | IDAHO FALLS FANNING FIELD, ID, USA | 43.52N | 112.07W | 1446 | -7.00 (NAM) | 82-06 | 725785 | -26.1 | -26 | -40.6 | 40.7 | 33.2 | 35.5 | 35.1 | 35 | 34.6 | 36 | 30.8 | 33.7 | 33 | 33 | 32.5 | 33 | 310 | United_StatesIdahoIDAHO FALLS FANNING FIELD
United_States | Idaho | JOSLIN FLD MAGIC VA | JOSLIN FLD MAGIC VA, ID, USA | 42.48N | 114.48W | 1297 | -7.00 (NAM) | 97-06 | 725866 | -16.1 | -16 | -24.8 | 42.4 | 32.9 | 37.8 | 36.2 | 36 | 35.6333 | 38 | 31.3 | 36 | 33.9 | 34 | 33.7333 | 34 | 311 | United_StatesIdahoJOSLIN FLD MAGIC VA
United_States | Idaho | LEWISTON NEZ PERCE CNTY AP | LEWISTON NEZ PERCE CNTY AP, ID, USA | 46.38N | 117.01W | 438 | -8.00 (NAP) | 82-06 | 727830 | -14.2 | -14 | -27.9 | 44.1 | 35.9 | 39.5 | 38.7 | 38 | 38.0333 | 40 | 32.7 | 37.1 | 36.3 | 35 | 35.3667 | 35 | 312 | United_StatesIdahoLEWISTON NEZ PERCE CNTY AP
United_States | Idaho | MCCALL ARPT | MCCALL ARPT, ID, USA | 44.88N | 116.10W | 1530 | -7.00 (NAM) | 87-06 | 725864 | -26 | -26 | -32.5 | 37.1 | 29 | 32.7 | 31.3 | 31 | 31 | 33 | 27.1 | 30.9 | 29.5 | 29 | 29.1667 | 29 | 313 | United_StatesIdahoMCCALL ARPT
United_States | Idaho | MOUNTAIN HOME AFB | MOUNTAIN HOME AFB, ID, USA | 43.05N | 115.87W | 912 | -7.00 (NAM) | 82-06 | 726815 | -19 | -19 | -31.9 | 45.1 | 37.6 | 39.8 | 39.1 | 39 | 38.8333 | 40 | 34.6 | 37.8 | 37.2 | 37 | 36.5333 | 37 | 314 | United_StatesIdahoMOUNTAIN HOME AFB
United_States | Idaho | MULLAN (AWRS) | MULLAN (AWRS), ID, USA | 47.47N | 115.80W | 1011 | -8.00 (NAP) | 82-96 | 727836 | -21.1 | -21 | -32.4 | 36 | 30.7 | 32.4 | 32.4 | 32 | 31.8333 | 32 | 28.4 | 30.4 | 30.6 | 30 | 29.8 | 30 | 315 | United_StatesIdahoMULLAN (AWRS)
United_States | Idaho | POCATELLO REGIONAL AP | POCATELLO REGIONAL AP, ID, USA | 42.92N | 112.57W | 1365 | -7.00 (NAM) | 82-06 | 725780 | -24.3 | -24 | -39 | 41.2 | 34.4 | 37.3 | 36.4 | 36 | 36.0333 | 37 | 31.8 | 35.2 | 34.3 | 34 | 33.7667 | 34 | 316 | United_StatesIdahoPOCATELLO REGIONAL AP
United_States | Idaho | SALMON/LEMHI (AWOS) | SALMON/LEMHI (AWOS), ID, USA | 45.12N | 113.88W | 1233 | -7.00 (NAM) | 92-06 | 726865 | -23.6 | -24 | -32.8 | 40 | 31.6 | 36.2 | 33.6 | 34 | 33.8 | 36 | 28.7 | 33.5 | 31.9 | 31 | 31.3667 | 31 | 317 | United_StatesIdahoSALMON/LEMHI (AWOS)
United_States | Illinois | AURORA MUNICIPAL | AURORA MUNICIPAL, IL, USA | 41.77N | 88.47W | 215 | -6.00 (NAC) | 98-06 | 744655 | -24.9 | -25 | -32.3 | 40.7 | 33.8 | 35 | 33.8 | 34 | 34.2 | 35 | 32.4 | 32.8 | 31.8 | 32 | 32.3333 | 32 | 318 | United_StatesIllinoisAURORA MUNICIPAL
United_States | Illinois | CAHOKIA/ST. LOUIS | CAHOKIA/ST. LOUIS, IL, USA | 38.57N | 90.15W | 126 | -6.00 (NAC) | 97-06 | 725314 | -17.2 | -17 | -25.6 | 41.3 | 34.1 | 37.3 | 36.4 | 36 | 35.9333 | 37 | 32.8 | 35.8 | 33.9 | 34 | 34.1667 | 34 | 319 | United_StatesIllinoisCAHOKIA/ST. LOUIS
United_States | Illinois | CHICAGO MIDWAY AP | CHICAGO MIDWAY AP, IL, USA | 41.79N | 87.75W | 188 | -6.00 (NAC) | 82-06 | 725340 | -22.3 | -22 | -33.1 | 41.7 | 34.1 | 36.4 | 34.8 | 35 | 35.1 | 36 | 32.4 | 33.8 | 32.5 | 33 | 32.9 | 33 | 320 | United_StatesIllinoisCHICAGO MIDWAY AP
United_States | Illinois | CHICAGO OHARE INTL AP | CHICAGO OHARE INTL AP, IL, USA | 41.99N | 87.91W | 205 | -6.00 (NAC) | 82-06 | 725300 | -23.7 | -24 | -35.5 | 40.9 | 34.3 | 35.9 | 35 | 35 | 35.0667 | 36 | 32.4 | 33.6 | 32.4 | 33 | 32.8 | 33 | 321 | United_StatesIllinoisCHICAGO OHARE INTL AP
United_States | Illinois | DECATUR | DECATUR, IL, USA | 39.83N | 88.87W | 213 | -6.00 (NAC) | 82-06 | 725316 | -22 | -22 | -33 | 40.1 | 34.6 | 35.9 | 35.8 | 35 | 35.4333 | 36 | 32.7 | 33.9 | 33.4 | 33 | 33.3333 | 33 | 322 | United_StatesIllinoisDECATUR
United_States | Illinois | GLENVIEW NAS | GLENVIEW NAS, IL, USA | 42.08N | 87.82W | 199 | -6.00 (NAC) | 82-95 | 725306 | -24.3 | -24 | -36.3 | 40.7 | 35.1 | 36.1 | 36.7 | 36 | 35.9667 | 36 | 32.7 | 34.1 | 33.5 | 33 | 33.4333 | 33 | 323 | United_StatesIllinoisGLENVIEW NAS
United_States | Illinois | LAWRENCEVILLE\VIN. | LAWRENCEVILLE\VIN., IL, USA | 38.77N | 87.60W | 131 | -6.00 (NAC) | 97-06 | 725342 | -18.2 | -18 | -26.5 | 40.1 | 34 | 36.1 | 35.9 | 35 | 35.3333 | 36 | 32.7 | 34 | 33 | 33 | 33.2333 | 33 | 324 | United_StatesIllinoisLAWRENCEVILLE\VIN.
United_States | Illinois | MARSEILLES ISLAND | MARSEILLES ISLAND, IL, USA | 41.37N | 88.68W | 225 | -6.00 (NAC) | 82-96 | 744600 | -24.5 | -25 | -33.7 | 40.9 | 34.7 | 36.2 | 36.2 | 36 | 35.7 | 36 | 32.6 | 33.7 | 33.2 | 33 | 33.1667 | 33 | 325 | United_StatesIllinoisMARSEILLES ISLAND
United_States | Illinois | MATTOON/CHARLESTON | MATTOON/CHARLESTON, IL, USA | 39.48N | 88.28W | 220 | -6.00 (NAC) | 98-06 | 725317 | -19.7 | -20 | -27.7 | 38.4 | 32.9 | 35.2 | 33.8 | 34 | 33.9667 | 35 | 31.4 | 33 | 32.4 | 32 | 32.2667 | 32 | 326 | United_StatesIllinoisMATTOON/CHARLESTON
United_States | Illinois | MOLINE QUAD CITY INTL AP | MOLINE QUAD CITY INTL AP, IL, USA | 41.47N | 90.52W | 181 | -6.00 (NAC) | 82-06 | 725440 | -24.9 | -25 | -35.9 | 41 | 34.9 | 36.6 | 36.4 | 36 | 35.9667 | 37 | 32.9 | 34.3 | 33.4 | 34 | 33.5333 | 34 | 327 | United_StatesIllinoisMOLINE QUAD CITY INTL AP
United_States | Illinois | MOUNT VERNON (AWOS) | MOUNT VERNON (AWOS), IL, USA | 38.32N | 88.87W | 146 | -6.00 (NAC) | 92-06 | 724335 | -21.4 | -21 | -33.6 | 39 | 34.9 | 36.3 | 35.2 | 35 | 35.4667 | 36 | 33 | 34.1 | 33.7 | 34 | 33.6 | 34 | 328 | United_StatesIllinoisMOUNT VERNON (AWOS)
United_States | Illinois | PEORIA GREATER PEORIA AP | PEORIA GREATER PEORIA AP, IL, USA | 40.67N | 89.68W | 202 | -6.00 (NAC) | 82-06 | 725320 | -23.3 | -23 | -33.6 | 40.6 | 34.4 | 36.3 | 36.1 | 36 | 35.6 | 36 | 32.4 | 33.9 | 33.2 | 33 | 33.1667 | 33 | 329 | United_StatesIllinoisPEORIA GREATER PEORIA AP
United_States | Illinois | QUINCY MUNI BALDWIN FLD | QUINCY MUNI BALDWIN FLD, IL, USA | 39.94N | 91.19W | 234 | -6.00 (NAC) | 82-06 | 724396 | -22.7 | -23 | -32.5 | 41 | 34.1 | 37 | 36.8 | 36 | 35.9667 | 37 | 32.1 | 34.2 | 33.8 | 33 | 33.3667 | 33 | 330 | United_StatesIllinoisQUINCY MUNI BALDWIN FLD
United_States | Illinois | ROCKFORD GREATER ROCKFORD AP | ROCKFORD GREATER ROCKFORD AP, IL, USA | 42.20N | 89.09W | 227 | -6.00 (NAC) | 82-06 | 725430 | -26 | -26 | -36.5 | 40 | 34.5 | 35.1 | 35.2 | 35 | 34.9333 | 35 | 32.1 | 33.1 | 32.5 | 33 | 32.5667 | 33 | 331 | United_StatesIllinoisROCKFORD GREATER ROCKFORD AP
United_States | Illinois | SCOTT AFB/BELLEVILL | SCOTT AFB/BELLEVILL, IL, USA | 38.55N | 89.85W | 135 | -6.00 (NAC) | 82-06 | 724338 | -19 | -19 | -28 | 41 | 35.7 | 37.2 | 36.4 | 36 | 36.4333 | 37 | 33.7 | 35.1 | 34.8 | 35 | 34.5333 | 35 | 332 | United_StatesIllinoisSCOTT AFB/BELLEVILL
United_States | Illinois | SOUTHERN ILLINOIS | SOUTHERN ILLINOIS, IL, USA | 37.77N | 89.25W | 128 | -6.00 (NAC) | 96-06 | 724336 | -16.5 | -17 | -25.7 | 39.3 | 34 | 36.1 | 36.1 | 35 | 35.4 | 36 | 32.8 | 33.9 | 33.8 | 34 | 33.5 | 34 | 333 | United_StatesIllinoisSOUTHERN ILLINOIS
United_States | Illinois | SPRINGFIELD CAPITAL AP | SPRINGFIELD CAPITAL AP, IL, USA | 39.85N | 89.68W | 187 | -6.00 (NAC) | 82-06 | 724390 | -23.3 | -23 | -33.2 | 39.8 | 34.4 | 36 | 35.8 | 35 | 35.4 | 36 | 32.6 | 33.8 | 33.6 | 33 | 33.3333 | 33 | 334 | United_StatesIllinoisSPRINGFIELD CAPITAL AP
United_States | Illinois | STERLING ROCKFALLS | STERLING ROCKFALLS, IL, USA | 41.75N | 89.67W | 197 | -6.00 (NAC) | 92-06 | 725326 | -24.5 | -25 | -33.9 | 40.4 | 33.9 | 35.2 | 33.7 | 34 | 34.2667 | 35 | 32.3 | 32.5 | 31.6 | 32 | 32.1333 | 32 | 335 | United_StatesIllinoisSTERLING ROCKFALLS
United_States | Illinois | UNIV OF ILLINOIS WI | UNIV OF ILLINOIS WI, IL, USA | 40.03N | 88.27W | 236 | -6.00 (NAC) | 85-06 | 725315 | -23.1 | -23 | -33.6 | 40 | 35.1 | 35.8 | 35.1 | 35 | 35.3333 | 36 | 33 | 33.3 | 32.4 | 33 | 32.9 | 33 | 336 | United_StatesIllinoisUNIV OF ILLINOIS WI
United_States | Illinois | W. CHICAGO/DU PAGE | W. CHICAGO/DU PAGE, IL, USA | 41.92N | 88.25W | 231 | -6.00 (NAC) | 82-06 | 725305 | -24.3 | -24 | -33.8 | 40 | 33.9 | 34.6 | 34 | 34 | 34.1667 | 35 | 32.1 | 32.6 | 31.9 | 32 | 32.2 | 32 | 337 | United_StatesIllinoisW. CHICAGO/DU PAGE
United_States | Indiana | EVANSVILLE REGIONAL AP | EVANSVILLE REGIONAL AP, IN, USA | 38.04N | 87.54W | 118 | -6.00 (NAC) | 82-06 | 724320 | -18.8 | -19 | -31.4 | 39.7 | 35 | 36.4 | 36.2 | 36 | 35.8667 | 36 | 33.2 | 34.3 | 34.3 | 34 | 33.9333 | 34 | 338 | United_StatesIndianaEVANSVILLE REGIONAL AP
United_States | Indiana | FORT WAYNE INTL AP | FORT WAYNE INTL AP, IN, USA | 41.01N | 85.21W | 252 | -5.00 (NAE) | 82-06 | 725330 | -22.6 | -23 | -33.7 | 40 | 34.4 | 35.4 | 33.9 | 35 | 34.5667 | 35 | 32.4 | 32.9 | 31.7 | 32 | 32.3333 | 32 | 339 | United_StatesIndianaFORT WAYNE INTL AP
United_States | Indiana | GRISSOM ARB | GRISSOM ARB, IN, USA | 40.65N | 86.15W | 253 | -5.00 (NAE) | 82-01 | 725335 | -22.5 | -23 | -33.2 | 41.3 | 34.6 | 36.1 | 35.4 | 35 | 35.3667 | 36 | 32.4 | 33.7 | 32.5 | 33 | 32.8667 | 33 | 340 | United_StatesIndianaGRISSOM ARB
United_States | Indiana | HUNTINGBURG | HUNTINGBURG, IN, USA | 38.25N | 86.95W | 161 | -5.00 (NAE) | 94-06 | 724365 | N/A | N/A | N/A | N/A | 33.1 | 34.8 | 34 | 34 | 33.9667 | 35 | 32.3 | 32.9 | 32.7 | 33 | 32.6333 | 33 | 341 | United_StatesIndianaHUNTINGBURG
United_States | Indiana | INDIANAPOLIS INTL AP | INDIANAPOLIS INTL AP, IN, USA | 39.71N | 86.27W | 246 | -5.00 (NAE) | 82-06 | 724380 | -22.1 | -22 | -35.5 | 38.9 | 33.4 | 35.4 | 34.2 | 34 | 34.3333 | 35 | 31.7 | 33 | 32.3 | 32 | 32.3333 | 32 | 342 | United_StatesIndianaINDIANAPOLIS INTL AP
United_States | Indiana | LAFAYETTE PURDUE UNIV AP | LAFAYETTE PURDUE UNIV AP, IN, USA | 40.41N | 86.94W | 194 | -5.00 (NAE) | 82-06 | 724386 | -22.8 | -23 | -34.9 | 40.7 | 34.6 | 36.4 | 34.7 | 35 | 35.2333 | 36 | 32.8 | 33.9 | 32.7 | 33 | 33.1333 | 33 | 343 | United_StatesIndianaLAFAYETTE PURDUE UNIV AP
United_States | Indiana | MONROE CO | MONROE CO, IN, USA | 39.13N | 86.62W | 264 | -5.00 (NAE) | 98-06 | 724375 | -21.2 | -21 | -34.4 | 39.5 | 32.7 | 34.1 | 33 | 33 | 33.2667 | 34 | 32 | 32.7 | 32.3 | 32 | 32.3333 | 32 | 344 | United_StatesIndianaMONROE CO
United_States | Indiana | SOUTH BEND MICHIANA RGNL AP | SOUTH BEND MICHIANA RGNL AP, IN, USA | 41.71N | 86.33W | 236 | -5.00 (NAE) | 82-06 | 725350 | -22.2 | -22 | -32.6 | 40.2 | 34.2 | 35.5 | 34.1 | 35 | 34.6 | 36 | 32 | 32.9 | 31.6 | 32 | 32.1667 | 32 | 345 | United_StatesIndianaSOUTH BEND MICHIANA RGNL AP
United_States | Indiana | TERRE HAUTE/HULMAN | TERRE HAUTE/HULMAN, IN, USA | 39.45N | 87.32W | 175 | -5.00 (NAI) | 82-06 | 724373 | -22.5 | -23 | -34.7 | 40.1 | 34.8 | 35.8 | 34.1 | 35 | 34.9 | 36 | 32.9 | 33.7 | 32.6 | 33 | 33.0667 | 33 | 346 | United_StatesIndianaTERRE HAUTE/HULMAN
United_States | Iowa | AMES MUNI ARPT | AMES MUNI ARPT, IA, USA | 42.00N | 93.62W | 291 | -6.00 (NAC) | 97-06 | 725472 | -25.6 | -26 | -33.7 | 38.7 | 32.9 | 34 | 32.9 | 33 | 33.2667 | 34 | 32 | 32.6 | 31.2 | 32 | 31.9333 | 32 | 347 | United_StatesIowaAMES MUNI ARPT
United_States | Iowa | ANKENY REGIONAL ARP | ANKENY REGIONAL ARP, IA, USA | 41.68N | 93.55W | 275 | -6.00 (NAC) | 82-06 | 725466 | -22.2 | -22 | -29.5 | 42.7 | 36 | 37.2 | 37.8 | 37 | 37 | 37 | 32.7 | 34.9 | 35 | 34 | 34.2 | 34 | 348 | United_StatesIowaANKENY REGIONAL ARP
United_States | Iowa | ATLANTIC | ATLANTIC, IA, USA | 41.40N | 95.05W | 360 | -6.00 (NAC) | 95-06 | 725453 | N/A | N/A | N/A | N/A | 34 | 36 | 36.2 | 35 | 35.4 | 36 | 32.6 | 34 | 33 | 33 | 33.2 | 33 | 349 | United_StatesIowaATLANTIC
United_States | Iowa | BOONE MUNI | BOONE MUNI, IA, USA | 42.05N | 93.85W | 354 | -6.00 (NAC) | 95-06 | 725486 | N/A | N/A | N/A | N/A | 33.8 | 35.1 | 34.8 | 35 | 34.5667 | 35 | 32.3 | 33.5 | 32.4 | 33 | 32.7333 | 33 | 350 | United_StatesIowaBOONE MUNI
United_States | Iowa | BURLINGTON MUNICIPAL AP | BURLINGTON MUNICIPAL AP, IA, USA | 40.78N | 91.13W | 214 | -6.00 (NAC) | 82-06 | 725455 | -23 | -23 | -33.1 | 41 | 34.6 | 36.6 | 36 | 36 | 35.7333 | 37 | 32.7 | 34.4 | 33.1 | 33 | 33.4 | 33 | 351 | United_StatesIowaBURLINGTON MUNICIPAL AP
United_States | Iowa | CARROLL | CARROLL, IA, USA | 42.05N | 94.78W | 375 | -6.00 (NAC) | 95-06 | 725468 | N/A | N/A | N/A | N/A | 35.1 | 35.2 | 35 | 35 | 35.1 | 35 | 33.3 | 33 | 32.7 | 33 | 33 | 33 | 352 | United_StatesIowaCARROLL
United_States | Iowa | CEDAR RAPIDS MUNICIPAL AP | CEDAR RAPIDS MUNICIPAL AP, IA, USA | 41.88N | 91.71W | 266 | -6.00 (NAC) | 82-06 | 725450 | -26.3 | -26 | -34.1 | 39.7 | 33.8 | 35.5 | 35.5 | 35 | 34.9333 | 36 | 31.8 | 33.2 | 32.7 | 33 | 32.5667 | 33 | 353 | United_StatesIowaCEDAR RAPIDS MUNICIPAL AP
United_States | Iowa | CHARITON | CHARITON, IA, USA | 41.03N | 93.37W | 320 | -6.00 (NAC) | 95-06 | 725469 | -22.7 | -23 | -33.1 | 40.3 | 33.9 | 37.1 | 34.8 | 35 | 35.2667 | 37 | 32.4 | 34.9 | 32.9 | 33 | 33.4 | 33 | 354 | United_StatesIowaCHARITON
United_States | Iowa | CHARLES CITY | CHARLES CITY, IA, USA | 43.07N | 92.62W | 343 | -6.00 (NAC) | 95-06 | 725463 | N/A | N/A | N/A | N/A | 33.8 | 33 | 32.5 | 33 | 33.1 | 33 | 32.1 | 32.4 | 30.9 | 32 | 31.8 | 32 | 355 | United_StatesIowaCHARLES CITY
United_States | Iowa | CLARION | CLARION, IA, USA | 42.75N | 93.77W | 354 | -6.00 (NAC) | 95-06 | 725458 | N/A | N/A | N/A | N/A | 34 | 35.1 | 32.7 | 34 | 33.9333 | 35 | 32.3 | 32.9 | 31.2 | 32 | 32.1333 | 32 | 356 | United_StatesIowaCLARION
United_States | Iowa | CLINTON MUNI (AWOS) | CLINTON MUNI (AWOS), IA, USA | 41.83N | 90.33W | 216 | -6.00 (NAC) | 92-06 | 725473 | -24.8 | -25 | -32.9 | 38.3 | 33.7 | 34.5 | 33 | 34 | 33.7333 | 35 | 32.2 | 32.5 | 31.3 | 32 | 32 | 32 | 357 | United_StatesIowaCLINTON MUNI (AWOS)
United_States | Iowa | CRESTON | CRESTON, IA, USA | 41.02N | 94.37W | 394 | -6.00 (NAC) | 95-06 | 725474 | -23.1 | -23 | -29.3 | 43.1 | 32.7 | 36.3 | 36.4 | 35 | 35.1333 | 36 | 32.1 | 34.7 | 33.6 | 33 | 33.4667 | 33 | 358 | United_StatesIowaCRESTON
United_States | Iowa | DAVENPORT NEXRAD | DAVENPORT NEXRAD, IA, USA | 41.62N | 90.58W | 259 | -6.00 (NAC) | 97-06 | 725349 | -24.6 | -25 | -32.5 | 37.9 | 32.8 | 34 | 32.7 | 33 | 33.1667 | 34 | 31.4 | 32.5 | 31.2 | 32 | 31.7 | 32 | 359 | United_StatesIowaDAVENPORT NEXRAD
United_States | Iowa | DES MOINES INTL AP | DES MOINES INTL AP, IA, USA | 41.54N | 93.67W | 294 | -6.00 (NAC) | 82-06 | 725460 | -24.6 | -25 | -33 | 41.9 | 34.6 | 36.6 | 37.1 | 36 | 36.1 | 37 | 32 | 34.2 | 33.9 | 33 | 33.3667 | 33 | 360 | United_StatesIowaDES MOINES INTL AP
United_States | Iowa | DUBUQUE REGIONAL AP | DUBUQUE REGIONAL AP, IA, USA | 42.40N | 90.70W | 329 | -6.00 (NAC) | 87-06 | 725470 | -26.1 | -26 | -34.5 | 38.7 | 32.9 | 34.1 | 33.9 | 34 | 33.6333 | 34 | 30.7 | 32 | 31.1 | 31 | 31.2667 | 31 | 361 | United_StatesIowaDUBUQUE REGIONAL AP
United_States | Iowa | ESTHERVILLE MUNI | ESTHERVILLE MUNI, IA, USA | 43.40N | 94.75W | 401 | -6.00 (NAC) | 96-06 | 726499 | -26 | -26 | -30.5 | 37.6 | 33.9 | 33.9 | 32.2 | 33 | 33.3333 | 34 | 32.2 | 32.3 | 29.8 | 31 | 31.4333 | 31 | 362 | United_StatesIowaESTHERVILLE MUNI
United_States | Iowa | FAIR FIELD | FAIR FIELD, IA, USA | 41.05N | 91.98W | 244 | -6.00 (NAC) | 95-06 | 726498 | N/A | N/A | N/A | N/A | 34.1 | 37.3 | 36.1 | 36 | 35.8333 | 37 | 32.7 | 35 | 33.7 | 34 | 33.8 | 34 | 363 | United_StatesIowaFAIR FIELD
United_States | Iowa | FORT DODGE (AWOS) | FORT DODGE (AWOS), IA, USA | 42.55N | 94.18W | 355 | -6.00 (NAC) | 82-06 | 725490 | -27.2 | -27 | -34.7 | 41.1 | 34.2 | 34.7 | 35.1 | 35 | 34.6667 | 35 | 32.1 | 32.8 | 32.2 | 32 | 32.3667 | 32 | 364 | United_StatesIowaFORT DODGE (AWOS)
United_States | Iowa | KEOKUK MUNI | KEOKUK MUNI, IA, USA | 40.47N | 91.43W | 205 | -6.00 (NAC) | 95-06 | 725456 | N/A | N/A | N/A | N/A | 33 | 37.7 | 36.2 | 36 | 35.6333 | 38 | 32.3 | 35.2 | 34 | 34 | 33.8333 | 34 | 365 | United_StatesIowaKEOKUK MUNI
United_States | Iowa | MARSHALL TOWN MUNI | MARSHALL TOWN MUNI, IA, USA | 42.10N | 92.92W | 296 | -6.00 (NAC) | 99-06 | 725461 | -25.9 | -26 | -33.5 | 37.9 | 32.4 | 33.9 | 32.9 | 33 | 33.0667 | 34 | 31.1 | 32.5 | 31.2 | 32 | 31.6 | 32 | 366 | United_StatesIowaMARSHALL TOWN MUNI
United_States | Iowa | MASON CITY MUNICIPAL ARPT | MASON CITY MUNICIPAL ARPT, IA, USA | 43.16N | 93.33W | 373 | -6.00 (NAC) | 82-06 | 725485 | -28.3 | -28 | -37.1 | 40.8 | 34.5 | 35 | 34.4 | 35 | 34.6333 | 35 | 32 | 32.8 | 31.5 | 32 | 32.1 | 32 | 367 | United_StatesIowaMASON CITY MUNICIPAL ARPT
United_States | Iowa | OTTUMWA INDUSTRIAL AP | OTTUMWA INDUSTRIAL AP, IA, USA | 41.11N | 92.45W | 258 | -6.00 (NAC) | 82-06 | 725465 | -23.5 | -24 | -32.4 | 41.3 | 34.9 | 36.7 | 36.6 | 36 | 36.0667 | 37 | 32.4 | 34.5 | 33.2 | 33 | 33.3667 | 33 | 368 | United_StatesIowaOTTUMWA INDUSTRIAL AP
United_States | Iowa | SIOUX CITY SIOUX GATEWAY AP | SIOUX CITY SIOUX GATEWAY AP, IA, USA | 42.39N | 96.38W | 336 | -6.00 (NAC) | 82-06 | 725570 | -26.2 | -26 | -33.2 | 42.7 | 36.1 | 36.5 | 35.6 | 36 | 36.0667 | 37 | 33.3 | 34 | 33 | 33 | 33.4333 | 33 | 369 | United_StatesIowaSIOUX CITY SIOUX GATEWAY AP
United_States | Iowa | SPENCER | SPENCER, IA, USA | 43.17N | 95.15W | 408 | -6.00 (NAC) | 82-06 | 726500 | -28 | -28 | -33.3 | 41 | 35 | 36 | 33.9 | 35 | 34.9667 | 36 | 32.4 | 32.9 | 31.7 | 32 | 32.3333 | 32 | 370 | United_StatesIowaSPENCER
United_States | Iowa | STORM LAKE | STORM LAKE, IA, USA | 42.60N | 95.23W | 454 | -6.00 (NAC) | 95-06 | 725496 | N/A | N/A | N/A | N/A | 34.9 | 36.1 | 33 | 35 | 34.6667 | 36 | 32.8 | 33 | 31.9 | 33 | 32.5667 | 33 | 371 | United_StatesIowaSTORM LAKE
United_States | Iowa | WASHINGTON | WASHINGTON, IA, USA | 41.28N | 91.67W | 230 | -6.00 (NAC) | 95-06 | 725454 | N/A | N/A | N/A | N/A | 34.7 | 36.1 | 34.9 | 35 | 35.2333 | 36 | 32.8 | 34.1 | 32.8 | 33 | 33.2333 | 33 | 372 | United_StatesIowaWASHINGTON
United_States | Iowa | WATERLOO MUNICIPAL AP | WATERLOO MUNICIPAL AP, IA, USA | 42.55N | 92.40W | 268 | -6.00 (NAC) | 82-06 | 725480 | -27.7 | -28 | -38.3 | 41 | 34.5 | 35.5 | 35.8 | 35 | 35.2667 | 36 | 32.1 | 33.2 | 32.3 | 33 | 32.5333 | 33 | 373 | United_StatesIowaWATERLOO MUNICIPAL AP
United_States | Iowa | WEBSTER CITY | WEBSTER CITY, IA, USA | 42.43N | 93.87W | 342 | -6.00 (NAC) | 95-06 | 725478 | -25.1 | -25 | -30.7 | 38.5 | 34.9 | 35.2 | 33.8 | 35 | 34.6333 | 35 | 32.9 | 34 | 32.2 | 33 | 33.0333 | 33 | 374 | United_StatesIowaWEBSTER CITY
United_States | Kansas | CHANUTE MARTIN JOHNSON AP | CHANUTE MARTIN JOHNSON AP, KS, USA | 37.67N | 95.48W | 308 | -6.00 (NAC) | 82-06 | 724507 | -19.4 | -19 | -26 | 44.1 | 34.1 | 38.2 | 38.7 | 37 | 37 | 38 | 32.4 | 36.6 | 37.1 | 35 | 35.3667 | 35 | 375 | United_StatesKansasCHANUTE MARTIN JOHNSON AP
United_States | Kansas | COFFEYVILLE MUNI | COFFEYVILLE MUNI, KS, USA | 37.10N | 95.57W | 230 | -6.00 (NAC) | 97-06 | 724519 | -17.4 | -17 | -27.8 | 45 | 36 | 38 | 39.8 | 38 | 37.9333 | 38 | 32.9 | 37.3 | 37.8 | 36 | 36 | 36 | 376 | United_StatesKansasCOFFEYVILLE MUNI
United_States | Kansas | CONCORDIA BLOSSER MUNI AP | CONCORDIA BLOSSER MUNI AP, KS, USA | 39.55N | 97.65W | 452 | -6.00 (NAC) | 82-06 | 724580 | -21.2 | -21 | -31.4 | 45.2 | 37.4 | 40.3 | 39.5 | 39 | 39.0667 | 40 | 34.9 | 37.9 | 37.2 | 37 | 36.6667 | 37 | 377 | United_StatesKansasCONCORDIA BLOSSER MUNI AP
United_States | Kansas | DODGE CITY REGIONAL AP | DODGE CITY REGIONAL AP, KS, USA | 37.77N | 99.97W | 790 | -6.00 (NAC) | 82-06 | 724510 | -20 | -20 | -29.1 | 44.1 | 38.4 | 39.9 | 39.1 | 39 | 39.1333 | 40 | 35.6 | 38.2 | 37.4 | 37 | 37.0667 | 37 | 378 | United_StatesKansasDODGE CITY REGIONAL AP
United_States | Kansas | ELKHART (AWOS) | ELKHART (AWOS), KS, USA | 37.00N | 101.90W | 1099 | -6.00 (NAC) | 92-06 | 724604 | N/A | N/A | N/A | N/A | 38 | 39 | 37.9 | 38 | 38.3 | 39 | 36.9 | 37.6 | 36.4 | 37 | 36.9667 | 37 | 379 | United_StatesKansasELKHART (AWOS)
United_States | Kansas | FT RILEY/MARSHALL A | FT RILEY/MARSHALL A, KS, USA | 39.05N | 96.77W | 324 | -6.00 (NAC) | 82-95 | 724550 | -20.4 | -20 | -33.9 | 43.1 | 38.1 | 39.9 | 39.4 | 39 | 39.1333 | 40 | 34.9 | 37.7 | 37.5 | 37 | 36.7 | 37 | 380 | United_StatesKansasFT RILEY/MARSHALL A
United_States | Kansas | GARDEN CITY MUNICIPAL AP | GARDEN CITY MUNICIPAL AP, KS, USA | 37.93N | 100.73W | 878 | -6.00 (NAC) | 82-06 | 724515 | -21.7 | -22 | -30.7 | 43.5 | 39 | 39.1 | 39.1 | 39 | 39.0667 | 39 | 36.1 | 37.4 | 36.9 | 37 | 36.8 | 37 | 381 | United_StatesKansasGARDEN CITY MUNICIPAL AP
United_States | Kansas | GOODLAND RENNER FIELD | GOODLAND RENNER FIELD, KS, USA | 39.37N | 101.69W | 1124 | -7.00 (NAM) | 82-06 | 724650 | -23.1 | -23 | -34.2 | 42.2 | 37.4 | 38.6 | 37.5 | 38 | 37.8333 | 39 | 35 | 36.7 | 35.4 | 36 | 35.7 | 36 | 382 | United_StatesKansasGOODLAND RENNER FIELD
United_States | Kansas | GREAT BEND (AWOS) | GREAT BEND (AWOS), KS, USA | 38.35N | 98.87W | 575 | -6.00 (NAC) | 92-06 | 724517 | -19 | -19 | -22.7 | 44.2 | 37.9 | 40.7 | 38.8 | 39 | 39.1333 | 41 | 35.3 | 37.9 | 37.3 | 37 | 36.8333 | 37 | 383 | United_StatesKansasGREAT BEND (AWOS)
United_States | Kansas | HAYS MUNI (AWOS) | HAYS MUNI (AWOS), KS, USA | 38.85N | 99.27W | 609 | -6.00 (NAC) | 92-06 | 724518 | -20 | -20 | -24.3 | 45 | 38.9 | 41.2 | 39.2 | 40 | 39.7667 | 41 | 36.2 | 38.9 | 37.6 | 38 | 37.5667 | 38 | 384 | United_StatesKansasHAYS MUNI (AWOS)
United_States | Kansas | HILL CITY MUNICIPAL AP | HILL CITY MUNICIPAL AP, KS, USA | 39.38N | 99.83W | 677 | -6.00 (NAC) | 96-06 | 724655 | -21 | -21 | -28 | 44.1 | 38 | 42 | 39.8 | 40 | 39.9333 | 42 | 36.3 | 39.1 | 37.5 | 38 | 37.6333 | 38 | 385 | United_StatesKansasHILL CITY MUNICIPAL AP
United_States | Kansas | LAWRENCE MUNI ARPT | LAWRENCE MUNI ARPT, KS, USA | 39.00N | 95.22W | 254 | -6.00 (NAC) | 97-06 | 724508 | -21.2 | -21 | -31.7 | 44.7 | 34.9 | 38.7 | 40.2 | 38 | 37.9333 | 39 | 32.9 | 37.2 | 37.5 | 36 | 35.8667 | 36 | 386 | United_StatesKansasLAWRENCE MUNI ARPT
United_States | Kansas | LIBERAL MUNI | LIBERAL MUNI, KS, USA | 37.03N | 100.95W | 901 | -6.00 (NAC) | 92-06 | 724516 | -17.8 | -18 | -24.7 | 43 | 38.8 | 39 | 38 | 39 | 38.6 | 39 | 36.3 | 37.7 | 37.2 | 37 | 37.0667 | 37 | 387 | United_StatesKansasLIBERAL MUNI
United_States | Kansas | MANHATTAN RGNL | MANHATTAN RGNL, KS, USA | 39.13N | 96.67W | 330 | -6.00 (NAC) | 96-06 | 724555 | -21.6 | -22 | -29.6 | 45.3 | 36.3 | 40 | 41.1 | 39 | 39.1333 | 40 | 34 | 37.9 | 37.7 | 37 | 36.5333 | 37 | 388 | United_StatesKansasMANHATTAN RGNL
United_States | Kansas | MCCONNELL AFB | MCCONNELL AFB, KS, USA | 37.62N | 97.27W | 414 | -6.00 (NAC) | 82-06 | 724505 | -17.4 | -17 | -26.9 | 44.9 | 37.5 | 40.1 | 39.9 | 39 | 39.1667 | 40 | 35 | 37.7 | 37.8 | 37 | 36.8333 | 37 | 389 | United_StatesKansasMCCONNELL AFB
United_States | Kansas | MEDICINE LODGE ASOS | MEDICINE LODGE ASOS, KS, USA | 37.28N | 98.55W | 469 | -6.00 (NAC) | 83-06 | 724520 | -17.1 | -17 | -27.2 | 46 | 39.1 | 41.4 | 40.7 | 40 | 40.4 | 41 | 36.5 | 39.6 | 38.9 | 38 | 38.3333 | 38 | 390 | United_StatesKansasMEDICINE LODGE ASOS
United_States | Kansas | NEWTON (AWOS) | NEWTON (AWOS), KS, USA | 38.05N | 97.28W | 467 | -6.00 (NAC) | 92-06 | 724509 | -17.4 | -17 | -25.9 | 43.2 | 35.9 | 39.8 | 37.9 | 38 | 37.8667 | 40 | 33.1 | 37.6 | 37 | 36 | 35.9 | 36 | 391 | United_StatesKansasNEWTON (AWOS)
United_States | Kansas | OLATHE/JOHNSON CO. | OLATHE/JOHNSON CO., KS, USA | 38.85N | 94.73W | 334 | -6.00 (NAC) | 96-06 | 724468 | -19.5 | -20 | -25 | 42.5 | 32.8 | 37.4 | 37.8 | 36 | 36 | 37 | 32 | 35.9 | 36.1 | 35 | 34.6667 | 35 | 392 | United_StatesKansasOLATHE/JOHNSON CO.
United_States | Kansas | PARSONS\TRI CITY | PARSONS\TRI CITY, KS, USA | 37.33N | 95.52W | 274 | -6.00 (NAC) | 97-06 | 745431 | -18.6 | -19 | -25.5 | 44.4 | 34.8 | 37.8 | 38.9 | 37 | 37.1667 | 38 | 32.7 | 36.4 | 37.5 | 36 | 35.5333 | 36 | 393 | United_StatesKansasPARSONS\TRI CITY
United_States | Kansas | RUSSELL MUNICIPAL AP | RUSSELL MUNICIPAL AP, KS, USA | 38.87N | 98.83W | 568 | -6.00 (NAC) | 82-06 | 724585 | -21.3 | -21 | -30.9 | 45.5 | 38 | 40.9 | 39.1 | 39 | 39.3333 | 41 | 35.7 | 38.7 | 37.3 | 37 | 37.2333 | 37 | 394 | United_StatesKansasRUSSELL MUNICIPAL AP
United_States | Kansas | SALINA MUNICIPAL AP | SALINA MUNICIPAL AP, KS, USA | 38.81N | 97.66W | 391 | -6.00 (NAC) | 82-06 | 724586 | -20.2 | -20 | -31.1 | 44.9 | 38 | 41.3 | 40.1 | 40 | 39.8 | 41 | 36.1 | 39 | 38 | 38 | 37.7 | 38 | 395 | United_StatesKansasSALINA MUNICIPAL AP
United_States | Kansas | TOPEKA FORBES FIELD | TOPEKA FORBES FIELD, KS, USA | 38.95N | 95.66W | 329 | -6.00 (NAC) | 82-06 | 724565 | -20.4 | -20 | -30.4 | 44.3 | 34.8 | 38.1 | 38.6 | 37 | 37.1667 | 38 | 33 | 36.1 | 35.9 | 35 | 35 | 35 | 396 | United_StatesKansasTOPEKA FORBES FIELD
United_States | Kansas | TOPEKA MUNICIPAL AP | TOPEKA MUNICIPAL AP, KS, USA | 39.07N | 95.63W | 270 | -6.00 (NAC) | 82-06 | 724560 | -20.9 | -21 | -31.8 | 43.8 | 35.2 | 37.9 | 39.1 | 37 | 37.4 | 38 | 33.2 | 36.2 | 36.3 | 35 | 35.2333 | 35 | 397 | United_StatesKansasTOPEKA MUNICIPAL AP
United_States | Kansas | WICHITA MID-CONTINENT AP | WICHITA MID-CONTINENT AP, KS, USA | 37.65N | 97.43W | 408 | -6.00 (NAC) | 82-06 | 724500 | -18.2 | -18 | -28.6 | 44.7 | 38 | 40.5 | 39.7 | 39 | 39.4 | 41 | 35.2 | 38.3 | 37.7 | 37 | 37.0667 | 37 | 398 | United_StatesKansasWICHITA MID-CONTINENT AP
United_States | Kansas | WICHITA/COL. JABARA | WICHITA/COL. JABARA, KS, USA | 37.75N | 97.22W | 433 | -6.00 (NAC) | 95-06 | 724504 | -16.9 | -17 | -26.6 | 44.9 | 35.3 | 40.8 | 39.1 | 38 | 38.4 | 41 | 32.9 | 37.8 | 37.6 | 36 | 36.1 | 36 | 399 | United_StatesKansasWICHITA/COL. JABARA
United_States | Kansas | WINFIELD\ARK CITY | WINFIELD\ARK CITY, KS, USA | 37.30N | 97.00W | 353 | -6.00 (NAC) | 99-06 | 724502 | -17.2 | -17 | -21.6 | 44.4 | 36.3 | 40.1 | 40.9 | 39 | 39.1 | 40 | 33.7 | 38 | 38 | 37 | 36.5667 | 37 | 400 | United_StatesKansasWINFIELD\ARK CITY
United_States | Kentucky | BOWLING GREEN WARREN CO AP | BOWLING GREEN WARREN CO AP, KY, USA | 36.98N | 86.44W | 164 | -6.00 (NAC) | 82-06 | 746716 | -17 | -17 | -30.1 | 41.3 | 33.8 | 36.2 | 35.8 | 35 | 35.2667 | 36 | 32.4 | 33.9 | 33.9 | 33 | 33.4 | 33 | 401 | United_StatesKentuckyBOWLING GREEN WARREN CO AP
United_States | Kentucky | CAPITAL CITY ARPT | CAPITAL CITY ARPT, KY, USA | 38.18N | 84.90W | 245 | -5.00 (NAE) | 97-06 | 724233 | -17.2 | -17 | -25.7 | 41.5 | 32.8 | 34.8 | 35.9 | 35 | 34.5 | 35 | 31.4 | 32.9 | 32.9 | 32 | 32.4 | 32 | 402 | United_StatesKentuckyCAPITAL CITY ARPT
United_States | Kentucky | CINCINNATI NORTHERN KY AP | CINCINNATI NORTHERN KY AP, KY, USA | 39.04N | 84.67W | 269 | -5.00 (NAE) | 82-06 | 724210 | -20.9 | -21 | -34.2 | 40 | 33.5 | 35.6 | 34.8 | 35 | 34.6333 | 36 | 31.5 | 33.2 | 32.6 | 32 | 32.4333 | 32 | 403 | United_StatesKentuckyCINCINNATI NORTHERN KY AP
United_States | Kentucky | FORT CAMPBELL (AAF) | FORT CAMPBELL (AAF), KY, USA | 36.67N | 87.50W | 173 | -6.00 (NAC) | 82-06 | 746710 | -16.3 | -16 | -28.3 | 40.7 | 35 | 36.7 | 36.4 | 36 | 36.0333 | 37 | 32.9 | 34.5 | 34.6 | 34 | 34 | 34 | 404 | United_StatesKentuckyFORT CAMPBELL (AAF)
United_States | Kentucky | FORT KNOX/GODMAN | FORT KNOX/GODMAN, KY, USA | 37.90N | 85.97W | 239 | -5.00 (NAE) | 82-06 | 724240 | -17.8 | -18 | -30.1 | 41.5 | 34 | 36.9 | 36 | 36 | 35.6333 | 37 | 32.3 | 34 | 33.7 | 33 | 33.3333 | 33 | 405 | United_StatesKentuckyFORT KNOX/GODMAN
United_States | Kentucky | HENDERSON CITY | HENDERSON CITY, KY, USA | 37.82N | 87.68W | 117 | -6.00 (NAC) | 92-06 | 724238 | -19.4 | -19 | -36.7 | 38.5 | 34 | 35.1 | 36.1 | 35 | 35.0667 | 35 | 32.8 | 33.5 | 33.8 | 33 | 33.3667 | 33 | 406 | United_StatesKentuckyHENDERSON CITY
United_States | Kentucky | JACKSON JULIAN CARROLL AP | JACKSON JULIAN CARROLL AP, KY, USA | 37.59N | 83.31W | 414 | -5.00 (NAE) | 82-06 | 724236 | -17.9 | -18 | -30.9 | 38.5 | 32.1 | 34 | 34.1 | 33 | 33.4 | 34 | 30.4 | 32 | 31.9 | 31 | 31.4333 | 31 | 407 | United_StatesKentuckyJACKSON JULIAN CARROLL AP
United_States | Kentucky | LEXINGTON BLUEGRASS AP | LEXINGTON BLUEGRASS AP, KY, USA | 38.04N | 84.61W | 301 | -5.00 (NAE) | 82-06 | 724220 | -18.8 | -19 | -31.5 | 40.3 | 33.5 | 35.2 | 35 | 35 | 34.5667 | 35 | 31.5 | 33.2 | 33 | 33 | 32.5667 | 33 | 408 | United_StatesKentuckyLEXINGTON BLUEGRASS AP
United_States | Kentucky | LONDON-CORBIN AP | LONDON-CORBIN AP, KY, USA | 37.09N | 84.08W | 369 | -5.00 (NAE) | 82-06 | 724243 | -18 | -18 | -31.2 | 38.9 | 32.3 | 33.8 | 34 | 33 | 33.3667 | 34 | 30.7 | 32.3 | 32.3 | 32 | 31.7667 | 32 | 409 | United_StatesKentuckyLONDON-CORBIN AP
United_States | Kentucky | LOUISVILLE BOWMAN FIELD | LOUISVILLE BOWMAN FIELD, KY, USA | 38.23N | 85.66W | 170 | -5.00 (NAE) | 82-06 | 724235 | -17.7 | -18 | -31.5 | 41.6 | 34.4 | 37 | 36.2 | 36 | 35.8667 | 37 | 32.7 | 34.1 | 33.9 | 34 | 33.5667 | 34 | 410 | United_StatesKentuckyLOUISVILLE BOWMAN FIELD
United_States | Kentucky | LOUISVILLE STANDIFORD FIELD | LOUISVILLE STANDIFORD FIELD, KY, USA | 38.18N | 85.73W | 149 | -5.00 (NAE) | 82-06 | 724230 | -17.3 | -17 | -30.6 | 40.8 | 34.1 | 36.3 | 35.8 | 35 | 35.4 | 36 | 32.6 | 34.2 | 34 | 34 | 33.6 | 34 | 411 | United_StatesKentuckyLOUISVILLE STANDIFORD FIELD
United_States | Kentucky | PADUCAH BARKLEY REGIONAL AP | PADUCAH BARKLEY REGIONAL AP, KY, USA | 37.06N | 88.77W | 126 | -6.00 (NAC) | 82-06 | 724350 | -17.1 | -17 | -28.3 | 40 | 35 | 36.4 | 36.5 | 36 | 35.9667 | 36 | 33.4 | 34.7 | 34.7 | 34 | 34.2667 | 34 | 412 | United_StatesKentuckyPADUCAH BARKLEY REGIONAL AP
United_States | Kentucky | SOMERSET(AWOS) | SOMERSET(AWOS), KY, USA | 38.00N | 84.60W | 283 | -5.00 (NAE) | 92-06 | 724354 | -13 | -13 | -18.4 | 41.4 | 34.2 | 36.5 | 36.4 | 36 | 35.7 | 37 | 32.9 | 34.7 | 34.6 | 34 | 34.0667 | 34 | 413 | United_StatesKentuckySOMERSET(AWOS)
United_States | Louisiana | ALEXANDRIA ESLER REGIONAL AP | ALEXANDRIA ESLER REGIONAL AP, LA, USA | 31.40N | 92.30W | 36 | -6.00 (NAC) | 87-06 | 722487 | -6.6 | -7 | -10.3 | 44 | 36.2 | 37.7 | 38.1 | 37 | 37.3333 | 38 | 33.9 | 36 | 36.4 | 35 | 35.4333 | 35 | 414 | United_StatesLouisianaALEXANDRIA ESLER REGIONAL AP
United_States | Louisiana | ALEXANDRIA INTERNATIONAL | ALEXANDRIA INTERNATIONAL, LA, USA | 31.33N | 92.55W | 27 | -6.00 (NAC) | 82-06 | 747540 | -6.6 | -7 | -13.7 | 42 | 36.3 | 37.1 | 37.6 | 37 | 37 | 37 | 34.1 | 35.1 | 36 | 35 | 35.0667 | 35 | 415 | United_StatesLouisianaALEXANDRIA INTERNATIONAL
United_States | Louisiana | BARKSDALE AFB | BARKSDALE AFB, LA, USA | 32.50N | 93.67W | 54 | -6.00 (NAC) | 82-06 | 722485 | -8.7 | -9 | -17.1 | 42.8 | 36 | 37.7 | 37.9 | 37 | 37.2 | 38 | 34 | 35.9 | 36.5 | 35 | 35.4667 | 35 | 416 | United_StatesLouisianaBARKSDALE AFB
United_States | Louisiana | BATON ROUGE RYAN ARPT | BATON ROUGE RYAN ARPT, LA, USA | 30.54N | 91.15W | 23 | -6.00 (NAC) | 82-06 | 722317 | -6.2 | -6 | -14.6 | 39.6 | 35 | 35.4 | 35.9 | 35 | 35.4333 | 35 | 33.8 | 34.2 | 34.6 | 34 | 34.2 | 34 | 417 | United_StatesLouisianaBATON ROUGE RYAN ARPT
United_States | Louisiana | FORT POLK (ARMY) | FORT POLK (ARMY), LA, USA | 31.05N | 93.20W | 102 | -6.00 (NAC) | 82-06 | 722390 | -6.3 | -6 | -13.5 | 42 | 35.6 | 37.2 | 37.5 | 37 | 36.7667 | 37 | 33.9 | 35.1 | 35.8 | 35 | 34.9333 | 35 | 418 | United_StatesLouisianaFORT POLK (ARMY)
United_States | Louisiana | GRAND ISLE | GRAND ISLE, LA, USA | 29.27N | 89.95W | 10 | -6.00 (NAC) | 85-05 | 994290 | 0.4 | 0 | -9.8 | 35.1 | 31.3 | 32.4 | 32.7 | 32 | 32.1333 | 32 | 30.2 | 31.3 | 31.5 | 31 | 31 | 31 | 419 | United_StatesLouisianaGRAND ISLE
United_States | Louisiana | LAFAYETTE REGIONAL AP | LAFAYETTE REGIONAL AP, LA, USA | 30.21N | 91.99W | 13 | -6.00 (NAC) | 82-06 | 722405 | -5.7 | -6 | -15.3 | 39.5 | 34.9 | 35.3 | 36 | 35 | 35.4 | 35 | 33.6 | 34.1 | 34.7 | 34 | 34.1333 | 34 | 420 | United_StatesLouisianaLAFAYETTE REGIONAL AP
United_States | Louisiana | LAKE CHARLES REGIONAL ARPT | LAKE CHARLES REGIONAL ARPT, LA, USA | 30.13N | 93.23W | 3 | -6.00 (NAC) | 82-06 | 722400 | -4.7 | -5 | -11.9 | 40.5 | 34.3 | 35.3 | 36 | 35 | 35.2 | 35 | 33.1 | 34.1 | 34.7 | 34 | 33.9667 | 34 | 421 | United_StatesLouisianaLAKE CHARLES REGIONAL ARPT
United_States | Louisiana | MONROE REGIONAL AP | MONROE REGIONAL AP, LA, USA | 32.51N | 92.04W | 25 | -6.00 (NAC) | 82-06 | 722486 | -8 | -8 | -17.2 | 41.3 | 36.4 | 37.3 | 37.8 | 37 | 37.1667 | 37 | 34.6 | 35.8 | 36.2 | 36 | 35.5333 | 36 | 422 | United_StatesLouisianaMONROE REGIONAL AP
United_States | Louisiana | NEW ORLEANS ALVIN CALLENDER F | NEW ORLEANS ALVIN CALLENDER F, LA, USA | 29.83N | 90.03W | 0 | -6.00 (NAC) | 82-06 | 722316 | -4.5 | -5 | -13.6 | 38 | 33.9 | 34.5 | 34.9 | 34 | 34.4333 | 35 | 32.8 | 33.5 | 33.7 | 33 | 33.3333 | 33 | 423 | United_StatesLouisianaNEW ORLEANS ALVIN CALLENDER F
United_States | Louisiana | NEW ORLEANS INTL ARPT | NEW ORLEANS INTL ARPT, LA, USA | 29.99N | 90.25W | 6 | -6.00 (NAC) | 82-06 | 722310 | -3.9 | -4 | -12.2 | 38.6 | 34.4 | 35.6 | 35.5 | 35 | 35.1667 | 36 | 33.1 | 34.1 | 34.1 | 34 | 33.7667 | 34 | 424 | United_StatesLouisianaNEW ORLEANS INTL ARPT
United_States | Louisiana | NEW ORLEANS LAKEFRONT AP | NEW ORLEANS LAKEFRONT AP, LA, USA | 30.04N | 90.03W | 3 | -6.00 (NAC) | 85-06 | 722315 | -1.3 | -1 | -10.1 | 40.6 | 34.4 | 35.2 | 35.7 | 35 | 35.1 | 35 | 33.3 | 34 | 34.2 | 34 | 33.8333 | 34 | 425 | United_StatesLouisianaNEW ORLEANS LAKEFRONT AP
United_States | Louisiana | PATTERSON MEMORIAL | PATTERSON MEMORIAL, LA, USA | 29.72N | 91.33W | 3 | -6.00 (NAC) | 92-06 | 722329 | -2.5 | -3 | -11 | 41 | 33.9 | 36.3 | 36 | 35 | 35.4 | 36 | 32.7 | 33.8 | 33.9 | 33 | 33.4667 | 33 | 426 | United_StatesLouisianaPATTERSON MEMORIAL
United_States | Louisiana | SALT POINT (RAMOS) | SALT POINT (RAMOS), LA, USA | 29.60N | 91.30W | 3 | -6.00 (NAC) | 89-06 | 722403 | N/A | N/A | N/A | N/A | 33.5 | 34.3 | 34.4 | 34 | 34.0667 | 34 | 32.4 | 33.1 | 33.1 | 33 | 32.8667 | 33 | 427 | United_StatesLouisianaSALT POINT (RAMOS)
United_States | Louisiana | SHREVEPORT DOWNTOWN | SHREVEPORT DOWNTOWN, LA, USA | 32.54N | 93.74W | 55 | -6.00 (NAC) | 97-06 | 722484 | -6 | -6 | -8.8 | 44.7 | 37.3 | 39 | 39 | 38 | 38.4333 | 39 | 35.2 | 37.3 | 37.4 | 37 | 36.6333 | 37 | 428 | United_StatesLouisianaSHREVEPORT DOWNTOWN
United_States | Louisiana | SHREVEPORT REGIONAL ARPT | SHREVEPORT REGIONAL ARPT, LA, USA | 32.45N | 93.82W | 79 | -6.00 (NAC) | 82-06 | 722480 | -7.9 | -8 | -15.9 | 42.5 | 36.4 | 38.1 | 38.7 | 38 | 37.7333 | 38 | 34.2 | 36.1 | 36.8 | 36 | 35.7 | 36 | 429 | United_StatesLouisianaSHREVEPORT REGIONAL ARPT
United_States | Louisiana | SOUTHWEST PASS | SOUTHWEST PASS, LA, USA | 28.90N | 89.43W | 12 | -6.00 (NAC) | 89-06 | 994010 | 1.9 | 2 | -6.6 | 35.7 | 30.8 | 31.8 | 32.2 | 32 | 31.6 | 32 | 29.9 | 30.8 | 31.3 | 31 | 30.6667 | 31 | 430 | United_StatesLouisianaSOUTHWEST PASS
United_States | Maine | AUBURN-LEWISTON | AUBURN-LEWISTON, ME, USA | 44.05N | 70.28W | 88 | -5.00 (NAE) | 92-06 | 726184 | -26.7 | -27 | -37.4 | 38.3 | 32.4 | 32.8 | 32.5 | 33 | 32.5667 | 33 | 29.5 | 30.6 | 30.1 | 30 | 30.0667 | 30 | 431 | United_StatesMaineAUBURN-LEWISTON
United_States | Maine | AUGUSTA AIRPORT | AUGUSTA AIRPORT, ME, USA | 44.32N | 69.80W | 110 | -5.00 (NAE) | 82-06 | 726185 | -23.4 | -23 | -30.6 | 37.9 | 32.1 | 33 | 32.2 | 32 | 32.4333 | 33 | 29.1 | 30.3 | 30 | 30 | 29.8 | 30 | 432 | United_StatesMaineAUGUSTA AIRPORT
United_States | Maine | BANGOR INTERNATIONAL AP | BANGOR INTERNATIONAL AP, ME, USA | 44.81N | 68.82W | 59 | -5.00 (NAE) | 82-06 | 726088 | -26.7 | -27 | -35.1 | 37.6 | 32.8 | 32.9 | 32.6 | 33 | 32.7667 | 33 | 29.8 | 30.6 | 30.2 | 30 | 30.2 | 30 | 433 | United_StatesMaineBANGOR INTERNATIONAL AP
United_States | Maine | BAR HARBOR (AWOS) | BAR HARBOR (AWOS), ME, USA | 44.45N | 68.37W | 26 | -5.00 (NAE) | 92-06 | 726077 | -22 | -22 | -31.2 | 35.8 | 29 | 29.9 | 30.1 | 30 | 29.6667 | 30 | 26 | 27.5 | 27.3 | 27 | 26.9333 | 27 | 434 | United_StatesMaineBAR HARBOR (AWOS)
United_States | Maine | BRUNSWICK NAS | BRUNSWICK NAS, ME, USA | 43.90N | 69.93W | 23 | -5.00 (NAE) | 82-06 | 743920 | -24.4 | -24 | -33.1 | 37.6 | 31.8 | 32.7 | 32.3 | 32 | 32.2667 | 33 | 28.8 | 30.2 | 29.8 | 30 | 29.6 | 30 | 435 | United_StatesMaineBRUNSWICK NAS
United_States | Maine | CARIBOU MUNICIPAL ARPT | CARIBOU MUNICIPAL ARPT, ME, USA | 46.87N | 68.03W | 190 | -5.00 (NAE) | 82-06 | 727120 | -30.6 | -31 | -37.9 | 35.9 | 30.9 | 31.5 | 30.7 | 31 | 31.0333 | 32 | 28.2 | 28.8 | 28.3 | 28 | 28.4333 | 28 | 436 | United_StatesMaineCARIBOU MUNICIPAL ARPT
United_States | Maine | GREENVILLE (AMOS) | GREENVILLE (AMOS), ME, USA | 45.47N | 69.58W | 316 | -5.00 (NAE) | 91-06 | 726190 | -29.6 | -30 | -40.6 | 35.1 | 30.2 | 30 | 30.1 | 30 | 30.1 | 30 | 27.7 | 27.8 | 27.7 | 28 | 27.7333 | 28 | 437 | United_StatesMaineGREENVILLE (AMOS)
United_States | Maine | HOULTON INTL ARPT | HOULTON INTL ARPT, ME, USA | 46.12N | 67.79W | 145 | -5.00 (NAE) | 82-06 | 727033 | -32.2 | -32 | -40.5 | 37.3 | 32 | 31.7 | 31.7 | 32 | 31.8 | 32 | 29 | 29.5 | 29.1 | 29 | 29.2 | 29 | 438 | United_StatesMaineHOULTON INTL ARPT
United_States | Maine | LORING AFB/LIMESTON | LORING AFB/LIMESTON, ME, USA | 46.95N | 67.88W | 227 | -5.00 (NAE) | 82-94 | 727125 | -28.8 | -29 | -32.9 | 36 | 30.4 | 31.7 | 30.3 | 31 | 30.8 | 32 | 27.3 | 29 | 28 | 28 | 28.1 | 28 | 439 | United_StatesMaineLORING AFB/LIMESTON
United_States | Maine | MATINICUS ROCK | MATINICUS ROCK, ME, USA | 43.78N | 68.87W | 27 | -5.00 (NAE) | 85-06 | 994370 | -18.1 | -18 | -24 | 27.8 | 19.5 | 21.8 | 21.6 | 21 | 20.9667 | 22 | 17.3 | 20 | 20.2 | 19 | 19.1667 | 19 | 440 | United_StatesMaineMATINICUS ROCK
United_States | Maine | MT DESERT ROCK | MT DESERT ROCK, ME, USA | 43.97N | 68.12W | 16 | -5.00 (NAE) | 89-06 | 994060 | -17.8 | -18 | -24.1 | 25.2 | 18.2 | 20.8 | 20.8 | 20 | 19.9333 | 21 | 16 | 18.9 | 19.4 | 18 | 18.1 | 18 | 441 | United_StatesMaineMT DESERT ROCK
United_States | Maine | NORTHERN AROOSTOOK | NORTHERN AROOSTOOK, ME, USA | 47.28N | 68.30W | 309 | -5.00 (NAE) | 95-06 | 726083 | -28.3 | -28 | -35.2 | 34.6 | 30.8 | 28.8 | 30.8 | 30 | 30.1333 | 29 | 27.5 | 27.2 | 27.7 | 27 | 27.4667 | 27 | 442 | United_StatesMaineNORTHERN AROOSTOOK
United_States | Maine | PORTLAND INTL JETPORT | PORTLAND INTL JETPORT, ME, USA | 43.64N | 70.30W | 19 | -5.00 (NAE) | 82-06 | 726060 | -22.7 | -23 | -30.2 | 38.5 | 32.4 | 33.1 | 32.5 | 33 | 32.6667 | 33 | 29.2 | 30.4 | 29.6 | 30 | 29.7333 | 30 | 443 | United_StatesMainePORTLAND INTL JETPORT
United_States | Maine | PRESQUE ISLE MUNICIP | PRESQUE ISLE MUNICIP, ME, USA | 46.69N | 68.03W | 163 | -5.00 (NAE) | 92-06 | 727130 | -34.1 | -34 | -45.1 | 36.1 | 31.7 | 31.3 | 31.3 | 31 | 31.4333 | 31 | 29 | 28.8 | 28.6 | 29 | 28.8 | 29 | 444 | United_StatesMainePRESQUE ISLE MUNICIP
United_States | Maine | ROCKLAND/KNOX(AWOS) | ROCKLAND/KNOX(AWOS), ME, USA | 44.07N | 69.10W | 17 | -5.00 (NAE) | 92-06 | 726079 | -21.3 | -21 | -30.1 | 34.4 | 28.9 | 30.9 | 29.1 | 30 | 29.6333 | 31 | 26.3 | 27.6 | 27 | 27 | 26.9667 | 27 | 445 | United_StatesMaineROCKLAND/KNOX(AWOS)
United_States | Maine | SANFORD MUNI (AWOS) | SANFORD MUNI (AWOS), ME, USA | 43.40N | 70.72W | 74 | -5.00 (NAE) | 92-06 | 726064 | -27.2 | -27 | -36.9 | 37.9 | 32.8 | 34 | 32.9 | 33 | 33.2333 | 34 | 31.1 | 31.2 | 30.2 | 31 | 30.8333 | 31 | 446 | United_StatesMaineSANFORD MUNI (AWOS)
United_States | Maine | WATERVILLE (AWOS) | WATERVILLE (AWOS), ME, USA | 44.53N | 69.68W | 101 | -5.00 (NAE) | 92-06 | 726073 | N/A | N/A | N/A | N/A | 32.2 | 32.4 | 32.1 | 32 | 32.2333 | 32 | 28.8 | 29.1 | 29.1 | 29 | 29 | 29 | 447 | United_StatesMaineWATERVILLE (AWOS)
United_States | Maine | WISCASSET | WISCASSET, ME, USA | 43.97N | 69.72W | 21 | -5.00 (NAE) | 95-06 | 727135 | -22.8 | -23 | -34.4 | 36.8 | 31.3 | 32.4 | 32.2 | 32 | 31.9667 | 32 | 28 | 29.2 | 28.9 | 29 | 28.7 | 29 | 448 | United_StatesMaineWISCASSET
United_States | Maryland | ANDREWS AFB | ANDREWS AFB, MD, USA | 38.82N | 76.87W | 86 | -5.00 (NAE) | 82-06 | 745940 | -14.8 | -15 | -24.2 | 40.9 | 34.6 | 36.9 | 36.2 | 36 | 35.9 | 37 | 32.6 | 34.9 | 33.8 | 34 | 33.7667 | 34 | 449 | United_StatesMarylandANDREWS AFB
United_States | Maryland | BALTIMORE BLT-WASHNGTN INT'L | BALTIMORE BLT-WASHNGTN INT'L, MD, USA | 39.17N | 76.68W | 47 | -5.00 (NAE) | 82-06 | 724060 | -14.9 | -15 | -24 | 41.3 | 34.8 | 36.7 | 36 | 36 | 35.8333 | 37 | 32.9 | 34.8 | 33.7 | 34 | 33.8 | 34 | 450 | United_StatesMarylandBALTIMORE BLT-WASHNGTN INT'L
United_States | Maryland | PATUXENT RIVER NAS | PATUXENT RIVER NAS, MD, USA | 38.28N | 76.40W | 12 | -5.00 (NAE) | 82-06 | 724040 | -12.5 | -13 | -20.4 | 39.9 | 34 | 36 | 34.7 | 35 | 34.9 | 36 | 32.2 | 34 | 32.4 | 33 | 32.8667 | 33 | 451 | United_StatesMarylandPATUXENT RIVER NAS
United_States | Maryland | SALISBURY WICOMICO CO AP | SALISBURY WICOMICO CO AP, MD, USA | 38.34N | 75.51W | 18 | -5.00 (NAE) | 82-06 | 724045 | -14.4 | -14 | -22.3 | 39.6 | 34.4 | 35.9 | 34.9 | 35 | 35.0667 | 36 | 32.5 | 34.1 | 32.8 | 33 | 33.1333 | 33 | 452 | United_StatesMarylandSALISBURY WICOMICO CO AP
United_States | Maryland | THOMAS POINT | THOMAS POINT, MD, USA | 38.90N | 76.43W | 12 | -5.00 (NAE) | 85-06 | 994400 | -10.2 | -10 | -19.3 | 36 | 30.9 | 32.6 | 31.7 | 32 | 31.7333 | 33 | 28.9 | 30.7 | 30 | 30 | 29.8667 | 30 | 453 | United_StatesMarylandTHOMAS POINT
United_States | Massachusetts | BARNSTABLE MUNI BOA | BARNSTABLE MUNI BOA, MA, USA | 41.67N | 70.27W | 17 | -5.00 (NAE) | 87-06 | 725067 | -15.8 | -16 | -24.6 | 39.6 | 30 | 32.2 | 31.2 | 31 | 31.1333 | 32 | 27.1 | 29.1 | 28.7 | 28 | 28.3 | 28 | 454 | United_StatesMassachusettsBARNSTABLE MUNI BOA
United_States | Massachusetts | BOSTON LOGAN INT'L ARPT | BOSTON LOGAN INT'L ARPT, MA, USA | 42.36N | 71.01W | 9 | -5.00 (NAE) | 82-06 | 725090 | -16.5 | -17 | -22.9 | 39.5 | 34 | 35.4 | 34.1 | 35 | 34.5 | 35 | 31.3 | 32.8 | 31.9 | 32 | 32 | 32 | 455 | United_StatesMassachusettsBOSTON LOGAN INT'L ARPT
United_States | Massachusetts | BUZZARDS BAY | BUZZARDS BAY, MA, USA | 41.38N | 71.03W | 17 | -5.00 (NAE) | 85-06 | 994140 | -14.9 | -15 | -20.8 | 29.5 | 23.8 | 26.7 | 25.5 | 25 | 25.3333 | 27 | 21.7 | 24.4 | 24.2 | 23 | 23.4333 | 23 | 456 | United_StatesMassachusettsBUZZARDS BAY
United_States | Massachusetts | CHATHAM MUNI ARPT | CHATHAM MUNI ARPT, MA, USA | 41.68N | 70.00W | 19 | -5.00 (NAE) | 82-06 | 725069 | N/A | N/A | N/A | N/A | 27.8 | 31.2 | 30.1 | 30 | 29.7 | 31 | 25 | 27.8 | 27.5 | 27 | 26.7667 | 27 | 457 | United_StatesMassachusettsCHATHAM MUNI ARPT
United_States | Massachusetts | LAWRENCE MUNI | LAWRENCE MUNI, MA, USA | 42.72N | 71.12W | 46 | -5.00 (NAE) | 97-06 | 744904 | -18.1 | -18 | -26.7 | 38.8 | 32.9 | 33.9 | 33.8 | 34 | 33.5333 | 34 | 31.4 | 32.2 | 32.1 | 32 | 31.9 | 32 | 458 | United_StatesMassachusettsLAWRENCE MUNI
United_States | Massachusetts | MARTHAS VINEYARD | MARTHAS VINEYARD, MA, USA | 41.40N | 70.62W | 21 | -5.00 (NAE) | 97-06 | 725066 | -16.9 | -17 | -23.9 | 36.3 | 28.8 | 31.3 | 31.3 | 30 | 30.4667 | 31 | 26.3 | 28 | 28 | 27 | 27.4333 | 27 | 459 | United_StatesMassachusettsMARTHAS VINEYARD
United_States | Massachusetts | NEW BEDFORD RGNL | NEW BEDFORD RGNL, MA, USA | 41.67N | 70.95W | 25 | -5.00 (NAE) | 96-06 | 725065 | -16.9 | -17 | -25.9 | 39.8 | 31.4 | 33.8 | 32.8 | 33 | 32.6667 | 34 | 29 | 32 | 30.8 | 31 | 30.6 | 31 | 460 | United_StatesMassachusettsNEW BEDFORD RGNL
United_States | Massachusetts | NORWOOD MEMORIAL | NORWOOD MEMORIAL, MA, USA | 42.18N | 71.18W | 15 | -5.00 (NAE) | 98-06 | 725098 | N/A | N/A | N/A | N/A | 32.9 | 34.8 | 34 | 34 | 33.9 | 35 | 31.3 | 32.5 | 32.2 | 32 | 32 | 32 | 461 | United_StatesMassachusettsNORWOOD MEMORIAL
United_States | Massachusetts | OTIS ANGB | OTIS ANGB, MA, USA | 41.65N | 70.52W | 40 | -5.00 (NAE) | 82-06 | 725060 | -16.2 | -16 | -23.9 | 36.9 | 30.9 | 32.2 | 31.1 | 31 | 31.4 | 32 | 27.6 | 29.4 | 28.7 | 29 | 28.5667 | 29 | 462 | United_StatesMassachusettsOTIS ANGB
United_States | Massachusetts | PLYMOUTH MUNICIPAL | PLYMOUTH MUNICIPAL, MA, USA | 41.92N | 70.73W | 45 | -5.00 (NAE) | 95-06 | 725064 | -17.8 | -18 | -25.9 | 40 | 32.3 | 34 | 33.7 | 33 | 33.3333 | 34 | 29.9 | 32.1 | 30.2 | 31 | 30.7333 | 31 | 463 | United_StatesMassachusettsPLYMOUTH MUNICIPAL
United_States | Massachusetts | PROVINCETOWN (AWOS) | PROVINCETOWN (AWOS), MA, USA | 42.07N | 70.22W | 2 | -5.00 (NAE) | 92-06 | 725073 | -13.7 | -14 | -21.9 | 36.2 | 28.8 | 31.8 | 29 | 30 | 29.8667 | 32 | 26.3 | 28.8 | 27.6 | 28 | 27.5667 | 28 | 464 | United_StatesMassachusettsPROVINCETOWN (AWOS)
United_States | Massachusetts | SOUTH WEYMOUTH NAS | SOUTH WEYMOUTH NAS, MA, USA | 42.15N | 70.93W | 49 | -5.00 (NAE) | 82-93 | 725097 | -18.9 | -19 | -24.2 | 38.8 | 35.1 | 35.4 | 34.4 | 35 | 34.9667 | 35 | 31.7 | 32.8 | 32 | 32 | 32.1667 | 32 | 465 | United_StatesMassachusettsSOUTH WEYMOUTH NAS
United_States | Massachusetts | WORCESTER REGIONAL ARPT | WORCESTER REGIONAL ARPT, MA, USA | 42.27N | 71.88W | 310 | -5.00 (NAE) | 82-06 | 725095 | -20 | -20 | -26.2 | 35.3 | 30.8 | 32 | 31.2 | 31 | 31.3333 | 32 | 28.9 | 29.8 | 29.2 | 29 | 29.3 | 29 | 466 | United_StatesMassachusettsWORCESTER REGIONAL ARPT
United_States | Michigan | ALPENA COUNTY REGIONAL AP | ALPENA COUNTY REGIONAL AP, MI, USA | 45.07N | 83.58W | 211 | -5.00 (NAE) | 82-06 | 726390 | -25.5 | -26 | -34.4 | 39.9 | 33.5 | 33.8 | 32.7 | 33 | 33.3333 | 34 | 30.3 | 31.3 | 29.5 | 30 | 30.3667 | 30 | 467 | United_StatesMichiganALPENA COUNTY REGIONAL AP
United_States | Michigan | ANTRIM CO ARPT | ANTRIM CO ARPT, MI, USA | 44.98N | 85.20W | 190 | -5.00 (NAE) | 82-06 | 727436 | -24.6 | -25 | -36.1 | 38.4 | 32.5 | 32.8 | 32.4 | 33 | 32.5667 | 33 | 30.8 | 31.1 | 29 | 30 | 30.3 | 30 | 468 | United_StatesMichiganANTRIM CO ARPT
United_States | Michigan | BENTON HARBOR/ROSS | BENTON HARBOR/ROSS, MI, USA | 42.13N | 86.43W | 196 | -5.00 (NAE) | 96-06 | 726355 | -18.9 | -19 | -29.3 | 39.9 | 32.7 | 34 | 33 | 33 | 33.2333 | 34 | 31.2 | 32.2 | 30.2 | 31 | 31.2 | 31 | 469 | United_StatesMichiganBENTON HARBOR/ROSS
United_States | Michigan | CADILLAC WEXFORD CO AP | CADILLAC WEXFORD CO AP, MI, USA | 44.28N | 85.42W | 398 | -5.00 (NAE) | 93-06 | 726384 | -28.5 | -29 | -45.7 | 39.5 | 33.3 | 32.9 | 31.2 | 32 | 32.4667 | 33 | 31.2 | 30.9 | 28.6 | 30 | 30.2333 | 30 | 470 | United_StatesMichiganCADILLAC WEXFORD CO AP
United_States | Michigan | CHIPPEWA CO INTL | CHIPPEWA CO INTL, MI, USA | 46.25N | 84.47W | 250 | -5.00 (NAE) | 90-06 | 727344 | -27 | -27 | -39.3 | 38.7 | 30.2 | 30.9 | 28.9 | 30 | 30 | 31 | 27.7 | 27.9 | 27.1 | 28 | 27.5667 | 28 | 471 | United_StatesMichiganCHIPPEWA CO INTL
United_States | Michigan | COPPER HARBOR RAMOS | COPPER HARBOR RAMOS, MI, USA | 47.45N | 87.90W | 186 | -5.00 (NAE) | 82-06 | 725387 | -22.4 | -22 | -31.2 | 36.6 | 28 | 30.9 | 30.2 | 30 | 29.7 | 31 | 24.2 | 27.1 | 26.7 | 26 | 26 | 26 | 472 | United_StatesMichiganCOPPER HARBOR RAMOS
United_States | Michigan | DETROIT CITY AIRPORT | DETROIT CITY AIRPORT, MI, USA | 42.41N | 83.01W | 191 | -5.00 (NAE) | 82-06 | 725375 | -18.5 | -19 | -27.9 | 40 | 33.9 | 35.1 | 33.7 | 34 | 34.2333 | 35 | 32.1 | 32.9 | 31.7 | 32 | 32.2333 | 32 | 473 | United_StatesMichiganDETROIT CITY AIRPORT
United_States | Michigan | DETROIT METROPOLITAN ARPT | DETROIT METROPOLITAN ARPT, MI, USA | 42.22N | 83.35W | 202 | -5.00 (NAE) | 82-06 | 725370 | -20.3 | -20 | -30.9 | 39.4 | 34 | 34.8 | 33.9 | 34 | 34.2333 | 35 | 31.6 | 32.5 | 31.3 | 32 | 31.8 | 32 | 474 | United_StatesMichiganDETROIT METROPOLITAN ARPT
United_States | Michigan | DETROIT WILLOW RUN AP | DETROIT WILLOW RUN AP, MI, USA | 42.23N | 83.53W | 218 | -5.00 (NAE) | 90-06 | 725376 | -20.4 | -20 | -33.2 | 38.6 | 34.2 | 34.5 | 33.2 | 34 | 33.9667 | 35 | 32.3 | 32.4 | 31.2 | 32 | 31.9667 | 32 | 475 | United_StatesMichiganDETROIT WILLOW RUN AP
United_States | Michigan | ESCANABA (AWOS) | ESCANABA (AWOS), MI, USA | 45.75N | 87.03W | 187 | -5.00 (NAE) | 82-06 | 726480 | -26.3 | -26 | -34.8 | 37.1 | 29.5 | 30.9 | 28.8 | 30 | 29.7333 | 31 | 27 | 28 | 27.2 | 27 | 27.4 | 27 | 476 | United_StatesMichiganESCANABA (AWOS)
United_States | Michigan | FLINT BISHOP INTL ARPT | FLINT BISHOP INTL ARPT, MI, USA | 42.97N | 83.75W | 234 | -5.00 (NAE) | 82-06 | 726370 | -22.6 | -23 | -30.6 | 38.7 | 33.6 | 34.5 | 33.2 | 34 | 33.7667 | 35 | 31.2 | 32.1 | 30.8 | 31 | 31.3667 | 31 | 477 | United_StatesMichiganFLINT BISHOP INTL ARPT
United_States | Michigan | GRAND RAPIDS KENT COUNTY INT' | GRAND RAPIDS KENT COUNTY INT', MI, USA | 42.88N | 85.52W | 245 | -5.00 (NAE) | 82-06 | 726350 | -21.9 | -22 | -31.4 | 37.6 | 33.1 | 34 | 33.4 | 34 | 33.5 | 34 | 31.2 | 31.9 | 30.8 | 31 | 31.3 | 31 | 478 | United_StatesMichiganGRAND RAPIDS KENT COUNTY INT'
United_States | Michigan | GROSSE ISLE ARPT | GROSSE ISLE ARPT, MI, USA | 42.10N | 83.15W | 176 | -5.00 (NAE) | 97-06 | 725373 | -16.4 | -16 | -24.3 | 39.6 | 32.7 | 34 | 32.9 | 33 | 33.2 | 34 | 30.3 | 32.4 | 31.1 | 31 | 31.2667 | 31 | 479 | United_StatesMichiganGROSSE ISLE ARPT
United_States | Michigan | HANCOCK HOUGHTON CO AP | HANCOCK HOUGHTON CO AP, MI, USA | 47.17N | 88.51W | 329 | -6.00 (NAC) | 82-06 | 727440 | -23.9 | -24 | -31.9 | 39.1 | 31.8 | 32.9 | 30.8 | 32 | 31.8333 | 33 | 28.1 | 29.1 | 28.1 | 28 | 28.4333 | 28 | 480 | United_StatesMichiganHANCOCK HOUGHTON CO AP
United_States | Michigan | HARBOR BEACH(RAMOS) | HARBOR BEACH(RAMOS), MI, USA | 44.02N | 82.80W | 183 | -5.00 (NAE) | 82-06 | 725386 | -17 | -17 | -25.3 | 38.8 | 32.9 | 34.7 | 33.4 | 34 | 33.6667 | 35 | 30.2 | 31.8 | 30.7 | 31 | 30.9 | 31 | 481 | United_StatesMichiganHARBOR BEACH(RAMOS)
United_States | Michigan | HOLLAND/TULIP CITY | HOLLAND/TULIP CITY, MI, USA | 42.75N | 86.10W | 210 | -5.00 (NAE) | 97-06 | 725394 | -18.9 | -19 | -25.3 | 37.2 | 32.5 | 32.8 | 32.2 | 33 | 32.5 | 33 | 31 | 31.3 | 29.1 | 30 | 30.4667 | 30 | 482 | United_StatesMichiganHOLLAND/TULIP CITY
United_States | Michigan | HOUGHTON LAKE ROSCOMMON CO AR | HOUGHTON LAKE ROSCOMMON CO AR, MI, USA | 44.37N | 84.69W | 354 | -5.00 (NAE) | 83-06 | 726380 | -26.4 | -26 | -36.6 | 38.7 | 32.8 | 32.7 | 32 | 33 | 32.5 | 33 | 30 | 30.6 | 29.5 | 30 | 30.0333 | 30 | 483 | United_StatesMichiganHOUGHTON LAKE ROSCOMMON CO AR
United_States | Michigan | HOWELL | HOWELL, MI, USA | 42.63N | 83.98W | 293 | -5.00 (NAE) | 94-06 | 725378 | -19.7 | -20 | -27.4 | 38.8 | 33 | 34.1 | 33 | 33 | 33.3667 | 34 | 32.2 | 32.5 | 31.1 | 32 | 31.9333 | 32 | 484 | United_StatesMichiganHOWELL
United_States | Michigan | IRON MOUNTAIN/FORD | IRON MOUNTAIN/FORD, MI, USA | 45.82N | 88.12W | 360 | -6.00 (NAC) | 82-06 | 727437 | -29 | -29 | -37.6 | 39.6 | 33 | 33.8 | 32.3 | 33 | 33.0333 | 34 | 30.1 | 31.3 | 28.8 | 30 | 30.0667 | 30 | 485 | United_StatesMichiganIRON MOUNTAIN/FORD
United_States | Michigan | IRONWOOD (AWOS) | IRONWOOD (AWOS), MI, USA | 46.53N | 90.13W | 375 | -6.00 (NAC) | 82-06 | 727445 | -29.5 | -30 | -38.5 | 38.7 | 31.4 | 33.1 | 31.9 | 32 | 32.1333 | 33 | 28.8 | 30 | 28.1 | 29 | 28.9667 | 29 | 486 | United_StatesMichiganIRONWOOD (AWOS)
United_States | Michigan | JACKSON REYNOLDS FIELD | JACKSON REYNOLDS FIELD, MI, USA | 42.26N | 84.46W | 311 | -5.00 (NAE) | 82-06 | 725395 | -22.2 | -22 | -31.1 | 37.1 | 32.8 | 33.2 | 32.6 | 33 | 32.8667 | 33 | 30.9 | 31.4 | 30.3 | 31 | 30.8667 | 31 | 487 | United_StatesMichiganJACKSON REYNOLDS FIELD
United_States | Michigan | KALAMAZOO BATTLE CR | KALAMAZOO BATTLE CR, MI, USA | 42.23N | 85.55W | 273 | -5.00 (NAE) | 98-06 | 726357 | -19.9 | -20 | -29 | 38.4 | 33 | 33.7 | 32.6 | 33 | 33.1 | 34 | 32.1 | 32.3 | 31 | 32 | 31.8 | 32 | 488 | United_StatesMichiganKALAMAZOO BATTLE CR
United_States | Michigan | LANSING CAPITAL CITY ARPT | LANSING CAPITAL CITY ARPT, MI, USA | 42.78N | 84.58W | 266 | -5.00 (NAE) | 82-06 | 725390 | -24.1 | -24 | -32.9 | 38 | 33.5 | 34.1 | 33.5 | 34 | 33.7 | 34 | 31.2 | 32 | 30.8 | 31 | 31.3333 | 31 | 489 | United_StatesMichiganLANSING CAPITAL CITY ARPT
United_States | Michigan | MACKINACK ISLAND | MACKINACK ISLAND, MI, USA | 45.87N | 84.63W | 300 | -5.00 (NAE) | 82-06 | 727435 | -25.6 | -26 | -38.7 | 38.7 | 31 | 33.1 | 31.4 | 32 | 31.8333 | 33 | 27.7 | 29.5 | 28 | 28 | 28.4 | 28 | 490 | United_StatesMichiganMACKINACK ISLAND
United_States | Michigan | MANISTEE (AWOS) | MANISTEE (AWOS), MI, USA | 44.27N | 86.25W | 189 | -5.00 (NAE) | 91-06 | 726385 | -21.4 | -21 | -31.4 | 36.2 | 31.2 | 32.1 | 31.2 | 32 | 31.5 | 32 | 29 | 29.1 | 28.1 | 29 | 28.7333 | 29 | 491 | United_StatesMichiganMANISTEE (AWOS)
United_States | Michigan | MANISTIQUE (AMOS) | MANISTIQUE (AMOS), MI, USA | 45.95N | 86.23W | 178 | -5.00 (NAE) | 82-04 | 726399 | -22.2 | -22 | -31.3 | 31.4 | 25 | 27.8 | 27.4 | 27 | 26.7333 | 28 | 22.7 | 25.4 | 25.8 | 25 | 24.6333 | 25 | 492 | United_StatesMichiganMANISTIQUE (AMOS)
United_States | Michigan | MARQUETTE COUNTY ARPT | MARQUETTE COUNTY ARPT, MI, USA | 46.53N | 87.55W | 431 | -6.00 (NAC) | 82-99 | 727430 | -30.2 | -30 | -39.2 | 38.5 | 31.7 | 33 | 30.6 | 32 | 31.7667 | 33 | 28.1 | 29.7 | 27.8 | 29 | 28.5333 | 29 | 493 | United_StatesMichiganMARQUETTE COUNTY ARPT
United_States | Michigan | MENOMINEE (AWOS) | MENOMINEE (AWOS), MI, USA | 45.13N | 87.63W | 191 | -6.00 (NAC) | 92-06 | 726487 | -25.8 | -26 | -36 | 39 | 32.1 | 32.7 | 31.2 | 32 | 32 | 33 | 28.9 | 30.9 | 28 | 29 | 29.2667 | 29 | 494 | United_StatesMichiganMENOMINEE (AWOS)
United_States | Michigan | MUSKEGON COUNTY ARPT | MUSKEGON COUNTY ARPT, MI, USA | 43.17N | 86.24W | 193 | -5.00 (NAE) | 82-06 | 726360 | -19.6 | -20 | -28.1 | 36.1 | 31.4 | 32 | 31.4 | 32 | 31.6 | 32 | 29.4 | 30.1 | 29.4 | 30 | 29.6333 | 30 | 495 | United_StatesMichiganMUSKEGON COUNTY ARPT
United_States | Michigan | NEWBERRY LUCE CO. | NEWBERRY LUCE CO., MI, USA | 46.32N | 85.45W | 265 | -5.00 (NAE) | 88-06 | 726394 | -25.8 | -26 | -36 | 37.2 | 29.1 | 32.4 | 29.9 | 30 | 30.4667 | 32 | 27.5 | 29.9 | 27.4 | 28 | 28.2667 | 28 | 496 | United_StatesMichiganNEWBERRY LUCE CO.
United_States | Michigan | OAKLAND CO INTL | OAKLAND CO INTL, MI, USA | 42.67N | 83.42W | 306 | -5.00 (NAE) | 88-06 | 726375 | -20 | -20 | -27.1 | 37.5 | 32.9 | 33.7 | 33 | 33 | 33.2 | 34 | 31.2 | 32 | 31 | 31 | 31.4 | 31 | 497 | United_StatesMichiganOAKLAND CO INTL
United_States | Michigan | OSCODA WURTSMITH AFB | OSCODA WURTSMITH AFB, MI, USA | 44.45N | 83.37W | 193 | -5.00 (NAE) | 82-06 | 726395 | -22.2 | -22 | -30.3 | 40.7 | 33.6 | 35.3 | 33.7 | 34 | 34.2 | 35 | 31 | 32.4 | 30.7 | 31 | 31.3667 | 31 | 498 | United_StatesMichiganOSCODA WURTSMITH AFB
United_States | Michigan | PASSAGE ISLAND | PASSAGE ISLAND, MI, USA | 48.22N | 88.37W | 209 | -6.00 (NAC) | 85-06 | 994090 | -23.8 | -24 | -31.4 | 27.8 | 18.5 | 21.8 | 21.8 | 21 | 20.7 | 22 | 16.3 | 20 | 20.4 | 19 | 18.9 | 19 | 499 | United_StatesMichiganPASSAGE ISLAND
United_States | Michigan | PELLSTON EMMET COUNTY AP | PELLSTON EMMET COUNTY AP, MI, USA | 45.57N | 84.80W | 218 | -5.00 (NAE) | 82-06 | 727347 | -29.2 | -29 | -37.8 | 37.8 | 32.6 | 33 | 31.6 | 32 | 32.4 | 33 | 29.9 | 30.9 | 29.1 | 30 | 29.9667 | 30 | 500 | United_StatesMichiganPELLSTON EMMET COUNTY AP
United_States | Michigan | ROCK OF AGES | ROCK OF AGES, MI, USA | 47.87N | 89.32W | 223 | -6.00 (NAC) | 85-06 | 994130 | -26.1 | -26 | -33.4 | 31.8 | 22.3 | 24.9 | 24.2 | 24 | 23.8 | 25 | 19.1 | 21.7 | 22.2 | 21 | 21 | 21 | 501 | United_StatesMichiganROCK OF AGES
United_States | Michigan | SAGINAW TRI CITY INTL AP | SAGINAW TRI CITY INTL AP, MI, USA | 43.53N | 84.08W | 204 | -5.00 (NAE) | 82-06 | 726379 | -21.3 | -21 | -29.3 | 39.4 | 34.1 | 34.9 | 33.6 | 34 | 34.2 | 35 | 31.6 | 32.3 | 30.8 | 32 | 31.5667 | 32 | 502 | United_StatesMichiganSAGINAW TRI CITY INTL AP
United_States | Michigan | SAULT STE MARIE SANDERSON FIE | SAULT STE MARIE SANDERSON FIE, MI, USA | 46.47N | 84.37W | 221 | -5.00 (NAE) | 82-06 | 727340 | -28.6 | -29 | -40.1 | 36.6 | 30 | 31.7 | 30.2 | 31 | 30.6333 | 32 | 27.4 | 29 | 27.6 | 28 | 28 | 28 | 503 | United_StatesMichiganSAULT STE MARIE SANDERSON FIE
United_States | Michigan | SELFRIDGE ANGB | SELFRIDGE ANGB, MI, USA | 42.62N | 82.83W | 177 | -5.00 (NAE) | 82-06 | 725377 | -19.7 | -20 | -27.1 | 40 | 33.9 | 35 | 33.7 | 34 | 34.2 | 35 | 31.8 | 32.5 | 31.2 | 32 | 31.8333 | 32 | 504 | United_StatesMichiganSELFRIDGE ANGB
United_States | Michigan | ST.CLAIR COUNTY INT | ST.CLAIR COUNTY INT, MI, USA | 42.92N | 82.53W | 198 | -5.00 (NAE) | 94-06 | 725384 | -21.6 | -22 | -32.1 | 49.4 | 32.9 | 33.3 | 32.9 | 33 | 33.0333 | 33 | 32 | 32.4 | 31 | 32 | 31.8 | 32 | 505 | United_StatesMichiganST.CLAIR COUNTY INT
United_States | Michigan | STANNARD ROCK | STANNARD ROCK, MI, USA | 47.18N | 87.22W | 212 | -5.00 (NAE) | 85-06 | 994200 | -19.7 | -20 | -27.2 | 34.4 | 25.1 | 26.4 | 26 | 26 | 25.8333 | 26 | 22.3 | 23.4 | 23.8 | 23 | 23.1667 | 23 | 506 | United_StatesMichiganSTANNARD ROCK
United_States | Michigan | STURGIS\KIRSH MUNI | STURGIS\KIRSH MUNI, MI, USA | 41.82N | 85.43W | 282 | -5.00 (NAE) | 99-06 | 725383 | -21.2 | -21 | -30.3 | 47.5 | 33 | 32.8 | 32.7 | 33 | 32.8333 | 33 | 32.1 | 32.1 | 30.9 | 32 | 31.7 | 32 | 507 | United_StatesMichiganSTURGIS\KIRSH MUNI
United_States | Michigan | TRAVERSE CITY CHERRY CAPITAL | TRAVERSE CITY CHERRY CAPITAL, MI, USA | 44.74N | 85.58W | 192 | -5.00 (NAE) | 82-06 | 726387 | -22.5 | -23 | -32.8 | 38.5 | 33.5 | 34.1 | 33.4 | 34 | 33.6667 | 34 | 31.1 | 31.9 | 30.5 | 31 | 31.1667 | 31 | 508 | United_StatesMichiganTRAVERSE CITY CHERRY CAPITAL
United_States | Minnesota | AITKIN NDB(AWOS) | AITKIN NDB(AWOS), MN, USA | 46.55N | 93.68W | 367 | -6.00 (NAC) | 92-06 | 727504 | -33.4 | -33 | -45.7 | 37.1 | 31.1 | 32.4 | 31.2 | 32 | 31.5667 | 32 | 28.7 | 30.1 | 28.4 | 29 | 29.0667 | 29 | 509 | United_StatesMinnesotaAITKIN NDB(AWOS)
United_States | Minnesota | ALBERT LEA (AWOS) | ALBERT LEA (AWOS), MN, USA | 43.68N | 93.37W | 383 | -6.00 (NAC) | 92-06 | 726589 | -27.7 | -28 | -38.3 | 38.2 | 33 | 33.8 | 31.8 | 33 | 32.8667 | 34 | 31.1 | 32 | 29.8 | 31 | 30.9667 | 31 | 510 | United_StatesMinnesotaALBERT LEA (AWOS)
United_States | Minnesota | ALEXANDRIA MUNICIPAL AP | ALEXANDRIA MUNICIPAL AP, MN, USA | 45.88N | 95.39W | 436 | -6.00 (NAC) | 82-06 | 726557 | -31.3 | -31 | -40.1 | 39.6 | 33.7 | 34.6 | 33.2 | 34 | 33.8333 | 35 | 30.6 | 31.7 | 30.7 | 31 | 31 | 31 | 511 | United_StatesMinnesotaALEXANDRIA MUNICIPAL AP
United_States | Minnesota | AUSTIN MUNI | AUSTIN MUNI, MN, USA | 43.67N | 92.93W | 375 | -6.00 (NAC) | 92-06 | 727566 | -27.8 | -28 | -37.7 | 39.3 | 32.7 | 33.8 | 32.4 | 33 | 32.9667 | 34 | 30.7 | 32.1 | 29.8 | 31 | 30.8667 | 31 | 512 | United_StatesMinnesotaAUSTIN MUNI
United_States | Minnesota | BAUDETTE INTERNATIONAL AP | BAUDETTE INTERNATIONAL AP, MN, USA | 48.73N | 94.61W | 330 | -6.00 (NAC) | 95-06 | 727476 | -35 | -35 | -47.4 | 36.3 | 32.4 | 32.2 | 31.2 | 32 | 31.9333 | 32 | 28.8 | 29.6 | 28.4 | 29 | 28.9333 | 29 | 513 | United_StatesMinnesotaBAUDETTE INTERNATIONAL AP
United_States | Minnesota | BEMIDJI MUNICIPAL | BEMIDJI MUNICIPAL, MN, USA | 47.50N | 94.93W | 420 | -6.00 (NAC) | 87-06 | 727550 | -34.3 | -34 | -44.5 | 37.8 | 32.4 | 32.9 | 33 | 33 | 32.7667 | 33 | 29.4 | 30.9 | 30 | 30 | 30.1 | 30 | 514 | United_StatesMinnesotaBEMIDJI MUNICIPAL
United_States | Minnesota | BENSON MUNI | BENSON MUNI, MN, USA | 45.32N | 95.65W | 317 | -6.00 (NAC) | 94-06 | 727507 | -29.6 | -30 | -39.5 | 40.2 | 34 | 36.1 | 33.8 | 35 | 34.6333 | 36 | 32 | 32.6 | 31.2 | 32 | 31.9333 | 32 | 515 | United_StatesMinnesotaBENSON MUNI
United_States | Minnesota | BRAINERD/WIELAND | BRAINERD/WIELAND, MN, USA | 46.40N | 94.13W | 374 | -6.00 (NAC) | 89-06 | 726555 | -32.8 | -33 | -46.6 | 39 | 32.3 | 34.1 | 32.5 | 33 | 32.9667 | 34 | 29.4 | 32 | 29.8 | 30 | 30.4 | 30 | 516 | United_StatesMinnesotaBRAINERD/WIELAND
United_States | Minnesota | CAMBRIDGE MUNI | CAMBRIDGE MUNI, MN, USA | 45.57N | 93.27W | 287 | -6.00 (NAC) | 92-06 | 727503 | -30.7 | -31 | -42.4 | 46.3 | 33.5 | 37.1 | 34.1 | 35 | 34.9 | 37 | 31.1 | 32.9 | 30.9 | 32 | 31.6333 | 32 | 517 | United_StatesMinnesotaCAMBRIDGE MUNI
United_States | Minnesota | CLOQUET (AWOS) | CLOQUET (AWOS), MN, USA | 46.70N | 92.50W | 390 | -6.00 (NAC) | 92-06 | 726558 | -31.3 | -31 | -43.4 | 36.5 | 31.5 | 32.5 | 31.2 | 32 | 31.7333 | 33 | 27.9 | 29.7 | 27.9 | 29 | 28.5 | 29 | 518 | United_StatesMinnesotaCLOQUET (AWOS)
United_States | Minnesota | CRANE LAKE (AWOS) | CRANE LAKE (AWOS), MN, USA | 46.27N | 92.57W | 350 | -6.00 (NAC) | 92-06 | 727473 | -34 | -34 | -42 | 39.3 | 33.3 | 32.6 | 31.6 | 33 | 32.5 | 33 | 29 | 29.8 | 28.8 | 29 | 29.2 | 29 | 519 | United_StatesMinnesotaCRANE LAKE (AWOS)
United_States | Minnesota | CROOKSTON MUNI FLD | CROOKSTON MUNI FLD, MN, USA | 47.85N | 96.62W | 273 | -6.00 (NAC) | 92-06 | 727452 | -33.5 | -34 | -45.6 | 47.1 | 32.3 | 32.4 | 32.4 | 32 | 32.3667 | 32 | 29.2 | 30 | 29.7 | 30 | 29.6333 | 30 | 520 | United_StatesMinnesotaCROOKSTON MUNI FLD
United_States | Minnesota | DETROIT LAKES(AWOS) | DETROIT LAKES(AWOS), MN, USA | 46.83N | 95.88W | 426 | -6.00 (NAC) | 92-06 | 727457 | -32.3 | -32 | -46.2 | 38.3 | 32.6 | 32.5 | 32.6 | 33 | 32.5667 | 33 | 29.4 | 31.1 | 29.8 | 30 | 30.1 | 30 | 521 | United_StatesMinnesotaDETROIT LAKES(AWOS)
United_States | Minnesota | DULUTH HARBOR (CGS) | DULUTH HARBOR (CGS), MN, USA | 46.77N | 92.08W | 186 | -6.00 (NAC) | 83-06 | 727456 | -26.9 | -27 | -35.1 | 40.5 | 31.3 | 33 | 32.3 | 32 | 32.2 | 33 | 27.5 | 31 | 28.8 | 29 | 29.1 | 29 | 522 | United_StatesMinnesotaDULUTH HARBOR (CGS)
United_States | Minnesota | DULUTH INTERNATIONAL ARPT | DULUTH INTERNATIONAL ARPT, MN, USA | 46.84N | 92.19W | 432 | -6.00 (NAC) | 82-06 | 727450 | -32.1 | -32 | -41 | 36.8 | 30.6 | 32.2 | 31.1 | 31 | 31.3 | 32 | 27.6 | 29.5 | 28.2 | 28 | 28.4333 | 28 | 523 | United_StatesMinnesotaDULUTH INTERNATIONAL ARPT
United_States | Minnesota | ELY MUNI | ELY MUNI, MN, USA | 47.82N | 91.83W | 455 | -6.00 (NAC) | 92-06 | 727459 | -36.7 | -37 | -48.8 | 38.3 | 32.7 | 32.2 | 31.4 | 32 | 32.1 | 32 | 28.9 | 29 | 27.9 | 29 | 28.6 | 29 | 524 | United_StatesMinnesotaELY MUNI
United_States | Minnesota | EVELETH MUNI (AWOS) | EVELETH MUNI (AWOS), MN, USA | 47.40N | 92.50W | 421 | -6.00 (NAC) | 92-06 | 727474 | -35.3 | -35 | -47.8 | 37.8 | 32.3 | 32.9 | 31.3 | 32 | 32.1667 | 33 | 29 | 30.1 | 28 | 29 | 29.0333 | 29 | 525 | United_StatesMinnesotaEVELETH MUNI (AWOS)
United_States | Minnesota | FAIRMONT MUNI(AWOS) | FAIRMONT MUNI(AWOS), MN, USA | 43.65N | 94.42W | 354 | -6.00 (NAC) | 92-06 | 726586 | -26.2 | -26 | -33.3 | 38.4 | 33.8 | 32.9 | 32.3 | 33 | 33 | 33 | 31.5 | 32 | 29.9 | 31 | 31.1333 | 31 | 526 | United_StatesMinnesotaFAIRMONT MUNI(AWOS)
United_States | Minnesota | FARIBAULT MUNI AWOS | FARIBAULT MUNI AWOS, MN, USA | 44.33N | 93.32W | 322 | -6.00 (NAC) | 92-06 | 726563 | -29.2 | -29 | -42.8 | 39 | 32.9 | 34 | 32.5 | 33 | 33.1333 | 34 | 31.2 | 32.4 | 29.9 | 31 | 31.1667 | 31 | 527 | United_StatesMinnesotaFARIBAULT MUNI AWOS
United_States | Minnesota | FERGUS FALLS(AWOS) | FERGUS FALLS(AWOS), MN, USA | 46.28N | 96.15W | 361 | -6.00 (NAC) | 92-06 | 726560 | -30.7 | -31 | -40.9 | 42.5 | 33.8 | 34.7 | 33.5 | 34 | 34 | 35 | 30.9 | 32.1 | 31.1 | 31 | 31.3667 | 31 | 528 | United_StatesMinnesotaFERGUS FALLS(AWOS)
United_States | Minnesota | FLYING CLOUD | FLYING CLOUD, MN, USA | 44.82N | 93.45W | 283 | -6.00 (NAC) | 97-06 | 726579 | -27.1 | -27 | -35 | 37.9 | 33.6 | 35.2 | 34 | 34 | 34.2667 | 35 | 31.1 | 32.8 | 31.3 | 32 | 31.7333 | 32 | 529 | United_StatesMinnesotaFLYING CLOUD
United_States | Minnesota | FOSSTON(AWOS) | FOSSTON(AWOS), MN, USA | 47.58N | 95.77W | 388 | -6.00 (NAC) | 92-06 | 727505 | -35.4 | -35 | -51.6 | 39.7 | 31.7 | 32.9 | 32.5 | 32 | 32.3667 | 33 | 28.9 | 30.8 | 29.1 | 30 | 29.6 | 30 | 530 | United_StatesMinnesotaFOSSTON(AWOS)
United_States | Minnesota | GLENWOOD (ASOS) | GLENWOOD (ASOS), MN, USA | 45.65N | 95.32W | 425 | -6.00 (NAC) | 95-06 | 726547 | -29.5 | -30 | -39.6 | 39.7 | 32.9 | 36 | 33 | 34 | 33.9667 | 36 | 30.8 | 32.5 | 31 | 31 | 31.4333 | 31 | 531 | United_StatesMinnesotaGLENWOOD (ASOS)
United_States | Minnesota | GRAND MARAIS MUNI | GRAND MARAIS MUNI, MN, USA | 47.83N | 90.38W | 548 | -6.00 (NAC) | 97-06 | 727454 | -30.2 | -30 | -35.4 | 35.5 | 27.6 | 29.1 | 28.8 | 29 | 28.5 | 29 | 25.1 | 27.4 | 26.2 | 26 | 26.2333 | 26 | 532 | United_StatesMinnesotaGRAND MARAIS MUNI
United_States | Minnesota | GRAND RAPIDS(AWOS) | GRAND RAPIDS(AWOS), MN, USA | 47.22N | 93.52W | 413 | -6.00 (NAC) | 92-06 | 727458 | -32.3 | -32 | -41.7 | 36.5 | 31.6 | 32.2 | 30.9 | 32 | 31.5667 | 32 | 28.7 | 29.1 | 27.6 | 28 | 28.4667 | 28 | 533 | United_StatesMinnesotaGRAND RAPIDS(AWOS)
United_States | Minnesota | HALLOCK | HALLOCK, MN, USA | 48.78N | 96.95W | 250 | -6.00 (NAC) | 92-06 | 727478 | -34.1 | -34 | -45.3 | 39.8 | 33.3 | 32.9 | 33.7 | 33 | 33.3 | 33 | 30 | 31.1 | 31.2 | 31 | 30.7667 | 31 | 534 | United_StatesMinnesotaHALLOCK
United_States | Minnesota | HIBBING CHISHOLM-HIBBING AP | HIBBING CHISHOLM-HIBBING AP, MN, USA | 47.39N | 92.84W | 414 | -6.00 (NAC) | 82-06 | 727455 | -35.8 | -36 | -45.6 | 36.1 | 31.6 | 31.9 | 31.4 | 32 | 31.6333 | 32 | 28.5 | 29.8 | 28.7 | 29 | 29 | 29 | 535 | United_StatesMinnesotaHIBBING CHISHOLM-HIBBING AP
United_States | Minnesota | HUTCHINSON (AWOS) | HUTCHINSON (AWOS), MN, USA | 44.87N | 94.38W | 323 | -6.00 (NAC) | 92-06 | 726569 | -29.8 | -30 | -40.3 | 38.7 | 34 | 34.1 | 32.5 | 34 | 33.5333 | 34 | 32 | 32.4 | 30.2 | 32 | 31.5333 | 32 | 536 | United_StatesMinnesotaHUTCHINSON (AWOS)
United_States | Minnesota | INTERNATIONAL FALLS INTL AP | INTERNATIONAL FALLS INTL AP, MN, USA | 48.57N | 93.40W | 361 | -6.00 (NAC) | 82-06 | 727470 | -37.2 | -37 | -46 | 38.1 | 32.6 | 32.2 | 32 | 32 | 32.2667 | 32 | 29.3 | 29.6 | 29.1 | 29 | 29.3333 | 29 | 537 | United_StatesMinnesotaINTERNATIONAL FALLS INTL AP
United_States | Minnesota | LITCHFIELD MUNI | LITCHFIELD MUNI, MN, USA | 45.10N | 94.50W | 347 | -6.00 (NAC) | 92-06 | 726583 | -28.3 | -28 | -37.1 | 38.7 | 33.6 | 33.6 | 32.3 | 33 | 33.1667 | 34 | 31 | 32 | 29.5 | 31 | 30.8333 | 31 | 538 | United_StatesMinnesotaLITCHFIELD MUNI
United_States | Minnesota | LITTLE FALLS (AWOS) | LITTLE FALLS (AWOS), MN, USA | 45.95N | 94.35W | 342 | -6.00 (NAC) | 92-06 | 726578 | -32 | -32 | -43.9 | 39.2 | 34 | 34.8 | 33.7 | 34 | 34.1667 | 35 | 31.3 | 32.6 | 31.1 | 32 | 31.6667 | 32 | 539 | United_StatesMinnesotaLITTLE FALLS (AWOS)
United_States | Minnesota | MANKATO(AWOS) | MANKATO(AWOS), MN, USA | 44.22N | 93.92W | 311 | -6.00 (NAC) | 92-06 | 726585 | -26.1 | -26 | -34.1 | 39.2 | 33.8 | 33 | 32.2 | 33 | 33 | 33 | 31.3 | 32.1 | 29.4 | 31 | 30.9333 | 31 | 540 | United_StatesMinnesotaMANKATO(AWOS)
United_States | Minnesota | MARSHALL/RYAN(AWOS) | MARSHALL/RYAN(AWOS), MN, USA | 44.45N | 95.82W | 359 | -6.00 (NAC) | 92-06 | 726559 | -26.9 | -27 | -34.6 | 39.7 | 33.9 | 34.9 | 32.5 | 34 | 33.7667 | 35 | 31.4 | 32.4 | 30.9 | 32 | 31.5667 | 32 | 541 | United_StatesMinnesotaMARSHALL/RYAN(AWOS)
United_States | Minnesota | MINNEAPOLIS/BLAINE | MINNEAPOLIS/BLAINE, MN, USA | 45.15N | 93.22W | 278 | -6.00 (NAC) | 97-06 | 726577 | -26 | -26 | -34 | 39.4 | 32.8 | 35.1 | 33.7 | 34 | 33.8667 | 35 | 30.9 | 32.7 | 30.9 | 32 | 31.5 | 32 | 542 | United_StatesMinnesotaMINNEAPOLIS/BLAINE
United_States | Minnesota | MINNEAPOLIS/CRYSTAL | MINNEAPOLIS/CRYSTAL, MN, USA | 45.07N | 93.35W | 265 | -6.00 (NAC) | 97-06 | 726575 | -26.4 | -26 | -34 | 40 | 33 | 36.1 | 33.9 | 34 | 34.3333 | 36 | 30.9 | 32.8 | 31.3 | 32 | 31.6667 | 32 | 543 | United_StatesMinnesotaMINNEAPOLIS/CRYSTAL
United_States | Minnesota | MINNEAPOLIS-ST PAUL INT'L ARP | MINNEAPOLIS-ST PAUL INT'L ARP, MN, USA | 44.88N | 93.23W | 255 | -6.00 (NAC) | 82-06 | 726580 | -28.1 | -28 | -37.6 | 40.9 | 34.2 | 35.8 | 34.3 | 35 | 34.7667 | 36 | 31.6 | 33.2 | 31.4 | 32 | 32.0667 | 32 | 544 | United_StatesMinnesotaMINNEAPOLIS-ST PAUL INT'L ARP
United_States | Minnesota | MONTEVIDEO (AWOS) | MONTEVIDEO (AWOS), MN, USA | 44.97N | 95.72W | 315 | -6.00 (NAC) | 92-06 | 726553 | -28.1 | -28 | -38.1 | 39.2 | 34.1 | 33.9 | 32.9 | 34 | 33.6333 | 34 | 31.6 | 32.3 | 30.9 | 32 | 31.6 | 32 | 545 | United_StatesMinnesotaMONTEVIDEO (AWOS)
United_States | Minnesota | MORA MUNI (AWOS) | MORA MUNI (AWOS), MN, USA | 45.88N | 93.27W | 309 | -6.00 (NAC) | 92-06 | 727475 | -30.5 | -31 | -42.1 | 37.6 | 33 | 33.4 | 32.4 | 33 | 32.9333 | 33 | 30.2 | 32 | 30 | 31 | 30.7333 | 31 | 546 | United_StatesMinnesotaMORA MUNI (AWOS)
United_States | Minnesota | MORRIS MUNI (AWOS) | MORRIS MUNI (AWOS), MN, USA | 45.72N | 95.97W | 347 | -6.00 (NAC) | 92-06 | 726565 | -30.2 | -30 | -41.3 | 39.5 | 33 | 33 | 32.5 | 33 | 32.8333 | 33 | 31.1 | 31.3 | 29.4 | 31 | 30.6 | 31 | 547 | United_StatesMinnesotaMORRIS MUNI (AWOS)
United_States | Minnesota | NEW ULM MUNI (AWOS) | NEW ULM MUNI (AWOS), MN, USA | 44.32N | 94.50W | 308 | -6.00 (NAC) | 92-06 | 726567 | -27.4 | -27 | -35.7 | 39.5 | 34.1 | 34 | 32.7 | 34 | 33.6 | 34 | 32.1 | 32.3 | 30.8 | 32 | 31.7333 | 32 | 548 | United_StatesMinnesotaNEW ULM MUNI (AWOS)
United_States | Minnesota | ORR | ORR, MN, USA | 48.02N | 92.87W | 397 | -6.00 (NAC) | 93-06 | 726544 | -35.1 | -35 | -46.5 | 38.5 | 32.2 | 32.5 | 31 | 32 | 31.9 | 33 | 28.6 | 29.7 | 27.9 | 29 | 28.7333 | 29 | 549 | United_StatesMinnesotaORR
United_States | Minnesota | OWATONNA (AWOS) | OWATONNA (AWOS), MN, USA | 44.12N | 93.25W | 350 | -6.00 (NAC) | 92-06 | 726568 | -27.8 | -28 | -35.8 | 38.3 | 33 | 33 | 32.2 | 33 | 32.7333 | 33 | 31.2 | 32.1 | 30.1 | 31 | 31.1333 | 31 | 550 | United_StatesMinnesotaOWATONNA (AWOS)
United_States | Minnesota | PARK RAPIDS MUNICIPAL AP | PARK RAPIDS MUNICIPAL AP, MN, USA | 46.90N | 95.07W | 440 | -6.00 (NAC) | 95-06 | 727453 | -34.4 | -34 | -46.4 | 37.8 | 32.3 | 33 | 32.8 | 33 | 32.7 | 33 | 29 | 31.1 | 29.6 | 30 | 29.9 | 30 | 551 | United_StatesMinnesotaPARK RAPIDS MUNICIPAL AP
United_States | Minnesota | PEQUOT LAKE (AMOS) | PEQUOT LAKE (AMOS), MN, USA | 46.60N | 94.32W | 390 | -6.00 (NAC) | 82-95 | 727500 | -34.7 | -35 | -42.2 | 41.7 | 32.7 | 36.2 | 33 | 34 | 33.9667 | 36 | 30.1 | 32.3 | 30.6 | 31 | 31 | 31 | 552 | United_StatesMinnesotaPEQUOT LAKE (AMOS)
United_States | Minnesota | PIPESTONE (AWOS) | PIPESTONE (AWOS), MN, USA | 43.98N | 96.32W | 529 | -6.00 (NAC) | 92-06 | 726566 | -28 | -28 | -37.7 | 39.2 | 33 | 33.9 | 32.4 | 33 | 33.1 | 34 | 30.9 | 32.2 | 29.9 | 31 | 31 | 31 | 553 | United_StatesMinnesotaPIPESTONE (AWOS)
United_States | Minnesota | PRINCETON MUNI | PRINCETON MUNI, MN, USA | 45.55N | 93.60W | 306 | -6.00 (NAC) | 97-06 | 726682 | -29.2 | -29 | -40 | 39.3 | 32.8 | 35.2 | 33.7 | 34 | 33.9 | 35 | 29.9 | 32.6 | 31 | 31 | 31.1667 | 31 | 554 | United_StatesMinnesotaPRINCETON MUNI
United_States | Minnesota | RED WING | RED WING, MN, USA | 44.58N | 92.48W | 239 | -6.00 (NAC) | 92-06 | 726564 | -28.2 | -28 | -36.2 | 39.9 | 33.4 | 35.1 | 33.8 | 34 | 34.1 | 35 | 31.3 | 32.8 | 31.1 | 32 | 31.7333 | 32 | 555 | United_StatesMinnesotaRED WING
United_States | Minnesota | REDWOOD FALLS MUNI | REDWOOD FALLS MUNI, MN, USA | 44.55N | 95.08W | 314 | -6.00 (NAC) | 82-06 | 726556 | -28.7 | -29 | -37.3 | 40.7 | 35.1 | 36.2 | 34.4 | 35 | 35.2333 | 36 | 32.5 | 33.3 | 32 | 33 | 32.6 | 33 | 556 | United_StatesMinnesotaREDWOOD FALLS MUNI
United_States | Minnesota | ROCHESTER INTERNATIONAL ARPT | ROCHESTER INTERNATIONAL ARPT, MN, USA | 43.90N | 92.49W | 402 | -6.00 (NAC) | 82-06 | 726440 | -29 | -29 | -37.9 | 39.5 | 33 | 33.3 | 33.1 | 33 | 33.1333 | 33 | 30.6 | 31.3 | 30 | 31 | 30.6333 | 31 | 557 | United_StatesMinnesotaROCHESTER INTERNATIONAL ARPT
United_States | Minnesota | ROSEAU MUNI (AWOS) | ROSEAU MUNI (AWOS), MN, USA | 48.85N | 95.70W | 323 | -6.00 (NAC) | 92-06 | 727477 | -35.2 | -35 | -47.7 | 39.2 | 32.2 | 32.6 | 32.3 | 32 | 32.3667 | 33 | 28.9 | 30.2 | 29 | 29 | 29.3667 | 29 | 558 | United_StatesMinnesotaROSEAU MUNI (AWOS)
United_States | Minnesota | SILVER BAY | SILVER BAY, MN, USA | 47.20N | 91.40W | 331 | -6.00 (NAC) | 92-06 | 727556 | -33.9 | -34 | -45.7 | 38.2 | 30.3 | 32.4 | 30.1 | 31 | 30.9333 | 32 | 27.5 | 29.1 | 27.6 | 28 | 28.0667 | 28 | 559 | United_StatesMinnesotaSILVER BAY
United_States | Minnesota | SOUTH ST PAUL MUNI | SOUTH ST PAUL MUNI, MN, USA | 44.85N | 93.15W | 250 | -6.00 (NAC) | 95-06 | 726603 | -26.4 | -26 | -37.8 | 39 | 33.9 | 34.8 | 34 | 34 | 34.2333 | 35 | 31.3 | 32.8 | 31.2 | 32 | 31.7667 | 32 | 560 | United_StatesMinnesotaSOUTH ST PAUL MUNI
United_States | Minnesota | ST CLOUD REGIONAL ARPT | ST CLOUD REGIONAL ARPT, MN, USA | 45.55N | 94.05W | 312 | -6.00 (NAC) | 82-06 | 726550 | -32 | -32 | -42.5 | 39.6 | 34 | 35.3 | 33.7 | 34 | 34.3333 | 35 | 30.9 | 32.5 | 30.9 | 31 | 31.4333 | 31 | 561 | United_StatesMinnesotaST CLOUD REGIONAL ARPT
United_States | Minnesota | ST JAMES MUNI ARPT | ST JAMES MUNI ARPT, MN, USA | 43.98N | 94.55W | 325 | -6.00 (NAC) | 97-06 | 726554 | -25.3 | -25 | -30.8 | 38.3 | 33.9 | 33.8 | 32.4 | 33 | 33.3667 | 34 | 32.2 | 32.4 | 30.1 | 32 | 31.5667 | 32 | 562 | United_StatesMinnesotaST JAMES MUNI ARPT
United_States | Minnesota | ST PAUL DOWNTOWN AP | ST PAUL DOWNTOWN AP, MN, USA | 44.93N | 93.05W | 217 | -6.00 (NAC) | 92-06 | 726584 | -27.9 | -28 | -38.3 | 40 | 34.1 | 36.1 | 32.3 | 34 | 34.1667 | 36 | 31.3 | 32.9 | 29.6 | 31 | 31.2667 | 31 | 563 | United_StatesMinnesotaST PAUL DOWNTOWN AP
United_States | Minnesota | THIEF RIVER(AWOS) | THIEF RIVER(AWOS), MN, USA | 48.07N | 96.18W | 340 | -6.00 (NAC) | 92-06 | 727555 | -33.4 | -33 | -44 | 38.3 | 32.1 | 32.1 | 32.2 | 32 | 32.1333 | 32 | 28.9 | 29 | 28.9 | 29 | 28.9333 | 29 | 564 | United_StatesMinnesotaTHIEF RIVER(AWOS)
United_States | Minnesota | TOFTE (RAMOS) | TOFTE (RAMOS), MN, USA | 47.58N | 90.83W | 241 | -6.00 (NAC) | 82-96 | 727554 | -29.2 | -29 | -36.4 | 34.8 | 26.3 | 28.8 | 28.5 | 28 | 27.8667 | 29 | 22.2 | 26.3 | 25.2 | 25 | 24.5667 | 25 | 565 | United_StatesMinnesotaTOFTE (RAMOS)
United_States | Minnesota | TWO HARBORS | TWO HARBORS, MN, USA | 47.05N | 91.75W | 328 | -6.00 (NAC) | 92-06 | 727444 | -30.9 | -31 | -42.1 | 37.3 | 30.2 | 32.1 | 30.9 | 31 | 31.0667 | 32 | 27.3 | 29 | 27.6 | 28 | 27.9667 | 28 | 566 | United_StatesMinnesotaTWO HARBORS
United_States | Minnesota | WHEATON NDB (AWOS) | WHEATON NDB (AWOS), MN, USA | 45.70N | 96.50W | 313 | -6.00 (NAC) | 92-06 | 727533 | -30 | -30 | -41.6 | 39.4 | 33.5 | 33 | 32.9 | 33 | 33.1333 | 33 | 31.2 | 32 | 30.2 | 31 | 31.1333 | 31 | 567 | United_StatesMinnesotaWHEATON NDB (AWOS)
United_States | Minnesota | WILLMAR | WILLMAR, MN, USA | 45.12N | 95.08W | 344 | -6.00 (NAC) | 92-06 | 726576 | -31.1 | -31 | -40.2 | 37.9 | 33.6 | 33.7 | 31.2 | 33 | 32.8333 | 34 | 31.1 | 31.5 | 28.9 | 31 | 30.5 | 31 | 568 | United_StatesMinnesotaWILLMAR
United_States | Minnesota | WINONA MUNI (AWOS) | WINONA MUNI (AWOS), MN, USA | 44.08N | 91.70W | 200 | -6.00 (NAC) | 92-06 | 726588 | -27.6 | -28 | -41.6 | 48 | 33.8 | 36.1 | 35.2 | 35 | 35.0333 | 36 | 32.1 | 32.9 | 32.3 | 32 | 32.4333 | 32 | 569 | United_StatesMinnesotaWINONA MUNI (AWOS)
United_States | Minnesota | WORTHINGTON (AWOS) | WORTHINGTON (AWOS), MN, USA | 43.65N | 95.58W | 480 | -6.00 (NAC) | 92-06 | 726587 | -25.9 | -26 | -29.5 | 38.7 | 33 | 33.8 | 32.1 | 33 | 32.9667 | 34 | 31.1 | 31.3 | 29.1 | 31 | 30.5 | 31 | 570 | United_StatesMinnesotaWORTHINGTON (AWOS)
United_States | Mississippi | COLUMBUS AFB | COLUMBUS AFB, MS, USA | 33.65N | 88.45W | 68 | -6.00 (NAC) | 82-00 | 723306 | -10.8 | -11 | -19.7 | 41.9 | 36.4 | 37.4 | 37.9 | 37 | 37.2333 | 37 | 34.6 | 35.8 | 36 | 35 | 35.4667 | 35 | 571 | United_StatesMississippiCOLUMBUS AFB
United_States | Mississippi | GOLDEN TRI(AWOS) | GOLDEN TRI(AWOS), MS, USA | 33.45N | 88.58W | 80 | -6.00 (NAC) | 92-06 | 723307 | -10.4 | -10 | -16.7 | 42.4 | 35.1 | 37.3 | 37.9 | 37 | 36.7667 | 37 | 33.6 | 36 | 36.3 | 35 | 35.3 | 35 | 572 | United_StatesMississippiGOLDEN TRI(AWOS)
United_States | Mississippi | GREENWOOD LEFLORE ARPT | GREENWOOD LEFLORE ARPT, MS, USA | 33.50N | 90.08W | 41 | -6.00 (NAC) | 82-06 | 722359 | -10 | -10 | -18.6 | 42.7 | 35.2 | 36.8 | 37.4 | 36 | 36.4667 | 37 | 33.8 | 35.2 | 36 | 35 | 35 | 35 | 573 | United_StatesMississippiGREENWOOD LEFLORE ARPT
United_States | Mississippi | HATTIESBURG LAUREL | HATTIESBURG LAUREL, MS, USA | 31.47N | 89.33W | 93 | -6.00 (NAC) | 91-06 | 722348 | -7.8 | -8 | -13.4 | 41.9 | 36.1 | 37.6 | 37.4 | 37 | 37.0333 | 38 | 33.8 | 35.2 | 35.4 | 35 | 34.8 | 35 | 574 | United_StatesMississippiHATTIESBURG LAUREL
United_States | Mississippi | JACKSON INTERNATIONAL AP | JACKSON INTERNATIONAL AP, MS, USA | 32.32N | 90.08W | 101 | -6.00 (NAC) | 82-06 | 722350 | -9.3 | -9 | -17.9 | 41.5 | 35.6 | 36.8 | 37.6 | 37 | 36.6667 | 37 | 34 | 35 | 35.6 | 35 | 34.8667 | 35 | 575 | United_StatesMississippiJACKSON INTERNATIONAL AP
United_States | Mississippi | KEESLER AFB/BILOXI | KEESLER AFB/BILOXI, MS, USA | 30.42N | 88.92W | 8 | -6.00 (NAC) | 82-01 | 747686 | -5.8 | -6 | -16.9 | 40.5 | 34.1 | 36.2 | 36.3 | 36 | 35.5333 | 36 | 32.8 | 34.1 | 34.4 | 34 | 33.7667 | 34 | 576 | United_StatesMississippiKEESLER AFB/BILOXI
United_States | Mississippi | MCCOMB PIKE COUNTY AP | MCCOMB PIKE COUNTY AP, MS, USA | 31.18N | 90.47W | 129 | -6.00 (NAC) | 82-06 | 722358 | -8.1 | -8 | -16.7 | 40.3 | 35.2 | 36.2 | 36.5 | 36 | 35.9667 | 36 | 33.7 | 34.5 | 34.8 | 34 | 34.3333 | 34 | 577 | United_StatesMississippiMCCOMB PIKE COUNTY AP
United_States | Mississippi | MERIDIAN KEY FIELD | MERIDIAN KEY FIELD, MS, USA | 32.33N | 88.75W | 95 | -6.00 (NAC) | 82-06 | 722340 | -9.9 | -10 | -18.2 | 41.6 | 36 | 37 | 37.5 | 37 | 36.8333 | 37 | 34 | 35.2 | 35.4 | 35 | 34.8667 | 35 | 578 | United_StatesMississippiMERIDIAN KEY FIELD
United_States | Mississippi | MERIDIAN NAAS | MERIDIAN NAAS, MS, USA | 32.55N | 88.57W | 97 | -6.00 (NAC) | 82-98 | 722345 | -10.9 | -11 | -20.7 | 42.1 | 37.1 | 37.9 | 37.7 | 38 | 37.5667 | 38 | 35.3 | 36 | 35.9 | 36 | 35.7333 | 36 | 579 | United_StatesMississippiMERIDIAN NAAS
United_States | Mississippi | NATCHEZ/HARDY(AWOS) | NATCHEZ/HARDY(AWOS), MS, USA | 31.62N | 91.30W | 83 | -6.00 (NAC) | 92-06 | 722357 | -7 | -7 | -13 | 38.6 | 33.7 | 35.9 | 36.3 | 35 | 35.3 | 36 | 32.5 | 33.9 | 34.1 | 34 | 33.5 | 34 | 580 | United_StatesMississippiNATCHEZ/HARDY(AWOS)
United_States | Mississippi | TUPELO C D LEMONS ARPT | TUPELO C D LEMONS ARPT, MS, USA | 34.26N | 88.77W | 110 | -6.00 (NAC) | 83-06 | 723320 | -11.5 | -12 | -21 | 42.2 | 35.6 | 37.1 | 37.5 | 37 | 36.7333 | 37 | 33.8 | 35.2 | 35.8 | 35 | 34.9333 | 35 | 581 | United_StatesMississippiTUPELO C D LEMONS ARPT
United_States | Missouri | CAPE GIRARDEAU MUNICIPAL AP | CAPE GIRARDEAU MUNICIPAL AP, MO, USA | 37.23N | 89.57W | 107 | -6.00 (NAC) | 82-06 | 723489 | -18.4 | -18 | -29.5 | 40.8 | 35.3 | 36.9 | 36.5 | 36 | 36.2333 | 37 | 33.6 | 35 | 34.6 | 34 | 34.4 | 34 | 582 | United_StatesMissouriCAPE GIRARDEAU MUNICIPAL AP
United_States | Missouri | COLUMBIA REGIONAL AIRPORT | COLUMBIA REGIONAL AIRPORT, MO, USA | 38.82N | 92.22W | 274 | -6.00 (NAC) | 82-06 | 724450 | -21 | -21 | -30.8 | 43.5 | 34.2 | 37.1 | 37.7 | 36 | 36.3333 | 37 | 31.9 | 34.7 | 35.1 | 34 | 33.9 | 34 | 583 | United_StatesMissouriCOLUMBIA REGIONAL AIRPORT
United_States | Missouri | JEFFERSON CITY MEM | JEFFERSON CITY MEM, MO, USA | 38.58N | 92.15W | 167 | -6.00 (NAC) | 97-06 | 724458 | -18.6 | -19 | -24.4 | 41.2 | 33.7 | 37.6 | 37.4 | 36 | 36.2333 | 38 | 32.5 | 35.9 | 35.1 | 35 | 34.5 | 35 | 584 | United_StatesMissouriJEFFERSON CITY MEM
United_States | Missouri | JOPLIN MUNICIPAL AP | JOPLIN MUNICIPAL AP, MO, USA | 37.15N | 94.50W | 300 | -6.00 (NAC) | 82-06 | 723495 | -17.9 | -18 | -28.1 | 42.7 | 34.7 | 37.3 | 38 | 37 | 36.6667 | 37 | 32.9 | 35.5 | 36.3 | 35 | 34.9 | 35 | 585 | United_StatesMissouriJOPLIN MUNICIPAL AP
United_States | Missouri | KAISER MEM (AWOS) | KAISER MEM (AWOS), MO, USA | 38.10N | 92.55W | 265 | -6.00 (NAC) | 92-06 | 724459 | -18.2 | -18 | -26.9 | 44.1 | 33.6 | 37.8 | 38 | 36 | 36.4667 | 38 | 32.5 | 35.3 | 36.2 | 35 | 34.6667 | 35 | 586 | United_StatesMissouriKAISER MEM (AWOS)
United_States | Missouri | KANSAS CITY DOWNTOWN AP | KANSAS CITY DOWNTOWN AP, MO, USA | 39.12N | 94.59W | 229 | -6.00 (NAC) | 82-06 | 724463 | -19.1 | -19 | -29.9 | 43.7 | 35.7 | 38 | 38.5 | 37 | 37.4 | 38 | 33.5 | 36.5 | 36.1 | 35 | 35.3667 | 35 | 587 | United_StatesMissouriKANSAS CITY DOWNTOWN AP
United_States | Missouri | KANSAS CITY INT'L ARPT | KANSAS CITY INT'L ARPT, MO, USA | 39.30N | 94.72W | 312 | -6.00 (NAC) | 82-06 | 724460 | -21.2 | -21 | -31.5 | 43.5 | 34.9 | 37.5 | 38.6 | 37 | 37 | 38 | 32.7 | 35.6 | 35.8 | 35 | 34.7 | 35 | 588 | United_StatesMissouriKANSAS CITY INT'L ARPT
United_States | Missouri | KIRKSVILLE REGIONAL AP | KIRKSVILLE REGIONAL AP, MO, USA | 40.10N | 92.54W | 294 | -6.00 (NAC) | 82-06 | 724455 | -22 | -22 | -31.8 | 42 | 34 | 36.9 | 37 | 36 | 35.9667 | 37 | 32 | 34.9 | 34.3 | 34 | 33.7333 | 34 | 589 | United_StatesMissouriKIRKSVILLE REGIONAL AP
United_States | Missouri | POPLAR BLUFF(AMOS) | POPLAR BLUFF(AMOS), MO, USA | 36.77N | 90.47W | 146 | -6.00 (NAC) | 82-06 | 723300 | -16.2 | -16 | -26.6 | 42.3 | 34.6 | 36.2 | 36.4 | 36 | 35.7333 | 36 | 32.9 | 34.5 | 34.1 | 34 | 33.8333 | 34 | 590 | United_StatesMissouriPOPLAR BLUFF(AMOS)
United_States | Missouri | SEDALIA MEMORIAL | SEDALIA MEMORIAL, MO, USA | 38.70N | 93.18W | 277 | -6.00 (NAC) | 97-06 | 724453 | -18.3 | -18 | -23 | 43.1 | 33 | 37.7 | 38 | 36 | 36.2333 | 38 | 32.3 | 36.1 | 36.2 | 35 | 34.8667 | 35 | 591 | United_StatesMissouriSEDALIA MEMORIAL
United_States | Missouri | SPICKARD (AMOS) | SPICKARD (AMOS), MO, USA | 40.25N | 93.72W | 270 | -6.00 (NAC) | 82-96 | 725400 | N/A | N/A | N/A | N/A | 36.1 | 37.9 | 38.2 | 37 | 37.4 | 38 | 33.1 | 35.3 | 35.5 | 35 | 34.6333 | 35 | 592 | United_StatesMissouriSPICKARD (AMOS)
United_States | Missouri | SPRINGFIELD REGIONAL ARPT | SPRINGFIELD REGIONAL ARPT, MO, USA | 37.24N | 93.39W | 387 | -6.00 (NAC) | 82-06 | 724400 | -19.1 | -19 | -29.1 | 42.2 | 33.8 | 36.9 | 37.1 | 36 | 35.9333 | 37 | 32 | 34.8 | 35.3 | 34 | 34.0333 | 34 | 593 | United_StatesMissouriSPRINGFIELD REGIONAL ARPT
United_States | Missouri | ST LOUIS LAMBERT INT'L ARPT | ST LOUIS LAMBERT INT'L ARPT, MO, USA | 38.75N | 90.37W | 216 | -6.00 (NAC) | 82-06 | 724340 | -18.8 | -19 | -30.1 | 41.7 | 35 | 37.4 | 37.6 | 37 | 36.6667 | 37 | 33.4 | 35.6 | 35.3 | 35 | 34.7667 | 35 | 594 | United_StatesMissouriST LOUIS LAMBERT INT'L ARPT
United_States | Missouri | ST LOUIS SPIRIT OF ST LOUIS A | ST LOUIS SPIRIT OF ST LOUIS A, MO, USA | 38.66N | 90.66W | 141 | -6.00 (NAC) | 86-06 | 724345 | -19.5 | -20 | -30.9 | 41.5 | 35.3 | 37.3 | 37.4 | 37 | 36.6667 | 37 | 33.1 | 35.3 | 35 | 34 | 34.4667 | 34 | 595 | United_StatesMissouriST LOUIS SPIRIT OF ST LOUIS A
United_States | Missouri | VICHY ROLLA NATL ARPT | VICHY ROLLA NATL ARPT, MO, USA | 38.13N | 91.77W | 347 | -6.00 (NAC) | 82-06 | 724456 | -19 | -19 | -24.9 | 41.9 | 34.3 | 37.6 | 37.2 | 36 | 36.3667 | 38 | 32.1 | 35.4 | 35.4 | 34 | 34.3 | 34 | 596 | United_StatesMissouriVICHY ROLLA NATL ARPT
United_States | Missouri | WHITEMAN AFB | WHITEMAN AFB, MO, USA | 38.73N | 93.55W | 255 | -6.00 (NAC) | 82-06 | 724467 | -20.4 | -20 | -30.1 | 43 | 34.8 | 37.7 | 38.2 | 37 | 36.9 | 38 | 32.8 | 36.1 | 36.2 | 35 | 35.0333 | 35 | 597 | United_StatesMissouriWHITEMAN AFB
United_States | Montana | BILLINGS LOGAN INT'L ARPT | BILLINGS LOGAN INT'L ARPT, MT, USA | 45.81N | 108.54W | 1088 | -7.00 (NAM) | 82-06 | 726770 | -26.6 | -27 | -38.2 | 42.7 | 35.7 | 37.7 | 36.6 | 37 | 36.6667 | 38 | 32.4 | 35.4 | 34.4 | 34 | 34.0667 | 34 | 598 | United_StatesMontanaBILLINGS LOGAN INT'L ARPT
United_States | Montana | BOZEMAN GALLATIN FIELD | BOZEMAN GALLATIN FIELD, MT, USA | 45.79N | 111.15W | 1356 | -7.00 (NAM) | 82-06 | 726797 | -32.7 | -33 | -43.3 | 40.5 | 32.7 | 35.8 | 35 | 35 | 34.5 | 36 | 29.5 | 33.6 | 32.6 | 32 | 31.9 | 32 | 599 | United_StatesMontanaBOZEMAN GALLATIN FIELD
United_States | Montana | BUTTE BERT MOONEY ARPT | BUTTE BERT MOONEY ARPT, MT, USA | 45.95N | 112.51W | 1687 | -7.00 (NAM) | 82-06 | 726785 | -35.3 | -35 | -47.2 | 37.6 | 30.4 | 33.8 | 32.5 | 32 | 32.2333 | 34 | 27.8 | 31.6 | 30.3 | 30 | 29.9 | 30 | 600 | United_StatesMontanaBUTTE BERT MOONEY ARPT
United_States | Montana | CUT BANK MUNI AP | CUT BANK MUNI AP, MT, USA | 48.61N | 112.38W | 1170 | -7.00 (NAM) | 83-06 | 727796 | -33.4 | -33 | -45.3 | 39.8 | 29.2 | 33.9 | 34 | 32 | 32.3667 | 34 | 26.3 | 32 | 31.9 | 30 | 30.0667 | 30 | 601 | United_StatesMontanaCUT BANK MUNI AP
United_States | Montana | DILLON AIRPORT | DILLON AIRPORT, MT, USA | 45.26N | 112.55W | 1592 | -7.00 (NAM) | 97-06 | 726796 | -26.3 | -26 | -38 | 38.1 | 29.8 | 34 | 32.9 | 32 | 32.2333 | 34 | 27.5 | 32.5 | 31.2 | 30 | 30.4 | 30 | 602 | United_StatesMontanaDILLON AIRPORT
United_States | Montana | GLASGOW INTL ARPT | GLASGOW INTL ARPT, MT, USA | 48.21N | 106.62W | 699 | -7.00 (NAM) | 82-06 | 727680 | -33 | -33 | -43.8 | 42.3 | 36.6 | 37.2 | 37.1 | 37 | 36.9667 | 37 | 32.7 | 34.9 | 34.7 | 34 | 34.1 | 34 | 603 | United_StatesMontanaGLASGOW INTL ARPT
United_States | Montana | GLENDIVE(AWOS) | GLENDIVE(AWOS), MT, USA | 47.13N | 104.80W | 749 | -7.00 (NAM) | 92-06 | 726676 | -30.7 | -31 | -38.9 | 43 | 34 | 37.5 | 37.3 | 36 | 36.2667 | 38 | 31 | 35.2 | 34.7 | 34 | 33.6333 | 34 | 604 | United_StatesMontanaGLENDIVE(AWOS)
United_States | Montana | GREAT FALLS | GREAT FALLS, MT, USA | 47.45N | 111.38W | 1130 | -7.00 (NAM) | 94-06 | 727760 | N/A | N/A | N/A | N/A | 30.9 | 35.7 | 34.6 | 34 | 33.7333 | 36 | 27.4 | 33.1 | 32.3 | 31 | 30.9333 | 31 | 605 | United_StatesMontanaGREAT FALLS
United_States | Montana | GREAT FALLS INTL ARPT | GREAT FALLS INTL ARPT, MT, USA | 47.47N | 111.38W | 1115 | -7.00 (NAM) | 82-06 | 727750 | -31.2 | -31 | -42.5 | 40.7 | 33.1 | 36.3 | 35.7 | 35 | 35.0333 | 36 | 30.2 | 33.9 | 33.1 | 32 | 32.4 | 32 | 606 | United_StatesMontanaGREAT FALLS INTL ARPT
United_States | Montana | HAVRE CITY-COUNTY AP | HAVRE CITY-COUNTY AP, MT, USA | 48.56N | 109.78W | 792 | -7.00 (NAM) | 82-06 | 727770 | -35.1 | -35 | -47.7 | 42.9 | 35 | 37.4 | 37.4 | 37 | 36.6 | 37 | 31.4 | 35.1 | 34.6 | 34 | 33.7 | 34 | 607 | United_StatesMontanaHAVRE CITY-COUNTY AP
United_States | Montana | HELENA REGIONAL AIRPORT | HELENA REGIONAL AIRPORT, MT, USA | 46.61N | 111.96W | 1179 | -7.00 (NAM) | 82-06 | 727720 | -29.8 | -30 | -42.5 | 41 | 33.4 | 36.8 | 35.7 | 35 | 35.3 | 37 | 30.9 | 34.4 | 33.1 | 33 | 32.8 | 33 | 608 | United_StatesMontanaHELENA REGIONAL AIRPORT
United_States | Montana | JORDAN (RAMOS) | JORDAN (RAMOS), MT, USA | 47.33N | 106.93W | 811 | -7.00 (NAM) | 83-06 | 727684 | -36.8 | -37 | -47.3 | 43.6 | 37.4 | 37.8 | 37.3 | 38 | 37.5 | 38 | 33.7 | 35.9 | 35.3 | 35 | 34.9667 | 35 | 609 | United_StatesMontanaJORDAN (RAMOS)
United_States | Montana | KALISPELL GLACIER PK INT'L AR | KALISPELL GLACIER PK INT'L AR, MT, USA | 48.30N | 114.26W | 906 | -7.00 (NAM) | 82-06 | 727790 | -27.4 | -27 | -39.5 | 38.6 | 31 | 34.5 | 33.7 | 33 | 33.0667 | 35 | 28.5 | 32.5 | 31.9 | 31 | 30.9667 | 31 | 610 | United_StatesMontanaKALISPELL GLACIER PK INT'L AR
United_States | Montana | LEWISTOWN MUNICIPAL ARPT | LEWISTOWN MUNICIPAL ARPT, MT, USA | 47.05N | 109.47W | 1264 | -7.00 (NAM) | 82-06 | 726776 | -31.4 | -31 | -43.2 | 39.6 | 30.8 | 35 | 34.7 | 34 | 33.5 | 35 | 27.4 | 32.8 | 32.4 | 31 | 30.8667 | 31 | 611 | United_StatesMontanaLEWISTOWN MUNICIPAL ARPT
United_States | Montana | MALMSTROM AFB | MALMSTROM AFB, MT, USA | 47.52N | 111.18W | 1056 | -7.00 (NAM) | 82-06 | 727755 | -30.3 | -30 | -40.3 | 42 | 32.9 | 36.2 | 37 | 35 | 35.3667 | 36 | 30.3 | 33.9 | 34 | 33 | 32.7333 | 33 | 612 | United_StatesMontanaMALMSTROM AFB
United_States | Montana | MILES CITY MUNICIPAL ARPT | MILES CITY MUNICIPAL ARPT, MT, USA | 46.43N | 105.89W | 803 | -7.00 (NAM) | 82-06 | 742300 | -31.1 | -31 | -42.5 | 44.7 | 38 | 39.2 | 38.7 | 39 | 38.6333 | 39 | 34.1 | 37.2 | 36.4 | 36 | 35.9 | 36 | 613 | United_StatesMontanaMILES CITY MUNICIPAL ARPT
United_States | Montana | MISSOULA INTERNATIONAL AP | MISSOULA INTERNATIONAL AP, MT, USA | 46.92N | 114.09W | 972 | -7.00 (NAM) | 82-06 | 727730 | -25 | -25 | -37.9 | 40.5 | 33 | 36.9 | 35.4 | 35 | 35.1 | 37 | 30.3 | 34.3 | 33.2 | 33 | 32.6 | 33 | 614 | United_StatesMontanaMISSOULA INTERNATIONAL AP
United_States | Montana | SIDNEY-RICHLAND | SIDNEY-RICHLAND, MT, USA | 47.70N | 104.20W | 605 | -7.00 (NAM) | 92-06 | 727687 | -32.4 | -32 | -39.3 | 42.4 | 35.2 | 37.3 | 37 | 37 | 36.5 | 37 | 31.2 | 34.1 | 33.8 | 33 | 33.0333 | 33 | 615 | United_StatesMontanaSIDNEY-RICHLAND
United_States | Nebraska | AINSWORTH MUNICIPAL | AINSWORTH MUNICIPAL, NE, USA | 42.58N | 100.00W | 789 | -6.00 (NAC) | 95-06 | 725556 | -25.9 | -26 | -33.6 | 45.4 | 34.9 | 39.8 | 37.3 | 37 | 37.3333 | 40 | 31.6 | 37.1 | 34 | 34 | 34.2333 | 34 | 616 | United_StatesNebraskaAINSWORTH MUNICIPAL
United_States | Nebraska | ALLIANCE MUNICIPAL | ALLIANCE MUNICIPAL, NE, USA | 42.05N | 102.80W | 1198 | -7.00 (NAM) | 96-06 | 725635 | -29.8 | -30 | -41.6 | 43.8 | 37.3 | 39.1 | 37.3 | 38 | 37.9 | 39 | 33.9 | 37.3 | 35 | 35 | 35.4 | 35 | 617 | United_StatesNebraskaALLIANCE MUNICIPAL
United_States | Nebraska | BEATRICE MUNICIPAL | BEATRICE MUNICIPAL, NE, USA | 40.30N | 96.75W | 403 | -6.00 (NAC) | 95-06 | 725515 | -23.2 | -23 | -30.3 | 42.8 | 35.2 | 38.8 | 37.8 | 37 | 37.2667 | 39 | 33.7 | 37.1 | 35.6 | 35 | 35.4667 | 35 | 618 | United_StatesNebraskaBEATRICE MUNICIPAL
United_States | Nebraska | BREWSTER FIELD ARPT | BREWSTER FIELD ARPT, NE, USA | 40.45N | 99.33W | 704 | -6.00 (NAC) | 96-06 | 725628 | -21.7 | -22 | -26.9 | 41.9 | 36.1 | 37.9 | 37.1 | 37 | 37.0333 | 38 | 33.5 | 36.1 | 33.9 | 35 | 34.5 | 35 | 619 | United_StatesNebraskaBREWSTER FIELD ARPT
United_States | Nebraska | COLUMBUS MUNI | COLUMBUS MUNI, NE, USA | 41.45N | 97.33W | 451 | -6.00 (NAC) | 92-06 | 725565 | -24.9 | -25 | -30.6 | 40.7 | 34.1 | 37.2 | 36 | 36 | 35.7667 | 37 | 32.6 | 34.2 | 33 | 33 | 33.2667 | 33 | 620 | United_StatesNebraskaCOLUMBUS MUNI
United_States | Nebraska | FREMONT MUNI ARPT | FREMONT MUNI ARPT, NE, USA | 41.45N | 96.52W | 379 | -6.00 (NAC) | 96-06 | 725564 | N/A | N/A | N/A | N/A | 34.3 | 37.1 | 36 | 36 | 35.8 | 37 | 32.7 | 34.8 | 32.8 | 33 | 33.4333 | 33 | 621 | United_StatesNebraskaFREMONT MUNI ARPT
United_States | Nebraska | GRAND ISLAND CENTRAL NE REGIO | GRAND ISLAND CENTRAL NE REGIO, NE, USA | 40.96N | 98.31W | 566 | -6.00 (NAC) | 82-06 | 725520 | -24.7 | -25 | -32.7 | 44.9 | 36.7 | 38.8 | 37.3 | 38 | 37.6 | 39 | 33.9 | 36 | 34.9 | 35 | 34.9333 | 35 | 622 | United_StatesNebraskaGRAND ISLAND CENTRAL NE REGIO
United_States | Nebraska | HASTINGS MUNICIPAL | HASTINGS MUNICIPAL, NE, USA | 40.60N | 98.43W | 596 | -6.00 (NAC) | 95-06 | 725525 | -23 | -23 | -29.2 | 42.4 | 36.1 | 38.7 | 37.2 | 37 | 37.3333 | 39 | 33.6 | 36.9 | 34.1 | 35 | 34.8667 | 35 | 623 | United_StatesNebraskaHASTINGS MUNICIPAL
United_States | Nebraska | KEARNEY MUNI (AWOS) | KEARNEY MUNI (AWOS), NE, USA | 40.73N | 99.00W | 649 | -6.00 (NAC) | 92-06 | 725526 | -22.8 | -23 | -31.1 | 42.2 | 35.9 | 37.5 | 36.2 | 37 | 36.5333 | 38 | 32.9 | 35.1 | 33.7 | 34 | 33.9 | 34 | 624 | United_StatesNebraskaKEARNEY MUNI (AWOS)
United_States | Nebraska | LINCOLN MUNICIPAL ARPT | LINCOLN MUNICIPAL ARPT, NE, USA | 40.83N | 96.76W | 362 | -6.00 (NAC) | 82-06 | 725510 | -24.1 | -24 | -33.6 | 44.6 | 37 | 38.9 | 38.1 | 38 | 38 | 39 | 34.1 | 36.5 | 35.8 | 35 | 35.4667 | 35 | 625 | United_StatesNebraskaLINCOLN MUNICIPAL ARPT
United_States | Nebraska | MCCOOK MUNICIPAL | MCCOOK MUNICIPAL, NE, USA | 40.20N | 100.58W | 786 | -6.00 (NAC) | 96-06 | 725625 | -21.9 | -22 | -29.9 | 46.5 | 38.7 | 42.1 | 38.8 | 40 | 39.8667 | 42 | 37.2 | 38.8 | 37.1 | 38 | 37.7 | 38 | 626 | United_StatesNebraskaMCCOOK MUNICIPAL
United_States | Nebraska | NORFOLK KARL STEFAN MEM ARPT | NORFOLK KARL STEFAN MEM ARPT, NE, USA | 41.98N | 97.44W | 473 | -6.00 (NAC) | 82-06 | 725560 | -25.6 | -26 | -34 | 43.3 | 35.9 | 37.4 | 36.4 | 37 | 36.5667 | 37 | 33.3 | 35 | 34.2 | 34 | 34.1667 | 34 | 627 | United_StatesNebraskaNORFOLK KARL STEFAN MEM ARPT
United_States | Nebraska | NORTH PLATTE REGIONAL AP | NORTH PLATTE REGIONAL AP, NE, USA | 41.12N | 100.67W | 850 | -6.00 (NAC) | 82-06 | 725620 | -26.2 | -26 | -37.4 | 43.9 | 36.6 | 38.9 | 37.1 | 38 | 37.5333 | 39 | 33.7 | 36.1 | 34.8 | 35 | 34.8667 | 35 | 628 | United_StatesNebraskaNORTH PLATTE REGIONAL AP
United_States | Nebraska | O`NEILL/BAKER FIELD | O`NEILL/BAKER FIELD, NE, USA | 42.47N | 98.68W | 619 | -6.00 (NAC) | 95-06 | 725566 | -25.3 | -25 | -31.5 | 44.8 | 35.9 | 38.9 | 37.5 | 37 | 37.4333 | 39 | 32.3 | 36 | 34 | 34 | 34.1 | 34 | 629 | United_StatesNebraskaO`NEILL/BAKER FIELD
United_States | Nebraska | OFFUTT AFB/BELLEVUE | OFFUTT AFB/BELLEVUE, NE, USA | 41.12N | 95.92W | 319 | -6.00 (NAC) | 82-06 | 725540 | -22.4 | -22 | -29.4 | 44 | 36 | 38 | 37.1 | 37 | 37.0333 | 38 | 33 | 35.1 | 34.5 | 34 | 34.2 | 34 | 630 | United_StatesNebraskaOFFUTT AFB/BELLEVUE
United_States | Nebraska | OMAHA EPPLEY AIRFIELD | OMAHA EPPLEY AIRFIELD, NE, USA | 41.31N | 95.90W | 299 | -6.00 (NAC) | 82-06 | 725500 | -24.3 | -24 | -32.5 | 44 | 35.6 | 38.2 | 37.1 | 37 | 36.9667 | 38 | 33.3 | 35.2 | 34.5 | 34 | 34.3333 | 34 | 631 | United_StatesNebraskaOMAHA EPPLEY AIRFIELD
United_States | Nebraska | OMAHA WSFO | OMAHA WSFO, NE, USA | 41.37N | 96.02W | 399 | -6.00 (NAC) | 82-93 | 725530 | -24.5 | -25 | -33.1 | 42.7 | 36 | 36.1 | 36.5 | 36 | 36.2 | 36 | 33.1 | 34 | 33.7 | 34 | 33.6 | 34 | 632 | United_StatesNebraskaOMAHA WSFO
United_States | Nebraska | SCOTTSBLUFF W B HEILIG FIELD | SCOTTSBLUFF W B HEILIG FIELD, NE, USA | 41.87N | 103.60W | 1206 | -7.00 (NAM) | 82-06 | 725660 | -27.9 | -28 | -42.1 | 43.1 | 37.1 | 38.9 | 36.6 | 38 | 37.5333 | 39 | 33.9 | 36.7 | 34.6 | 35 | 35.0667 | 35 | 633 | United_StatesNebraskaSCOTTSBLUFF W B HEILIG FIELD
United_States | Nebraska | SIDNEY MUNICIPAL AP | SIDNEY MUNICIPAL AP, NE, USA | 41.10N | 102.99W | 1313 | -7.00 (NAM) | 82-06 | 725610 | -26.6 | -27 | -40 | 44.2 | 36.1 | 38.6 | 36.2 | 37 | 36.9667 | 39 | 32.9 | 36.2 | 34.2 | 34 | 34.4333 | 34 | 634 | United_StatesNebraskaSIDNEY MUNICIPAL AP
United_States | Nebraska | TEKAMAH (ASOS) | TEKAMAH (ASOS), NE, USA | 41.77N | 96.17W | 312 | -6.00 (NAC) | 95-06 | 725527 | -25.7 | -26 | -30.5 | 42.3 | 35.9 | 37.3 | 35.9 | 36 | 36.3667 | 37 | 33 | 34.8 | 32.8 | 34 | 33.5333 | 34 | 635 | United_StatesNebraskaTEKAMAH (ASOS)
United_States | Nebraska | VALENTINE MILLER FIELD | VALENTINE MILLER FIELD, NE, USA | 42.86N | 100.55W | 792 | -6.00 (NAC) | 82-06 | 725670 | -29.4 | -29 | -40.5 | 46 | 37.6 | 39.7 | 37.9 | 38 | 38.4 | 40 | 33.9 | 37.1 | 35.6 | 36 | 35.5333 | 36 | 636 | United_StatesNebraskaVALENTINE MILLER FIELD
United_States | Nevada | CALIENTE (AMOS) | CALIENTE (AMOS), NV, USA | 37.62N | 114.52W | 1335 | -8.00 (NAP) | 82-02 | 724870 | N/A | N/A | N/A | N/A | 37.7 | 39.1 | 37.8 | 38 | 38.2 | 39 | 36.2 | 37.4 | 36.4 | 37 | 36.6667 | 37 | 637 | United_StatesNevadaCALIENTE (AMOS)
United_States | Nevada | ELKO MUNICIPAL ARPT | ELKO MUNICIPAL ARPT, NV, USA | 40.83N | 115.79W | 1547 | -8.00 (NAP) | 82-06 | 725825 | -23.8 | -24 | -36.2 | 41.7 | 34.2 | 37.5 | 35.6 | 36 | 35.7667 | 38 | 32.3 | 35.7 | 34.2 | 34 | 34.0667 | 34 | 638 | United_StatesNevadaELKO MUNICIPAL ARPT
United_States | Nevada | ELY YELLAND FIELD | ELY YELLAND FIELD, NV, USA | 39.30N | 114.85W | 1909 | -8.00 (NAP) | 82-06 | 724860 | -25 | -25 | -35.8 | 38.9 | 32.4 | 35.3 | 33.3 | 34 | 33.6667 | 35 | 30.9 | 33.4 | 31.9 | 32 | 32.0667 | 32 | 639 | United_StatesNevadaELY YELLAND FIELD
United_States | Nevada | EUREKA (RAMOS) | EUREKA (RAMOS), NV, USA | 39.52N | 115.97W | 1993 | -8.00 (NAP) | 83-06 | 725824 | -19.7 | -20 | -30.6 | 39.9 | 32.5 | 36.2 | 33.8 | 34 | 34.1667 | 36 | 30.6 | 33.7 | 32.3 | 32 | 32.2 | 32 | 640 | United_StatesNevadaEUREKA (RAMOS)
United_States | Nevada | FALLON NAAS | FALLON NAAS, NV, USA | 39.42N | 118.70W | 1199 | -8.00 (NAP) | 90-06 | 724885 | N/A | N/A | N/A | N/A | 36.9 | 39.3 | 39.3 | 39 | 38.5 | 39 | 35 | 37.7 | 37.1 | 37 | 36.6 | 37 | 641 | United_StatesNevadaFALLON NAAS
United_States | Nevada | LAS VEGAS MCCARRAN INTL AP | LAS VEGAS MCCARRAN INTL AP, NV, USA | 36.08N | 115.16W | 665 | -8.00 (NAP) | 82-06 | 723860 | -3.8 | -4 | -11 | 47.6 | 42.9 | 44.8 | 43 | 44 | 43.5667 | 45 | 41.2 | 43 | 41.7 | 42 | 41.9667 | 42 | 642 | United_StatesNevadaLAS VEGAS MCCARRAN INTL AP
United_States | Nevada | LOVELOCK DERBY FIELD | LOVELOCK DERBY FIELD, NV, USA | 40.07N | 118.57W | 1190 | -8.00 (NAP) | 88-06 | 725805 | -19.3 | -19 | -32.7 | 44.1 | 36.6 | 40.3 | 38 | 38 | 38.3 | 40 | 34.7 | 37.9 | 36.7 | 36 | 36.4333 | 36 | 643 | United_StatesNevadaLOVELOCK DERBY FIELD
United_States | Nevada | MERCURY DESERT ROCK AP | MERCURY DESERT ROCK AP, NV, USA | 36.62N | 116.03W | 1009 | -8.00 (NAP) | 83-06 | 723870 | -6.9 | -7 | -13.4 | 46.5 | 40.7 | 42.4 | 41.4 | 42 | 41.5 | 42 | 38.3 | 40.7 | 39.2 | 39 | 39.4 | 39 | 644 | United_StatesNevadaMERCURY DESERT ROCK AP
United_States | Nevada | NELLIS AFB | NELLIS AFB, NV, USA | 36.23N | 115.03W | 573 | -8.00 (NAP) | 82-06 | 723865 | -5.6 | -6 | -14.2 | 49.1 | 43.8 | 45.9 | 43.9 | 45 | 44.5333 | 46 | 41.7 | 43.4 | 42.4 | 43 | 42.5 | 43 | 645 | United_StatesNevadaNELLIS AFB
United_States | Nevada | RENO TAHOE INTERNATIONAL AP | RENO TAHOE INTERNATIONAL AP, NV, USA | 39.48N | 119.77W | 1341 | -8.00 (NAP) | 82-06 | 724880 | -14.7 | -15 | -26 | 40.8 | 34.9 | 37.9 | 36.5 | 36 | 36.4333 | 38 | 32.9 | 36 | 35 | 35 | 34.6333 | 35 | 646 | United_StatesNevadaRENO TAHOE INTERNATIONAL AP
United_States | Nevada | TONOPAH AIRPORT | TONOPAH AIRPORT, NV, USA | 38.06N | 117.09W | 1656 | -8.00 (NAP) | 82-06 | 724855 | -16.9 | -17 | -25.5 | 40 | 35 | 37.3 | 36 | 36 | 36.1 | 37 | 33.4 | 36 | 34.6 | 35 | 34.6667 | 35 | 647 | United_StatesNevadaTONOPAH AIRPORT
United_States | Nevada | WINNEMUCCA MUNICIPAL ARPT | WINNEMUCCA MUNICIPAL ARPT, NV, USA | 40.90N | 117.81W | 1315 | -8.00 (NAP) | 82-06 | 725830 | -21.2 | -21 | -35.3 | 43.8 | 35.8 | 39 | 37.5 | 37 | 37.4333 | 39 | 33.9 | 37 | 35.8 | 36 | 35.5667 | 36 | 648 | United_StatesNevadaWINNEMUCCA MUNICIPAL ARPT
United_States | New_Hampshire | BERLIN MUNICIPAL | BERLIN MUNICIPAL, NH, USA | 44.58N | 71.18W | 353 | -5.00 (NAE) | 95-06 | 726160 | -32 | -32 | -41.9 | 36.8 | 32.2 | 31.2 | 31.3 | 32 | 31.5667 | 31 | 28.8 | 28.9 | 28.6 | 29 | 28.7667 | 29 | 649 | United_StatesNew_HampshireBERLIN MUNICIPAL
United_States | New_Hampshire | CONCORD MUNICIPAL ARPT | CONCORD MUNICIPAL ARPT, NH, USA | 43.20N | 71.50W | 106 | -5.00 (NAE) | 82-06 | 726050 | -25.2 | -25 | -36.2 | 38.2 | 33.3 | 34.2 | 33.7 | 34 | 33.7333 | 34 | 31.1 | 32 | 31.4 | 32 | 31.5 | 32 | 650 | United_StatesNew_HampshireCONCORD MUNICIPAL ARPT
United_States | New_Hampshire | DILLANT HOPKINS | DILLANT HOPKINS, NH, USA | 42.90N | 72.27W | 153 | -5.00 (NAE) | 92-06 | 726165 | -25.1 | -25 | -35.1 | 37.7 | 32.7 | 32.9 | 32.8 | 33 | 32.8 | 33 | 30.9 | 31.2 | 30.2 | 31 | 30.7667 | 31 | 651 | United_StatesNew_HampshireDILLANT HOPKINS
United_States | New_Hampshire | ISLE OF SHOALS | ISLE OF SHOALS, NH, USA | 42.97N | 70.62W | 19 | -5.00 (NAE) | 85-06 | 994270 | -17.4 | -17 | -24.7 | 35.4 | 28.5 | 29.4 | 29.1 | 29 | 29 | 29 | 25.6 | 27.2 | 26.5 | 26 | 26.4333 | 26 | 652 | United_StatesNew_HampshireISLE OF SHOALS
United_States | New_Hampshire | JAFFREY MUNICIPAL | JAFFREY MUNICIPAL, NH, USA | 42.80N | 72.00W | 317 | -5.00 (NAE) | 97-06 | 726163 | -23 | -23 | -32.7 | 35.9 | 32.1 | 32.2 | 32.3 | 32 | 32.2 | 32 | 29.1 | 29.8 | 29.7 | 30 | 29.5333 | 30 | 653 | United_StatesNew_HampshireJAFFREY MUNICIPAL
United_States | New_Hampshire | LACONIA MUNI (AWOS) | LACONIA MUNI (AWOS), NH, USA | 43.57N | 71.42W | 166 | -5.00 (NAE) | 92-06 | 726155 | -23.6 | -24 | -34.1 | 37.7 | 32.8 | 32.8 | 32.5 | 33 | 32.7 | 33 | 30.9 | 31.1 | 29.9 | 31 | 30.6333 | 31 | 654 | United_StatesNew_HampshireLACONIA MUNI (AWOS)
United_States | New_Hampshire | LEBANON MUNICIPAL | LEBANON MUNICIPAL, NH, USA | 43.63N | 72.30W | 182 | -5.00 (NAE) | 82-03 | 726116 | -26.7 | -27 | -35.4 | 38 | 32.9 | 33.6 | 33 | 33 | 33.1667 | 34 | 30.3 | 31.3 | 31 | 31 | 30.8667 | 31 | 655 | United_StatesNew_HampshireLEBANON MUNICIPAL
United_States | New_Hampshire | MANCHESTER AIRPORT | MANCHESTER AIRPORT, NH, USA | 42.93N | 71.44W | 71 | -5.00 (NAE) | 84-06 | 743945 | -21 | -21 | -27.7 | 41.6 | 34.4 | 35.5 | 34 | 35 | 34.6333 | 36 | 32.4 | 33 | 32.1 | 33 | 32.5 | 33 | 656 | United_StatesNew_HampshireMANCHESTER AIRPORT
United_States | New_Hampshire | MOUNT WASHINGTON | MOUNT WASHINGTON, NH, USA | 44.27N | 71.30W | 1910 | -5.00 (NAE) | 82-06 | 726130 | -35.5 | -36 | -42 | 22.3 | 17.8 | 18 | 17.5 | 18 | 17.7667 | 18 | 15.6 | 16.1 | 15.7 | 16 | 15.8 | 16 | 657 | United_StatesNew_HampshireMOUNT WASHINGTON
United_States | New_Hampshire | PEASE INTL TRADEPOR | PEASE INTL TRADEPOR, NH, USA | 43.08N | 70.82W | 31 | -5.00 (NAE) | 82-06 | 726055 | -19.4 | -19 | -26.4 | 37.8 | 32.6 | 33.9 | 33.4 | 33 | 33.3 | 34 | 30.2 | 31.6 | 31.1 | 31 | 30.9667 | 31 | 658 | United_StatesNew_HampshirePEASE INTL TRADEPOR
United_States | New_Jersey | ATLANTIC CITY INTL AP | ATLANTIC CITY INTL AP, NJ, USA | 39.46N | 74.46W | 20 | -5.00 (NAE) | 82-06 | 724070 | -16.4 | -16 | -25.1 | 39.7 | 34.5 | 35.8 | 34.9 | 35 | 35.0667 | 36 | 32.1 | 33.8 | 32.6 | 33 | 32.8333 | 33 | 659 | United_StatesNew_JerseyATLANTIC CITY INTL AP
United_States | New_Jersey | BELMAR-FARMINGDALE | BELMAR-FARMINGDALE, NJ, USA | 40.18N | 74.13W | 26 | -5.00 (NAE) | 92-06 | 724084 | -14.3 | -14 | -23.8 | 39.6 | 32.9 | 35.8 | 34.8 | 35 | 34.5 | 36 | 31.4 | 32.9 | 32.1 | 32 | 32.1333 | 32 | 660 | United_StatesNew_JerseyBELMAR-FARMINGDALE
United_States | New_Jersey | CAPE MAY CO | CAPE MAY CO, NJ, USA | 39.00N | 74.90W | 7 | -5.00 (NAE) | 92-06 | 745966 | -12.7 | -13 | -19.7 | 37.1 | 32 | 34 | 32.9 | 33 | 32.9667 | 34 | 29.7 | 32.3 | 31.2 | 31 | 31.0667 | 31 | 661 | United_StatesNew_JerseyCAPE MAY CO
United_States | New_Jersey | MCGUIRE AFB | MCGUIRE AFB, NJ, USA | 40.02N | 74.60W | 45 | -5.00 (NAE) | 82-06 | 724096 | -15.8 | -16 | -23.3 | 41.2 | 34.1 | 36.2 | 35.9 | 35 | 35.4 | 36 | 32.5 | 34.1 | 32.9 | 33 | 33.1667 | 33 | 662 | United_StatesNew_JerseyMCGUIRE AFB
United_States | New_Jersey | MILLVILLE MUNICIPAL AP | MILLVILLE MUNICIPAL AP, NJ, USA | 39.37N | 75.08W | 23 | -5.00 (NAE) | 82-06 | 724075 | -17 | -17 | -25.6 | 39.4 | 34.1 | 35.8 | 34.3 | 35 | 34.7333 | 36 | 32 | 33.7 | 32.4 | 33 | 32.7 | 33 | 663 | United_StatesNew_JerseyMILLVILLE MUNICIPAL AP
United_States | New_Jersey | NEWARK INTERNATIONAL ARPT | NEWARK INTERNATIONAL ARPT, NJ, USA | 40.72N | 74.17W | 9 | -5.00 (NAE) | 82-06 | 725020 | -14.7 | -15 | -23.2 | 40.9 | 35.2 | 37 | 36.2 | 36 | 36.1333 | 37 | 33.2 | 34.8 | 33.5 | 34 | 33.8333 | 34 | 664 | United_StatesNew_JerseyNEWARK INTERNATIONAL ARPT
United_States | New_Jersey | TETERBORO AIRPORT | TETERBORO AIRPORT, NJ, USA | 40.85N | 74.06W | 2 | -5.00 (NAE) | 82-06 | 725025 | -15.8 | -16 | -24.5 | 40.5 | 34.1 | 36.3 | 35 | 35 | 35.1333 | 36 | 32.4 | 33.9 | 32.5 | 33 | 32.9333 | 33 | 665 | United_StatesNew_JerseyTETERBORO AIRPORT
United_States | New_Jersey | TRENTON MERCER COUNTY AP | TRENTON MERCER COUNTY AP, NJ, USA | 40.28N | 74.81W | 65 | -5.00 (NAE) | 84-06 | 724095 | N/A | N/A | N/A | N/A | 34 | 36.7 | 34.8 | 35 | 35.1667 | 37 | 32.4 | 34 | 32.5 | 33 | 32.9667 | 33 | 666 | United_StatesNew_JerseyTRENTON MERCER COUNTY AP
United_States | New_Mexico | ALAMOGORDO WHITE SA | ALAMOGORDO WHITE SA, NM, USA | 32.83N | 105.98W | 1313 | -7.00 (NAM) | 96-06 | 722693 | N/A | N/A | N/A | N/A | 39.2 | 39.1 | 37.9 | 39 | 38.7333 | 39 | 37.7 | 37.8 | 37 | 38 | 37.5 | 38 | 667 | United_StatesNew_MexicoALAMOGORDO WHITE SA
United_States | New_Mexico | ALBUQUERQUE INTL ARPT | ALBUQUERQUE INTL ARPT, NM, USA | 35.04N | 106.62W | 1620 | -7.00 (NAM) | 82-06 | 723650 | -12 | -12 | -20.2 | 40.8 | 37.3 | 36.9 | 35 | 36 | 36.4 | 37 | 34.9 | 35.4 | 33.5 | 35 | 34.6 | 35 | 668 | United_StatesNew_MexicoALBUQUERQUE INTL ARPT
United_States | New_Mexico | CANNON AFB/CLOVIS | CANNON AFB/CLOVIS, NM, USA | 34.38N | 103.32W | 1309 | -7.00 (NAM) | 82-02 | 722686 | -14 | -14 | -20.1 | 43.8 | 39.3 | 38.1 | 36.4 | 38 | 37.9333 | 38 | 36.4 | 36.2 | 34.8 | 36 | 35.8 | 36 | 669 | United_StatesNew_MexicoCANNON AFB/CLOVIS
United_States | New_Mexico | CARLSBAD CAVERN CITY AIR TERM | CARLSBAD CAVERN CITY AIR TERM, NM, USA | 32.34N | 104.26W | 994 | -7.00 (NAM) | 85-06 | 722687 | -10.6 | -11 | -18.4 | 46.4 | 42.2 | 41.1 | 38.9 | 41 | 40.7333 | 41 | 39.6 | 38.7 | 37.3 | 39 | 38.5333 | 39 | 670 | United_StatesNew_MexicoCARLSBAD CAVERN CITY AIR TERM
United_States | New_Mexico | CLAYTON MUNICIPAL AIRPARK | CLAYTON MUNICIPAL AIRPARK, NM, USA | 36.45N | 103.15W | 1516 | -7.00 (NAM) | 82-06 | 723600 | -18.7 | -19 | -29 | 40.4 | 36.6 | 36.2 | 35.1 | 36 | 35.9667 | 36 | 34.1 | 34.7 | 33.5 | 34 | 34.1 | 34 | 671 | United_StatesNew_MexicoCLAYTON MUNICIPAL AIRPARK
United_States | New_Mexico | CLOVIS MUNI (AWOS) | CLOVIS MUNI (AWOS), NM, USA | 34.43N | 103.08W | 1284 | -7.00 (NAM) | 92-06 | 722689 | -14.3 | -14 | -22.8 | 42 | 38.2 | 37.4 | 36.1 | 37 | 37.2333 | 37 | 36.3 | 36.1 | 33.8 | 35 | 35.4 | 35 | 672 | United_StatesNew_MexicoCLOVIS MUNI (AWOS)
United_States | New_Mexico | FARMINGTON FOUR CORNERS REGL | FARMINGTON FOUR CORNERS REGL, NM, USA | 36.74N | 108.23W | 1677 | -7.00 (NAM) | 82-06 | 723658 | -16.8 | -17 | -26.1 | 42 | 36.4 | 37.3 | 35.5 | 36 | 36.4 | 37 | 34 | 35.7 | 33.5 | 34 | 34.4 | 34 | 673 | United_StatesNew_MexicoFARMINGTON FOUR CORNERS REGL
United_States | New_Mexico | GALLUP SEN CLARKE FLD | GALLUP SEN CLARKE FLD, NM, USA | 35.51N | 108.79W | 1971 | -7.00 (NAM) | 82-06 | 723627 | -22.8 | -23 | -32.9 | 38.9 | 34.4 | 35.1 | 33.6 | 34 | 34.3667 | 35 | 32.4 | 33.4 | 31.6 | 32 | 32.4667 | 32 | 674 | United_StatesNew_MexicoGALLUP SEN CLARKE FLD
United_States | New_Mexico | HOLLOMAN AFB | HOLLOMAN AFB, NM, USA | 32.85N | 106.10W | 1248 | -7.00 (NAM) | 82-01 | 747320 | -10.7 | -11 | -16.6 | 44 | 39.6 | 38.9 | 36.8 | 38 | 38.4333 | 39 | 37.6 | 37.1 | 35.1 | 37 | 36.6 | 37 | 675 | United_StatesNew_MexicoHOLLOMAN AFB
United_States | New_Mexico | ROSWELL INDUSTRIAL AIR PARK | ROSWELL INDUSTRIAL AIR PARK, NM, USA | 33.31N | 104.54W | 1118 | -7.00 (NAM) | 82-06 | 722680 | -13.1 | -13 | -21.8 | 44.3 | 40.1 | 39.1 | 37.5 | 39 | 38.9 | 39 | 38.1 | 37.3 | 36 | 37 | 37.1333 | 37 | 676 | United_StatesNew_MexicoROSWELL INDUSTRIAL AIR PARK
United_States | New_Mexico | SIERRA BLANCA RGNL | SIERRA BLANCA RGNL, NM, USA | 33.47N | 105.53W | 2078 | -7.00 (NAM) | 96-06 | 722683 | -13 | -13 | -19.9 | 37 | 33 | 32.5 | 31.2 | 32 | 32.2333 | 33 | 32 | 31 | 28.9 | 31 | 30.6333 | 31 | 677 | United_StatesNew_MexicoSIERRA BLANCA RGNL
United_States | New_Mexico | TAOS MUNI APT(AWOS) | TAOS MUNI APT(AWOS), NM, USA | 36.45N | 105.67W | 2161 | -7.00 (NAM) | 92-06 | 723663 | -22.7 | -23 | -29.7 | 36.8 | 32.7 | 32.9 | 31.4 | 32 | 32.3333 | 33 | 31.1 | 31.4 | 29.1 | 31 | 30.5333 | 31 | 678 | United_StatesNew_MexicoTAOS MUNI APT(AWOS)
United_States | New_Mexico | TRUTH OR CONSEQUENCES MUNI AP | TRUTH OR CONSEQUENCES MUNI AP, NM, USA | 33.24N | 107.27W | 1481 | -7.00 (NAM) | 82-06 | 722710 | -10.4 | -10 | -30.4 | 43.5 | 39.5 | 38.1 | 36.1 | 38 | 37.9 | 38 | 37.2 | 36.5 | 34.4 | 36 | 36.0333 | 36 | 679 | United_StatesNew_MexicoTRUTH OR CONSEQUENCES MUNI AP
United_States | New_Mexico | WHITE SANDS | WHITE SANDS, NM, USA | 32.38N | 106.48W | 1244 | -7.00 (NAM) | 82-93 | 722690 | -12 | -12 | -20.1 | 43 | 39.6 | 38.7 | 36.3 | 38 | 38.2 | 39 | 37.9 | 36.9 | 35 | 37 | 36.6 | 37 | 680 | United_StatesNew_MexicoWHITE SANDS
United_States | New_York | ALBANY COUNTY AP | ALBANY COUNTY AP, NY, USA | 42.75N | 73.80W | 89 | -5.00 (NAE) | 82-06 | 725180 | -22.8 | -23 | -33 | 38.2 | 33 | 33.6 | 33 | 33 | 33.2 | 34 | 30.6 | 31.8 | 30.8 | 31 | 31.0667 | 31 | 681 | United_StatesNew_YorkALBANY COUNTY AP
United_States | New_York | AMBROSE LIGHT | AMBROSE LIGHT, NY, USA | 40.45N | 73.80W | 21 | -5.00 (NAE) | 85-06 | 994100 | -12.8 | -13 | -18.7 | 35.7 | 29.4 | 31.5 | 30.4 | 30 | 30.4333 | 32 | 26.8 | 29.2 | 27.6 | 28 | 27.8667 | 28 | 682 | United_StatesNew_YorkAMBROSE LIGHT
United_States | New_York | BINGHAMTON EDWIN A LINK FIELD | BINGHAMTON EDWIN A LINK FIELD, NY, USA | 42.21N | 75.98W | 499 | -5.00 (NAE) | 82-06 | 725150 | -21.6 | -22 | -29.1 | 37 | 30.6 | 32.1 | 31.5 | 31 | 31.4 | 32 | 28.3 | 29.8 | 29.2 | 29 | 29.1 | 29 | 683 | United_StatesNew_YorkBINGHAMTON EDWIN A LINK FIELD
United_States | New_York | BUFFALO NIAGARA INTL AP | BUFFALO NIAGARA INTL AP, NY, USA | 42.94N | 78.74W | 215 | -5.00 (NAE) | 82-06 | 725280 | -19.5 | -20 | -28.1 | 36.9 | 31.7 | 32.4 | 31.7 | 32 | 31.9333 | 32 | 29.3 | 30.3 | 29.6 | 30 | 29.7333 | 30 | 684 | United_StatesNew_YorkBUFFALO NIAGARA INTL AP
United_States | New_York | DUNKIRK | DUNKIRK, NY, USA | 42.48N | 79.35W | 197 | -5.00 (NAE) | 85-06 | 994250 | -15.6 | -16 | -24.9 | 36.2 | 28.7 | 29.1 | 29 | 29 | 28.9333 | 29 | 26.3 | 27.4 | 27.4 | 27 | 27.0333 | 27 | 685 | United_StatesNew_YorkDUNKIRK
United_States | New_York | ELMIRA CORNING REGIONAL AP | ELMIRA CORNING REGIONAL AP, NY, USA | 42.16N | 76.89W | 291 | -5.00 (NAE) | 82-06 | 725156 | -23.4 | -23 | -32.2 | 39.6 | 32.9 | 35 | 33.2 | 34 | 33.7 | 35 | 30.9 | 32.4 | 31.2 | 32 | 31.5 | 32 | 686 | United_StatesNew_YorkELMIRA CORNING REGIONAL AP
United_States | New_York | FORT DRUM/WHEELER-S | FORT DRUM/WHEELER-S, NY, USA | 44.05N | 75.73W | 207 | -5.00 (NAE) | 89-06 | 743700 | -28.1 | -28 | -38.2 | 36.6 | 31.4 | 32.1 | 31.4 | 32 | 31.6333 | 32 | 29.2 | 30 | 29.1 | 29 | 29.4333 | 29 | 687 | United_StatesNew_YorkFORT DRUM/WHEELER-S
United_States | New_York | GALLOO ISLAND | GALLOO ISLAND, NY, USA | 43.88N | 76.43W | 76 | -5.00 (NAE) | 85-02 | 994320 | -22 | -22 | -29.7 | 32.4 | 25.3 | 27.2 | 27.9 | 27 | 26.8 | 27 | 23.2 | 25.6 | 26.1 | 25 | 24.9667 | 25 | 688 | United_StatesNew_YorkGALLOO ISLAND
United_States | New_York | GLENS FALLS AP | GLENS FALLS AP, NY, USA | 43.34N | 73.61W | 102 | -5.00 (NAE) | 82-06 | 725185 | -28.5 | -29 | -38.7 | 37.7 | 32.8 | 33.3 | 32.4 | 33 | 32.8333 | 33 | 30.2 | 31.2 | 30.1 | 31 | 30.5 | 31 | 689 | United_StatesNew_YorkGLENS FALLS AP
United_States | New_York | GRIFFISS AFB | GRIFFISS AFB, NY, USA | 43.23N | 75.40W | 158 | -5.00 (NAE) | 82-94 | 725196 | -25.8 | -26 | -31.3 | 37.7 | 32.9 | 34.1 | 33.1 | 33 | 33.3667 | 34 | 30.2 | 31.8 | 30.5 | 31 | 30.8333 | 31 | 690 | United_StatesNew_YorkGRIFFISS AFB
United_States | New_York | ISLIP LONG ISL MACARTHUR AP | ISLIP LONG ISL MACARTHUR AP, NY, USA | 40.79N | 73.10W | 33 | -5.00 (NAE) | 82-06 | 725035 | -15.3 | -15 | -22.6 | 39.9 | 32.4 | 34.2 | 32.5 | 33 | 33.0333 | 34 | 29.9 | 31.8 | 30.5 | 31 | 30.7333 | 31 | 691 | United_StatesNew_YorkISLIP LONG ISL MACARTHUR AP
United_States | New_York | JAMESTOWN (AWOS) | JAMESTOWN (AWOS), NY, USA | 42.15N | 79.27W | 525 | -5.00 (NAE) | 91-06 | 725235 | -20.1 | -20 | -31.5 | 36.7 | 29.1 | 30.9 | 29.7 | 30 | 29.9 | 31 | 27.7 | 28 | 27.6 | 28 | 27.7667 | 28 | 692 | United_StatesNew_YorkJAMESTOWN (AWOS)
United_States | New_York | MASSENA AP | MASSENA AP, NY, USA | 44.94N | 74.85W | 65 | -5.00 (NAE) | 82-06 | 726223 | -30.4 | -30 | -39.8 | 37 | 32.2 | 32.8 | 32.3 | 32 | 32.4333 | 33 | 30 | 31 | 30.1 | 30 | 30.3667 | 30 | 693 | United_StatesNew_YorkMASSENA AP
United_States | New_York | MONTICELLO(AWOS) | MONTICELLO(AWOS), NY, USA | 41.70N | 74.80W | 428 | -5.00 (NAE) | 92-06 | 725145 | N/A | N/A | N/A | N/A | 30.1 | 32.3 | 32.4 | 32 | 31.6 | 32 | 28 | 30.2 | 29.3 | 29 | 29.1667 | 29 | 694 | United_StatesNew_YorkMONTICELLO(AWOS)
United_States | New_York | NEW YORK J F KENNEDY INT'L AR | NEW YORK J F KENNEDY INT'L AR, NY, USA | 40.66N | 73.80W | 7 | -5.00 (NAE) | 82-06 | 744860 | -13.7 | -14 | -21.3 | 39.9 | 33.3 | 35.3 | 33.7 | 34 | 34.1 | 35 | 30.6 | 32.3 | 31.1 | 31 | 31.3333 | 31 | 695 | United_StatesNew_YorkNEW YORK J F KENNEDY INT'L AR
United_States | New_York | NEW YORK LAGUARDIA ARPT | NEW YORK LAGUARDIA ARPT, NY, USA | 40.78N | 73.88W | 9 | -5.00 (NAE) | 82-06 | 725030 | -13.7 | -14 | -22 | 40.2 | 34.3 | 35.9 | 35 | 35 | 35.0667 | 36 | 32.1 | 33.7 | 32.6 | 33 | 32.8 | 33 | 696 | United_StatesNew_YorkNEW YORK LAGUARDIA ARPT
United_States | New_York | NEWBURGH/STEWART | NEWBURGH/STEWART, NY, USA | 41.50N | 74.10W | 177 | -5.00 (NAE) | 82-06 | 725038 | -20 | -20 | -30.5 | 39.9 | 32.6 | 34.9 | 33.9 | 34 | 33.8 | 35 | 30.8 | 32.3 | 31.2 | 31 | 31.4333 | 31 | 697 | United_StatesNew_YorkNEWBURGH/STEWART
United_States | New_York | NIAGARA FALLS AF | NIAGARA FALLS AF, NY, USA | 43.11N | 78.95W | 179 | -5.00 (NAE) | 82-06 | 725287 | -20.3 | -20 | -29.9 | 37.5 | 32.3 | 33.3 | 32.4 | 33 | 32.6667 | 33 | 30 | 31.2 | 30.2 | 30 | 30.4667 | 30 | 698 | United_StatesNew_YorkNIAGARA FALLS AF
United_States | New_York | PLATTSBURGH AFB | PLATTSBURGH AFB, NY, USA | 44.65N | 73.47W | 72 | -5.00 (NAE) | 82-95 | 726225 | -28 | -28 | -36.8 | 37.5 | 32.8 | 32.4 | 31.7 | 32 | 32.3 | 32 | 29.2 | 30.2 | 29.1 | 30 | 29.5 | 30 | 699 | United_StatesNew_YorkPLATTSBURGH AFB
United_States | New_York | POUGHKEEPSIE DUTCHESS CO AP | POUGHKEEPSIE DUTCHESS CO AP, NY, USA | 41.63N | 73.88W | 49 | -5.00 (NAE) | 82-06 | 725036 | -22.3 | -22 | -31.6 | 41 | 33.9 | 36.3 | 34.6 | 35 | 34.9333 | 36 | 31.8 | 33.4 | 32.3 | 33 | 32.5 | 33 | 700 | United_StatesNew_YorkPOUGHKEEPSIE DUTCHESS CO AP
United_States | New_York | REPUBLIC | REPUBLIC, NY, USA | 40.72N | 73.40W | 26 | -5.00 (NAE) | 96-06 | 744864 | -13 | -13 | -21.2 | 40.8 | 32.8 | 35 | 33.9 | 34 | 33.9 | 35 | 31 | 32.6 | 32 | 32 | 31.8667 | 32 | 701 | United_StatesNew_YorkREPUBLIC
United_States | New_York | ROCHESTER GREATER ROCHESTER I | ROCHESTER GREATER ROCHESTER I, NY, USA | 43.12N | 77.68W | 169 | -5.00 (NAE) | 82-06 | 725290 | -20 | -20 | -29.3 | 38.2 | 32.4 | 33.7 | 33 | 33 | 33.0333 | 34 | 30.1 | 31.5 | 30.4 | 31 | 30.6667 | 31 | 702 | United_StatesNew_YorkROCHESTER GREATER ROCHESTER I
United_States | New_York | SUPERIOR SHOALS | SUPERIOR SHOALS, NY, USA | 44.48N | 75.80W | 79 | -5.00 (NAE) | 94-06 | 994580 | -23.1 | -23 | -34.3 | 32.8 | 28.3 | 28.6 | 28.9 | 29 | 28.6 | 29 | 26.2 | 27.4 | 27.2 | 27 | 26.9333 | 27 | 703 | United_StatesNew_YorkSUPERIOR SHOALS
United_States | New_York | SYRACUSE HANCOCK INT'L ARPT | SYRACUSE HANCOCK INT'L ARPT, NY, USA | 43.11N | 76.10W | 127 | -5.00 (NAE) | 82-06 | 725190 | -23.6 | -24 | -34 | 38.9 | 32.9 | 33.4 | 33.6 | 33 | 33.3 | 33 | 30.7 | 31.6 | 30.9 | 31 | 31.0667 | 31 | 704 | United_StatesNew_YorkSYRACUSE HANCOCK INT'L ARPT
United_States | New_York | UTICA ONEIDA COUNTY AP | UTICA ONEIDA COUNTY AP, NY, USA | 43.15N | 75.38W | 227 | -5.00 (NAE) | 82-06 | 725197 | -24.4 | -24 | -32.2 | 37 | 31.9 | 32.8 | 32.4 | 32 | 32.3667 | 33 | 30 | 30.9 | 29.9 | 30 | 30.2667 | 30 | 705 | United_StatesNew_YorkUTICA ONEIDA COUNTY AP
United_States | New_York | WATERTOWN AP | WATERTOWN AP, NY, USA | 43.99N | 76.02W | 102 | -5.00 (NAE) | 82-06 | 726227 | -32 | -32 | -42.1 | 36.4 | 30.5 | 31.2 | 31.5 | 31 | 31.0667 | 31 | 28.4 | 29.4 | 29.3 | 29 | 29.0333 | 29 | 706 | United_StatesNew_YorkWATERTOWN AP
United_States | New_York | WHITE PLAINS WESTCHESTER CO A | WHITE PLAINS WESTCHESTER CO A, NY, USA | 41.07N | 73.71W | 121 | -5.00 (NAE) | 82-06 | 725037 | -16.7 | -17 | -25.4 | 39.4 | 32.8 | 34.7 | 33.7 | 34 | 33.7333 | 35 | 30.9 | 32.4 | 31.2 | 32 | 31.5 | 32 | 707 | United_StatesNew_YorkWHITE PLAINS WESTCHESTER CO A
United_States | North_Carolina | ASHEVILLE REGIONAL ARPT | ASHEVILLE REGIONAL ARPT, NC, USA | 35.43N | 82.54W | 661 | -5.00 (NAE) | 82-06 | 723150 | -15.2 | -15 | -26.1 | 36.9 | 31.6 | 33.2 | 32.7 | 33 | 32.5 | 33 | 29.8 | 31.5 | 30.8 | 31 | 30.7 | 31 | 708 | United_StatesNorth_CarolinaASHEVILLE REGIONAL ARPT
United_States | North_Carolina | CAPE HATTERAS | CAPE HATTERAS, NC, USA | 35.27N | 75.55W | 3 | -5.00 (NAE) | 96-06 | 723040 | -4.1 | -4 | -11 | 34.5 | 30 | 31.5 | 31.6 | 31 | 31.0333 | 32 | 29 | 30.2 | 30.5 | 30 | 29.9 | 30 | 709 | United_StatesNorth_CarolinaCAPE HATTERAS
United_States | North_Carolina | CAPE LOOKOUT | CAPE LOOKOUT, NC, USA | 34.62N | 76.52W | 11 | -5.00 (NAE) | 85-06 | 994160 | -6 | -6 | -13.3 | 32.9 | 28.7 | 30.6 | 30.2 | 30 | 29.8333 | 31 | 27.9 | 29.7 | 29.3 | 29 | 28.9667 | 29 | 710 | United_StatesNorth_CarolinaCAPE LOOKOUT
United_States | North_Carolina | CHARLOTTE DOUGLAS INTL ARPT | CHARLOTTE DOUGLAS INTL ARPT, NC, USA | 35.21N | 80.94W | 234 | -5.00 (NAE) | 82-06 | 723140 | -11.1 | -11 | -20.3 | 40.7 | 35 | 36.8 | 35.7 | 36 | 35.8333 | 37 | 33.1 | 34.9 | 34 | 34 | 34 | 34 | 711 | United_StatesNorth_CarolinaCHARLOTTE DOUGLAS INTL ARPT
United_States | North_Carolina | CHERRY POINT MCAS | CHERRY POINT MCAS, NC, USA | 34.90N | 76.88W | 9 | -5.00 (NAE) | 82-06 | 723090 | -9.3 | -9 | -18.7 | 40.7 | 34.7 | 36.3 | 35.1 | 35 | 35.3667 | 36 | 32.7 | 34.2 | 33 | 33 | 33.3 | 33 | 712 | United_StatesNorth_CarolinaCHERRY POINT MCAS
United_States | North_Carolina | DIAMOND SHOALS (LS) | DIAMOND SHOALS (LS), NC, USA | 35.15N | 75.30W | 0 | -5.00 (NAE) | 89-03 | 994030 | -3 | -3 | -11.2 | 32.3 | 28.5 | 29.6 | 29.1 | 29 | 29.0667 | 30 | 27.5 | 28.7 | 28.5 | 28 | 28.2333 | 28 | 713 | United_StatesNorth_CarolinaDIAMOND SHOALS (LS)
United_States | North_Carolina | FAYETTEVILLE RGNL G | FAYETTEVILLE RGNL G, NC, USA | 34.98N | 78.88W | 59 | -5.00 (NAE) | 82-06 | 723035 | -10.2 | -10 | -19.8 | 42.2 | 36.4 | 37.5 | 37.3 | 37 | 37.0667 | 38 | 34.1 | 35.7 | 34.8 | 35 | 34.8667 | 35 | 714 | United_StatesNorth_CarolinaFAYETTEVILLE RGNL G
United_States | North_Carolina | FORT BRAGG/SIMMONS | FORT BRAGG/SIMMONS, NC, USA | 35.13N | 78.93W | 93 | -5.00 (NAE) | 82-01 | 746930 | -10.4 | -10 | -21.5 | 43 | 37.2 | 37.8 | 37 | 37 | 37.3333 | 38 | 34.9 | 36.2 | 34.8 | 35 | 35.3 | 35 | 715 | United_StatesNorth_CarolinaFORT BRAGG/SIMMONS
United_States | North_Carolina | FRYING PAN SHOALS | FRYING PAN SHOALS, NC, USA | 33.48N | 77.58W | 24 | -5.00 (NAE) | 89-05 | 994040 | -1.7 | -2 | -10.5 | 31.7 | 29.1 | 30.1 | 30.1 | 30 | 29.7667 | 30 | 27.8 | 29.1 | 29.2 | 29 | 28.7 | 29 | 716 | United_StatesNorth_CarolinaFRYING PAN SHOALS
United_States | North_Carolina | GREENSBORO PIEDMONT TRIAD INT | GREENSBORO PIEDMONT TRIAD INT, NC, USA | 36.10N | 79.94W | 270 | -5.00 (NAE) | 82-06 | 723170 | -13 | -13 | -21.5 | 39.7 | 33.8 | 35.3 | 34.9 | 35 | 34.6667 | 35 | 32.1 | 33.7 | 33 | 33 | 32.9333 | 33 | 717 | United_StatesNorth_CarolinaGREENSBORO PIEDMONT TRIAD INT
United_States | North_Carolina | HATTERAS BILLY MITCHELL AP | HATTERAS BILLY MITCHELL AP, NC, USA | 35.23N | 75.62W | 3 | -5.00 (NAE) | 82-06 | 723139 | -5.8 | -6 | -14.1 | 36 | 31 | 32.6 | 31.9 | 32 | 31.8333 | 33 | 29.7 | 31.3 | 31 | 31 | 30.6667 | 31 | 718 | United_StatesNorth_CarolinaHATTERAS BILLY MITCHELL AP
United_States | North_Carolina | HICKORY REGIONAL AP | HICKORY REGIONAL AP, NC, USA | 35.74N | 81.39W | 362 | -5.00 (NAE) | 82-06 | 723145 | -12.5 | -13 | -21.2 | 40.5 | 33.8 | 35.9 | 35.4 | 35 | 35.0333 | 36 | 32.2 | 34.1 | 33 | 33 | 33.1 | 33 | 719 | United_StatesNorth_CarolinaHICKORY REGIONAL AP
United_States | North_Carolina | JACKSONVILLE (AWOS) | JACKSONVILLE (AWOS), NC, USA | 34.83N | 77.62W | 29 | -5.00 (NAE) | 92-06 | 723069 | -10.5 | -11 | -15.3 | 40.8 | 35.9 | 36.8 | 35.9 | 36 | 36.2 | 37 | 33.2 | 34.9 | 33.7 | 34 | 33.9333 | 34 | 720 | United_StatesNorth_CarolinaJACKSONVILLE (AWOS)
United_States | North_Carolina | NEW BERN CRAVEN CO REGL AP | NEW BERN CRAVEN CO REGL AP, NC, USA | 35.07N | 77.05W | 7 | -5.00 (NAE) | 82-06 | 723095 | -9.4 | -9 | -19.3 | 39.8 | 35.3 | 36.1 | 35.3 | 36 | 35.5667 | 36 | 33.3 | 34.4 | 33.6 | 34 | 33.7667 | 34 | 721 | United_StatesNorth_CarolinaNEW BERN CRAVEN CO REGL AP
United_States | North_Carolina | NEW RIVER MCAF | NEW RIVER MCAF, NC, USA | 34.70N | 77.43W | 8 | -5.00 (NAE) | 82-06 | 723096 | -9.3 | -9 | -19.1 | 39.7 | 35 | 36.2 | 35 | 35 | 35.4 | 36 | 33 | 34.3 | 33.3 | 34 | 33.5333 | 34 | 722 | United_StatesNorth_CarolinaNEW RIVER MCAF
United_States | North_Carolina | PITT GREENVILLE ARP | PITT GREENVILLE ARP, NC, USA | 35.63N | 77.40W | 8 | -5.00 (NAE) | 94-06 | 723065 | -9.5 | -10 | -15.8 | 40.5 | 37 | 37.3 | 37.2 | 37 | 37.1667 | 37 | 34.1 | 35.2 | 34.2 | 35 | 34.5 | 35 | 723 | United_StatesNorth_CarolinaPITT GREENVILLE ARP
United_States | North_Carolina | POPE AFB | POPE AFB, NC, USA | 35.17N | 79.02W | 66 | -5.00 (NAE) | 82-06 | 723030 | -10.4 | -10 | -18.8 | 42.7 | 37.4 | 37.9 | 37.5 | 38 | 37.6 | 38 | 35 | 36.3 | 35.2 | 36 | 35.5 | 36 | 724 | United_StatesNorth_CarolinaPOPE AFB
United_States | North_Carolina | RALEIGH DURHAM INTERNATIONAL | RALEIGH DURHAM INTERNATIONAL, NC, USA | 35.87N | 78.79W | 133 | -5.00 (NAE) | 82-06 | 723060 | -11.9 | -12 | -20.9 | 40.9 | 34.9 | 36.4 | 36.4 | 36 | 35.9 | 36 | 33.1 | 34.8 | 33.9 | 34 | 33.9333 | 34 | 725 | United_StatesNorth_CarolinaRALEIGH DURHAM INTERNATIONAL
United_States | North_Carolina | RICHMOND INTERNATIONAL AP | RICHMOND INTERNATIONAL AP, NC, USA | 37.51N | 77.32W | 50 | -5.00 (NAE) | 82-06 | 724010 | -13.2 | -13 | -22.2 | 40.9 | 35.6 | 36.6 | 36.1 | 36 | 36.1 | 37 | 33.5 | 35.1 | 34.1 | 34 | 34.2333 | 34 | 726 | United_StatesNorth_CarolinaRICHMOND INTERNATIONAL AP
United_States | North_Carolina | SEYMOUR-JOHNSON AFB | SEYMOUR-JOHNSON AFB, NC, USA | 35.33N | 77.97W | 33 | -5.00 (NAE) | 82-05 | 723066 | -10.1 | -10 | -20.1 | 42.1 | 36.4 | 37.7 | 37.3 | 37 | 37.1333 | 38 | 34.6 | 36.1 | 34.8 | 35 | 35.1667 | 35 | 727 | United_StatesNorth_CarolinaSEYMOUR-JOHNSON AFB
United_States | North_Carolina | SOUTHERN PINES AWOS | SOUTHERN PINES AWOS, NC, USA | 35.23N | 79.40W | 141 | -5.00 (NAE) | 92-06 | 723143 | -12.5 | -13 | -17.9 | 48.7 | 36.2 | 36.4 | 36.2 | 36 | 36.2667 | 36 | 33.8 | 34.9 | 34 | 34 | 34.2333 | 34 | 728 | United_StatesNorth_CarolinaSOUTHERN PINES AWOS
United_States | North_Carolina | WILMINGTON INTERNATIONAL ARPT | WILMINGTON INTERNATIONAL ARPT, NC, USA | 34.27N | 77.91W | 12 | -5.00 (NAE) | 82-06 | 723013 | -8.7 | -9 | -17 | 39.5 | 35 | 36.1 | 35 | 35 | 35.3667 | 36 | 32.9 | 34.4 | 33.2 | 34 | 33.5 | 34 | 729 | United_StatesNorth_CarolinaWILMINGTON INTERNATIONAL ARPT
United_States | North_Carolina | WINSTON-SALEM REYNOLDS AP | WINSTON-SALEM REYNOLDS AP, NC, USA | 36.13N | 80.22W | 296 | -5.00 (NAE) | 82-06 | 723193 | -12.5 | -13 | -21.7 | 39.1 | 33.7 | 35.7 | 34.8 | 35 | 34.7333 | 36 | 32.2 | 34 | 32.8 | 33 | 33 | 33 | 730 | United_StatesNorth_CarolinaWINSTON-SALEM REYNOLDS AP
United_States | North_Dakota | BISMARCK MUNICIPAL ARPT | BISMARCK MUNICIPAL ARPT, ND, USA | 46.77N | 100.75W | 506 | -6.00 (NAC) | 82-06 | 727640 | -33.1 | -33 | -43.9 | 44.8 | 35.8 | 38 | 36.8 | 37 | 36.8667 | 38 | 31.9 | 34.6 | 33.9 | 33 | 33.4667 | 33 | 731 | United_StatesNorth_DakotaBISMARCK MUNICIPAL ARPT
United_States | North_Dakota | DEVILS LAKE (AMOS) | DEVILS LAKE (AMOS), ND, USA | 48.10N | 98.87W | 443 | -6.00 (NAC) | 82-92 | 727580 | -33.3 | -33 | -40.4 | 40.4 | 35.4 | 35.4 | 35.5 | 35 | 35.4333 | 35 | 31 | 32.3 | 32.8 | 32 | 32.0333 | 32 | 732 | United_StatesNorth_DakotaDEVILS LAKE (AMOS)
United_States | North_Dakota | DEVILS LAKE(AWOS) | DEVILS LAKE(AWOS), ND, USA | 48.12N | 98.92W | 443 | -6.00 (NAC) | 91-06 | 727573 | -32.8 | -33 | -42.4 | 38.1 | 31.4 | 32.5 | 32.4 | 32 | 32.1 | 33 | 28.5 | 29.8 | 29.6 | 29 | 29.3 | 29 | 733 | United_StatesNorth_DakotaDEVILS LAKE(AWOS)
United_States | North_Dakota | DICKINSON MUNICIPAL AP | DICKINSON MUNICIPAL AP, ND, USA | 46.80N | 102.80W | 787 | -7.00 (NAM) | 82-06 | 727645 | -31.2 | -31 | -38.2 | 42.9 | 33.3 | 37.5 | 36.4 | 36 | 35.7333 | 38 | 30.7 | 33.9 | 34 | 33 | 32.8667 | 33 | 734 | United_StatesNorth_DakotaDICKINSON MUNICIPAL AP
United_States | North_Dakota | FARGO HECTOR INTERNATIONAL AP | FARGO HECTOR INTERNATIONAL AP, ND, USA | 46.93N | 96.81W | 274 | -6.00 (NAC) | 82-06 | 727530 | -31.5 | -32 | -40.1 | 41.5 | 34.1 | 35.5 | 34.9 | 35 | 34.8333 | 36 | 31.5 | 32.4 | 32.2 | 32 | 32.0333 | 32 | 735 | United_StatesNorth_DakotaFARGO HECTOR INTERNATIONAL AP
United_States | North_Dakota | GRAND FORKS AFB | GRAND FORKS AFB, ND, USA | 47.97N | 97.40W | 276 | -6.00 (NAC) | 82-06 | 727575 | -31.8 | -32 | -41.1 | 42.3 | 34.5 | 34.9 | 35.2 | 35 | 34.8667 | 35 | 31.3 | 32.2 | 32.4 | 32 | 31.9667 | 32 | 736 | United_StatesNorth_DakotaGRAND FORKS AFB
United_States | North_Dakota | GRAND FORKS INTERNATIONAL AP | GRAND FORKS INTERNATIONAL AP, ND, USA | 47.95N | 97.18W | 254 | -6.00 (NAC) | 82-06 | 727576 | -33 | -33 | -42.3 | 42 | 33.9 | 34 | 34.6 | 34 | 34.1667 | 34 | 30.9 | 31.4 | 32 | 31 | 31.4333 | 31 | 737 | United_StatesNorth_DakotaGRAND FORKS INTERNATIONAL AP
United_States | North_Dakota | JAMESTOWN MUNICIPAL ARPT | JAMESTOWN MUNICIPAL ARPT, ND, USA | 46.93N | 98.68W | 455 | -6.00 (NAC) | 82-06 | 727535 | -30.6 | -31 | -39.6 | 42.2 | 34.4 | 36.3 | 36.1 | 36 | 35.6 | 36 | 31.2 | 32.7 | 33.1 | 32 | 32.3333 | 32 | 738 | United_StatesNorth_DakotaJAMESTOWN MUNICIPAL ARPT
United_States | North_Dakota | LIDGERWOOD (RAMOS) | LIDGERWOOD (RAMOS), ND, USA | 46.10N | 97.15W | 351 | -6.00 (NAC) | 83-96 | 727534 | -30.8 | -31 | -38.2 | 44.2 | 34.8 | 37.9 | 36.2 | 36 | 36.3 | 38 | 32.4 | 33.7 | 32.5 | 33 | 32.8667 | 33 | 739 | United_StatesNorth_DakotaLIDGERWOOD (RAMOS)
United_States | North_Dakota | MINOT AFB | MINOT AFB, ND, USA | 48.42N | 101.35W | 497 | -6.00 (NAC) | 82-06 | 727675 | -32.5 | -33 | -43.1 | 42.8 | 36.1 | 35.7 | 37.2 | 36 | 36.3333 | 36 | 32.4 | 32.4 | 34.1 | 33 | 32.9667 | 33 | 740 | United_StatesNorth_DakotaMINOT AFB
United_States | North_Dakota | MINOT FAA AP | MINOT FAA AP, ND, USA | 48.26N | 101.28W | 522 | -6.00 (NAC) | 82-06 | 727676 | -30.6 | -31 | -40.3 | 41.1 | 34.8 | 35.1 | 35.9 | 35 | 35.2667 | 35 | 31.2 | 32.3 | 33.2 | 32 | 32.2333 | 32 | 741 | United_StatesNorth_DakotaMINOT FAA AP
United_States | North_Dakota | WILLISTON SLOULIN INTL AP | WILLISTON SLOULIN INTL AP, ND, USA | 48.20N | 103.64W | 581 | -6.00 (NAC) | 82-06 | 727670 | -34 | -34 | -44 | 43 | 36.3 | 37.4 | 37.6 | 37 | 37.1 | 37 | 32.7 | 34.7 | 34.8 | 34 | 34.0667 | 34 | 742 | United_StatesNorth_DakotaWILLISTON SLOULIN INTL AP
United_States | Ohio | AKRON AKRON-CANTON REG AP | AKRON AKRON-CANTON REG AP, OH, USA | 40.92N | 81.44W | 377 | -5.00 (NAE) | 82-06 | 725210 | -21 | -21 | -33.6 | 37.8 | 32.3 | 33.7 | 33 | 33 | 33 | 34 | 30.4 | 31.7 | 30.9 | 31 | 31 | 31 | 743 | United_StatesOhioAKRON AKRON-CANTON REG AP
United_States | Ohio | CINCINNATI MUNICIPAL AP LUNKI | CINCINNATI MUNICIPAL AP LUNKI, OH, USA | 39.10N | 84.42W | 152 | -5.00 (NAE) | 82-06 | 724297 | -18.8 | -19 | -31.9 | 40.3 | 33.9 | 36.1 | 35.3 | 35 | 35.1 | 36 | 32.2 | 34 | 33.3 | 33 | 33.1667 | 33 | 744 | United_StatesOhioCINCINNATI MUNICIPAL AP LUNKI
United_States | Ohio | CLEVELAND HOPKINS INTL AP | CLEVELAND HOPKINS INTL AP, OH, USA | 41.41N | 81.85W | 245 | -5.00 (NAE) | 82-06 | 725240 | -20 | -20 | -31.4 | 38.9 | 33 | 34.2 | 33.1 | 33 | 33.4333 | 34 | 31.1 | 32.1 | 31.1 | 31 | 31.4333 | 31 | 745 | United_StatesOhioCLEVELAND HOPKINS INTL AP
United_States | Ohio | COLUMBUS PORT COLUMBUS INTL A | COLUMBUS PORT COLUMBUS INTL A, OH, USA | 39.99N | 82.88W | 249 | -5.00 (NAE) | 82-06 | 724280 | -19.6 | -20 | -32.5 | 39 | 33.8 | 35.1 | 34.1 | 34 | 34.3333 | 35 | 31.8 | 32.9 | 32.3 | 32 | 32.3333 | 32 | 746 | United_StatesOhioCOLUMBUS PORT COLUMBUS INTL A
United_States | Ohio | DAYTON INTERNATIONAL AIRPORT | DAYTON INTERNATIONAL AIRPORT, OH, USA | 39.91N | 84.22W | 306 | -5.00 (NAE) | 82-06 | 724290 | -21.4 | -21 | -34.3 | 39.2 | 33.5 | 34.8 | 33.9 | 34 | 34.0667 | 35 | 31.3 | 32.5 | 31.9 | 32 | 31.9 | 32 | 747 | United_StatesOhioDAYTON INTERNATIONAL AIRPORT
United_States | Ohio | FINDLAY AIRPORT | FINDLAY AIRPORT, OH, USA | 41.01N | 83.67W | 248 | -5.00 (NAE) | 82-06 | 725366 | -21.5 | -22 | -33.3 | 39 | 33.8 | 34.9 | 33.6 | 34 | 34.1 | 35 | 31.8 | 32.5 | 31.4 | 32 | 31.9 | 32 | 748 | United_StatesOhioFINDLAY AIRPORT
United_States | Ohio | LANCASTER\FAIRFIEL | LANCASTER\FAIRFIEL, OH, USA | 39.75N | 82.65W | 264 | -5.00 (NAE) | 99-06 | 724294 | -21.4 | -21 | -34.9 | 39 | 32.8 | 33.9 | 33.9 | 34 | 33.5333 | 34 | 31.3 | 32.4 | 32.4 | 32 | 32.0333 | 32 | 749 | United_StatesOhioLANCASTER\FAIRFIEL
United_States | Ohio | MANSFIELD LAHM MUNICIPAL ARPT | MANSFIELD LAHM MUNICIPAL ARPT, OH, USA | 40.82N | 82.52W | 400 | -5.00 (NAE) | 82-06 | 725246 | -21.8 | -22 | -33 | 37.3 | 32.3 | 33.3 | 32.2 | 33 | 32.6 | 33 | 30.3 | 31.2 | 30.5 | 31 | 30.6667 | 31 | 750 | United_StatesOhioMANSFIELD LAHM MUNICIPAL ARPT
United_States | Ohio | OHIO STATE UNIVERSI | OHIO STATE UNIVERSI, OH, USA | 40.07N | 83.07W | 283 | -5.00 (NAE) | 97-06 | 724288 | -17.9 | -18 | -28 | 36.6 | 32.8 | 33.6 | 33.1 | 33 | 33.1667 | 34 | 32 | 32.4 | 32.2 | 32 | 32.2 | 32 | 751 | United_StatesOhioOHIO STATE UNIVERSI
United_States | Ohio | RICKENBACKER ANGB | RICKENBACKER ANGB, OH, USA | 39.82N | 82.93W | 230 | -5.00 (NAE) | 82-06 | 724285 | -19.2 | -19 | -31 | 45.6 | 34.1 | 36 | 35 | 35 | 35.0333 | 36 | 32.4 | 33.7 | 32.8 | 33 | 32.9667 | 33 | 752 | United_StatesOhioRICKENBACKER ANGB
United_States | Ohio | SOUTH BASS ISLAND | SOUTH BASS ISLAND, OH, USA | 41.62N | 82.83W | 178 | -5.00 (NAE) | 85-06 | 994340 | -17 | -17 | -25 | 35.9 | 29.7 | 31 | 30.7 | 30 | 30.4667 | 31 | 27.7 | 29.4 | 29 | 29 | 28.7 | 29 | 753 | United_StatesOhioSOUTH BASS ISLAND
United_States | Ohio | TOLEDO EXPRESS AIRPORT | TOLEDO EXPRESS AIRPORT, OH, USA | 41.59N | 83.80W | 211 | -5.00 (NAE) | 82-06 | 725360 | -21.2 | -21 | -32.6 | 40.1 | 34.6 | 35.4 | 34.1 | 35 | 34.7 | 35 | 32.3 | 32.9 | 31.8 | 32 | 32.3333 | 32 | 754 | United_StatesOhioTOLEDO EXPRESS AIRPORT
United_States | Ohio | WRIGHT-PATERSON AFB | WRIGHT-PATERSON AFB, OH, USA | 39.83N | 84.05W | 250 | -5.00 (NAE) | 82-06 | 745700 | -20.9 | -21 | -32.4 | 39.4 | 34 | 35.5 | 34.1 | 35 | 34.5333 | 36 | 32.2 | 33.2 | 32.4 | 33 | 32.6 | 33 | 755 | United_StatesOhioWRIGHT-PATERSON AFB
United_States | Ohio | YOUNGSTOWN REGIONAL AIRPORT | YOUNGSTOWN REGIONAL AIRPORT, OH, USA | 41.25N | 80.67W | 362 | -5.00 (NAE) | 82-06 | 725250 | -20.6 | -21 | -32.2 | 37.7 | 32.5 | 33.8 | 33 | 33 | 33.1 | 34 | 30.2 | 31.6 | 30.9 | 31 | 30.9 | 31 | 756 | United_StatesOhioYOUNGSTOWN REGIONAL AIRPORT
United_States | Ohio | ZANESVILLE MUNICIPAL AP | ZANESVILLE MUNICIPAL AP, OH, USA | 39.94N | 81.89W | 275 | -5.00 (NAE) | 82-06 | 724286 | -20.7 | -21 | -33 | 39.3 | 32.8 | 34.4 | 33.9 | 34 | 33.7 | 34 | 31.1 | 32.4 | 32.1 | 32 | 31.8667 | 32 | 757 | United_StatesOhioZANESVILLE MUNICIPAL AP
United_States | Oklahoma | ALTUS AFB | ALTUS AFB, OK, USA | 34.67N | 99.27W | 414 | -6.00 (NAC) | 82-00 | 723520 | -13 | -13 | -21.3 | 47.1 | 42 | 41.4 | 40.8 | 41 | 41.4 | 41 | 38.1 | 39.7 | 39 | 39 | 38.9333 | 39 | 758 | United_StatesOklahomaALTUS AFB
United_States | Oklahoma | CLINTON-SHERMAN | CLINTON-SHERMAN, OK, USA | 35.33N | 99.20W | 586 | -6.00 (NAC) | 96-06 | 723526 | -13.2 | -13 | -18.7 | 44.7 | 38 | 40.9 | 39 | 39 | 39.3 | 41 | 36.2 | 38.8 | 37.8 | 38 | 37.6 | 38 | 759 | United_StatesOklahomaCLINTON-SHERMAN
United_States | Oklahoma | FORT SILL | FORT SILL, OK, USA | 34.65N | 98.40W | 369 | -6.00 (NAC) | 82-99 | 723550 | -13.2 | -13 | -22.8 | 45 | 38.7 | 40.9 | 39.4 | 40 | 39.6667 | 41 | 36.1 | 38.6 | 37.7 | 37 | 37.4667 | 37 | 760 | United_StatesOklahomaFORT SILL
United_States | Oklahoma | GAGE AIRPORT | GAGE AIRPORT, OK, USA | 36.30N | 99.78W | 671 | -6.00 (NAC) | 87-06 | 723527 | -18.5 | -19 | -27.5 | 43.3 | 38 | 39.1 | 39 | 39 | 38.7 | 39 | 35.9 | 37.6 | 37.5 | 37 | 37 | 37 | 761 | United_StatesOklahomaGAGE AIRPORT
United_States | Oklahoma | HOBART MUNICIPAL AP | HOBART MUNICIPAL AP, OK, USA | 35.01N | 99.05W | 479 | -6.00 (NAC) | 87-06 | 723525 | -13.8 | -14 | -23.6 | 45.8 | 39.7 | 41 | 39.9 | 40 | 40.2 | 41 | 37 | 39.1 | 38.3 | 38 | 38.1333 | 38 | 762 | United_StatesOklahomaHOBART MUNICIPAL AP
United_States | Oklahoma | LAWTON MUNICIPAL | LAWTON MUNICIPAL, OK, USA | 34.57N | 98.42W | 338 | -6.00 (NAC) | 96-06 | 723575 | -11.6 | -12 | -14.7 | 45.4 | 38.3 | 41.2 | 41 | 40 | 40.1667 | 41 | 36.2 | 39.1 | 38.9 | 38 | 38.0667 | 38 | 763 | United_StatesOklahomaLAWTON MUNICIPAL
United_States | Oklahoma | MCALESTER MUNICIPAL AP | MCALESTER MUNICIPAL AP, OK, USA | 34.90N | 95.78W | 235 | -6.00 (NAC) | 82-06 | 723566 | -13.8 | -14 | -23.5 | 44.5 | 35.4 | 39.7 | 39.1 | 38 | 38.0667 | 40 | 33.7 | 37.4 | 37.5 | 36 | 36.2 | 36 | 764 | United_StatesOklahomaMCALESTER MUNICIPAL AP
United_States | Oklahoma | OKLAHOMA CITY WILL ROGERS WOR | OKLAHOMA CITY WILL ROGERS WOR, OK, USA | 35.39N | 97.60W | 398 | -6.00 (NAC) | 82-06 | 723530 | -14.4 | -14 | -22.9 | 44.4 | 36.3 | 40 | 39 | 38 | 38.4333 | 40 | 34.3 | 37.7 | 37.4 | 36 | 36.4667 | 36 | 765 | United_StatesOklahomaOKLAHOMA CITY WILL ROGERS WOR
United_States | Oklahoma | OKLAHOMA CITY/WILEY | OKLAHOMA CITY/WILEY, OK, USA | 35.53N | 97.65W | 396 | -6.00 (NAC) | 85-06 | 723544 | -14.7 | -15 | -22.9 | 44.3 | 36.4 | 40 | 38.6 | 38 | 38.3333 | 40 | 34.5 | 37.7 | 37.3 | 37 | 36.5 | 37 | 766 | United_StatesOklahomaOKLAHOMA CITY/WILEY
United_States | Oklahoma | PONCA CITY MUNICIPAL AP | PONCA CITY MUNICIPAL AP, OK, USA | 36.73N | 97.10W | 304 | -6.00 (NAC) | 82-06 | 723546 | -15.7 | -16 | -24.1 | 46.2 | 37.2 | 40.1 | 39.7 | 39 | 39 | 40 | 35.1 | 37.9 | 37.9 | 37 | 36.9667 | 37 | 767 | United_StatesOklahomaPONCA CITY MUNICIPAL AP
United_States | Oklahoma | STILLWATER RGNL | STILLWATER RGNL, OK, USA | 36.15N | 97.08W | 308 | -6.00 (NAC) | 96-06 | 723545 | -14.8 | -15 | -17.9 | 47 | 37.1 | 41.1 | 41.2 | 40 | 39.8 | 41 | 34.8 | 38.8 | 38.7 | 37 | 37.4333 | 37 | 768 | United_StatesOklahomaSTILLWATER RGNL
United_States | Oklahoma | TINKER AFB | TINKER AFB, OK, USA | 35.42N | 97.38W | 384 | -6.00 (NAC) | 82-06 | 723540 | -13.8 | -14 | -21.2 | 44.2 | 36.1 | 39.1 | 38.9 | 38 | 38.0333 | 39 | 34.1 | 37.4 | 37.4 | 36 | 36.3 | 36 | 769 | United_StatesOklahomaTINKER AFB
United_States | Oklahoma | TULSA INTERNATIONAL AIRPORT | TULSA INTERNATIONAL AIRPORT, OK, USA | 36.20N | 95.89W | 206 | -6.00 (NAC) | 82-06 | 723560 | -15 | -15 | -24.8 | 44.8 | 35.9 | 39 | 39.1 | 38 | 38 | 39 | 34.1 | 37.2 | 37.7 | 36 | 36.3333 | 36 | 770 | United_StatesOklahomaTULSA INTERNATIONAL AIRPORT
United_States | Oklahoma | TULSA/LLOYD JONES | TULSA/LLOYD JONES, OK, USA | 36.03N | 95.98W | 193 | -6.00 (NAC) | 97-06 | 723564 | -14.4 | -14 | -20.9 | 45.2 | 36.3 | 38.9 | 40 | 38 | 38.4 | 39 | 33.9 | 37.7 | 37.9 | 37 | 36.5 | 37 | 771 | United_StatesOklahomaTULSA/LLOYD JONES
United_States | Oklahoma | VANCE AFB | VANCE AFB, OK, USA | 36.33N | 97.92W | 408 | -6.00 (NAC) | 82-01 | 723535 | -16.4 | -16 | -25.9 | 45.1 | 38.2 | 40.1 | 39.6 | 39 | 39.3 | 40 | 36 | 38.3 | 38 | 37 | 37.4333 | 37 | 772 | United_StatesOklahomaVANCE AFB
United_States | Oregon | ASTORIA REGIONAL AIRPORT | ASTORIA REGIONAL AIRPORT, OR, USA | 46.16N | 123.88W | 7 | -8.00 (NAP) | 82-06 | 727910 | -5.4 | -5 | -13.9 | 36 | 27.2 | 26.5 | 27 | 27 | 26.9 | 27 | 21.8 | 22.7 | 23 | 23 | 22.5 | 23 | 773 | United_StatesOregonASTORIA REGIONAL AIRPORT
United_States | Oregon | AURORA STATE | AURORA STATE, OR, USA | 45.25N | 122.77W | 60 | -8.00 (NAP) | 97-06 | 726959 | -5.4 | -5 | -11.4 | 42 | 35 | 37.3 | 35 | 36 | 35.7667 | 37 | 30.9 | 32.8 | 32.6 | 32 | 32.1 | 32 | 774 | United_StatesOregonAURORA STATE
United_States | Oregon | BAKER MUNICIPAL AP | BAKER MUNICIPAL AP, OR, USA | 44.84N | 117.81W | 1028 | -8.00 (NAP) | 88-06 | 726886 | -23.1 | -23 | -34.3 | 42.2 | 32.7 | 36.4 | 36.1 | 35 | 35.0667 | 36 | 29.8 | 34 | 33.9 | 33 | 32.5667 | 33 | 775 | United_StatesOregonBAKER MUNICIPAL AP
United_States | Oregon | BURNS MUNICIPAL ARPT | BURNS MUNICIPAL ARPT, OR, USA | 43.59N | 118.95W | 1271 | -8.00 (NAP) | 91-06 | 726830 | -22.8 | -23 | -31.1 | 42.1 | 33 | 37.5 | 35.4 | 35 | 35.3 | 38 | 30.2 | 34.4 | 33.6 | 33 | 32.7333 | 33 | 776 | United_StatesOregonBURNS MUNICIPAL ARPT
United_States | Oregon | CAPE ARAGO (LS) | CAPE ARAGO (LS), OR, USA | 43.33N | 124.37W | 23 | -8.00 (NAP) | 85-06 | 994240 | -0.3 | 0 | -8.6 | 30.1 | 17.3 | 18.7 | 20.5 | 19 | 18.8333 | 19 | 16.2 | 17.4 | 18.7 | 17 | 17.4333 | 17 | 777 | United_StatesOregonCAPE ARAGO (LS)
United_States | Oregon | CORVALLIS MUNI | CORVALLIS MUNI, OR, USA | 44.48N | 123.28W | 77 | -8.00 (NAP) | 90-06 | 726945 | -7.8 | -8 | -16.2 | 43.1 | 35 | 37.5 | 37 | 37 | 36.5 | 38 | 31.1 | 33.7 | 33.7 | 33 | 32.8333 | 33 | 778 | United_StatesOregonCORVALLIS MUNI
United_States | Oregon | EUGENE MAHLON SWEET ARPT | EUGENE MAHLON SWEET ARPT, OR, USA | 44.13N | 123.21W | 114 | -8.00 (NAP) | 82-06 | 726930 | -8 | -8 | -15.6 | 42 | 33.4 | 36.5 | 35.3 | 35 | 35.0667 | 37 | 29.2 | 33 | 32.7 | 32 | 31.6333 | 32 | 779 | United_StatesOregonEUGENE MAHLON SWEET ARPT
United_States | Oregon | KLAMATH FALLS INTL AP | KLAMATH FALLS INTL AP, OR, USA | 42.15N | 121.72W | 1247 | -8.00 (NAP) | 82-06 | 725895 | -17.7 | -18 | -27.6 | 40.9 | 32.4 | 35.3 | 34.8 | 34 | 34.1667 | 35 | 29.7 | 33.1 | 32.5 | 32 | 31.7667 | 32 | 780 | United_StatesOregonKLAMATH FALLS INTL AP
United_States | Oregon | LA GRANDE MUNI AP | LA GRANDE MUNI AP, OR, USA | 45.29N | 118.01W | 828 | -8.00 (NAP) | 92-06 | 726884 | -16.9 | -17 | -24.2 | 41.5 | 32.3 | 37.3 | 36.3 | 35 | 35.3 | 37 | 28.8 | 34 | 33.9 | 32 | 32.2333 | 32 | 781 | United_StatesOregonLA GRANDE MUNI AP
United_States | Oregon | LAKEVIEW (AWOS) | LAKEVIEW (AWOS), OR, USA | 42.17N | 120.40W | 1441 | -8.00 (NAP) | 92-06 | 725976 | -20.6 | -21 | -27.9 | 39 | 31.1 | 34.4 | 33 | 33 | 32.8333 | 34 | 27.9 | 32.5 | 32 | 31 | 30.8 | 31 | 782 | United_StatesOregonLAKEVIEW (AWOS)
United_States | Oregon | MC MINNVILLE MUNI | MC MINNVILLE MUNI, OR, USA | 45.18N | 123.13W | 51 | -8.00 (NAP) | 97-06 | 726881 | -5.3 | -5 | -9.8 | 43.2 | 34.1 | 37.4 | 36 | 36 | 35.8333 | 37 | 30.9 | 33 | 32.8 | 32 | 32.2333 | 32 | 783 | United_StatesOregonMC MINNVILLE MUNI
United_States | Oregon | MEACHAM | MEACHAM, OR, USA | 45.51N | 118.43W | 1136 | -8.00 (NAP) | 82-06 | 726885 | -27.7 | -28 | -45.1 | 38.6 | 29.3 | 33.3 | 32.7 | 32 | 31.7667 | 33 | 27 | 31 | 30.5 | 30 | 29.5 | 30 | 784 | United_StatesOregonMEACHAM
United_States | Oregon | MEDFORD ROGUE VALLEY INTL AP | MEDFORD ROGUE VALLEY INTL AP, OR, USA | 42.39N | 122.87W | 405 | -8.00 (NAP) | 82-06 | 725970 | -7.7 | -8 | -16.1 | 44.8 | 37 | 39.9 | 39.4 | 39 | 38.7667 | 40 | 34 | 37.4 | 36.8 | 36 | 36.0667 | 36 | 785 | United_StatesOregonMEDFORD ROGUE VALLEY INTL AP
United_States | Oregon | NEWPORT STATE BEACH | NEWPORT STATE BEACH, OR, USA | 44.62N | 124.07W | 11 | -8.00 (NAP) | 85-06 | 994280 | -2 | -2 | -10 | 36.9 | 18.5 | 18.1 | 18.9 | 19 | 18.5 | 18 | 15.9 | 16.8 | 17.3 | 17 | 16.6667 | 17 | 786 | United_StatesOregonNEWPORT STATE BEACH
United_States | Oregon | NORTH BEND MUNI AIRPORT | NORTH BEND MUNI AIRPORT, OR, USA | 43.42N | 124.25W | 5 | -8.00 (NAP) | 82-06 | 726917 | -3.5 | -4 | -11.3 | 34.8 | 21.5 | 22.2 | 22.7 | 22 | 22.1333 | 22 | 18.9 | 20.5 | 21.2 | 20 | 20.2 | 20 | 787 | United_StatesOregonNORTH BEND MUNI AIRPORT
United_States | Oregon | PENDLETON E OR REGIONAL AP | PENDLETON E OR REGIONAL AP, OR, USA | 45.70N | 118.83W | 462 | -8.00 (NAP) | 82-06 | 726880 | -16.1 | -16 | -33.6 | 43.8 | 35.5 | 38.9 | 37.4 | 37 | 37.2667 | 39 | 32.5 | 36.3 | 35.2 | 35 | 34.6667 | 35 | 788 | United_StatesOregonPENDLETON E OR REGIONAL AP
United_States | Oregon | PORTLAND INTERNATIONAL AP | PORTLAND INTERNATIONAL AP, OR, USA | 45.59N | 122.60W | 33 | -8.00 (NAP) | 82-06 | 726980 | -6.4 | -6 | -14.9 | 41.9 | 34.3 | 36.4 | 35.4 | 35 | 35.3667 | 36 | 30 | 32.8 | 32.3 | 32 | 31.7 | 32 | 789 | United_StatesOregonPORTLAND INTERNATIONAL AP
United_States | Oregon | PORTLAND/HILLSBORO | PORTLAND/HILLSBORO, OR, USA | 45.53N | 122.95W | 62 | -8.00 (NAP) | 82-06 | 726986 | -8.4 | -8 | -16.8 | 42.3 | 34.2 | 37.2 | 36.1 | 36 | 35.8333 | 37 | 30.2 | 33.3 | 32.7 | 32 | 32.0667 | 32 | 790 | United_StatesOregonPORTLAND/HILLSBORO
United_States | Oregon | REDMOND ROBERTS FIELD | REDMOND ROBERTS FIELD, OR, USA | 44.25N | 121.15W | 940 | -8.00 (NAP) | 82-06 | 726835 | -19.2 | -19 | -31.2 | 41.4 | 33.6 | 36.9 | 35.6 | 35 | 35.3667 | 37 | 30.9 | 34.1 | 33.2 | 33 | 32.7333 | 33 | 791 | United_StatesOregonREDMOND ROBERTS FIELD
United_States | Oregon | SALEM MCNARY FIELD | SALEM MCNARY FIELD, OR, USA | 44.91N | 123.00W | 61 | -8.00 (NAP) | 82-06 | 726940 | -8.4 | -8 | -15.9 | 42 | 34.8 | 37 | 35.5 | 36 | 35.7667 | 37 | 30.5 | 33.3 | 32.7 | 32 | 32.1667 | 32 | 792 | United_StatesOregonSALEM MCNARY FIELD
United_States | Oregon | SEXTON SUMMIT | SEXTON SUMMIT, OR, USA | 42.62N | 123.38W | 1171 | -8.00 (NAP) | 82-06 | 725975 | -7.8 | -8 | -17.6 | 36.8 | 29.1 | 31.5 | 31.1 | 31 | 30.5667 | 32 | 26 | 28.4 | 28.3 | 28 | 27.5667 | 28 | 793 | United_StatesOregonSEXTON SUMMIT
United_States | Pennsylvania | ALLENTOWN LEHIGH VALLEY INTL | ALLENTOWN LEHIGH VALLEY INTL, PA, USA | 40.65N | 75.45W | 117 | -5.00 (NAE) | 82-06 | 725170 | -17.4 | -17 | -26.9 | 38.7 | 33.5 | 35.1 | 34.2 | 34 | 34.2667 | 35 | 31.5 | 33 | 32 | 32 | 32.1667 | 32 | 794 | United_StatesPennsylvaniaALLENTOWN LEHIGH VALLEY INTL
United_States | Pennsylvania | ALTOONA BLAIR CO ARPT | ALTOONA BLAIR CO ARPT, PA, USA | 40.30N | 78.32W | 448 | -5.00 (NAE) | 82-06 | 725126 | -19.2 | -19 | -30.9 | 38.7 | 32.1 | 33.5 | 33 | 33 | 32.8667 | 34 | 30 | 31.5 | 30.9 | 31 | 30.8 | 31 | 795 | United_StatesPennsylvaniaALTOONA BLAIR CO ARPT
United_States | Pennsylvania | BRADFORD REGIONAL AP | BRADFORD REGIONAL AP, PA, USA | 41.80N | 78.64W | 655 | -5.00 (NAE) | 82-06 | 725266 | -24.7 | -25 | -35.5 | 34.6 | 29.1 | 30.8 | 30 | 30 | 29.9667 | 31 | 27.6 | 28.8 | 27.8 | 28 | 28.0667 | 28 | 796 | United_StatesPennsylvaniaBRADFORD REGIONAL AP
United_States | Pennsylvania | BUTLER CO. (AWOS) | BUTLER CO. (AWOS), PA, USA | 40.78N | 79.95W | 380 | -5.00 (NAE) | 92-06 | 725124 | -19.1 | -19 | -30.5 | 37.1 | 31.4 | 32.6 | 32.6 | 32 | 32.2 | 33 | 29.8 | 31.1 | 30.9 | 31 | 30.6 | 31 | 797 | United_StatesPennsylvaniaBUTLER CO. (AWOS)
United_States | Pennsylvania | DUBOIS FAA AP | DUBOIS FAA AP, PA, USA | 41.18N | 78.90W | 556 | -5.00 (NAE) | 82-06 | 725125 | -22.1 | -22 | -33 | 36.5 | 30.4 | 32.2 | 31.3 | 31 | 31.3 | 32 | 28.6 | 29.9 | 29 | 29 | 29.1667 | 29 | 798 | United_StatesPennsylvaniaDUBOIS FAA AP
United_States | Pennsylvania | ERIE INTERNATIONAL AP | ERIE INTERNATIONAL AP, PA, USA | 42.08N | 80.18W | 225 | -5.00 (NAE) | 82-06 | 725260 | -18 | -18 | -30.3 | 37.5 | 31.3 | 32.4 | 31.4 | 32 | 31.7 | 32 | 29.5 | 30.1 | 29.6 | 30 | 29.7333 | 30 | 799 | United_StatesPennsylvaniaERIE INTERNATIONAL AP
United_States | Pennsylvania | FRANKLIN | FRANKLIN, PA, USA | 41.44N | 79.85W | 469 | -5.00 (NAE) | 92-06 | 725267 | -20.1 | -20 | -28.1 | 34.8 | 30.9 | 31.4 | 31.2 | 31 | 31.1667 | 31 | 28.9 | 29.1 | 28.9 | 29 | 28.9667 | 29 | 800 | United_StatesPennsylvaniaFRANKLIN
United_States | Pennsylvania | HARRISBURG CAPITAL CITY ARPT | HARRISBURG CAPITAL CITY ARPT, PA, USA | 40.22N | 76.85W | 106 | -5.00 (NAE) | 82-06 | 725118 | -16.9 | -17 | -26.2 | 41.1 | 34.1 | 36.7 | 35 | 35 | 35.2667 | 37 | 32.1 | 34.1 | 32.6 | 33 | 32.9333 | 33 | 801 | United_StatesPennsylvaniaHARRISBURG CAPITAL CITY ARPT
United_States | Pennsylvania | JOHNSTOWN CAMBRIA COUNTY AP | JOHNSTOWN CAMBRIA COUNTY AP, PA, USA | 40.30N | 78.83W | 696 | -5.00 (NAE) | 89-06 | 725127 | -19.9 | -20 | -29.7 | 37.2 | 30.3 | 32.4 | 31.1 | 31 | 31.2667 | 32 | 28.4 | 29.6 | 28.8 | 29 | 28.9333 | 29 | 802 | United_StatesPennsylvaniaJOHNSTOWN CAMBRIA COUNTY AP
United_States | Pennsylvania | MIDDLETOWN HARRISBURG INTL AP | MIDDLETOWN HARRISBURG INTL AP, PA, USA | 40.19N | 76.76W | 95 | -5.00 (NAE) | 82-06 | 725115 | -15.4 | -15 | -26.3 | 41.8 | 34.6 | 36.8 | 35 | 35 | 35.4667 | 37 | 32.4 | 34.1 | 32.7 | 33 | 33.0667 | 33 | 803 | United_StatesPennsylvaniaMIDDLETOWN HARRISBURG INTL AP
United_States | Pennsylvania | PHILADELPHIA INTERNATIONAL AP | PHILADELPHIA INTERNATIONAL AP, PA, USA | 39.87N | 75.23W | 9 | -5.00 (NAE) | 82-06 | 724080 | -14.1 | -14 | -24.4 | 40.5 | 34.6 | 36.4 | 35.5 | 36 | 35.5 | 36 | 32.8 | 34.4 | 33.3 | 34 | 33.5 | 34 | 804 | United_StatesPennsylvaniaPHILADELPHIA INTERNATIONAL AP
United_States | Pennsylvania | PHILADELPHIA NE PHILADELPHIA | PHILADELPHIA NE PHILADELPHIA, PA, USA | 40.08N | 75.01W | 36 | -5.00 (NAE) | 82-06 | 724085 | -15.3 | -15 | -24.2 | 40.3 | 34.6 | 36.5 | 35 | 35 | 35.3667 | 37 | 32.5 | 34.5 | 32.8 | 33 | 33.2667 | 33 | 805 | United_StatesPennsylvaniaPHILADELPHIA NE PHILADELPHIA
United_States | Pennsylvania | PITTSBURGH ALLEGHENY CO AP | PITTSBURGH ALLEGHENY CO AP, PA, USA | 40.36N | 79.92W | 388 | -5.00 (NAE) | 82-06 | 725205 | -19.5 | -20 | -32.2 | 38.8 | 32.7 | 34 | 33.5 | 33 | 33.4 | 34 | 30.9 | 32.3 | 31.7 | 32 | 31.6333 | 32 | 806 | United_StatesPennsylvaniaPITTSBURGH ALLEGHENY CO AP
United_States | Pennsylvania | PITTSBURGH INTERNATIONAL AP | PITTSBURGH INTERNATIONAL AP, PA, USA | 40.50N | 80.23W | 367 | -5.00 (NAE) | 82-06 | 725200 | -19.5 | -20 | -31.2 | 38.9 | 32.7 | 34.1 | 33.7 | 34 | 33.5 | 34 | 30.5 | 32 | 31.7 | 31 | 31.4 | 31 | 807 | United_StatesPennsylvaniaPITTSBURGH INTERNATIONAL AP
United_States | Pennsylvania | READING SPAATZ FIELD | READING SPAATZ FIELD, PA, USA | 40.37N | 75.96W | 108 | -5.00 (NAE) | 85-06 | 725103 | N/A | N/A | N/A | N/A | 33.8 | 37.2 | 34.8 | 35 | 35.2667 | 37 | 32.1 | 34.3 | 32.2 | 33 | 32.8667 | 33 | 808 | United_StatesPennsylvaniaREADING SPAATZ FIELD
United_States | Pennsylvania | WASHINGTON (AWOS) | WASHINGTON (AWOS), PA, USA | 40.13N | 80.28W | 361 | -5.00 (NAE) | 92-06 | 725117 | N/A | N/A | N/A | N/A | 32.2 | 32.8 | 32.8 | 33 | 32.6 | 33 | 30.1 | 31.3 | 31.3 | 31 | 30.9 | 31 | 809 | United_StatesPennsylvaniaWASHINGTON (AWOS)
United_States | Pennsylvania | WILKES-BARRE SCRANTON INTL AP | WILKES-BARRE SCRANTON INTL AP, PA, USA | 41.34N | 75.73W | 293 | -5.00 (NAE) | 82-06 | 725130 | -19.3 | -19 | -28.9 | 38.4 | 32.2 | 34 | 33.2 | 33 | 33.1333 | 34 | 30.2 | 31.8 | 31 | 31 | 31 | 31 | 810 | United_StatesPennsylvaniaWILKES-BARRE SCRANTON INTL AP
United_States | Pennsylvania | WILLIAMSPORT REGIONAL AP | WILLIAMSPORT REGIONAL AP, PA, USA | 41.24N | 76.92W | 160 | -5.00 (NAE) | 82-06 | 725140 | -19.1 | -19 | -29.1 | 39.6 | 33.5 | 35.6 | 34.4 | 35 | 34.5 | 36 | 31.2 | 33 | 31.8 | 32 | 32 | 32 | 811 | United_StatesPennsylvaniaWILLIAMSPORT REGIONAL AP
United_States | Pennsylvania | WILLOW GROVE NAS | WILLOW GROVE NAS, PA, USA | 40.20N | 75.15W | 110 | -5.00 (NAE) | 82-98 | 724086 | -16.7 | -17 | -24.8 | 39.3 | 34.8 | 36 | 34.5 | 35 | 35.1 | 36 | 32.8 | 34.1 | 32.5 | 33 | 33.1333 | 33 | 812 | United_StatesPennsylvaniaWILLOW GROVE NAS
United_States | Rhode_Island | BLOCK ISLAND STATE ARPT | BLOCK ISLAND STATE ARPT, RI, USA | 41.17N | 71.58W | 33 | -5.00 (NAE) | 90-06 | 725058 | -14.2 | -14 | -19.2 | 34.4 | 27.8 | 30.6 | 29.8 | 29 | 29.4 | 31 | 25.1 | 28 | 27.3 | 27 | 26.8 | 27 | 813 | United_StatesRhode_IslandBLOCK ISLAND STATE ARPT
United_States | Rhode_Island | PAWTUCKET (AWOS) | PAWTUCKET (AWOS), RI, USA | 41.92N | 71.50W | 134 | -5.00 (NAE) | 92-06 | 725054 | N/A | N/A | N/A | N/A | 32.1 | 32.8 | 33.7 | 33 | 32.8667 | 33 | 29.1 | 31.1 | 31 | 30 | 30.4 | 30 | 814 | United_StatesRhode_IslandPAWTUCKET (AWOS)
United_States | Rhode_Island | PROVIDENCE T F GREEN STATE AR | PROVIDENCE T F GREEN STATE AR, RI, USA | 41.72N | 71.43W | 19 | -5.00 (NAE) | 82-06 | 725070 | -17 | -17 | -24.8 | 40.2 | 33.1 | 35 | 33.9 | 34 | 34 | 35 | 30.7 | 32.4 | 31.4 | 32 | 31.5 | 32 | 815 | United_StatesRhode_IslandPROVIDENCE T F GREEN STATE AR
United_States | South_Carolina | ANDERSON COUNTY AP | ANDERSON COUNTY AP, SC, USA | 34.50N | 82.71W | 236 | -5.00 (NAE) | 87-06 | 723125 | -9.9 | -10 | -15.4 | 41.3 | 35.2 | 36.8 | 36.3 | 36 | 36.1 | 37 | 33.7 | 35.2 | 34.5 | 34 | 34.4667 | 34 | 816 | United_StatesSouth_CarolinaANDERSON COUNTY AP
United_States | South_Carolina | BEAUFORT MCAS | BEAUFORT MCAS, SC, USA | 32.48N | 80.72W | 12 | -5.00 (NAE) | 82-06 | 722085 | -6.4 | -6 | -14.7 | 42.2 | 36.2 | 37.2 | 36 | 36 | 36.4667 | 37 | 33.9 | 35.2 | 34.1 | 34 | 34.4 | 34 | 817 | United_StatesSouth_CarolinaBEAUFORT MCAS
United_States | South_Carolina | CHARLESTON INTL ARPT | CHARLESTON INTL ARPT, SC, USA | 32.90N | 80.04W | 15 | -5.00 (NAE) | 82-06 | 722080 | -7 | -7 | -14.7 | 40.2 | 35.5 | 36.6 | 35.5 | 36 | 35.8667 | 37 | 33.6 | 34.9 | 33.9 | 34 | 34.1333 | 34 | 818 | United_StatesSouth_CarolinaCHARLESTON INTL ARPT
United_States | South_Carolina | COLUMBIA METRO ARPT | COLUMBIA METRO ARPT, SC, USA | 33.94N | 81.12W | 69 | -5.00 (NAE) | 82-06 | 723100 | -9.5 | -10 | -17 | 42.5 | 36.9 | 38.4 | 37.4 | 38 | 37.5667 | 38 | 35 | 36.5 | 35.4 | 36 | 35.6333 | 36 | 819 | United_StatesSouth_CarolinaCOLUMBIA METRO ARPT
United_States | South_Carolina | FLORENCE REGIONAL AP | FLORENCE REGIONAL AP, SC, USA | 34.19N | 79.73W | 46 | -5.00 (NAE) | 82-06 | 723106 | -9.3 | -9 | -17.3 | 41.7 | 36.5 | 37.7 | 37 | 37 | 37.0667 | 38 | 34.3 | 36 | 34.6 | 35 | 34.9667 | 35 | 820 | United_StatesSouth_CarolinaFLORENCE REGIONAL AP
United_States | South_Carolina | FOLLY ISLAND | FOLLY ISLAND, SC, USA | 32.68N | 79.88W | 5 | -5.00 (NAE) | 85-06 | 994230 | -3.4 | -3 | -10.5 | 36.6 | 31.2 | 32.8 | 31.9 | 32 | 31.9667 | 33 | 29.4 | 31.2 | 30.6 | 30 | 30.4 | 30 | 821 | United_StatesSouth_CarolinaFOLLY ISLAND
United_States | South_Carolina | GREER GREENV'L-SPARTANBRG AP | GREER GREENV'L-SPARTANBRG AP, SC, USA | 34.90N | 82.22W | 296 | -5.00 (NAE) | 82-06 | 723120 | -11.1 | -11 | -19.5 | 41 | 34.9 | 36.6 | 36.2 | 36 | 35.9 | 37 | 33.1 | 34.8 | 33.9 | 34 | 33.9333 | 34 | 822 | United_StatesSouth_CarolinaGREER GREENV'L-SPARTANBRG AP
United_States | South_Carolina | MYRTLE BEACH AFB | MYRTLE BEACH AFB, SC, USA | 33.68N | 78.92W | 8 | -5.00 (NAE) | 82-06 | 747910 | -8.3 | -8 | -17 | 40.9 | 34.1 | 36 | 35.1 | 35 | 35.0667 | 36 | 32.2 | 33.8 | 33 | 33 | 33 | 33 | 823 | United_StatesSouth_CarolinaMYRTLE BEACH AFB
United_States | South_Carolina | SHAW AFB/SUMTER | SHAW AFB/SUMTER, SC, USA | 33.97N | 80.47W | 74 | -5.00 (NAE) | 82-06 | 747900 | -8.9 | -9 | -16 | 42 | 36 | 37.6 | 37.2 | 37 | 36.9333 | 38 | 33.8 | 35.8 | 34.8 | 35 | 34.8 | 35 | 824 | United_StatesSouth_CarolinaSHAW AFB/SUMTER
United_States | South_Dakota | ABERDEEN REGIONAL ARPT | ABERDEEN REGIONAL ARPT, SD, USA | 45.45N | 98.42W | 396 | -6.00 (NAC) | 82-06 | 726590 | -32.3 | -32 | -43.5 | 44.2 | 34.8 | 37.6 | 35.3 | 36 | 35.9 | 38 | 31.6 | 33.8 | 32.5 | 33 | 32.6333 | 33 | 825 | United_StatesSouth_DakotaABERDEEN REGIONAL ARPT
United_States | South_Dakota | BROOKINGS (AWOS) | BROOKINGS (AWOS), SD, USA | 44.30N | 96.82W | 502 | -6.00 (NAC) | 92-06 | 726515 | -29.5 | -30 | -37.3 | 38.9 | 32.4 | 34.1 | 32.6 | 33 | 33.0333 | 34 | 29.9 | 32.2 | 30.3 | 31 | 30.8 | 31 | 826 | United_StatesSouth_DakotaBROOKINGS (AWOS)
United_States | South_Dakota | BUFFALO (AMOS) | BUFFALO (AMOS), SD, USA | 45.60N | 103.55W | 915 | -7.00 (NAM) | 89-06 | 726627 | -28.8 | -29 | -36.7 | 47.6 | 36 | 40.2 | 37.8 | 38 | 38 | 40 | 31.3 | 36.7 | 35.2 | 34 | 34.4 | 34 | 827 | United_StatesSouth_DakotaBUFFALO (AMOS)
United_States | South_Dakota | CHAMBERLAIN (AMOS) | CHAMBERLAIN (AMOS), SD, USA | 43.80N | 99.32W | 530 | -6.00 (NAC) | 82-06 | 726530 | -26.9 | -27 | -34.4 | 47.4 | 35.9 | 41 | 38 | 38 | 38.3 | 41 | 32.8 | 37 | 35.4 | 35 | 35.0667 | 35 | 828 | United_StatesSouth_DakotaCHAMBERLAIN (AMOS)
United_States | South_Dakota | CHAN GURNEY MUNI | CHAN GURNEY MUNI, SD, USA | 42.92N | 97.38W | 408 | -6.00 (NAC) | 92-06 | 726525 | -25.3 | -25 | -33 | 42.2 | 35 | 37.5 | 35 | 36 | 35.8333 | 38 | 32.3 | 34 | 32.4 | 33 | 32.9 | 33 | 829 | United_StatesSouth_DakotaCHAN GURNEY MUNI
United_States | South_Dakota | CUSTER (RAMOS) | CUSTER (RAMOS), SD, USA | 43.73N | 103.62W | 1707 | -7.00 (NAM) | 85-06 | 726514 | -28.1 | -28 | -37.8 | 37.6 | 31.2 | 33.9 | 32.2 | 32 | 32.4333 | 34 | 27.7 | 31.8 | 30 | 30 | 29.8333 | 30 | 830 | United_StatesSouth_DakotaCUSTER (RAMOS)
United_States | South_Dakota | ELLSWORTH AFB | ELLSWORTH AFB, SD, USA | 44.15N | 103.10W | 980 | -7.00 (NAM) | 82-06 | 726625 | -25.9 | -26 | -37.2 | 44.8 | 37.5 | 38.8 | 37.9 | 38 | 38.0667 | 39 | 32.8 | 35.9 | 35.1 | 35 | 34.6 | 35 | 831 | United_StatesSouth_DakotaELLSWORTH AFB
United_States | South_Dakota | HURON REGIONAL ARPT | HURON REGIONAL ARPT, SD, USA | 44.39N | 98.23W | 393 | -6.00 (NAC) | 82-06 | 726540 | -30.4 | -30 | -41.4 | 45.3 | 35.5 | 37.8 | 36.6 | 37 | 36.6333 | 38 | 32.3 | 35 | 34 | 34 | 33.7667 | 34 | 832 | United_StatesSouth_DakotaHURON REGIONAL ARPT
United_States | South_Dakota | MITCHELL (AWOS) | MITCHELL (AWOS), SD, USA | 43.77N | 98.03W | 397 | -6.00 (NAC) | 92-06 | 726545 | -26.9 | -27 | -38 | 46 | 35.1 | 39 | 36 | 37 | 36.7 | 39 | 32.3 | 35.8 | 32.6 | 34 | 33.5667 | 34 | 833 | United_StatesSouth_DakotaMITCHELL (AWOS)
United_States | South_Dakota | MOBRIDGE | MOBRIDGE, SD, USA | 45.53N | 100.43W | 508 | -6.00 (NAC) | 82-06 | 726685 | -29.7 | -30 | -40.3 | 46.5 | 35.1 | 38.8 | 37.4 | 37 | 37.1 | 39 | 32.4 | 35.7 | 34.1 | 34 | 34.0667 | 34 | 834 | United_StatesSouth_DakotaMOBRIDGE
United_States | South_Dakota | PIERRE MUNICIPAL AP | PIERRE MUNICIPAL AP, SD, USA | 44.38N | 100.29W | 526 | -6.00 (NAC) | 82-06 | 726686 | -27.8 | -28 | -38.5 | 47.4 | 37.7 | 41.2 | 39.6 | 40 | 39.5 | 41 | 33.5 | 37.7 | 36.6 | 36 | 35.9333 | 36 | 835 | United_StatesSouth_DakotaPIERRE MUNICIPAL AP
United_States | South_Dakota | RAPID CITY REGIONAL ARPT | RAPID CITY REGIONAL ARPT, SD, USA | 44.05N | 103.05W | 966 | -7.00 (NAM) | 82-06 | 726620 | -27.4 | -27 | -37.2 | 45 | 37.1 | 39.7 | 37.7 | 38 | 38.1667 | 40 | 32.8 | 36.6 | 35.3 | 35 | 34.9 | 35 | 836 | United_StatesSouth_DakotaRAPID CITY REGIONAL ARPT
United_States | South_Dakota | SIOUX FALLS FOSS FIELD | SIOUX FALLS FOSS FIELD, SD, USA | 43.58N | 96.75W | 435 | -6.00 (NAC) | 82-06 | 726510 | -28.6 | -29 | -37 | 44 | 35.5 | 37.1 | 35.3 | 36 | 35.9667 | 37 | 32.3 | 34.1 | 32.7 | 33 | 33.0333 | 33 | 837 | United_StatesSouth_DakotaSIOUX FALLS FOSS FIELD
United_States | South_Dakota | WATERTOWN MUNICIPAL AP | WATERTOWN MUNICIPAL AP, SD, USA | 44.93N | 97.15W | 530 | -6.00 (NAC) | 82-06 | 726546 | -29.3 | -29 | -37.8 | 40.9 | 34.8 | 35.9 | 33.5 | 35 | 34.7333 | 36 | 31.1 | 32.7 | 31 | 32 | 31.6 | 32 | 838 | United_StatesSouth_DakotaWATERTOWN MUNICIPAL AP
United_States | Tennessee | BRISTOL TRI CITY AIRPORT | BRISTOL TRI CITY AIRPORT, TN, USA | 36.48N | 82.40W | 465 | -5.00 (NAE) | 82-06 | 723183 | -16.5 | -17 | -28.3 | 38.4 | 32.1 | 34 | 34 | 33 | 33.3667 | 34 | 30.7 | 32.2 | 32.1 | 32 | 31.6667 | 32 | 839 | United_StatesTennesseeBRISTOL TRI CITY AIRPORT
United_States | Tennessee | CHATTANOOGA LOVELL FIELD AP | CHATTANOOGA LOVELL FIELD AP, TN, USA | 35.03N | 85.20W | 210 | -5.00 (NAE) | 82-06 | 723240 | -12.2 | -12 | -23.2 | 40.6 | 34.9 | 36.7 | 36.2 | 36 | 35.9333 | 37 | 33.2 | 34.8 | 34.5 | 34 | 34.1667 | 34 | 840 | United_StatesTennesseeCHATTANOOGA LOVELL FIELD AP
United_States | Tennessee | CROSSVILLE MEMORIAL AP | CROSSVILLE MEMORIAL AP, TN, USA | 35.95N | 85.09W | 570 | -6.00 (NAC) | 82-06 | 723265 | -17.9 | -18 | -30.2 | 38.2 | 31.6 | 33.3 | 32.8 | 33 | 32.5667 | 33 | 29.8 | 31.6 | 31.1 | 31 | 30.8333 | 31 | 841 | United_StatesTennesseeCROSSVILLE MEMORIAL AP
United_States | Tennessee | DYERSBURG MUNICIPAL AP | DYERSBURG MUNICIPAL AP, TN, USA | 36.02N | 89.32W | 103 | -6.00 (NAC) | 92-06 | 723347 | -11.9 | -12 | -18.3 | 39 | 34.1 | 36.2 | 36.3 | 36 | 35.5333 | 36 | 33 | 34.1 | 34.4 | 34 | 33.8333 | 34 | 842 | United_StatesTennesseeDYERSBURG MUNICIPAL AP
United_States | Tennessee | JACKSON MCKELLAR-SIPES REGL A | JACKSON MCKELLAR-SIPES REGL A, TN, USA | 35.59N | 88.92W | 129 | -6.00 (NAC) | 82-06 | 723346 | -14.6 | -15 | -24.8 | 40 | 34.8 | 36.1 | 36.7 | 36 | 35.8667 | 36 | 33.3 | 34.7 | 35 | 34 | 34.3333 | 34 | 843 | United_StatesTennesseeJACKSON MCKELLAR-SIPES REGL A
United_States | Tennessee | KNOXVILLE MCGHEE TYSON AP | KNOXVILLE MCGHEE TYSON AP, TN, USA | 35.82N | 83.99W | 299 | -5.00 (NAE) | 82-06 | 723260 | -14.5 | -15 | -27.8 | 39.8 | 34 | 35.6 | 35.2 | 35 | 34.9333 | 36 | 32.1 | 33.9 | 33.3 | 33 | 33.1 | 33 | 844 | United_StatesTennesseeKNOXVILLE MCGHEE TYSON AP
United_States | Tennessee | MEMPHIS INTERNATIONAL AP | MEMPHIS INTERNATIONAL AP, TN, USA | 35.06N | 89.99W | 101 | -6.00 (NAC) | 82-06 | 723340 | -11.8 | -12 | -21.5 | 41 | 35.7 | 36.8 | 37.4 | 37 | 36.6333 | 37 | 34.1 | 35.4 | 35.7 | 35 | 35.0667 | 35 | 845 | United_StatesTennesseeMEMPHIS INTERNATIONAL AP
United_States | Tennessee | MILLINGTON MUNI ARP | MILLINGTON MUNI ARP, TN, USA | 35.35N | 89.87W | 98 | -6.00 (NAC) | 82-06 | 723284 | -13.6 | -14 | -26.5 | 41.9 | 36.3 | 37.7 | 37.8 | 37 | 37.2667 | 38 | 34.9 | 36.2 | 36.4 | 36 | 35.8333 | 36 | 846 | United_StatesTennesseeMILLINGTON MUNI ARP
United_States | Tennessee | NASHVILLE INTERNATIONAL AP | NASHVILLE INTERNATIONAL AP, TN, USA | 36.12N | 86.69W | 184 | -6.00 (NAC) | 82-06 | 723270 | -15.2 | -15 | -27.7 | 40.8 | 34.6 | 36.6 | 36.6 | 36 | 35.9333 | 37 | 33 | 34.6 | 34.7 | 34 | 34.1 | 34 | 847 | United_StatesTennesseeNASHVILLE INTERNATIONAL AP
United_States | Territory or Island | GUAM ANDERSEN AFB | ANDERSEN AFB, Guam | 13.57N | 144.92E | 162 | 10.00 (PCW) | 82-06 | 912180 | 21.8 |  | 20.1 | 34.2 | 31.2 | 31.2 | 31.1 | 31 | 31.1667 |  | 30.8 | 30.5 | 30.2 | 31 | 30.5 |  | 848 | United_StatesTerritory or IslandGUAM ANDERSEN AFB
United_States | Territory or Island | GUAM WFO | GUAM WFO, Guam | 13.48N | 144.80E | 77 | 10.00 (PCW) | 82-06 | 912120 | 21.4 |  | 18.9 | 37.8 | 32.9 | 32.2 | 32.2 | 32 | 32.4333 |  | 31.9 | 31.6 | 31.5 | 32 | 31.6667 |  | 849 | United_StatesTerritory or IslandGUAM WFO
United_States | Territory or Island | MIDWAY ISLAND NAS | MIDWAY ISLAND NAS, United States Minor Outlying Islands | 28.20N | 177.38W | 4 | -11.00 (PCM) | 82-99 | 910660 | 13 |  | 10.3 | 36.6 | 30.6 | 31.2 | 31.7 | 31 | 31.1667 |  | 29.7 | 30.4 | 30.9 | 30 | 30.3333 |  | 850 | United_StatesTerritory or IslandMIDWAY ISLAND NAS
United_States | Territory or Island | PAGO PAGO WSO AP | PAGO PAGO WSO AP, American Samoa | 14.33S | 170.71W | 3 | -11.00 (PCM) | 82-06 | 917650 | 21.1 |  | 18.2 | 37 | 31 | 30.8 | 30.8 | 31 | 30.8667 |  | 30.2 | 30.1 | 30.1 | 30 | 30.1333 |  | 851 | United_StatesTerritory or IslandPAGO PAGO WSO AP
United_States | Territory or Island | WAKE ISLAND | WAKE ISLAND, United States Minor Outlying Islands | 19.28N | 166.64E | 4 | 12.00 (FJI) | 82-06 | 912450 | 20.4 |  | 18.4 | 34.2 | 32.2 | 32.3 | 32.6 | 32 | 32.3667 |  | 31.3 | 31.8 | 32.1 | 32 | 31.7333 |  | 852 | United_StatesTerritory or IslandWAKE ISLAND
United_States | Texas | ABILENE DYESS AFB | ABILENE DYESS AFB, TX, USA | 32.43N | 99.85W | 545 | -6.00 (NAC) | 82-06 | 690190 | -12.2 | -12 | -22.8 | 44.9 | 40.4 | 40.4 | 39.4 | 40 | 40.0667 | 40 | 37.7 | 38.5 | 37.9 | 38 | 38.0333 | 38 | 853 | United_StatesTexasABILENE DYESS AFB
United_States | Texas | ABILENE REGIONAL AP | ABILENE REGIONAL AP, TX, USA | 32.41N | 99.68W | 546 | -6.00 (NAC) | 82-06 | 722660 | -10.9 | -11 | -21.5 | 43.3 | 38.1 | 38.9 | 38.5 | 39 | 38.5 | 39 | 35.9 | 37.2 | 37.1 | 37 | 36.7333 | 37 | 854 | United_StatesTexasABILENE REGIONAL AP
United_States | Texas | ALICE INTL AP | ALICE INTL AP, TX, USA | 27.74N | 98.03W | 55 | -6.00 (NAC) | 82-06 | 722517 | -2 | -2 | -7.9 | 45.6 | 37.9 | 38.9 | 38.9 | 39 | 38.5667 | 39 | 36.3 | 37.5 | 37.6 | 37 | 37.1333 | 37 | 855 | United_StatesTexasALICE INTL AP
United_States | Texas | AMARILLO INTERNATIONAL AP | AMARILLO INTERNATIONAL AP, TX, USA | 35.22N | 101.71W | 1099 | -6.00 (NAC) | 82-06 | 723630 | -17.3 | -17 | -26.5 | 42.7 | 38.8 | 37.9 | 36.8 | 38 | 37.8333 | 38 | 35.9 | 36.2 | 35.1 | 36 | 35.7333 | 36 | 856 | United_StatesTexasAMARILLO INTERNATIONAL AP
United_States | Texas | AUSTIN/BERGSTROM | AUSTIN/BERGSTROM, TX, USA | 30.18N | 97.68W | 151 | -6.00 (NAC) | 82-06 | 722540 | -7.1 | -7 | -15.7 | 44 | 37.4 | 38.6 | 39.1 | 38 | 38.3667 | 39 | 35.6 | 37.3 | 37.8 | 37 | 36.9 | 37 | 857 | United_StatesTexasAUSTIN/BERGSTROM
United_States | Texas | BEEVILLE CHASE NAAS | BEEVILLE CHASE NAAS, TX, USA | 28.37N | 97.67W | 58 | -6.00 (NAC) | 82-92 | 722556 | -5 | -5 | -15.1 | 44 | 38.4 | 38.9 | 39.2 | 39 | 38.8333 | 39 | 36.6 | 37.4 | 38 | 37 | 37.3333 | 37 | 858 | United_StatesTexasBEEVILLE CHASE NAAS
United_States | Texas | BROWNSVILLE S PADRE ISL INTL | BROWNSVILLE S PADRE ISL INTL, TX, USA | 25.91N | 97.43W | 7 | -6.00 (NAC) | 82-06 | 722500 | 0.2 | 0 | -7.7 | 40.8 | 35.2 | 35.9 | 36.3 | 36 | 35.8 | 36 | 34.4 | 35.1 | 35.4 | 35 | 34.9667 | 35 | 859 | United_StatesTexasBROWNSVILLE S PADRE ISL INTL
United_States | Texas | BURNET MUNI. | BURNET MUNI., TX, USA | 30.73N | 98.23W | 391 | -6.00 (NAC) | 97-06 | 722542 | -5.5 | -6 | -9.2 | 45.7 | 37 | 37.5 | 37.7 | 37 | 37.4 | 38 | 34.1 | 36.3 | 37.1 | 36 | 35.8333 | 36 | 860 | United_StatesTexasBURNET MUNI.
United_States | Texas | CAMP MABRY | CAMP MABRY, TX, USA | 30.32N | 97.77W | 201 | -6.00 (NAC) | 82-06 | 722544 | -5.4 | -5 | -14.9 | 43.8 | 37.3 | 38.5 | 39 | 38 | 38.2667 | 39 | 35.3 | 37.2 | 37.5 | 37 | 36.6667 | 37 | 861 | United_StatesTexasCAMP MABRY
United_States | Texas | CHILDRESS MUNICIPAL AP | CHILDRESS MUNICIPAL AP, TX, USA | 34.43N | 100.29W | 595 | -6.00 (NAC) | 88-06 | 723604 | -12.2 | -12 | -21.2 | 47.2 | 40.7 | 40.1 | 38.7 | 40 | 39.8333 | 40 | 37.5 | 38 | 37.4 | 38 | 37.6333 | 38 | 862 | United_StatesTexasCHILDRESS MUNICIPAL AP
United_States | Texas | COLLEGE STATION EASTERWOOD FL | COLLEGE STATION EASTERWOOD FL, TX, USA | 30.59N | 96.36W | 100 | -6.00 (NAC) | 82-06 | 722445 | -6.4 | -6 | -15.4 | 43.8 | 37.2 | 38 | 38.9 | 38 | 38.0333 | 38 | 35.3 | 37.1 | 37.4 | 37 | 36.6 | 37 | 863 | United_StatesTexasCOLLEGE STATION EASTERWOOD FL
United_States | Texas | CORPUS CHRISTI INTL ARPT | CORPUS CHRISTI INTL ARPT, TX, USA | 27.77N | 97.51W | 13 | -6.00 (NAC) | 82-06 | 722510 | -2.8 | -3 | -10.9 | 41.8 | 34.9 | 36.1 | 36.7 | 36 | 35.9 | 36 | 33.8 | 35.1 | 35.6 | 35 | 34.8333 | 35 | 864 | United_StatesTexasCORPUS CHRISTI INTL ARPT
United_States | Texas | CORPUS CHRISTI NAS | CORPUS CHRISTI NAS, TX, USA | 27.70N | 97.28W | 6 | -6.00 (NAC) | 82-06 | 722515 | -0.9 | -1 | -10.8 | 41.2 | 34 | 34.1 | 34.9 | 34 | 34.3333 | 34 | 33 | 33.5 | 34.1 | 34 | 33.5333 | 34 | 865 | United_StatesTexasCORPUS CHRISTI NAS
United_States | Texas | COTULLA FAA AP | COTULLA FAA AP, TX, USA | 28.46N | 99.22W | 146 | -6.00 (NAC) | 82-06 | 722526 | -4.1 | -4 | -11.6 | 44.5 | 39.5 | 40.5 | 40.3 | 40 | 40.1 | 41 | 38.1 | 38.8 | 38.9 | 39 | 38.6 | 39 | 866 | United_StatesTexasCOTULLA FAA AP
United_States | Texas | COX FLD | COX FLD, TX, USA | 33.63N | 95.45W | 171 | -6.00 (NAC) | 93-06 | 722587 | -9.9 | -10 | -15.5 | 43.5 | 36.1 | 38 | 38.9 | 38 | 37.6667 | 38 | 33.9 | 37.1 | 37.5 | 36 | 36.1667 | 36 | 867 | United_StatesTexasCOX FLD
United_States | Texas | DALHART MUNICIPAL AP | DALHART MUNICIPAL AP, TX, USA | 36.02N | 102.55W | 1217 | -6.00 (NAC) | 88-06 | 722636 | -17.3 | -17 | -25.3 | 42.2 | 38.3 | 37.9 | 37 | 38 | 37.7333 | 38 | 36.3 | 36.3 | 35.1 | 36 | 35.9 | 36 | 868 | United_StatesTexasDALHART MUNICIPAL AP
United_States | Texas | DALLAS HENSLEY FIELD NAS | DALLAS HENSLEY FIELD NAS, TX, USA | 32.73N | 96.97W | 151 | -6.00 (NAC) | 82-96 | 722585 | -9.2 | -9 | -20.3 | 43.1 | 37 | 38.9 | 39.2 | 38 | 38.3667 | 39 | 35.2 | 37.3 | 38 | 37 | 36.8333 | 37 | 869 | United_StatesTexasDALLAS HENSLEY FIELD NAS
United_States | Texas | DALLAS LOVE FIELD | DALLAS LOVE FIELD, TX, USA | 32.85N | 96.85W | 149 | -6.00 (NAC) | 82-06 | 722583 | -8.2 | -8 | -17.7 | 44.2 | 37.3 | 39.4 | 39.6 | 39 | 38.7667 | 39 | 35.7 | 37.9 | 38.1 | 37 | 37.2333 | 37 | 870 | United_StatesTexasDALLAS LOVE FIELD
United_States | Texas | DALLAS/REDBIRD ARPT | DALLAS/REDBIRD ARPT, TX, USA | 32.68N | 96.87W | 201 | -6.00 (NAC) | 97-06 | 722599 | -7.6 | -8 | -11.2 | 45.5 | 37.4 | 39.8 | 39.1 | 39 | 38.7667 | 40 | 36 | 37.9 | 37.9 | 37 | 37.2667 | 37 | 871 | United_StatesTexasDALLAS/REDBIRD ARPT
United_States | Texas | DALLAS-FORT WORTH INTL AP | DALLAS-FORT WORTH INTL AP, TX, USA | 32.90N | 97.04W | 182 | -6.00 (NAC) | 82-06 | 722590 | -9.1 | -9 | -18.3 | 44.7 | 37.1 | 39.3 | 39.9 | 39 | 38.7667 | 39 | 35.4 | 37.8 | 38.3 | 37 | 37.1667 | 37 | 872 | United_StatesTexasDALLAS-FORT WORTH INTL AP
United_States | Texas | DEL RIO INTERNATIONAL AP | DEL RIO INTERNATIONAL AP, TX, USA | 29.37N | 100.92W | 313 | -6.00 (NAC) | 82-06 | 722610 | -3.5 | -4 | -8.7 | 43.7 | 40.1 | 40.1 | 39.2 | 40 | 39.8 | 40 | 37.8 | 38.4 | 37.9 | 38 | 38.0333 | 38 | 873 | United_StatesTexasDEL RIO INTERNATIONAL AP
United_States | Texas | DRAUGHON MILLER CEN | DRAUGHON MILLER CEN, TX, USA | 31.15N | 97.40W | 213 | -6.00 (NAC) | 85-06 | 722577 | -6.8 | -7 | -12.5 | 43.1 | 37.3 | 38.8 | 38.8 | 38 | 38.3 | 39 | 35.3 | 37.4 | 37.6 | 37 | 36.7667 | 37 | 874 | United_StatesTexasDRAUGHON MILLER CEN
United_States | Texas | EL PASO INTERNATIONAL AP | EL PASO INTERNATIONAL AP, TX, USA | 31.81N | 106.38W | 1194 | -7.00 (NAM) | 82-06 | 722700 | -8.9 | -9 | -16.4 | 44.5 | 40.6 | 39.8 | 37.8 | 39 | 39.4 | 40 | 38.6 | 37.8 | 36.1 | 38 | 37.5 | 38 | 875 | United_StatesTexasEL PASO INTERNATIONAL AP
United_States | Texas | FORT HOOD/GRAY AAF | FORT HOOD/GRAY AAF, TX, USA | 31.07N | 97.83W | 312 | -6.00 (NAC) | 82-06 | 722576 | -7.5 | -8 | -17.8 | 43.5 | 37.6 | 39 | 39.2 | 39 | 38.6 | 39 | 35.3 | 37.6 | 37.8 | 37 | 36.9 | 37 | 876 | United_StatesTexasFORT HOOD/GRAY AAF
United_States | Texas | FORT STOCKTON PECOS | FORT STOCKTON PECOS, TX, USA | 30.92N | 102.92W | 941 | -6.00 (NAC) | 98-06 | 722618 | -7.6 | -8 | -12.4 | 43.6 | 40.9 | 38.9 | 38 | 39 | 39.2667 | 39 | 38 | 37.6 | 37.1 | 38 | 37.5667 | 38 | 877 | United_StatesTexasFORT STOCKTON PECOS
United_States | Texas | FORT WORTH ALLIANCE | FORT WORTH ALLIANCE, TX, USA | 32.98N | 97.32W | 226 | -6.00 (NAC) | 92-06 | 722594 | -8.6 | -9 | -14.2 | 46 | 37.7 | 39.9 | 40.9 | 40 | 39.5 | 40 | 36.1 | 38.1 | 38.8 | 38 | 37.6667 | 38 | 878 | United_StatesTexasFORT WORTH ALLIANCE
United_States | Texas | FORT WORTH MEACHAM | FORT WORTH MEACHAM, TX, USA | 32.82N | 97.36W | 215 | -6.00 (NAC) | 82-06 | 722596 | -9.5 | -10 | -18.6 | 44.7 | 37.5 | 39.8 | 39.9 | 39 | 39.0667 | 40 | 35.8 | 38 | 38.5 | 37 | 37.4333 | 37 | 879 | United_StatesTexasFORT WORTH MEACHAM
United_States | Texas | FORT WORTH NAS | FORT WORTH NAS, TX, USA | 32.77N | 97.44W | 198 | -6.00 (NAC) | 82-05 | 722595 | -9.8 | -10 | -20.7 | 43.3 | 37.6 | 39.7 | 39.3 | 39 | 38.8667 | 40 | 35.8 | 37.9 | 37.9 | 37 | 37.2 | 37 | 880 | United_StatesTexasFORT WORTH NAS
United_States | Texas | GALVESTON/SCHOLES | GALVESTON/SCHOLES, TX, USA | 29.27N | 94.86W | 3 | -6.00 (NAC) | 82-06 | 722420 | -1.6 | -2 | -12.2 | 39 | 32.9 | 33.5 | 34.1 | 34 | 33.5 | 34 | 32.2 | 32.8 | 33.2 | 33 | 32.7333 | 33 | 881 | United_StatesTexasGALVESTON/SCHOLES
United_States | Texas | GEORGETOWN (AWOS) | GEORGETOWN (AWOS), TX, USA | 30.68N | 97.68W | 240 | -6.00 (NAC) | 92-06 | 722547 | -6.6 | -7 | -9.7 | 44.4 | 36.1 | 37.9 | 38.7 | 38 | 37.5667 | 38 | 34 | 36.8 | 37.4 | 36 | 36.0667 | 36 | 882 | United_StatesTexasGEORGETOWN (AWOS)
United_States | Texas | HARLINGEN RIO GRANDE VALLEY I | HARLINGEN RIO GRANDE VALLEY I, TX, USA | 26.23N | 97.65W | 11 | -6.00 (NAC) | 86-06 | 722505 | -0.1 | 0 | -8.4 | 39.7 | 37.3 | 37.7 | 37.9 | 38 | 37.6333 | 38 | 36.1 | 37 | 37.1 | 37 | 36.7333 | 37 | 883 | United_StatesTexasHARLINGEN RIO GRANDE VALLEY I
United_States | Texas | HONDO MUNICIPAL AP | HONDO MUNICIPAL AP, TX, USA | 29.36N | 99.17W | 284 | -6.00 (NAC) | 83-06 | 722533 | -6.9 | -7 | -14.3 | 43.1 | 37.8 | 38.3 | 38 | 38 | 38.0333 | 38 | 36.2 | 37.2 | 37.3 | 37 | 36.9 | 37 | 884 | United_StatesTexasHONDO MUNICIPAL AP
United_States | Texas | HOUSTON BUSH INTERCONTINENTAL | HOUSTON BUSH INTERCONTINENTAL, TX, USA | 29.99N | 95.36W | 32 | -6.00 (NAC) | 82-06 | 722430 | -4.4 | -4 | -13.5 | 42.4 | 35.7 | 37.3 | 37.5 | 37 | 36.8333 | 37 | 34.4 | 35.7 | 36.2 | 35 | 35.4333 | 35 | 885 | United_StatesTexasHOUSTON BUSH INTERCONTINENTAL
United_States | Texas | HOUSTON WILLIAM P HOBBY AP | HOUSTON WILLIAM P HOBBY AP, TX, USA | 29.65N | 95.28W | 14 | -6.00 (NAC) | 82-06 | 722435 | -3.1 | -3 | -12.3 | 41 | 35.2 | 36.3 | 36.4 | 36 | 35.9667 | 36 | 33.8 | 34.7 | 35.1 | 35 | 34.5333 | 35 | 886 | United_StatesTexasHOUSTON WILLIAM P HOBBY AP
United_States | Texas | HOUSTON/D.W. HOOKS | HOUSTON/D.W. HOOKS, TX, USA | 30.07N | 95.55W | 46 | -6.00 (NAC) | 98-06 | 722429 | -4.1 | -4 | -9.8 | 47 | 36.3 | 37.9 | 37.9 | 37 | 37.3667 | 38 | 34 | 37 | 36.3 | 36 | 35.7667 | 36 | 887 | United_StatesTexasHOUSTON/D.W. HOOKS
United_States | Texas | HOUSTON/ELLINGTON | HOUSTON/ELLINGTON, TX, USA | 29.60N | 95.17W | 12 | -6.00 (NAC) | 82-06 | 722436 | -2.6 | -3 | -11 | 42 | 35.4 | 37 | 37.2 | 37 | 36.5333 | 37 | 34.1 | 35.2 | 35.7 | 35 | 35 | 35 | 888 | United_StatesTexasHOUSTON/ELLINGTON
United_States | Texas | JUNCTION KIMBLE COUNTY AP | JUNCTION KIMBLE COUNTY AP, TX, USA | 30.51N | 99.77W | 533 | -6.00 (NAC) | 82-06 | 747400 | -9.9 | -10 | -18.4 | 42.6 | 38.5 | 38.7 | 38.8 | 39 | 38.6667 | 39 | 36.3 | 37.2 | 37.3 | 37 | 36.9333 | 37 | 889 | United_StatesTexasJUNCTION KIMBLE COUNTY AP
United_States | Texas | KELLY AFB | KELLY AFB, TX, USA | 29.38N | 98.58W | 208 | -6.00 (NAC) | 82-05 | 722535 | -6.4 | -6 | -17.5 | 44 | 38.8 | 39.1 | 38.9 | 39 | 38.9333 | 39 | 36.4 | 37.8 | 37.6 | 37 | 37.2667 | 37 | 890 | United_StatesTexasKELLY AFB
United_States | Texas | KILLEEN MUNI (AWOS) | KILLEEN MUNI (AWOS), TX, USA | 31.08N | 97.68W | 258 | -6.00 (NAC) | 87-06 | 722575 | -6.3 | -6 | -12.4 | 43.4 | 37.3 | 38.7 | 38.9 | 38 | 38.3 | 39 | 35.2 | 37.3 | 37.6 | 37 | 36.7 | 37 | 891 | United_StatesTexasKILLEEN MUNI (AWOS)
United_States | Texas | KINGSVILLE | KINGSVILLE, TX, USA | 27.50N | 97.82W | 18 | -6.00 (NAC) | 82-06 | 722516 | -2.6 | -3 | -11.6 | 41.3 | 36.8 | 37.4 | 37.8 | 37 | 37.3333 | 37 | 35.5 | 36.2 | 36.5 | 36 | 36.0667 | 36 | 892 | United_StatesTexasKINGSVILLE
United_States | Texas | LAREDO INTL AIRPORT | LAREDO INTL AIRPORT, TX, USA | 27.55N | 99.47W | 155 | -6.00 (NAC) | 82-06 | 722520 | -1.6 | -2 | -9.1 | 45 | 41 | 40.4 | 40.3 | 41 | 40.5667 | 40 | 38.9 | 38.9 | 38.9 | 39 | 38.9 | 39 | 893 | United_StatesTexasLAREDO INTL AIRPORT
United_States | Texas | LAUGHLIN AFB | LAUGHLIN AFB, TX, USA | 29.37N | 100.78W | 327 | -6.00 (NAC) | 82-01 | 722615 | -5.1 | -5 | -14 | 46.7 | 41.4 | 42.2 | 41.1 | 42 | 41.5667 | 42 | 39 | 40 | 39.2 | 39 | 39.4 | 39 | 894 | United_StatesTexasLAUGHLIN AFB
United_States | Texas | LONGVIEW GREGG COUNTY AP | LONGVIEW GREGG COUNTY AP, TX, USA | 32.39N | 94.71W | 114 | -6.00 (NAC) | 83-06 | 722470 | -8.2 | -8 | -17.3 | 43.4 | 37.1 | 38.7 | 38.9 | 38 | 38.2333 | 39 | 34.6 | 37.1 | 37.4 | 36 | 36.3667 | 36 | 895 | United_StatesTexasLONGVIEW GREGG COUNTY AP
United_States | Texas | LUBBOCK INTERNATIONAL AP | LUBBOCK INTERNATIONAL AP, TX, USA | 33.67N | 101.82W | 988 | -6.00 (NAC) | 82-06 | 722670 | -13.5 | -14 | -21 | 44.7 | 39.3 | 38.7 | 37.1 | 38 | 38.3667 | 39 | 36.9 | 36.9 | 35.6 | 36 | 36.4667 | 36 | 896 | United_StatesTexasLUBBOCK INTERNATIONAL AP
United_States | Texas | LUFKIN ANGELINA CO | LUFKIN ANGELINA CO, TX, USA | 31.23N | 94.75W | 96 | -6.00 (NAC) | 82-06 | 722446 | -7.1 | -7 | -13.9 | 43.2 | 36.4 | 37.9 | 38.3 | 38 | 37.5333 | 38 | 34.2 | 36.1 | 36.7 | 36 | 35.6667 | 36 | 897 | United_StatesTexasLUFKIN ANGELINA CO
United_States | Texas | MARFA AP | MARFA AP, TX, USA | 30.37N | 104.02W | 1478 | -7.00 (NAM) | 82-06 | 722640 | -13.7 | -14 | -21.2 | 40.8 | 37.3 | 35.7 | 34 | 36 | 35.6667 | 36 | 35 | 33.7 | 32.4 | 34 | 33.7 | 34 | 898 | United_StatesTexasMARFA AP
United_States | Texas | MC GREGOR (AWOS) | MC GREGOR (AWOS), TX, USA | 31.48N | 97.32W | 180 | -6.00 (NAC) | 92-06 | 722563 | -6.7 | -7 | -11.8 | 43.8 | 37.4 | 39 | 39 | 38 | 38.4667 | 39 | 36.1 | 37.7 | 37.8 | 37 | 37.2 | 37 | 899 | United_StatesTexasMC GREGOR (AWOS)
United_States | Texas | MCALLEN MILLER INTL AP | MCALLEN MILLER INTL AP, TX, USA | 26.18N | 98.24W | 34 | -6.00 (NAC) | 82-06 | 722506 | -0.4 | 0 | -7.9 | 43.6 | 37.9 | 38.8 | 38.9 | 39 | 38.5333 | 39 | 37 | 37.6 | 37.8 | 37 | 37.4667 | 37 | 900 | United_StatesTexasMCALLEN MILLER INTL AP
United_States | Texas | MCKINNEY MUNI ARPT | MCKINNEY MUNI ARPT, TX, USA | 33.18N | 96.58W | 176 | -6.00 (NAC) | 98-06 | 722541 | -9.5 | -10 | -15.5 | 47 | 37.1 | 39.2 | 40.2 | 39 | 38.8333 | 39 | 35.2 | 37.9 | 38 | 37 | 37.0333 | 37 | 901 | United_StatesTexasMCKINNEY MUNI ARPT
United_States | Texas | MIDLAND INTERNATIONAL AP | MIDLAND INTERNATIONAL AP, TX, USA | 31.93N | 102.21W | 872 | -6.00 (NAC) | 82-06 | 722650 | -11.4 | -11 | -20.6 | 45.5 | 40.7 | 39.7 | 38.4 | 40 | 39.6 | 40 | 37.9 | 37.5 | 36.8 | 37 | 37.4 | 37 | 902 | United_StatesTexasMIDLAND INTERNATIONAL AP
United_States | Texas | NACOGDOCHES (AWOS) | NACOGDOCHES (AWOS), TX, USA | 31.58N | 94.72W | 108 | -6.00 (NAC) | 92-06 | 722499 | -7.4 | -7 | -12.7 | 42.8 | 37 | 37.9 | 37.7 | 38 | 37.5333 | 38 | 34 | 36.3 | 36.3 | 36 | 35.5333 | 36 | 903 | United_StatesTexasNACOGDOCHES (AWOS)
United_States | Texas | PALACIOS MUNICIPAL AP | PALACIOS MUNICIPAL AP, TX, USA | 28.73N | 96.25W | 5 | -6.00 (NAC) | 87-06 | 722555 | -2.7 | -3 | -10.4 | 39.9 | 33.1 | 34 | 34.8 | 34 | 33.9667 | 34 | 32.4 | 32.9 | 33.7 | 33 | 33 | 33 | 904 | United_StatesTexasPALACIOS MUNICIPAL AP
United_States | Texas | PINE SPRINGS GUADALUPE MOUNTA | PINE SPRINGS GUADALUPE MOUNTA, TX, USA | 31.83N | 104.81W | 1663 | -7.00 (NAM) | 82-06 | 722620 | -11.9 | -12 | -21.7 | 41.4 | 37.1 | 36.2 | 34 | 36 | 35.7667 | 36 | 34.6 | 33.6 | 32 | 33 | 33.4 | 33 | 905 | United_StatesTexasPINE SPRINGS GUADALUPE MOUNTA
United_States | Texas | PORT ARANSAS | PORT ARANSAS, TX, USA | 27.82N | 97.05W | 6 | -6.00 (NAC) | 85-06 | 994110 | -0.1 | 0 | -8.8 | 35.5 | 29.6 | 29.9 | 30.6 | 30 | 30.0333 | 30 | 29 | 29.5 | 30 | 30 | 29.5 | 30 | 906 | United_StatesTexasPORT ARANSAS
United_States | Texas | PORT ARTHUR JEFFERSON COUNTY | PORT ARTHUR JEFFERSON COUNTY, TX, USA | 29.95N | 94.02W | 5 | -6.00 (NAC) | 82-06 | 722410 | -3.9 | -4 | -10.8 | 40.4 | 34.5 | 35.4 | 36.2 | 35 | 35.3667 | 35 | 33.3 | 34.1 | 34.7 | 34 | 34.0333 | 34 | 907 | United_StatesTexasPORT ARTHUR JEFFERSON COUNTY
United_States | Texas | RANDOLPH AFB | RANDOLPH AFB, TX, USA | 29.53N | 98.28W | 232 | -6.00 (NAC) | 82-01 | 722536 | -5.8 | -6 | -13.6 | 44 | 38.2 | 38.8 | 38.7 | 39 | 38.5667 | 39 | 36 | 37.4 | 37.3 | 37 | 36.9 | 37 | 908 | United_StatesTexasRANDOLPH AFB
United_States | Texas | REESE AFB | REESE AFB, TX, USA | 33.60N | 102.05W | 1014 | -6.00 (NAC) | 82-97 | 722675 | -13.9 | -14 | -20.9 | 46.9 | 40.1 | 40.1 | 37.5 | 39 | 39.2333 | 40 | 37.1 | 37.8 | 36 | 37 | 36.9667 | 37 | 909 | United_StatesTexasREESE AFB
United_States | Texas | ROCKPORT/ARANSAS CO | ROCKPORT/ARANSAS CO, TX, USA | 28.08N | 97.05W | 8 | -6.00 (NAC) | 96-06 | 722524 | -0.2 | 0 | -4.9 | 42.4 | 33.8 | 33.9 | 34.9 | 34 | 34.2 | 34 | 32.8 | 32.9 | 33.9 | 33 | 33.2 | 33 | 910 | United_StatesTexasROCKPORT/ARANSAS CO
United_States | Texas | SABINE | SABINE, TX, USA | 29.67N | 94.05W | 6 | -6.00 (NAC) | 85-06 | 994260 | -2.9 | -3 | -10.6 | 37.5 | 31.4 | 31.8 | 32.9 | 32 | 32.0333 | 32 | 30.1 | 30.7 | 31.4 | 31 | 30.7333 | 31 | 911 | United_StatesTexasSABINE
United_States | Texas | SAN ANGELO MATHIS FIELD | SAN ANGELO MATHIS FIELD, TX, USA | 31.35N | 100.49W | 577 | -6.00 (NAC) | 82-06 | 722630 | -10.2 | -10 | -20 | 44.3 | 39.3 | 39.7 | 38.6 | 39 | 39.2 | 40 | 36.9 | 37.8 | 37.3 | 37 | 37.3333 | 37 | 912 | United_StatesTexasSAN ANGELO MATHIS FIELD
United_States | Texas | SAN ANTONIO INTL AP | SAN ANTONIO INTL AP, TX, USA | 29.53N | 98.46W | 247 | -6.00 (NAC) | 82-06 | 722530 | -5.8 | -6 | -14.1 | 42.8 | 37.3 | 38 | 37.9 | 38 | 37.7333 | 38 | 35.7 | 36.8 | 36.9 | 36 | 36.4667 | 36 | 913 | United_StatesTexasSAN ANTONIO INTL AP
United_States | Texas | SAN ANTONIO/STINSON | SAN ANTONIO/STINSON, TX, USA | 29.34N | 98.47W | 176 | -6.00 (NAC) | 98-06 | 722523 | -3.8 | -4 | -7.9 | 43.8 | 38.7 | 38.9 | 38.7 | 39 | 38.7667 | 39 | 36.4 | 37.7 | 37.6 | 37 | 37.2333 | 37 | 914 | United_StatesTexasSAN ANTONIO/STINSON
United_States | Texas | SAN MARCOS MUNI | SAN MARCOS MUNI, TX, USA | 29.88N | 97.87W | 182 | -6.00 (NAC) | 92-06 | 722539 | -5.1 | -5 | -9.2 | 44.2 | 37.4 | 37.7 | 38 | 38 | 37.7 | 38 | 35.8 | 37.1 | 37.3 | 37 | 36.7333 | 37 | 915 | United_StatesTexasSAN MARCOS MUNI
United_States | Texas | SANDERSON (RAMOS) | SANDERSON (RAMOS), TX, USA | 30.17N | 102.42W | 865 | -6.00 (NAC) | 82-96 | 747300 | -8.2 | -8 | -19.4 | 44.5 | 39.9 | 39 | 36.7 | 39 | 38.5333 | 39 | 36.8 | 36.5 | 35.4 | 36 | 36.2333 | 36 | 916 | United_StatesTexasSANDERSON (RAMOS)
United_States | Texas | STEPHENVILLE CLARK FIELD | STEPHENVILLE CLARK FIELD, TX, USA | 32.22N | 98.18W | 403 | -6.00 (NAC) | 84-06 | 722600 | -10.2 | -10 | -22.5 | 41.9 | 36.3 | 37.7 | 37.9 | 37 | 37.3 | 38 | 34.2 | 36.1 | 36.9 | 36 | 35.7333 | 36 | 917 | United_StatesTexasSTEPHENVILLE CLARK FIELD
United_States | Texas | VICTORIA REGIONAL AP | VICTORIA REGIONAL AP, TX, USA | 28.86N | 96.93W | 36 | -6.00 (NAC) | 82-06 | 722550 | -4.2 | -4 | -12.3 | 42.1 | 35.7 | 36.8 | 37.4 | 37 | 36.6333 | 37 | 34.4 | 35.6 | 36 | 35 | 35.3333 | 35 | 918 | United_StatesTexasVICTORIA REGIONAL AP
United_States | Texas | WACO REGIONAL AP | WACO REGIONAL AP, TX, USA | 31.61N | 97.23W | 155 | -6.00 (NAC) | 82-06 | 722560 | -8 | -8 | -18.2 | 44.3 | 37.7 | 39.3 | 39.9 | 39 | 38.9667 | 39 | 35.9 | 38 | 38.4 | 37 | 37.4333 | 37 | 919 | United_StatesTexasWACO REGIONAL AP
United_States | Texas | WICHITA FALLS MUNICIPAL ARPT | WICHITA FALLS MUNICIPAL ARPT, TX, USA | 33.98N | 98.49W | 314 | -6.00 (NAC) | 82-06 | 723510 | -12.2 | -12 | -22.4 | 45.1 | 38.8 | 41.2 | 40.7 | 40 | 40.2333 | 41 | 36.5 | 39.4 | 39.1 | 38 | 38.3333 | 38 | 920 | United_StatesTexasWICHITA FALLS MUNICIPAL ARPT
United_States | Texas | WINK WINKLER COUNTY AP | WINK WINKLER COUNTY AP, TX, USA | 31.78N | 103.20W | 860 | -6.00 (NAC) | 88-06 | 722656 | -11 | -11 | -17.5 | 47.8 | 42.6 | 42.2 | 41.3 | 42 | 42.0333 | 42 | 40.7 | 39.9 | 38.3 | 40 | 39.6333 | 40 | 921 | United_StatesTexasWINK WINKLER COUNTY AP
United_States | Utah | CEDAR CITY MUNICIPAL AP | CEDAR CITY MUNICIPAL AP, UT, USA | 37.70N | 113.10W | 1712 | -7.00 (NAM) | 82-06 | 724755 | -20.9 | -21 | -31.8 | 39.7 | 34.7 | 36.5 | 34.7 | 35 | 35.3 | 37 | 32.9 | 34.8 | 33.2 | 34 | 33.6333 | 34 | 922 | United_StatesUtahCEDAR CITY MUNICIPAL AP
United_States | Utah | HILL AFB/OGDEN | HILL AFB/OGDEN, UT, USA | 41.12N | 111.97W | 1459 | -7.00 (NAM) | 82-06 | 725755 | -16.1 | -16 | -24.5 | 40.8 | 35 | 37.1 | 35 | 36 | 35.7 | 37 | 32.1 | 34.9 | 33.3 | 33 | 33.4333 | 33 | 923 | United_StatesUtahHILL AFB/OGDEN
United_States | Utah | LOGAN-CACHE AIRPORT | LOGAN-CACHE AIRPORT, UT, USA | 41.79N | 111.85W | 1358 | -7.00 (NAM) | 98-06 | 724796 | -23.6 | -24 | -37.1 | 41.1 | 33.8 | 37.6 | 36.1 | 36 | 35.8333 | 38 | 32.2 | 36.2 | 33.9 | 34 | 34.1 | 34 | 924 | United_StatesUtahLOGAN-CACHE AIRPORT
United_States | Utah | MILFORD MUNICIPAL AP | MILFORD MUNICIPAL AP, UT, USA | 38.44N | 113.03W | 1534 | -7.00 (NAM) | 82-06 | 724797 | -22.1 | -22 | -33 | 41.8 | 36.1 | 38.7 | 36.3 | 37 | 37.0333 | 39 | 34 | 37.1 | 34.4 | 35 | 35.1667 | 35 | 925 | United_StatesUtahMILFORD MUNICIPAL AP
United_States | Utah | PRICE/CARBON COUNTY | PRICE/CARBON COUNTY, UT, USA | 39.62N | 110.75W | 1799 | -7.00 (NAM) | 82-06 | 724700 | -18.7 | -19 | -28.4 | 38.8 | 34.1 | 36.4 | 33.9 | 35 | 34.8 | 36 | 32.4 | 34.3 | 32.4 | 33 | 33.0333 | 33 | 926 | United_StatesUtahPRICE/CARBON COUNTY
United_States | Utah | PROVO MUNI (AWOS) | PROVO MUNI (AWOS), UT, USA | 40.22N | 111.72W | 1369 | -7.00 (NAM) | 92-06 | 725724 | -15 | -15 | -26.9 | 41.5 | 35.2 | 37.7 | 35.3 | 36 | 36.0667 | 38 | 32.7 | 36 | 33.1 | 34 | 33.9333 | 34 | 927 | United_StatesUtahPROVO MUNI (AWOS)
United_States | Utah | SAINT GEORGE (AWOS) | SAINT GEORGE (AWOS), UT, USA | 37.08N | 113.60W | 896 | -7.00 (NAM) | 92-06 | 724754 | -5.8 | -6 | -8.9 | 46.4 | 42 | 43.7 | 42.1 | 43 | 42.6 | 44 | 39.1 | 42.1 | 40.9 | 41 | 40.7 | 41 | 928 | United_StatesUtahSAINT GEORGE (AWOS)
United_States | Utah | SALT LAKE CITY INT'L ARPT | SALT LAKE CITY INT'L ARPT, UT, USA | 40.79N | 111.97W | 1288 | -7.00 (NAM) | 82-06 | 725720 | -16.3 | -16 | -27.3 | 42.6 | 36.8 | 38.7 | 37.2 | 38 | 37.5667 | 39 | 34.5 | 37.1 | 35.4 | 36 | 35.6667 | 36 | 929 | United_StatesUtahSALT LAKE CITY INT'L ARPT
United_States | Utah | VERNAL | VERNAL, UT, USA | 40.43N | 109.52W | 1608 | -7.00 (NAM) | 98-06 | 725705 | -20.2 | -20 | -29.5 | 39.4 | 34.1 | 37 | 33.9 | 35 | 35 | 37 | 32.4 | 35.2 | 32.5 | 33 | 33.3667 | 33 | 930 | United_StatesUtahVERNAL
United_States | Utah | WENDOVER USAF AUXILIARY FIELD | WENDOVER USAF AUXILIARY FIELD, UT, USA | 40.72N | 114.02W | 1291 | -7.00 (NAM) | 82-06 | 725810 | -16.1 | -16 | -27.5 | 41.8 | 36.3 | 38 | 36.4 | 37 | 36.9 | 38 | 33.8 | 36.5 | 34.8 | 35 | 35.0333 | 35 | 931 | United_StatesUtahWENDOVER USAF AUXILIARY FIELD
United_States | Vermont | BURLINGTON INTERNATIONAL AP | BURLINGTON INTERNATIONAL AP, VT, USA | 44.47N | 73.15W | 104 | -5.00 (NAE) | 82-06 | 726170 | -26.1 | -26 | -35.8 | 38.8 | 33 | 33.7 | 32.7 | 33 | 33.1333 | 34 | 30.5 | 31.3 | 30.4 | 31 | 30.7333 | 31 | 932 | United_StatesVermontBURLINGTON INTERNATIONAL AP
United_States | Vermont | MONTPELIER AP | MONTPELIER AP, VT, USA | 44.20N | 72.58W | 342 | -5.00 (NAE) | 82-06 | 726145 | -27.9 | -28 | -36.8 | 37.2 | 31.3 | 31.7 | 30.8 | 31 | 31.2667 | 32 | 28.9 | 29.5 | 28.5 | 29 | 28.9667 | 29 | 933 | United_StatesVermontMONTPELIER AP
United_States | Vermont | MORRISVILLE\STONE | MORRISVILLE\STONE, VT, USA | 44.53N | 72.62W | 223 | -5.00 (NAE) | 97-06 | 726114 | -28.3 | -28 | -39 | 37.8 | 32.4 | 31.4 | 32.2 | 32 | 32 | 31 | 29.2 | 29.1 | 29 | 29 | 29.1 | 29 | 934 | United_StatesVermontMORRISVILLE\STONE
United_States | Vermont | RUTLAND STATE | RUTLAND STATE, VT, USA | 43.52N | 72.95W | 246 | -5.00 (NAE) | 92-06 | 725165 | -25.8 | -26 | -36.8 | 36.2 | 31.3 | 31.3 | 31.2 | 31 | 31.2667 | 31 | 28.8 | 29.1 | 28.7 | 29 | 28.8667 | 29 | 935 | United_StatesVermontRUTLAND STATE
United_States | Vermont | SPRINGFIELD/HARTNES | SPRINGFIELD/HARTNES, VT, USA | 43.35N | 72.52W | 176 | -5.00 (NAE) | 96-06 | 726115 | -24.5 | -25 | -33.6 | 40.9 | 32.5 | 32.8 | 32.7 | 33 | 32.6667 | 33 | 30.9 | 31.2 | 30 | 31 | 30.7 | 31 | 936 | United_StatesVermontSPRINGFIELD/HARTNES
United_States | Virginia | ABINGTON | ABINGTON, VA, USA | 36.68N | 82.03W | 631 | -5.00 (NAE) | 95-06 | 724058 | -15.8 | -16 | -24.4 | 35 | 32.2 | 32.4 | 33.7 | 33 | 32.7667 | 32 | 30.9 | 31.1 | 32.2 | 31 | 31.4 | 31 | 937 | United_StatesVirginia ABINGTON
United_States | Virginia | CHESAPEAKE | CHESAPEAKE, VA, USA | 36.90N | 75.72W | 23 | -5.00 (NAE) | 89-06 | 994020 | -7.7 | -8 | -15 | 33.9 | 28.9 | 30.7 | 30.2 | 30 | 29.9333 | 31 | 27.1 | 29.3 | 28.6 | 28 | 28.3333 | 28 | 938 | United_StatesVirginia CHESAPEAKE
United_States | Virginia | DANVILLE FAA AP | DANVILLE FAA AP, VA, USA | 36.57N | 79.34W | 180 | -5.00 (NAE) | 94-06 | 724106 | -11.8 | -12 | -19 | 40.6 | 34.2 | 36.2 | 36 | 35 | 35.4667 | 36 | 32.6 | 34 | 34 | 34 | 33.5333 | 34 | 939 | United_StatesVirginia DANVILLE FAA AP
United_States | Virginia | DINWIDDIE CO | DINWIDDIE CO, VA, USA | 37.18N | 77.50W | 60 | -5.00 (NAE) | 92-06 | 724014 | -14.3 | -14 | -22.7 | 43.2 | 37.2 | 38 | 37.6 | 38 | 37.6 | 38 | 35 | 36.9 | 36.1 | 36 | 36 | 36 | 940 | United_StatesVirginia DINWIDDIE CO
United_States | Virginia | FARMVILLE | FARMVILLE, VA, USA | 37.35N | 78.43W | 125 | -5.00 (NAE) | 94-06 | 724017 | -16 | -16 | -27.1 | 41.1 | 34.7 | 37 | 37.1 | 36 | 36.2667 | 37 | 32.9 | 34.9 | 34.9 | 34 | 34.2333 | 34 | 941 | United_StatesVirginia FARMVILLE
United_States | Virginia | FORT BELVOIR/DAVISO | FORT BELVOIR/DAVISO, VA, USA | 38.72N | 77.18W | 27 | -5.00 (NAE) | 82-01 | 724037 | -16.5 | -17 | -27.6 | 42.1 | 36.1 | 37.8 | 37.2 | 37 | 37.0333 | 38 | 33.9 | 36 | 34.7 | 35 | 34.8667 | 35 | 942 | United_StatesVirginia FORT BELVOIR/DAVISO
United_States | Virginia | HILLSVILLE | HILLSVILLE, VA, USA | 36.77N | 80.82W | 834 | -5.00 (NAE) | 95-06 | 724107 | -14.5 | -15 | -19.6 | 35 | 29.9 | 31.4 | 31.3 | 31 | 30.8667 | 31 | 28 | 29.1 | 29.5 | 29 | 28.8667 | 29 | 943 | United_StatesVirginia HILLSVILLE
United_States | Virginia | HOT SPRINGS/INGALLS | HOT SPRINGS/INGALLS, VA, USA | 37.95N | 79.83W | 1156 | -5.00 (NAE) | 94-06 | 724115 | -19.3 | -19 | -28.5 | 35.2 | 27.9 | 30.5 | 29.7 | 29 | 29.3667 | 31 | 26.6 | 28.5 | 27.8 | 28 | 27.6333 | 28 | 944 | United_StatesVirginia HOT SPRINGS/INGALLS
United_States | Virginia | LANGLEY AFB/HAMPTON | LANGLEY AFB/HAMPTON, VA, USA | 37.08N | 76.37W | 3 | -5.00 (NAE) | 82-06 | 745980 | -10.2 | -10 | -18.5 | 40 | 34.4 | 36 | 35.1 | 35 | 35.1667 | 36 | 32.6 | 34.1 | 32.9 | 33 | 33.2 | 33 | 945 | United_StatesVirginia LANGLEY AFB/HAMPTON
United_States | Virginia | LEESBURG/GODFREY | LEESBURG/GODFREY, VA, USA | 39.08N | 77.57W | 119 | -5.00 (NAE) | 95-06 | 724055 | -14.4 | -14 | -19.6 | 39.7 | 35 | 37.1 | 37.1 | 36 | 36.4 | 37 | 33.2 | 35 | 34.8 | 34 | 34.3333 | 34 | 946 | United_StatesVirginia LEESBURG/GODFREY
United_States | Virginia | LYNCHBURG REGIONAL ARPT | LYNCHBURG REGIONAL ARPT, VA, USA | 37.34N | 79.21W | 286 | -5.00 (NAE) | 82-06 | 724100 | -15.1 | -15 | -24.5 | 39.3 | 33.3 | 35.2 | 35.1 | 35 | 34.5333 | 35 | 31.8 | 33.7 | 33 | 33 | 32.8333 | 33 | 947 | United_StatesVirginia LYNCHBURG REGIONAL ARPT
United_States | Virginia | MANASSAS MUNI(AWOS) | MANASSAS MUNI(AWOS), VA, USA | 38.72N | 77.52W | 59 | -5.00 (NAE) | 92-06 | 724036 | -16.4 | -16 | -25.7 | 39.5 | 33.9 | 35.9 | 35.8 | 35 | 35.2 | 36 | 32.4 | 33.8 | 33.7 | 33 | 33.3 | 33 | 948 | United_StatesVirginia MANASSAS MUNI(AWOS)
United_States | Virginia | MARION / WYTHEVILLE | MARION / WYTHEVILLE, VA, USA | 36.90N | 81.35W | 780 | -5.00 (NAE) | 95-06 | 724056 | -17.1 | -17 | -26.4 | 38.2 | 32.3 | 33 | 32.9 | 33 | 32.7333 | 33 | 30.3 | 32.1 | 32.1 | 32 | 31.5 | 32 | 949 | United_StatesVirginia MARION / WYTHEVILLE
United_States | Virginia | MARTINSVILLE | MARTINSVILLE, VA, USA | 36.63N | 80.02W | 287 | -5.00 (NAE) | 95-06 | 745985 | -14.8 | -15 | -23.2 | 39.6 | 35.2 | 36.2 | 36.3 | 36 | 35.9 | 36 | 32.9 | 34.1 | 34.1 | 34 | 33.7 | 34 | 950 | United_StatesVirginia MARTINSVILLE
United_States | Virginia | MECKLENBURG\BRUNS. | MECKLENBURG\BRUNS., VA, USA | 36.70N | 78.05W | 430 | -5.00 (NAE) | 97-06 | 724118 | N/A | N/A | N/A | N/A | 35.3 | 37.3 | 37 | 37 | 36.5333 | 37 | 33 | 35.1 | 34.9 | 34 | 34.3333 | 34 | 951 | United_StatesVirginia MECKLENBURG\BRUNS.
United_States | Virginia | MELFA/ACCOMACK ARPT | MELFA/ACCOMACK ARPT, VA, USA | 37.65N | 75.77W | 15 | -5.00 (NAE) | 82-06 | 724026 | N/A | N/A | N/A | N/A | 35 | 36.4 | 35.2 | 36 | 35.5333 | 36 | 32.9 | 34.3 | 33.7 | 34 | 33.6333 | 34 | 952 | United_StatesVirginia MELFA/ACCOMACK ARPT
United_States | Virginia | NEWPORT NEWS | NEWPORT NEWS, VA, USA | 37.13N | 76.49W | 16 | -5.00 (NAE) | 82-06 | 723086 | -11.4 | -11 | -19.4 | 42.4 | 35.1 | 36.9 | 36.1 | 36 | 36.0333 | 37 | 33.1 | 35.1 | 33.8 | 34 | 34 | 34 | 953 | United_StatesVirginia NEWPORT NEWS
United_States | Virginia | NORFOLK INTERNATIONAL AP | NORFOLK INTERNATIONAL AP, VA, USA | 36.90N | 76.19W | 9 | -5.00 (NAE) | 82-06 | 723080 | -9.1 | -9 | -18.1 | 39.9 | 35 | 36.4 | 35.3 | 36 | 35.5667 | 36 | 33.1 | 34.6 | 33.4 | 34 | 33.7 | 34 | 954 | United_StatesVirginia NORFOLK INTERNATIONAL AP
United_States | Virginia | NORFOLK NAS | NORFOLK NAS, VA, USA | 36.93N | 76.28W | 5 | -5.00 (NAE) | 82-06 | 723085 | -8.5 | -9 | -17.4 | 40.2 | 35 | 36.7 | 35.9 | 36 | 35.8667 | 37 | 32.9 | 34.9 | 33.3 | 34 | 33.7 | 34 | 955 | United_StatesVirginia NORFOLK NAS
United_States | Virginia | OCEANA NAS | OCEANA NAS, VA, USA | 36.82N | 76.03W | 7 | -5.00 (NAE) | 82-06 | 723075 | -9.5 | -10 | -17.7 | 39.3 | 34.1 | 35.9 | 34.9 | 35 | 34.9667 | 36 | 32.4 | 34.1 | 32.9 | 33 | 33.1333 | 33 | 956 | United_StatesVirginia OCEANA NAS
United_States | Virginia | QUANTICO MCAS | QUANTICO MCAS, VA, USA | 38.50N | 77.30W | 4 | -5.00 (NAE) | 84-06 | 724035 | -13.1 | -13 | -22.8 | 40.7 | 34.3 | 36.2 | 34.8 | 35 | 35.1 | 36 | 32.3 | 34 | 32.9 | 33 | 33.0667 | 33 | 957 | United_StatesVirginia QUANTICO MCAS
United_States | Virginia | ROANOKE REGIONAL AP | ROANOKE REGIONAL AP, VA, USA | 37.32N | 79.97W | 358 | -5.00 (NAE) | 82-06 | 724110 | -14.3 | -14 | -24 | 40.4 | 33.5 | 35.7 | 35.3 | 35 | 34.8333 | 36 | 31.8 | 33.6 | 33.1 | 33 | 32.8333 | 33 | 958 | United_StatesVirginia ROANOKE REGIONAL AP
United_States | Virginia | SHANNON ARPT | SHANNON ARPT, VA, USA | 38.27N | 77.45W | 26 | -5.00 (NAE) | 94-06 | 724033 | -14.8 | -15 | -25.3 | 40.5 | 35.2 | 37.2 | 37.4 | 37 | 36.6 | 37 | 33.3 | 34.9 | 35.7 | 35 | 34.6333 | 35 | 959 | United_StatesVirginia SHANNON ARPT
United_States | Virginia | STAUNTON/SHENANDOAH | STAUNTON/SHENANDOAH, VA, USA | 38.27N | 78.90W | 366 | -5.00 (NAE) | 94-06 | 724105 | -16.5 | -17 | -27.1 | 40.3 | 34.1 | 37.1 | 36.1 | 36 | 35.7667 | 37 | 32.7 | 34.1 | 34 | 34 | 33.6 | 34 | 960 | United_StatesVirginia STAUNTON/SHENANDOAH
United_States | Virginia | VIRGINIA TECH ARPT | VIRGINIA TECH ARPT, VA, USA | 37.22N | 80.42W | 650 | -5.00 (NAE) | 94-06 | 724113 | -15.3 | -15 | -21.1 | 35.6 | 31.3 | 32.7 | 32.8 | 32 | 32.2667 | 33 | 29.8 | 31.2 | 31.4 | 31 | 30.8 | 31 | 961 | United_StatesVirginia VIRGINIA TECH ARPT
United_States | Virginia | WALLOPS ISLAND UAU | WALLOPS ISLAND UAU, VA, USA | 37.94N | 75.50W | 15 | -5.00 (NAE) | 96-06 | 724020 | -11 | -11 | -19.7 | 37.8 | 33.4 | 34.6 | 33.9 | 34 | 33.9667 | 35 | 31.4 | 32.6 | 32.1 | 32 | 32.0333 | 32 | 962 | United_StatesVirginia WALLOPS ISLAND UAU
United_States | Virginia | WASHINGTON DC DULLES INT'L AR | WASHINGTON DC DULLES INT'L AR, VA, USA | 38.94N | 77.45W | 99 | -5.00 (NAE) | 82-06 | 724030 | -17.2 | -17 | -29 | 41.1 | 34.3 | 36.1 | 35.8 | 35 | 35.4 | 36 | 32.4 | 34.3 | 33.8 | 34 | 33.5 | 34 | 963 | United_StatesVirginia WASHINGTON DC DULLES INT'L AR
United_States | Virginia | WASHINGTON DC REAGAN AP | WASHINGTON DC REAGAN AP, VA, USA | 38.87N | 77.03W | 20 | -5.00 (NAE) | 82-06 | 724050 | -12.3 | -12 | -22.2 | 40.9 | 35.4 | 36.8 | 36 | 36 | 36.0667 | 37 | 33 | 35 | 34 | 34 | 34 | 34 | 964 | United_StatesVirginia WASHINGTON DC REAGAN AP
United_States | Virginia | WINCHESTER RGNL | WINCHESTER RGNL, VA, USA | 39.15N | 78.15W | 222 | -5.00 (NAE) | 95-06 | 724053 | -14.5 | -15 | -22.2 | 49.6 | 34.7 | 37.2 | 36.3 | 36 | 36.0667 | 37 | 32.5 | 34.7 | 33.6 | 34 | 33.6 | 34 | 965 | United_StatesVirginia WINCHESTER RGNL
United_States | Virginia | WISE/LONESOME PINE | WISE/LONESOME PINE, VA, USA | 36.98N | 82.53W | 817 | -5.00 (NAE) | 94-06 | 724117 | N/A | N/A | N/A | N/A | 30 | 31.3 | 31.3 | 31 | 30.8667 | 31 | 28.1 | 29.8 | 29.8 | 29 | 29.2333 | 29 | 966 | United_StatesVirginia WISE/LONESOME PINE
United_States | Washington | ARLINGTON MUNI | ARLINGTON MUNI, WA, USA | 48.17N | 122.17W | 42 | -8.00 (NAP) | 92-06 | 727945 | -8.8 | -9 | -17 | 37 | 28 | 32.3 | 29.2 | 30 | 29.8333 | 32 | 25.8 | 28.6 | 27.5 | 27 | 27.3 | 27 | 967 | United_StatesWashingtonARLINGTON MUNI
United_States | Washington | BELLINGHAM INTL AP | BELLINGHAM INTL AP, WA, USA | 48.79N | 122.54W | 46 | -8.00 (NAP) | 82-06 | 727976 | -10.1 | -10 | -20 | 34.8 | 27.6 | 28.9 | 28 | 28 | 28.1667 | 29 | 24.6 | 26.3 | 26 | 26 | 25.6333 | 26 | 968 | United_StatesWashingtonBELLINGHAM INTL AP
United_States | Washington | BREMERTON NATIONAL | BREMERTON NATIONAL, WA, USA | 47.48N | 122.75W | 137 | -8.00 (NAP) | 89-06 | 727928 | -7.5 | -8 | -16.2 | 39.1 | 31.7 | 34 | 31.5 | 32 | 32.4 | 34 | 27.6 | 30.1 | 28.9 | 29 | 28.8667 | 29 | 969 | United_StatesWashingtonBREMERTON NATIONAL
United_States | Washington | DESTRUCTION ISLAND | DESTRUCTION ISLAND, WA, USA | 47.67N | 124.48W | 39 | -8.00 (NAP) | 85-06 | 994070 | -1.5 | -2 | -8.6 | 26.6 | 20.1 | 19.1 | 19.5 | 20 | 19.5667 | 19 | 17.1 | 17.3 | 17.8 | 17 | 17.4 | 17 | 970 | United_StatesWashingtonDESTRUCTION ISLAND
United_States | Washington | FAIRCHILD AFB | FAIRCHILD AFB, WA, USA | 47.62N | 117.65W | 743 | -8.00 (NAP) | 82-06 | 727855 | -18.7 | -19 | -30.8 | 40.9 | 32.6 | 36.4 | 35.1 | 35 | 34.7 | 36 | 29.4 | 33.8 | 32.8 | 32 | 32 | 32 | 971 | United_StatesWashingtonFAIRCHILD AFB
United_States | Washington | FELTS FLD | FELTS FLD, WA, USA | 47.68N | 117.32W | 610 | -8.00 (NAP) | 82-06 | 727856 | -17 | -17 | -28.8 | 41.5 | 34.3 | 37.5 | 36.8 | 36 | 36.2 | 38 | 31.4 | 35.1 | 34.5 | 34 | 33.6667 | 34 | 972 | United_StatesWashingtonFELTS FLD
United_States | Washington | FRIDAY HARBOR | FRIDAY HARBOR, WA, USA | 48.52N | 123.02W | 33 | -8.00 (NAP) | 99-06 | 727985 | -5.4 | -5 | -13.1 | 36.5 | 28 | 29.1 | 27.3 | 28 | 28.1333 | 29 | 24.1 | 26.3 | 24.8 | 25 | 25.0667 | 25 | 973 | United_StatesWashingtonFRIDAY HARBOR
United_States | Washington | GRAY AAF | GRAY AAF, WA, USA | 47.08N | 122.58W | 92 | -8.00 (NAP) | 82-06 | 742071 | -10 | -10 | -19.7 | 39.2 | 31.6 | 34.1 | 32.2 | 33 | 32.6333 | 34 | 27.1 | 30.4 | 29.7 | 29 | 29.0667 | 29 | 974 | United_StatesWashingtonGRAY AAF
United_States | Washington | HANFORD | HANFORD, WA, USA | 46.57N | 119.60W | 223 | -8.00 (NAP) | 82-95 | 727840 | -16 | -16 | -29.3 | 45.5 | 39.6 | 40.7 | 39.4 | 40 | 39.9 | 41 | 36 | 38 | 37.6 | 37 | 37.2 | 37 | 975 | United_StatesWashingtonHANFORD
United_States | Washington | HOQUIAM AP | HOQUIAM AP, WA, USA | 46.97N | 123.94W | 5 | -8.00 (NAP) | 82-06 | 727923 | -4.3 | -4 | -10.6 | 35 | 28 | 28 | 27.4 | 28 | 27.8 | 28 | 21.7 | 24 | 23 | 23 | 22.9 | 23 | 976 | United_StatesWashingtonHOQUIAM AP
United_States | Washington | KELSO WB AP | KELSO WB AP, WA, USA | 46.12N | 122.89W | 6 | -8.00 (NAP) | 90-06 | 727924 | -7.7 | -8 | -15.8 | 41.4 | 32 | 35.1 | 32.9 | 33 | 33.3333 | 35 | 27 | 31.2 | 30.2 | 29 | 29.4667 | 29 | 977 | United_StatesWashingtonKELSO WB AP
United_States | Washington | MC CHORD AFB/TACOMA | MC CHORD AFB/TACOMA, WA, USA | 47.13N | 122.48W | 88 | -8.00 (NAP) | 82-06 | 742060 | -10.3 | -10 | -19.3 | 38.5 | 31.5 | 33.7 | 31.9 | 32 | 32.3667 | 34 | 27.7 | 30.2 | 29.3 | 29 | 29.0667 | 29 | 978 | United_StatesWashingtonMC CHORD AFB/TACOMA
United_States | Washington | OLYMPIA AIRPORT | OLYMPIA AIRPORT, WA, USA | 46.97N | 122.90W | 61 | -8.00 (NAP) | 82-06 | 727920 | -10.8 | -11 | -21.4 | 40 | 32.3 | 34.6 | 32.6 | 33 | 33.1667 | 35 | 28.3 | 30.8 | 30 | 30 | 29.7 | 30 | 979 | United_StatesWashingtonOLYMPIA AIRPORT
United_States | Washington | OMAK | OMAK, WA, USA | 48.42N | 119.53W | 382 | -8.00 (NAP) | 98-06 | 727890 | -16 | -16 | -26 | 42.6 | 35.2 | 39.1 | 37.8 | 37 | 37.3667 | 39 | 32.5 | 37.3 | 36.3 | 35 | 35.3667 | 35 | 980 | United_StatesWashingtonOMAK
United_States | Washington | PASCO | PASCO, WA, USA | 46.27N | 119.12W | 123 | -8.00 (NAP) | 83-06 | 727845 | -16.9 | -17 | -34.1 | 47.6 | 37.6 | 41.3 | 38.9 | 39 | 39.2667 | 41 | 34 | 38.1 | 37 | 36 | 36.3667 | 36 | 981 | United_StatesWashingtonPASCO
United_States | Washington | PEARSON FLD | PEARSON FLD, WA, USA | 45.62N | 122.65W | 8 | -8.00 (NAP) | 98-06 | 727918 | -7 | -7 | -14.7 | 42.2 | 34.8 | 37 | 34.1 | 35 | 35.3 | 37 | 31 | 32.5 | 32.2 | 32 | 31.9 | 32 | 982 | United_StatesWashingtonPEARSON FLD
United_States | Washington | PULLMAN/MOSCOW RGNL | PULLMAN/MOSCOW RGNL, WA, USA | 46.75N | 117.12W | 778 | -8.00 (NAP) | 87-06 | 727857 | -18.1 | -18 | -34.4 | 40.7 | 32.7 | 36.2 | 36.2 | 35 | 35.0333 | 36 | 29.3 | 33.7 | 33.7 | 32 | 32.2333 | 32 | 983 | United_StatesWashingtonPULLMAN/MOSCOW RGNL
United_States | Washington | QUILLAYUTE STATE AIRPORT | QUILLAYUTE STATE AIRPORT, WA, USA | 47.93N | 124.56W | 63 | -8.00 (NAP) | 82-06 | 727970 | -7.4 | -7 | -14.2 | 38 | 29.8 | 29.1 | 29.1 | 29 | 29.3333 | 29 | 23.9 | 25.4 | 25.1 | 25 | 24.8 | 25 | 984 | United_StatesWashingtonQUILLAYUTE STATE AIRPORT
United_States | Washington | SEATTLE BOEING FIELD | SEATTLE BOEING FIELD, WA, USA | 47.53N | 122.30W | 9 | -8.00 (NAP) | 82-06 | 727935 | -7.3 | -7 | -16.6 | 38.4 | 31.3 | 33.2 | 31.9 | 32 | 32.1333 | 33 | 27.7 | 30.4 | 29.1 | 29 | 29.0667 | 29 | 985 | United_StatesWashingtonSEATTLE BOEING FIELD
United_States | Washington | SEATTLE SEATTLE-TACOMA INTL A | SEATTLE SEATTLE-TACOMA INTL A, WA, USA | 47.46N | 122.31W | 132 | -8.00 (NAP) | 82-06 | 727930 | -6.3 | -6 | -15.2 | 38.8 | 31.3 | 33.1 | 31.1 | 32 | 31.8333 | 33 | 27.4 | 29.6 | 28.5 | 29 | 28.5 | 29 | 986 | United_StatesWashingtonSEATTLE SEATTLE-TACOMA INTL A
United_States | Washington | SHELTON/SANDERSON | SHELTON/SANDERSON, WA, USA | 47.24N | 123.15W | 82 | -8.00 (NAP) | 98-06 | 727925 | -7.1 | -7 | -14.5 | 41.2 | 32.4 | 35.3 | 32.4 | 33 | 33.3667 | 35 | 28.7 | 30.5 | 29.9 | 30 | 29.7 | 30 | 987 | United_StatesWashingtonSHELTON/SANDERSON
United_States | Washington | SMITH ISLAND | SMITH ISLAND, WA, USA | 48.32N | 122.83W | 18 | -8.00 (NAP) | 85-06 | 994180 | -2.9 | -3 | -12.1 | 26.7 | 20.3 | 21.7 | 20.8 | 21 | 20.9333 | 22 | 17.5 | 19 | 18.7 | 18 | 18.4 | 18 | 988 | United_StatesWashingtonSMITH ISLAND
United_States | Washington | SNOHOMISH CO | SNOHOMISH CO, WA, USA | 47.90N | 122.28W | 189 | -8.00 (NAP) | 98-06 | 727937 | -4.9 | -5 | -11.9 | 34.6 | 27.4 | 30.2 | 27.5 | 28 | 28.3667 | 30 | 24.9 | 27 | 25.2 | 26 | 25.7 | 26 | 989 | United_StatesWashingtonSNOHOMISH CO
United_States | Washington | SPOKANE INTERNATIONAL AP | SPOKANE INTERNATIONAL AP, WA, USA | 47.62N | 117.53W | 721 | -8.00 (NAP) | 82-06 | 727850 | -20.1 | -20 | -33.1 | 40.3 | 33 | 36.5 | 35.5 | 35 | 35 | 37 | 30 | 34.1 | 33.6 | 33 | 32.5667 | 33 | 990 | United_StatesWashingtonSPOKANE INTERNATIONAL AP
United_States | Washington | STAMPEDE PASS | STAMPEDE PASS, WA, USA | 47.29N | 121.34W | 1209 | -8.00 (NAP) | 82-06 | 727815 | -15.1 | -15 | -25.5 | 36.4 | 26.6 | 29 | 28.3 | 28 | 27.9667 | 29 | 23 | 26 | 25.8 | 25 | 24.9333 | 25 | 991 | United_StatesWashingtonSTAMPEDE PASS
United_States | Washington | TACOMA NARROWS | TACOMA NARROWS, WA, USA | 47.27N | 122.57W | 91 | -8.00 (NAP) | 93-06 | 727938 | -3.5 | -4 | -9.2 | 40.6 | 31.3 | 32.9 | 29.1 | 31 | 31.1 | 33 | 27.7 | 29 | 27.4 | 28 | 28.0333 | 28 | 992 | United_StatesWashingtonTACOMA NARROWS
United_States | Washington | TATOOSH ISLAND | TATOOSH ISLAND, WA, USA | 48.38N | 124.73W | 48 | -8.00 (NAP) | 85-06 | 994300 | -1.6 | -2 | -7.6 | 26.4 | 19.6 | 19 | 18.9 | 19 | 19.1667 | 19 | 16 | 16.8 | 17 | 17 | 16.6 | 17 | 993 | United_StatesWashingtonTATOOSH ISLAND
United_States | Washington | WALLA WALLA CITY COUNTY AP | WALLA WALLA CITY COUNTY AP, WA, USA | 46.10N | 118.29W | 367 | -8.00 (NAP) | 82-06 | 727846 | -14.3 | -14 | -32.3 | 45.3 | 36.7 | 40.6 | 38.8 | 39 | 38.7 | 41 | 33.1 | 37.7 | 36.5 | 36 | 35.7667 | 36 | 994 | United_StatesWashingtonWALLA WALLA CITY COUNTY AP
United_States | Washington | WENATCHEE/PANGBORN | WENATCHEE/PANGBORN, WA, USA | 47.40N | 120.21W | 375 | -8.00 (NAP) | 82-06 | 727825 | -16.2 | -16 | -28.7 | 41.9 | 35.8 | 37.8 | 36.5 | 37 | 36.7 | 38 | 32.2 | 35.8 | 34.6 | 34 | 34.2 | 34 | 995 | United_StatesWashingtonWENATCHEE/PANGBORN
United_States | Washington | WEST POINT (LS) | WEST POINT (LS), WA, USA | 47.67N | 122.43W | 9 | -8.00 (NAP) | 85-06 | 994350 | -2.8 | -3 | -11.5 | 27.7 | 22.1 | 23.7 | 22.9 | 23 | 22.9 | 24 | 19.9 | 21.5 | 21 | 21 | 20.8 | 21 | 996 | United_StatesWashingtonWEST POINT (LS)
United_States | Washington | WHIDBEY ISLAND NAS | WHIDBEY ISLAND NAS, WA, USA | 48.35N | 122.65W | 14 | -8.00 (NAP) | 82-06 | 690230 | -8.5 | -9 | -17.1 | 31 | 23.6 | 24.6 | 24 | 24 | 24.0667 | 25 | 20.6 | 22.2 | 22.1 | 22 | 21.6333 | 22 | 997 | United_StatesWashingtonWHIDBEY ISLAND NAS
United_States | Washington | WILLIAM R FAIRCHILD | WILLIAM R FAIRCHILD, WA, USA | 48.12N | 123.50W | 91 | -8.00 (NAP) | 85-06 | 727885 | -5.9 | -6 | -12.4 | 37.9 | 28.2 | 29.9 | 28.9 | 29 | 29 | 30 | 23.7 | 26.3 | 25.6 | 25 | 25.2 | 25 | 998 | United_StatesWashingtonWILLIAM R FAIRCHILD
United_States | Washington | YAKIMA AIR TERMINAL | YAKIMA AIR TERMINAL, WA, USA | 46.56N | 120.53W | 325 | -8.00 (NAP) | 82-06 | 727810 | -18 | -18 | -31.6 | 42.3 | 35.8 | 38 | 36.6 | 37 | 36.8 | 38 | 32.6 | 35.9 | 34.7 | 34 | 34.4 | 34 | 999 | United_StatesWashingtonYAKIMA AIR TERMINAL
United_States | West_Virginia | BECKLEY RALEIGH CO MEM AP | BECKLEY RALEIGH CO MEM AP, WV, USA | 37.80N | 81.13W | 766 | -5.00 (NAE) | 82-06 | 724120 | -19.7 | -20 | -31.3 | 35.4 | 29.4 | 31.2 | 30.9 | 31 | 30.5 | 31 | 27.9 | 29.3 | 29 | 29 | 28.7333 | 29 | 1000 | United_StatesWest_VirginiaBECKLEY RALEIGH CO MEM AP
United_States | West_Virginia | BLUEFIELD/MERCER CO | BLUEFIELD/MERCER CO, WV, USA | 37.30N | 81.21W | 874 | -5.00 (NAE) | 82-06 | 724125 | -19.4 | -19 | -31.7 | 35.9 | 29.2 | 31.1 | 31.4 | 31 | 30.5667 | 31 | 27.6 | 29.1 | 29.1 | 29 | 28.6 | 29 | 1001 | United_StatesWest_VirginiaBLUEFIELD/MERCER CO
United_States | West_Virginia | CHARLESTON YEAGER ARPT | CHARLESTON YEAGER ARPT, WV, USA | 38.38N | 81.59W | 299 | -5.00 (NAE) | 82-06 | 724140 | -18 | -18 | -29.9 | 39.4 | 33 | 35 | 34.6 | 34 | 34.2 | 35 | 31.6 | 33 | 32.8 | 32 | 32.4667 | 32 | 1002 | United_StatesWest_VirginiaCHARLESTON YEAGER ARPT
United_States | West_Virginia | ELKINS ELKINS-RANDOLPH CO ARP | ELKINS ELKINS-RANDOLPH CO ARP, WV, USA | 38.89N | 79.85W | 603 | -5.00 (NAE) | 82-06 | 724170 | -24.2 | -24 | -34 | 37.3 | 30.5 | 32.3 | 32 | 32 | 31.6 | 32 | 29 | 30.4 | 30.3 | 30 | 29.9 | 30 | 1003 | United_StatesWest_VirginiaELKINS ELKINS-RANDOLPH CO ARP
United_States | West_Virginia | HARRISON MARION RGN | HARRISON MARION RGN, WV, USA | 39.28N | 80.22W | 380 | -5.00 (NAE) | 98-06 | 724175 | -17.2 | -17 | -23.7 | 38 | 32.6 | 32.8 | 32.9 | 33 | 32.7667 | 33 | 31.1 | 31.4 | 32 | 32 | 31.5 | 32 | 1004 | United_StatesWest_VirginiaHARRISON MARION RGN
United_States | West_Virginia | HUNTINGTON TRI-STATE ARPT | HUNTINGTON TRI-STATE ARPT, WV, USA | 38.38N | 82.56W | 255 | -5.00 (NAE) | 82-06 | 724250 | -18 | -18 | -31 | 40.1 | 33.7 | 35.4 | 35.1 | 35 | 34.7333 | 35 | 31.8 | 33.3 | 33.1 | 33 | 32.7333 | 33 | 1005 | United_StatesWest_VirginiaHUNTINGTON TRI-STATE ARPT
United_States | West_Virginia | MARTINSBURG EASTERN WV REG AP | MARTINSBURG EASTERN WV REG AP, WV, USA | 39.40N | 77.98W | 163 | -5.00 (NAE) | 82-06 | 724177 | -17.9 | -18 | -29.2 | 41.8 | 34.9 | 37 | 35.5 | 36 | 35.8 | 37 | 32.6 | 34.6 | 33 | 33 | 33.4 | 33 | 1006 | United_StatesWest_VirginiaMARTINSBURG EASTERN WV REG AP
United_States | West_Virginia | MORGANTOWN HART FIELD | MORGANTOWN HART FIELD, WV, USA | 39.64N | 79.92W | 382 | -5.00 (NAE) | 82-06 | 724176 | -18.5 | -19 | -29.7 | 38.2 | 32.2 | 33.8 | 33.7 | 33 | 33.2333 | 34 | 30.4 | 32.1 | 31.7 | 31 | 31.4 | 31 | 1007 | United_StatesWest_VirginiaMORGANTOWN HART FIELD
United_States | West_Virginia | PARKERSBURG WOOD COUNTY AP | PARKERSBURG WOOD COUNTY AP, WV, USA | 39.35N | 81.44W | 263 | -5.00 (NAE) | 82-06 | 724273 | -19.3 | -19 | -31.6 | 39.3 | 33.2 | 34.7 | 34.1 | 34 | 34 | 35 | 31.2 | 32.7 | 32.5 | 32 | 32.1333 | 32 | 1008 | United_StatesWest_VirginiaPARKERSBURG WOOD COUNTY AP
United_States | Wisconsin | ANTIGO\LANG(AWOS) | ANTIGO\LANG(AWOS), WI, USA | 45.15N | 87.15W | 464 | -6.00 (NAC) | 97-06 | 726626 | N/A | N/A | N/A | N/A | 29.1 | 32.6 | 31.2 | 31 | 30.9667 | 33 | 27.7 | 30.8 | 28 | 29 | 28.8333 | 29 | 1009 | United_StatesWisconsinANTIGO\LANG(AWOS)
United_States | Wisconsin | APPLETON/OUTAGAMIE | APPLETON/OUTAGAMIE, WI, USA | 44.25N | 88.52W | 280 | -6.00 (NAC) | 92-06 | 726457 | -23.9 | -24 | -31.4 | 41.1 | 32.6 | 34.8 | 32.4 | 33 | 33.2667 | 35 | 30.2 | 32.3 | 29.9 | 31 | 30.8 | 31 | 1010 | United_StatesWisconsinAPPLETON/OUTAGAMIE
United_States | Wisconsin | DEVILS ISLAND | DEVILS ISLAND, WI, USA | 47.08N | 90.73W | 211 | -6.00 (NAC) | 85-06 | 994190 | -23.7 | -24 | -34.3 | 36 | 26.2 | 29.9 | 28.7 | 28 | 28.2667 | 30 | 23.1 | 26.3 | 25.7 | 25 | 25.0333 | 25 | 1011 | United_StatesWisconsinDEVILS ISLAND
United_States | Wisconsin | EAGLE RIVER UNION | EAGLE RIVER UNION, WI, USA | 45.93N | 89.27W | 500 | -6.00 (NAC) | 97-06 | 726504 | -31.4 | -31 | -36 | 37.1 | 31.1 | 32.2 | 30.3 | 31 | 31.2 | 32 | 27.9 | 29.1 | 27.7 | 28 | 28.2333 | 28 | 1012 | United_StatesWisconsinEAGLE RIVER UNION
United_States | Wisconsin | EAU CLAIRE COUNTY AP | EAU CLAIRE COUNTY AP, WI, USA | 44.87N | 91.49W | 273 | -6.00 (NAC) | 82-06 | 726435 | -29.5 | -30 | -40.4 | 40.8 | 34.2 | 36 | 33.9 | 35 | 34.7 | 36 | 31.4 | 33 | 31.1 | 32 | 31.8333 | 32 | 1013 | United_StatesWisconsinEAU CLAIRE COUNTY AP
United_States | Wisconsin | FOND DU LAC CO. | FOND DU LAC CO., WI, USA | 43.77N | 88.49W | 246 | -6.00 (NAC) | 97-06 | 726506 | -23.9 | -24 | -31.9 | 37.5 | 32.4 | 33.8 | 32.5 | 33 | 32.9 | 34 | 30.1 | 32.2 | 30 | 31 | 30.7667 | 31 | 1014 | United_StatesWisconsinFOND DU LAC CO.
United_States | Wisconsin | GREEN BAY AUSTIN STRAUBEL INT | GREEN BAY AUSTIN STRAUBEL INT, WI, USA | 44.51N | 88.12W | 214 | -6.00 (NAC) | 82-06 | 726450 | -27 | -27 | -36.5 | 39.3 | 33.4 | 34.2 | 32.7 | 33 | 33.4333 | 34 | 30.7 | 31.5 | 29.9 | 31 | 30.7 | 31 | 1015 | United_StatesWisconsinGREEN BAY AUSTIN STRAUBEL INT
United_States | Wisconsin | HAYWARD MUNI ARPT | HAYWARD MUNI ARPT, WI, USA | 46.03N | 91.45W | 370 | -6.00 (NAC) | 97-06 | 726508 | -32.1 | -32 | -38 | 42.5 | 32.1 | 36.2 | 32.4 | 34 | 33.5667 | 36 | 28.9 | 32.5 | 29.2 | 30 | 30.2 | 30 | 1016 | United_StatesWisconsinHAYWARD MUNI ARPT
United_States | Wisconsin | JUNEAU\DODGE CO | JUNEAU\DODGE CO, WI, USA | 43.43N | 88.70W | 285 | -6.00 (NAC) | 97-06 | 726509 | -23 | -23 | -27.8 | 37.5 | 32.4 | 32.9 | 32.3 | 33 | 32.5333 | 33 | 30.1 | 31.3 | 29.1 | 30 | 30.1667 | 30 | 1017 | United_StatesWisconsinJUNEAU\DODGE CO
United_States | Wisconsin | KENOSHA RGNL | KENOSHA RGNL, WI, USA | 42.58N | 87.92W | 232 | -6.00 (NAC) | 97-06 | 726505 | -23 | -23 | -30.3 | 41.8 | 32.9 | 35.9 | 33.9 | 34 | 34.2333 | 36 | 31.2 | 32.6 | 31.4 | 32 | 31.7333 | 32 | 1018 | United_StatesWisconsinKENOSHA RGNL
United_States | Wisconsin | LA CROSSE MUNICIPAL ARPT | LA CROSSE MUNICIPAL ARPT, WI, USA | 43.75N | 91.26W | 200 | -6.00 (NAC) | 82-06 | 726430 | -27.1 | -27 | -38.7 | 42.5 | 35 | 36.3 | 35.2 | 36 | 35.5 | 36 | 32.4 | 33.6 | 32.3 | 33 | 32.7667 | 33 | 1019 | United_StatesWisconsinLA CROSSE MUNICIPAL ARPT
United_States | Wisconsin | MADISON DANE CO REGIONAL ARPT | MADISON DANE CO REGIONAL ARPT, WI, USA | 43.14N | 89.35W | 264 | -6.00 (NAC) | 82-06 | 726410 | -26.3 | -26 | -36.7 | 39.2 | 33.5 | 34.3 | 33.9 | 34 | 33.9 | 34 | 31.3 | 32.2 | 31.2 | 32 | 31.5667 | 32 | 1020 | United_StatesWisconsinMADISON DANE CO REGIONAL ARPT
United_States | Wisconsin | MANITOWAC MUNI AWOS | MANITOWAC MUNI AWOS, WI, USA | 44.13N | 87.68W | 198 | -6.00 (NAC) | 92-06 | 726455 | -23.4 | -23 | -33.4 | 40.8 | 31.3 | 32.8 | 31.3 | 32 | 31.8 | 33 | 28 | 30 | 27.9 | 29 | 28.6333 | 29 | 1021 | United_StatesWisconsinMANITOWAC MUNI AWOS
United_States | Wisconsin | MARSHFIELD MUNI | MARSHFIELD MUNI, WI, USA | 44.63N | 90.18W | 389 | -6.00 (NAC) | 92-06 | 726574 | -27.4 | -27 | -36.4 | 41.1 | 33.4 | 34.8 | 32.2 | 33 | 33.4667 | 35 | 29.8 | 31.3 | 30.1 | 30 | 30.4 | 30 | 1022 | United_StatesWisconsinMARSHFIELD MUNI
United_States | Wisconsin | MILWAUKEE MITCHELL INTL AP | MILWAUKEE MITCHELL INTL AP, WI, USA | 42.95N | 87.90W | 211 | -6.00 (NAC) | 82-06 | 726400 | -23.5 | -24 | -34.9 | 40.6 | 34.1 | 34.9 | 34.3 | 34 | 34.4333 | 35 | 31.4 | 32.5 | 31.3 | 32 | 31.7333 | 32 | 1023 | United_StatesWisconsinMILWAUKEE MITCHELL INTL AP
United_States | Wisconsin | MOSINEE/CENTRAL WI | MOSINEE/CENTRAL WI, WI, USA | 44.78N | 89.67W | 389 | -6.00 (NAC) | 82-06 | 726465 | -28.3 | -28 | -37.3 | 39.1 | 31.4 | 33.8 | 31.3 | 32 | 32.1667 | 34 | 29.3 | 31.3 | 28.9 | 30 | 29.8333 | 30 | 1024 | United_StatesWisconsinMOSINEE/CENTRAL WI
United_States | Wisconsin | PARK FALLS MUNI | PARK FALLS MUNI, WI, USA | 45.93N | 90.45W | 469 | -6.00 (NAC) | 82-96 | 727410 | N/A | N/A | N/A | N/A | 30.8 | 31 | 30.4 | 31 | 30.7333 | 31 | 28.7 | 28.7 | 28.4 | 29 | 28.6 | 29 | 1025 | United_StatesWisconsinPARK FALLS MUNI
United_States | Wisconsin | PHILLIPS/PRICE CO. | PHILLIPS/PRICE CO., WI, USA | 45.70N | 90.40W | 449 | -6.00 (NAC) | 92-06 | 726468 | -31.8 | -32 | -40.1 | 37.3 | 31.3 | 32.8 | 31.2 | 32 | 31.7667 | 33 | 28.6 | 30.1 | 28.2 | 29 | 28.9667 | 29 | 1026 | United_StatesWisconsinPHILLIPS/PRICE CO.
United_States | Wisconsin | RHINELANDER ONEIDA | RHINELANDER ONEIDA, WI, USA | 45.63N | 89.47W | 507 | -6.00 (NAC) | 89-06 | 727415 | -30.3 | -30 | -34.8 | 38.5 | 31 | 33.2 | 32 | 32 | 32.0667 | 33 | 28 | 31.2 | 28.1 | 29 | 29.1 | 29 | 1027 | United_StatesWisconsinRHINELANDER ONEIDA
United_States | Wisconsin | RICE LAKE MUNICIPAL | RICE LAKE MUNICIPAL, WI, USA | 45.48N | 91.72W | 347 | -6.00 (NAC) | 97-06 | 726467 | -29.1 | -29 | -37.7 | 39.4 | 32.1 | 33.8 | 33 | 33 | 32.9667 | 34 | 28.9 | 32.2 | 29.8 | 30 | 30.3 | 30 | 1028 | United_StatesWisconsinRICE LAKE MUNICIPAL
United_States | Wisconsin | SHEBOYGAN | SHEBOYGAN, WI, USA | 43.75N | 87.68W | 189 | -6.00 (NAC) | 85-06 | 994330 | -22 | -22 | -30.1 | 37.1 | 29.8 | 31.7 | 30.8 | 31 | 30.7667 | 32 | 26.3 | 28.5 | 27.8 | 28 | 27.5333 | 28 | 1029 | United_StatesWisconsinSHEBOYGAN
United_States | Wisconsin | SHEBOYGAN | SHEBOYGAN, WI, USA | 43.78N | 87.85W | 228 | -6.00 (NAC) | 82-06 | 726425 | N/A | N/A | N/A | N/A | 32.2 | 33.6 | 32.9 | 33 | 32.9 | 34 | 29 | 32 | 29.6 | 30 | 30.2 | 30 | 1030 | United_StatesWisconsinSHEBOYGAN
United_States | Wisconsin | STURGEON BAY | STURGEON BAY, WI, USA | 44.85N | 87.42W | 221 | -6.00 (NAC) | 92-06 | 726458 | -23.8 | -24 | -34.5 | 38.7 | 30.7 | 32.4 | 31 | 31 | 31.3667 | 32 | 27.8 | 29.9 | 27.7 | 28 | 28.4667 | 28 | 1031 | United_StatesWisconsinSTURGEON BAY
United_States | Wisconsin | WATERTOWN | WATERTOWN, WI, USA | 43.17N | 88.72W | 254 | -6.00 (NAC) | 95-06 | 726464 | -24.6 | -25 | -32.7 | 38.2 | 32.7 | 33.7 | 32.8 | 33 | 33.0667 | 34 | 31.1 | 32.2 | 31 | 31 | 31.4333 | 31 | 1032 | United_StatesWisconsinWATERTOWN
United_States | Wisconsin | WAUSAU MUNICIPAL ARPT | WAUSAU MUNICIPAL ARPT, WI, USA | 44.93N | 89.63W | 365 | -6.00 (NAC) | 82-06 | 726463 | -29.3 | -29 | -37.9 | 39.1 | 32.8 | 34.1 | 32.5 | 33 | 33.1333 | 34 | 30.2 | 31.5 | 29.9 | 31 | 30.5333 | 31 | 1033 | United_StatesWisconsinWAUSAU MUNICIPAL ARPT
United_States | Wisconsin | WISCONSIN RAPIDS | WISCONSIN RAPIDS, WI, USA | 44.35N | 89.83W | 308 | -6.00 (NAC) | 97-06 | 726452 | -27.2 | -27 | -34.5 | 39.9 | 32.2 | 34 | 32.9 | 33 | 33.0333 | 34 | 29.8 | 32.3 | 30.7 | 31 | 30.9333 | 31 | 1034 | United_StatesWisconsinWISCONSIN RAPIDS
United_States | Wisconsin | WITTMAN RGNL | WITTMAN RGNL, WI, USA | 43.98N | 88.55W | 253 | -6.00 (NAC) | 96-06 | 726456 | -24.2 | -24 | -31.4 | 38.7 | 32.2 | 33.9 | 32.5 | 33 | 32.8667 | 34 | 30 | 32.2 | 29.8 | 31 | 30.6667 | 31 | 1035 | United_StatesWisconsinWITTMAN RGNL
United_States | Wyoming | BIG PINEY (AMOS) | BIG PINEY (AMOS), WY, USA | 42.58N | 110.11W | 2126 | -7.00 (NAM) | 82-06 | 726710 | -33.4 | -33 | -48.4 | 35.9 | 29.6 | 32.4 | 31.1 | 31 | 31.0333 | 32 | 27.4 | 30.5 | 28.4 | 29 | 28.7667 | 29 | 1036 | United_StatesWyoming BIG PINEY (AMOS)
United_States | Wyoming | CASPER NATRONA CO INTL AP | CASPER NATRONA CO INTL AP, WY, USA | 42.90N | 106.47W | 1612 | -7.00 (NAM) | 82-06 | 725690 | -28.8 | -29 | -41.5 | 39.8 | 35.1 | 37.1 | 35.3 | 36 | 35.8333 | 37 | 32.7 | 35 | 33.4 | 34 | 33.7 | 34 | 1037 | United_StatesWyoming CASPER NATRONA CO INTL AP
United_States | Wyoming | CHEYENNE MUNICIPAL ARPT | CHEYENNE MUNICIPAL ARPT, WY, USA | 41.16N | 104.81W | 1872 | -7.00 (NAM) | 82-06 | 725640 | -26 | -26 | -38.3 | 37.8 | 32.6 | 34.4 | 32.5 | 33 | 33.1667 | 34 | 29.8 | 32.5 | 30.7 | 31 | 31 | 31 | 1038 | United_StatesWyoming CHEYENNE MUNICIPAL ARPT
United_States | Wyoming | CODY MUNI (AWOS) | CODY MUNI (AWOS), WY, USA | 44.52N | 109.02W | 1553 | -7.00 (NAM) | 82-06 | 726700 | -27.9 | -28 | -38.5 | 39.6 | 33.7 | 35.6 | 33.7 | 34 | 34.3333 | 36 | 30.6 | 33 | 32 | 32 | 31.8667 | 32 | 1039 | United_StatesWyoming CODY MUNI (AWOS)
United_States | Wyoming | GILLETTE/GILLETTE-C | GILLETTE/GILLETTE-C, WY, USA | 44.35N | 105.53W | 1230 | -7.00 (NAM) | 82-06 | 726650 | -27.5 | -28 | -39.2 | 42.6 | 36.1 | 38.2 | 36.6 | 37 | 36.9667 | 38 | 32.9 | 36 | 34.1 | 34 | 34.3333 | 34 | 1040 | United_StatesWyoming GILLETTE/GILLETTE-C
United_States | Wyoming | JACKSON HOLE | JACKSON HOLE, WY, USA | 43.60N | 110.73W | 2016 | -7.00 (NAM) | 92-06 | 725776 | -30.9 | -31 | -37.8 | 36.2 | 27.5 | 32.3 | 30.9 | 30 | 30.2333 | 32 | 25.5 | 30.2 | 28.4 | 28 | 28.0333 | 28 | 1041 | United_StatesWyoming JACKSON HOLE
United_States | Wyoming | LANDER HUNT FIELD | LANDER HUNT FIELD, WY, USA | 42.82N | 108.73W | 1694 | -7.00 (NAM) | 82-06 | 725760 | -27.2 | -27 | -39.1 | 39.3 | 34 | 36 | 34.1 | 35 | 34.7 | 36 | 31.3 | 34 | 32.4 | 33 | 32.5667 | 33 | 1042 | United_StatesWyoming LANDER HUNT FIELD
United_States | Wyoming | LARAMIE GENERAL BREES FIELD | LARAMIE GENERAL BREES FIELD, WY, USA | 41.31N | 105.67W | 2217 | -7.00 (NAM) | 82-06 | 725645 | -30.5 | -31 | -38.7 | 35.6 | 30.6 | 32 | 29.8 | 31 | 30.8 | 32 | 28 | 30.2 | 28 | 29 | 28.7333 | 29 | 1043 | United_StatesWyoming LARAMIE GENERAL BREES FIELD
United_States | Wyoming | ROCK SPRINGS ARPT | ROCK SPRINGS ARPT, WY, USA | 41.59N | 109.07W | 2056 | -7.00 (NAM) | 82-06 | 725744 | -25.5 | -26 | -35.8 | 37.5 | 31.8 | 33.7 | 31.8 | 32 | 32.4333 | 34 | 29 | 32 | 29.9 | 30 | 30.3 | 30 | 1044 | United_StatesWyoming ROCK SPRINGS ARPT
United_States | Wyoming | SHERIDAN COUNTY ARPT | SHERIDAN COUNTY ARPT, WY, USA | 44.77N | 106.98W | 1209 | -7.00 (NAM) | 82-06 | 726660 | -29 | -29 | -39.9 | 42.9 | 35.8 | 38 | 37 | 37 | 36.9333 | 38 | 32.1 | 35.8 | 35 | 34 | 34.3 | 34 | 1045 | United_StatesWyoming SHERIDAN COUNTY ARPT
United_States | Wyoming | WORLAND MUNICIPAL | WORLAND MUNICIPAL, WY, USA | 43.97N | 107.95W | 1283 | -7.00 (NAM) | 82-06 | 726665 | -33.9 | -34 | -49.3 | 43.3 | 37.4 | 38.6 | 36.7 | 38 | 37.5667 | 39 | 34.5 | 36.2 | 34.6 | 35 | 35.1 | 35 | 1046 | United_StatesWyoming WORLAND MUNICIPAL
United_States | Wyoming | YELLOWSTONE LAKE (RAMOS) | YELLOWSTONE LAKE (RAMOS), WY, USA | 44.54N | 110.42W | 2388 | -7.00 (NAM) | 83-06 | 726664 | -33.3 | -33 | -40.9 | 32.9 | 24.8 | 27.4 | 25.8 | 26 | 26 | 27 | 22.3 | 25.4 | 23.6 | 24 | 23.7667 | 24 | 1047 | United_StatesWyoming YELLOWSTONE LAKE (RAMOS)
Uruguay |  | ARTIGAS | ARTIGAS, Uruguay | 30.38S | 56.50W | 120 | -3.00 (SAU) | 85-06 | 863300 | -1.9 |  | -5.3 | 41.1 | 26.3 | 26.8 | 30.2 | 28 | 27.7667 |  | 24.2 | 24.9 | 27.7 | 26 | 25.6
Uruguay |  | CARRASCO | CARRASCO, Uruguay | 34.83S | 56.00W | 32 | -3.00 (SAU) | 82-06 | 865800 | -0.8 |  | -4.8 | 39.9 | 23.2 | 23.9 | 26.1 | 24 | 24.4 |  | 20 | 20.1 | 22.2 | 21 | 20.7667
Uruguay |  | COLONIA | COLONIA, Uruguay | 34.45S | 57.83W | 22 | -3.00 (SAU) | 82-02 | 865600 | 1.2 |  | -2.3 | 39.4 | 23.1 | 23.9 | 27.1 | 25 | 24.7 |  | 20.2 | 19.9 | 23.3 | 21 | 21.1333
Uruguay |  | PASO DE LOS TOROS | PASO DE LOS TOROS, Uruguay | 32.80S | 56.52W | 75 | -3.00 (SAU) | 82-06 | 864600 | -1 |  | -3.9 | 41.7 | 25.2 | 25.9 | 28.9 | 27 | 26.6667 |  | 21.9 | 22.3 | 24.8 | 23 | 23
Uruguay |  | PRADO | PRADO, Uruguay | 34.85S | 56.20W | 16 | -3.00 (SAU) | 82-03 | 865850 | N/A |  | N/A | N/A | 22.2 | 24.7 | 27.1 | 25 | 24.6667 |  | 19.5 | 20.7 | 22.3 | 21 | 20.8333
Uruguay |  | RIVERA | RIVERA, Uruguay | 30.88S | 55.53W | 242 | -3.00 (SAU) | 82-06 | 863500 | 0.1 |  | -2.5 | 40.1 | 25.7 | 27 | 30 | 28 | 27.5667 |  | 23.6 | 24.6 | 27.2 | 25 | 25.1333
Uruguay |  | ROCHA | ROCHA, Uruguay | 34.48S | 54.30W | 18 | -3.00 (SAU) | 82-06 | 865650 | -1.7 |  | -4.2 | 39.5 | 23 | 24.8 | 25.9 | 25 | 24.5667 |  | 20.3 | 20.7 | 22 | 21 | 21
Uruguay |  | SALTO | SALTO, Uruguay | 31.38S | 57.95W | 33 | -3.00 (SAU) | 82-06 | 863600 | -1.3 |  | -4.3 | 42.8 | 25.7 | 26.9 | 30.2 | 28 | 27.6 |  | 23.5 | 24 | 27 | 25 | 24.8333
Uruguay |  | TREINTA Y TRES | TREINTA Y TRES, Uruguay | 33.22S | 54.38W | 46 | -3.00 (SAU) | 82-03 | 865000 | -2 |  | -4.2 | 41.3 | 24.1 | 26.3 | 28.4 | 26 | 26.2667 |  | 21.3 | 21.7 | 24.2 | 22 | 22.4
Uzbekistan |  | AK-BAJTAL | AK-BAJTAL, Uzbekistan | 43.15N | 64.33E | 234 | 5.00 (ASW) | 82-06 | 381780 | -21.6 |  | -32 | 47.8 | 41 | 42.2 | 40.7 | 41 | 41.3 |  | 38.9 | 39.8 | 38.6 | 39 | 39.1
Uzbekistan |  | BUHARA | BUHARA, Uzbekistan | 39.72N | 64.62E | 226 | 5.00 (ASW) | 85-06 | 386830 | -11.5 |  | -21 | 48.5 | 41 | 41.8 | 40.2 | 41 | 41 |  | 39 | 39.6 | 38.5 | 39 | 39.0333
Uzbekistan |  | BUZAUBAJ | BUZAUBAJ, Uzbekistan | 41.75N | 62.47E | 98 | 5.00 (ASW) | 82-06 | 384030 | -19.6 |  | -31 | 48.6 | 42.7 | 44 | 42.4 | 43 | 43.0333 |  | 40.6 | 41.5 | 40.5 | 41 | 40.8667
Uzbekistan |  | CHIMBAJ | CHIMBAJ, Uzbekistan | 42.95N | 59.82E | 66 | 5.00 (ASW) | 82-06 | 382620 | -20.2 |  | -30.1 | 46.2 | 39.9 | 39.7 | 39.4 | 40 | 39.6667 |  | 37.4 | 37.7 | 37 | 37 | 37.3667
Uzbekistan |  | DARGANATA | DARGANATA, Uzbekistan | 40.47N | 62.28E | 142 | 5.00 (ASW) | 82-06 | 385450 | -14.7 |  | -23.6 | 45.5 | 40.3 | 41.1 | 39.5 | 40 | 40.3 |  | 38.2 | 38.7 | 37.4 | 38 | 38.1
Uzbekistan |  | DZIZAK | DZIZAK, Uzbekistan | 40.12N | 67.83E | 345 | 5.00 (ASW) | 85-06 | 385790 | -10.8 |  | -19 | 43.2 | 38.8 | 39.5 | 37.9 | 39 | 38.7333 |  | 36.9 | 37.5 | 36.3 | 37 | 36.9
Uzbekistan |  | FERGANA | FERGANA, Uzbekistan | 40.37N | 71.75E | 577 | 5.00 (ASW) | 82-06 | 386180 | -10.2 |  | -18.7 | 42.1 | 37.6 | 38.4 | 36.9 | 38 | 37.6333 |  | 35.7 | 36.7 | 35.4 | 36 | 35.9333
Uzbekistan |  | KARSHI | KARSHI, Uzbekistan | 38.80N | 65.72E | 376 | 5.00 (ASW) | 84-06 | 388120 | -9.1 |  | -16.8 | 46.9 | 41 | 42.2 | 40.7 | 41 | 41.3 |  | 39.3 | 40.2 | 39.2 | 40 | 39.5667
Uzbekistan |  | KUNGRAD | KUNGRAD, Uzbekistan | 43.08N | 58.93E | 64 | 5.00 (ASW) | 84-06 | 381490 | -20.9 |  | -30.9 | 44.6 | 40.2 | 40 | 40.3 | 40 | 40.1667 |  | 37.9 | 38.1 | 37.7 | 38 | 37.9
Uzbekistan |  | NAMANGAN | NAMANGAN, Uzbekistan | 40.98N | 71.58E | 474 | 5.00 (ASW) | 85-06 | 386110 | -9.6 |  | -18.8 | 42 | 37.9 | 38.5 | 36.5 | 38 | 37.6333 |  | 36.1 | 36.8 | 35.1 | 36 | 36
Uzbekistan |  | NUKUS | NUKUS, Uzbekistan | 42.45N | 59.62E | 77 | 5.00 (ASW) | 85-06 | 382640 | -20.7 |  | -31.4 | 45.2 | 40.5 | 40.6 | 40.6 | 41 | 40.5667 |  | 38.6 | 38.8 | 38.5 | 39 | 38.6333
Uzbekistan |  | NURATA | NURATA, Uzbekistan | 40.55N | 65.68E | 485 | 5.00 (ASW) | 82-06 | 385650 | -15.5 |  | -24.5 | 45.3 | 39.7 | 40.7 | 39.3 | 40 | 39.9 |  | 37.5 | 38.3 | 37.4 | 38 | 37.7333
Uzbekistan |  | PSKEM | PSKEM, Uzbekistan | 41.90N | 70.37E | 1258 | 5.00 (ASW) | 84-06 | 384620 | -16.7 |  | -23.1 | 40 | 32.8 | 34.8 | 34.5 | 34 | 34.0333 |  | 30.1 | 32.5 | 32.4 | 32 | 31.6667
Uzbekistan |  | SAMARKAND | SAMARKAND, Uzbekistan | 39.57N | 66.95E | 724 | 5.00 (ASW) | 82-06 | 386960 | -12.2 |  | -21.6 | 42.1 | 37.6 | 38 | 36.9 | 38 | 37.5 |  | 35.5 | 36.1 | 35.3 | 36 | 35.6333
Uzbekistan |  | SYR-DARJA | SYR-DARJA, Uzbekistan | 40.82N | 68.68E | 264 | 5.00 (ASW) | 83-06 | 385830 | -13.5 |  | -26.3 | 44.2 | 39.5 | 39.7 | 38.4 | 39 | 39.2 |  | 37.3 | 37.8 | 36.6 | 37 | 37.2333
Uzbekistan |  | TAMDY | TAMDY, Uzbekistan | 41.73N | 64.62E | 237 | 5.00 (ASW) | 82-06 | 384130 | -16.6 |  | -27.3 | 47.2 | 41.8 | 43.2 | 41.4 | 42 | 42.1333 |  | 39.7 | 40.7 | 39.4 | 40 | 39.9333
Uzbekistan |  | TASHKENT | TASHKENT, Uzbekistan | 41.27N | 69.27E | 466 | 5.00 (ASW) | 82-06 | 384570 | -11.6 |  | -19.6 | 44.5 | 39.9 | 40.8 | 39.2 | 40 | 39.9667 |  | 37.7 | 38.8 | 37.7 | 38 | 38.0667
Uzbekistan |  | TERMEZ | TERMEZ, Uzbekistan | 37.23N | 67.27E | 310 | 5.00 (ASW) | 82-06 | 389270 | -8.9 |  | -16.6 | 47 | 42.5 | 43.2 | 41.4 | 42 | 42.3667 |  | 40.4 | 41.4 | 39.8 | 41 | 40.5333
Uzbekistan |  | URGENCH | URGENCH, Uzbekistan | 41.57N | 60.57E | 101 | 5.00 (ASW) | 84-06 | 383960 | -17 |  | -25.9 | 44 | 40.1 | 39.9 | 39.3 | 40 | 39.7667 |  | 38.1 | 38 | 37.3 | 38 | 37.8
Vanuatu |  | ANEITYUM | ANEITYUM, Vanuatu | 20.23S | 169.77E | 7 | 11.00 (PCC) | 82-06 | 915680 | N/A |  | N/A | N/A | 27.1 | 26.8 | 27.1 | 27 | 27 |  | 26.1 | 25.6 | 25.6 | 26 | 25.7667
Vanuatu |  | BAUERFIELD (EFATE) | BAUERFIELD (EFATE), Vanuatu | 17.70S | 168.30E | 21 | 11.00 (PCC) | 85-06 | 915570 | 12.2 |  | 8.9 | 33.9 | 28.6 | 28.4 | 28.7 | 29 | 28.5667 |  | 27.6 | 27.2 | 27.2 | 27 | 27.3333
Vanuatu |  | PEKOA AIRPORT (SANTO) | PEKOA AIRPORT (SANTO), Vanuatu | 15.52S | 167.22E | 44 | 11.00 (PCC) | 82-06 | 915540 | 16.4 |  | 12.7 | 36.1 | 28.7 | 28.1 | 28.6 | 28 | 28.4667 |  | 27.9 | 27.3 | 27.6 | 28 | 27.6
Venezuela |  | CARACAS/MAIQUETIA A | CARACAS/MAIQUETIA A, Venezuela | 10.60N | 66.98W | 48 | -4.00 (SAW) | 82-06 | 804150 | 19.4 |  | 16.9 | 41.1 | 33.8 | 33.1 | 34.1 | 34 | 33.6667 |  | 32.2 | 32.1 | 33 | 32 | 32.4333
Venezuela |  | GUANARE | GUANARE, Venezuela | 9.02N | 69.73W | 163 | -4.00 (SAW) | 83-05 | 804280 | N/A |  | N/A | N/A | 32.5 | 32.6 | 33.1 | 33 | 32.7333 |  | 31.8 | 31.8 | 32.1 | 32 | 31.9
Venezuela |  | SAN ANTONIO DEL TAC | SAN ANTONIO DEL TAC, Venezuela | 7.85N | 72.45W | 378 | -4.00 (SAW) | 83-05 | 804470 | N/A |  | N/A | N/A | 34.8 | 34.1 | 35 | 35 | 34.6333 |  | 33.5 | 33.1 | 33.9 | 34 | 33.5
Vietnam |  | BACH LONG VI | BACH LONG VI, Viet Nam | 20.13N | 107.72E | 56 | 7.00 (SEA) | 83-06 | 488390 | 10.7 |  | 9.2 | 42.1 | 33.4 | 33.4 | 33.2 | 33 | 33.3333 |  | 32.1 | 32.6 | 32.3 | 32 | 32.3333
Vietnam |  | CA MAU | CA MAU, Viet Nam | 9.18N | 105.15E | 2 | 7.00 (SEA) | 82-06 | 489140 | 20.2 |  | 16.1 | 38.8 | 33.6 | 33 | 32.7 | 33 | 33.1 |  | 32.7 | 32.4 | 32.1 | 32 | 32.4
Vietnam |  | CAO BANG | CAO BANG, Viet Nam | 22.67N | 106.25E | 243 | 7.00 (SEA) | 92-06 | 488080 | 3.9 |  | -1.2 | 39.7 | 34.7 | 35.1 | 34.9 | 35 | 34.9 |  | 33.4 | 33.8 | 33.7 | 34 | 33.6333
Vietnam |  | CON SON | CON SON, Viet Nam | 8.68N | 106.60E | 9 | 7.00 (SEA) | 85-06 | 489180 | 19.4 |  | 13.9 | 41.6 | 32.2 | 31.7 | 31.3 | 32 | 31.7333 |  | 31.5 | 31 | 30.8 | 31 | 31.1
Vietnam |  | DA NANG | DA NANG, Viet Nam | 16.07N | 108.35E | 7 | 7.00 (SEA) | 85-06 | 488550 | 13.1 |  | 5 | 40.3 | 37.2 | 37 | 36.2 | 37 | 36.8 |  | 36 | 35.7 | 35 | 36 | 35.5667
Vietnam |  | DONG HOI | DONG HOI, Viet Nam | 17.48N | 106.60E | 8 | 7.00 (SEA) | 82-06 | 488480 | 11.4 |  | 6.1 | 40.5 | 37.6 | 37.2 | 36.5 | 37 | 37.1 |  | 36.1 | 35.7 | 35 | 36 | 35.6
Vietnam |  | HA NOI | HA NOI, Viet Nam | 21.03N | 105.80E | 6 | 7.00 (SEA) | 82-06 | 488200 | 8.3 |  | 4.5 | 42.3 | 37.5 | 36.7 | 35.2 | 36 | 36.4667 |  | 35.9 | 35.2 | 34.1 | 35 | 35.0667
Vietnam |  | HUE | HUE, Viet Nam | 16.43N | 107.58E | 9 | 7.00 (SEA) | 92-06 | 488520 | 12.7 |  | 8.3 | 40.3 | 37 | 36.9 | 36.8 | 37 | 36.9 |  | 35.7 | 35.8 | 35.6 | 36 | 35.7
Vietnam |  | LANG SON | LANG SON, Viet Nam | 21.83N | 106.77E | 263 | 7.00 (SEA) | 92-06 | 488300 | 2.6 |  | -1.6 | 37.8 | 34 | 34.5 | 34 | 34 | 34.1667 |  | 32.9 | 33.4 | 33 | 33 | 33.1
Vietnam |  | LAO CAI | LAO CAI, Viet Nam | 22.50N | 103.97E | 97 | 7.00 (SEA) | 93-06 | 488030 | 8.1 |  | 2.5 | 40.8 | 36.9 | 36.2 | 35.6 | 36 | 36.2333 |  | 35.2 | 34.9 | 34.5 | 35 | 34.8667
Vietnam |  | NAM DINH | NAM DINH, Viet Nam | 20.43N | 106.15E | 3 | 7.00 (SEA) | 92-06 | 488230 | 8.3 |  | 4.1 | 38.7 | 36.4 | 36 | 35.2 | 36 | 35.8667 |  | 35.2 | 35 | 33.8 | 35 | 34.6667
Vietnam |  | NHA TRANG | NHA TRANG, Viet Nam | 12.22N | 109.22E | 4 | 7.00 (SEA) | 82-06 | 488770 | 16.8 |  | 9.9 | 41.2 | 34.1 | 33.7 | 34 | 34 | 33.9333 |  | 33.1 | 32.8 | 33 | 33 | 32.9667
Vietnam |  | PHAN THIET | PHAN THIET, Viet Nam | 10.93N | 108.10E | 5 | 7.00 (SEA) | 86-06 | 488870 | 18.1 |  | 13.3 | 39.5 | 34.2 | 33.5 | 33.6 | 34 | 33.7667 |  | 32.9 | 32.1 | 32.3 | 32 | 32.4333
Vietnam |  | PHU LIEN | PHU LIEN, Viet Nam | 20.80N | 106.63E | 116 | 7.00 (SEA) | 82-06 | 488260 | 7.3 |  | -1.1 | 41.4 | 35.2 | 34.7 | 34.4 | 35 | 34.7667 |  | 33.8 | 33.7 | 33.1 | 34 | 33.5333
Vietnam |  | PHU QUOC | PHU QUOC, Viet Nam | 10.22N | 103.97E | 4 | 7.00 (SEA) | 82-06 | 489170 | 18.2 |  | 11.8 | 39.4 | 32 | 31.6 | 31.1 | 32 | 31.5667 |  | 31.1 | 30.6 | 30.2 | 31 | 30.6333
Vietnam |  | QUY NHON | QUY NHON, Viet Nam | 13.77N | 109.22E | 6 | 7.00 (SEA) | 82-06 | 488700 | 16.2 |  | 9.6 | 41.1 | 36.9 | 36.8 | 36.6 | 37 | 36.7667 |  | 35.7 | 35.7 | 35.5 | 36 | 35.6333
Vietnam |  | SON LA | SON LA, Viet Nam | 21.33N | 103.90E | 676 | 7.00 (SEA) | 97-06 | 488060 | 3.9 |  | -1.5 | 36.7 | 32.8 | 32.3 | 32 | 32 | 32.3667 |  | 31.4 | 31 | 30.9 | 31 | 31.1
Vietnam |  | TAN SON HOA | TAN SON HOA, Viet Nam | 10.82N | 106.67E | 5 | 7.00 (SEA) | 82-06 | 489000 | 17.9 |  | 14.4 | 40.2 | 35.1 | 34.1 | 33.9 | 34 | 34.3667 |  | 34 | 33.1 | 33 | 33 | 33.3667
Vietnam |  | THANH HOA | THANH HOA, Viet Nam | 19.75N | 105.78E | 5 | 7.00 (SEA) | 92-06 | 488400 | 9.7 |  | 5.7 | 40.2 | 36.8 | 36.2 | 35.1 | 36 | 36.0333 |  | 35.4 | 34.8 | 33.6 | 35 | 34.6
Vietnam |  | VINH | VINH, Viet Nam | 18.67N | 105.68E | 6 | 7.00 (SEA) | 82-06 | 488450 | 9.4 |  | 5.5 | 40.1 | 37.5 | 37.6 | 36.5 | 37 | 37.2 |  | 36.3 | 36.1 | 34.8 | 36 | 35.7333
Wallis and Futuna |  | HIHIFO (ILE WALLIS) | HIHIFO (ILE WALLIS), Wallis and Futuna | 13.23S | 176.17W | 27 | 12.00 (FJI) | 82-06 | 917530 | 20.4 |  | 16.1 | 36.2 | 30.5 | 30.1 | 30.2 | 30 | 30.2667 |  | 30 | 29.7 | 29.7 | 30 | 29.8
Wallis and Futuna |  | MAOPOOPO (ILE FUTUNA) | MAOPOOPO (ILE FUTUNA), Wallis and Futuna | 14.32S | 178.12W | 36 | 12.00 (FJI) | 82-06 | 917540 | 21.3 |  | 19.5 | 34 | 30.1 | 29.7 | 29.7 | 30 | 29.8333 |  | 29.2 | 28.9 | 29.1 | 29 | 29.0667
Zimbabwe |  | HARARE (KUTSAGA) | HARARE (KUTSAGA), Zimbabwe | 17.92S | 31.13E | 1480 | 2.00 (AFS) | 82-06 | 677750 | 4.2 |  | 0 | 35 | 25.2 | 24.9 | 28.2 | 26 | 26.1 |  | 23.5 | 23.2 | 26.3 | 24 | 24.3333
Zimbabwe |  | MASVINGO | MASVINGO, Zimbabwe | 20.07S | 30.87E | 1095 | 2.00 (AFS) | 82-06 | 679750 | N/A |  | N/A | N/A | 27.6 | 26.9 | 31.4 | 29 | 28.6333 |  | 25.6 | 25.2 | 29.2 | 27 | 26.6667
BCN-Baja California-N
GRO-Guerrero
GUA-Guanajuato
JAL-Jalisco
MEX-México
NLE-Nuevo León
ROO-Quintana Roo
SIN-Sinaloa
SLP-San Luis Potosí
TAM-Tamaulipas
VER-Veracruz
YUC-Yucatán
ZAC-Zacatecas

## ASHRAE Temp. Info (hidden)
Sates | Location | Extreme Min. | High Temp (Deg. C) .4% and 2%avg. |  | Sates
Alabama | ANNISTON METROPOLITAN AP | -11 | 37 | 34 | Alabama
Alabama | AUBURN-OPELIKA APT | -9 | 36 | 33 | Alabama
Alabama | BATESVILLE (AWOS) | -13 | 38 | 35 | Alabama
Alabama | BIRMINGHAM MUNICIPAL AP | -12 | 37 | 34 | Alabama
Alabama | CAIRNS AAF/OZARK | -8 | 37 | 35 | Alabama
Alabama | CENTREVILLE WSMO | -11 | 36 | 34 | Alabama
Alabama | DAUPHIN ISLAND | -2 | 32 | 31 | Alabama
Alabama | DOTHAN MUNICIPAL | -8 | 37 | 35 | Alabama
Alabama | GADSEN MUNI (AWOS) | -12 | 36 | 34 | Alabama
Alabama | HUNTSVILLE INTL/JONES FIELD | -13 | 36 | 34 | Alabama
Alabama | MAXWELL AFB/MONTGOM | -6 | 38 | 36 | Alabama
Alabama | MOBILE REGIONAL AP | -7 | 36 | 34 | Alabama
Alabama | MONTGOMERY DANNELLY FIELD | -9 | 37 | 35 | Alabama
Alabama | MUSCLE SHOALS REGIONAL AP | -12 | 37 | 35 | Alabama
Alabama | TUSCALOOSA MUNICIPAL AP | -11 | 37 | 35 | Alabama
Alaska | ADAK NAS | -11 | 17 | 14 | Alaska
Alaska | AMBLER | N/A | 27 | 24 | Alaska
Alaska | ANAKTUVUK PASS | N/A | 24 | 21 | Alaska
Alaska | ANCHORAGE INTL AP | -26 | 24 | 21 | Alaska
Alaska | ANCHORAGE MERRILL FIELD | -26 | 25 | 22 | Alaska
Alaska | ANCHORAGE/ELMENDORF | -29 | 26 | 23 | Alaska
Alaska | ANNETTE ISLAND AP | -13 | 25 | 22 | Alaska
Alaska | ANVIK | -34 | 24 | 22 | Alaska
Alaska | BARROW W POST-W ROGERS ARPT | -43 | 18 | 13 | Alaska
Alaska | BARTER ISLAND (DEW) | N/A | 16 | 13 | Alaska
Alaska | BETHEL AIRPORT | -35 | 25 | 22 | Alaska
Alaska | BETTLES FIELD | -48 | 29 | 25 | Alaska
Alaska | BIG DELTA ALLEN AAF | -42 | 28 | 25 | Alaska
Alaska | CAPE LISBURNE(AWOS) | N/A | 17 | 14 | Alaska
Alaska | CAPE NEWENHAM AFS | N/A | 18 | 16 | Alaska
Alaska | CAPE ROMANZOFF AWOS | N/A | 20 | 18 | Alaska
Alaska | COLD BAY ARPT | -16 | 17 | 15 | Alaska
Alaska | CORDOVA | -22 | 24 | 21 | Alaska
Alaska | DEADHORSE | -45 | 23 | 18 | Alaska
Alaska | DILLINGHAM MUNI | -33 | 24 | 21 | Alaska
Alaska | DUTCH HARBOR | -10 | 19 | 16 | Alaska
Alaska | FAIRBANKS INTL ARPT | -43 | 30 | 26 | Alaska
Alaska | FAIRBANKS/EIELSON A | -44 | 30 | 26 | Alaska
Alaska | FIVE FINGER ISLAND | -9 | 20 | 18 | Alaska
Alaska | FORT YUKON | -49 | 29 | 26 | Alaska
Alaska | FT. RICHARDSON/BRYA | -31 | 26 | 23 | Alaska
Alaska | GALENA A. | -46 | 28 | 25 | Alaska
Alaska | GULKANA INTERMEDIATE FIELD | -41 | 27 | 25 | Alaska
Alaska | HOMER ARPT | -20 | 21 | 18 | Alaska
Alaska | HOOPER BAY | N/A | 19 | 17 | Alaska
Alaska | ILIAMNA ARPT | -29 | 26 | 21 | Alaska
Alaska | INDIAN MTN AFS AWOS | N/A | 27 | 24 | Alaska
Alaska | JUNEAU INT''L ARPT | -18 | 26 | 23 | Alaska
Alaska | KAKE SEAPLANE BASE | -14 | 22 | 20 | Alaska
Alaska | KENAI MUNICIPAL AP | -33 | 24 | 20 | Alaska
Alaska | KETCHIKAN INTL AP | -14 | 24 | 21 | Alaska
Alaska | KING SALMON ARPT | -34 | 25 | 22 | Alaska
Alaska | KLAWOCK | -12 | 22 | 21 | Alaska
Alaska | KODIAK AIRPORT | -17 | 24 | 20 | Alaska
Alaska | KOTZEBUE RALPH WEIN MEMORIAL | -39 | 23 | 19 | Alaska
Alaska | LAKE HOOD SEAPLANE | -24 | 26 | 23 | Alaska
Alaska | MCGRATH ARPT | -46 | 28 | 25 | Alaska
Alaska | MCKINLEY PARK | N/A | 26 | 23 | Alaska
Alaska | MEKORYUK | -29 | 18 | 15 | Alaska
Alaska | MIDDLETON ISL. AMOS | -9 | 20 | 17 | Alaska
Alaska | MINCHUMINA | N/A | 26 | 24 | Alaska
Alaska | NENANA MUNICIPAL AP | -46 | 30 | 26 | Alaska
Alaska | NOME MUNICIPAL ARPT | -36 | 24 | 20 | Alaska
Alaska | NORTHWAY AIRPORT | -47 | 28 | 25 | Alaska
Alaska | PALMER MUNICIPAL | -28 | 26 | 23 | Alaska
Alaska | PETERSBURG | -16 | 23 | 21 | Alaska
Alaska | POINT HOPE (AWOS) | N/A | 18 | 14 | Alaska
Alaska | PORT HEIDEN | -24 | 21 | 17 | Alaska
Alaska | SAINT MARY`S (AWOS) | -34 | 24 | 21 | Alaska
Alaska | SAND POINT | -12 | 18 | 15 | Alaska
Alaska | SEWARD | -17 | 26 | 20 | Alaska
Alaska | SHEMYA AFB | -8 | 13 | 11 | Alaska
Alaska | SHISHMAREF (AWOS) | N/A | 19 | 15 | Alaska
Alaska | SITKA JAPONSKI AP | -11 | 20 | 18 | Alaska
Alaska | SKAGWAY AIRPORT | -18 | 24 | 22 | Alaska
Alaska | SOLDOTNA | -33 | 25 | 22 | Alaska
Alaska | SPARREVOHN AFS | -35 | 24 | 22 | Alaska
Alaska | ST PAUL ISLAND ARPT | -18 | 14 | 12 | Alaska
Alaska | TALKEETNA STATE ARPT | -35 | 28 | 24 | Alaska
Alaska | TATALINA LRRS | N/A | 27 | 24 | Alaska
Alaska | TIN CITY AFS (AWOS) | N/A | 20 | 15 | Alaska
Alaska | TOGIAC VILLAGE AWOS | -31 | 22 | 19 | Alaska
Alaska | UNALAKLEET FIELD | N/A | 25 | 20 | Alaska
Alaska | VALDEZ PIONEER FIEL | -21 | 23 | 21 | Alaska
Alaska | VALDEZ WSO | -17 | 25 | 21 | Alaska
Alaska | WHITTIER | -16 | 24 | 21 | Alaska
Alaska | WRANGELL | -13 | 23 | 21 | Alaska
Alaska | YAKUTAT STATE ARPT | -20 | 22 | 19 | Alaska
Arizona | CASA GRANDA (AWOS) | -4 | 44 | 42 | Arizona
Arizona | DAVIS-MONTHAN AFB | -3 | 42 | 40 | Arizona
Arizona | DOUGLAS BISBEE-DOUGLAS INTL A | -9 | 39 | 37 | Arizona
Arizona | FLAGSTAFF AIRPORT | -21 | 32 | 29 | Arizona
Arizona | GRAND CANYON NATL P | -22 | 34 | 32 | Arizona
Arizona | KINGMAN (AMOS) | -8 | 41 | 38 | Arizona
Arizona | LUKE AFB/PHOENIX | -1 | 46 | 43 | Arizona
Arizona | NOGALES INTL | -6 | 39 | 37 | Arizona
Arizona | PAGE MUNI (AMOS) | -9 | 40 | 37 | Arizona
Arizona | PHOENIX SKY HARBOR INTL AP | 1 | 45 | 43 | Arizona
Arizona | PRESCOTT LOVE FIELD | -12 | 37 | 34 | Arizona
Arizona | SAFFORD (AMOS) | -7 | 42 | 39 | Arizona
Arizona | TUCSON INTERNATIONAL AP | -3 | 43 | 41 | Arizona
Arizona | WINSLOW MUNICIPAL AP | -15 | 39 | 36 | Arizona
Arizona | YUMA INTL AIRPORT | 2 | 46 | 43 | Arizona
Arizona | YUMA MCAS | 2 | 46 | 43 | Arizona
Arkansas | BENTONVILLE (AWOS) | -16 | 36 | 34 | Arkansas
Arkansas | EAKER AFB | -15 | 39 | 36 | Arkansas
Arkansas | EL DORADO GOODWIN FIELD | -9 | 38 | 36 | Arkansas
Arkansas | FAYETTEVILLE DRAKE FIELD | -17 | 37 | 34 | Arkansas
Arkansas | FLIPPIN (AWOS) | -15 | 38 | 35 | Arkansas
Arkansas | FORT SMITH REGIONAL AP | -13 | 39 | 36 | Arkansas
Arkansas | HARRISON FAA AP | -15 | 36 | 34 | Arkansas
Arkansas | JONESBORO MUNI | -15 | 37 | 35 | Arkansas
Arkansas | LITTLE ROCK ADAMS FIELD | -11 | 39 | 36 | Arkansas
Arkansas | LITTLE ROCK AFB | -13 | 40 | 37 | Arkansas
Arkansas | LITTLE ROCK/ADAMS F | -12 | 37 | 34 | Arkansas
Arkansas | PINE BLUFF FAA AP | -9 | 38 | 36 | Arkansas
Arkansas | ROGERS (AWOS) | -15 | 36 | 33 | Arkansas
Arkansas | SILOAM SPRING(AWOS) | -15 | 37 | 34 | Arkansas
Arkansas | STUTTGART (AWOS) | -9 | 37 | 35 | Arkansas
Arkansas | TEXARKANA WEBB FIELD | -9 | 39 | 36 | Arkansas
Arkansas | WALNUT RIDGE (AWOS) | -13 | 37 | 34 | Arkansas
California | ALAMEDA NAS | 3 | 30 | 26 | California
California | ARCATA AIRPORT | -3 | 21 | 19 | California
California | BAKERSFIELD MEADOWS FIELD | -2 | 42 | 39 | California
California | BEALE AFB/MARYSVILE | -3 | 41 | 38 | California
California | BISHOP AIRPORT | -13 | 40 | 38 | California
California | BLUE CANYON AP | -8 | 31 | 28 | California
California | BLYTHE RIVERSIDE CO ARPT | -1 | 47 | 44 | California
California | BURBANK-GLENDALE-PASSADENA AP | 1 | 38 | 35 | California
California | CAMARILLO (AWOS) | 1 | 28 | 27 | California
California | CAMP PENDLETON MCAS | -2 | 32 | 29 | California
California | CARLSBAD/PALOMAR | 4 | 28 | 25 | California
California | CASTLE AFB/MERCED | -3 | 40 | 37 | California
California | CRESCENT CITY FAA AI | -1 | 19 | 18 | California
California | DAGGETT BARSTOW-DAGGETT AP | -5 | 45 | 42 | California
California | EDWARDS AFB | -10 | 43 | 40 | California
California | EL TORO MCAS | 3 | 34 | 31 | California
California | EUREKA | -1 | 19 | 18 | California
California | FRESNO YOSEMITE INTL AP | -2 | 42 | 39 | California
California | FULLERTON MUNICIPAL | 2 | 34 | 31 | California
California | GEORGE AFB | -6 | 42 | 38 | California
California | HAYWARD AIR TERM | 1 | 33 | 28 | California
California | IMPERIAL | -1 | 46 | 44 | California
California | JACK NORTHROP FLD H | 4 | 31 | 26 | California
California | LANCASTER GEN WM FOX FIELD | -9 | 42 | 38 | California
California | LEMOORE REEVES NAS | -3 | 41 | 39 | California
California | LIVERMORE MUNICIPAL | -3 | 41 | 36 | California
California | LOMPOC (AWOS) | -2 | 26 | 23 | California
California | LONG BEACH DAUGHERTY FLD | 2 | 33 | 30 | California
California | LOS ANGELES INTL ARPT | 4 | 28 | 26 | California
California | MARCH AFB/RIVERSIDE | -2 | 40 | 37 | California
California | MCCLELLAN AFB | -3 | 41 | 38 | California
California | MODESTO CITY-COUNTY AP | -2 | 42 | 38 | California
California | MONTAGUE SISKIYOU COUNTY AP | N/A | 38 | 34 | California
California | MONTEREY PENINSULA | 1 | 24 | 22 | California
California | MOUNT SHASTA | -12 | 35 | 31 | California
California | MOUNTAIN VIEW MOFFETT FLD NAS | 0 | 33 | 29 | California
California | NAPA CO. AIRPORT | -4 | 35 | 31 | California
California | NORTON AFB/SAN BERN | -2 | 41 | 38 | California
California | OAKLAND METROPOLITAN ARPT | 1 | 29 | 25 | California
California | ONTARIO | -1 | 39 | 37 | California
California | PALM SPRINGS INTL | 3 | 47 | 44 | California
California | PALM SPRINGS THERMAL AP | -5 | 47 | 44 | California
California | PASO ROBLES MUNICIPAL ARPT | -6 | 42 | 38 | California
California | POINT ARENA | 2 | 17 | 15 | California
California | POINT ARGUELLO | 5 | 21 | 18 | California
California | POINT MUGU NF | 2 | 26 | 24 | California
California | PORTERVILLE (AWOS) | -2 | 41 | 38 | California
California | PT.PIEDRAS BLANCA | 3 | 21 | 20 | California
California | RED BLUFF MUNICIPAL ARPT | -4 | 44 | 40 | California
California | REDDING MUNICIPAL ARPT | -4 | 44 | 40 | California
California | RIVERSIDE MUNI | -1 | 39 | 36 | California
California | SACRAMENTO EXECUTIVE ARPT | -3 | 41 | 37 | California
California | SACRAMENTO MATHER AIRPORT | -3 | 42 | 38 | California
California | SACRAMENTO METROPOLITAN AP | -3 | 41 | 37 | California
California | SALINAS MUNICIPAL AP | -1 | 29 | 25 | California
California | SAN DIEGO LINDBERGH FIELD | 5 | 29 | 26 | California
California | SAN DIEGO MIRAMAR NAS | 1 | 32 | 30 | California
California | SAN DIEGO NORTH ISLAND NAS | 4 | 28 | 25 | California
California | SAN DIEGO/BROWN FLD | 2 | 31 | 28 | California
California | SAN DIEGO/MONTGOMER | 3 | 32 | 28 | California
California | SAN FRANCISCO INTL AP | 2 | 29 | 25 | California
California | SAN JOSE INTL AP | 0 | 36 | 32 | California
California | SAN LUIS CO RGNL | -2 | 32 | 28 | California
California | SANDBERG | -5 | 35 | 32 | California
California | SANTA BARBARA MUNICIPAL AP | -1 | 29 | 26 | California
California | SANTA MARIA PUBLIC ARPT | -3 | 29 | 25 | California
California | SANTA ROSA (AWOS) | -3 | 38 | 34 | California
California | STOCKTON METROPOLITAN ARPT | -3 | 41 | 38 | California
California | TRAVIS AFB/FAIRFLD | -3 | 40 | 36 | California
California | TRUCKEE-TAHOE | N/A | 34 | 30 | California
California | TUSTIN MCAF | 2 | 34 | 31 | California
California | UKIAH MUNICIPAL AP | -3 | 41 | 37 | California
California | VISALIA MUNI (AWOS) | -3 | 39 | 37 | California
Colorado | AKRON WASHINGTON CO AP | -23 | 38 | 34 | Colorado
Colorado | ALAMOSA SAN LUIS VALLEY RGNL | -30 | 32 | 29 | Colorado
Colorado | ASPEN PITKIN CO SAR | -24 | 32 | 28 | Colorado
Colorado | BUCKLEY ANGB/DENVER | -22 | 36 | 33 | Colorado
Colorado | COLORADO SPRINGS MUNI AP | -23 | 35 | 32 | Colorado
Colorado | CORTEZ/MONTEZUMA CO | -19 | 37 | 34 | Colorado
Colorado | CRAIG-MOFFAT | -31 | 35 | 31 | Colorado
Colorado | DENVER INTL AP | -23 | 37 | 34 | Colorado
Colorado | DENVER STAPLETON INT''L ARPT | -25 | 36 | 34 | Colorado
Colorado | DENVER/CENTENNIAL | -23 | 36 | 33 | Colorado
Colorado | DURANGO/LA PLATA CO | -21 | 34 | 32 | Colorado
Colorado | EAGLE COUNTY AP | -28 | 33 | 30 | Colorado
Colorado | FORT COLLINS (AWOS) | -23 | 38 | 34 | Colorado
Colorado | FORT COLLINS(SAWRS) | -23 | 34 | 32 | Colorado
Colorado | GRAND JUNCTION WALKER FIELD | -17 | 39 | 36 | Colorado
Colorado | GREELEY/WELD (AWOS) | -27 | 38 | 35 | Colorado
Colorado | GUNNISON CO. (AWOS) | -31 | 31 | 28 | Colorado
Colorado | HAYDEN/YAMPA (AWOS) | -25 | 33 | 30 | Colorado
Colorado | LA JUNTA MUNICIPAL AP | -21 | 40 | 37 | Colorado
Colorado | LAMAR MUNICIPAL | -22 | 40 | 37 | Colorado
Colorado | LIMON | -25 | 36 | 33 | Colorado
Colorado | MONTROSE CO. ARPT | -19 | 37 | 34 | Colorado
Colorado | PUEBLO MEMORIAL AP | -24 | 39 | 36 | Colorado
Colorado | RIFLE/GARFIELD RGNL | -22 | 38 | 34 | Colorado
Colorado | TRINIDAD LAS ANIMAS COUNTY AP | -23 | 36 | 33 | Colorado
Connecticut | BRIDGEPORT SIKORSKY MEMORIAL | -14 | 33 | 30 | Connecticut
Connecticut | HARTFORD BRADLEY INTL AP | -20 | 35 | 32 | Connecticut
Connecticut | HARTFORD BRAINARD FD | N/A | 36 | 32 | Connecticut
Connecticut | OXFORD (AWOS) | -19 | 33 | 30 | Connecticut
Connecticut | WILLIMANTIC (ASOS) | -19 | 34 | 32 | Connecticut
Delaware | DOVER AFB | -13 | 36 | 33 | Delaware
Delaware | GEORGETOWN/SUSSEX | -11 | 36 | 33 | Delaware
Delaware | WILMINGTON NEW CASTLE CNTY AP | -15 | 36 | 33 | Delaware
Florida | APALACHICOLA MUNI AP | -5 | 35 | 33 | Florida
Florida | CAPE SAN BLAS | -2 | 31 | 30 | Florida
Florida | CECIL FIELD | -6 | 37 | 35 | Florida
Florida | CRESTVIEW BOB SIKES AP | -9 | 37 | 35 | Florida
Florida | CROSS CITY AIRPORT | -6 | 36 | 34 | Florida
Florida | DAYTONA BEACH INTL AP | -2 | 35 | 33 | Florida
Florida | DESTIN FT. WALTON | N/A | 34 | 32 | Florida
Florida | EGLIN AFB/VALPARAIS | -6 | 36 | 33 | Florida
Florida | FORT LAUDERDALE HOLLYWOOD INT | 5 | 34 | 33 | Florida
Florida | FORT MYERS PAGE FIELD | 2 | 35 | 34 | Florida
Florida | GAINESVILLE REGIONAL AP | -5 | 35 | 34 | Florida
Florida | HOMESTEAD AFB | 5 | 34 | 33 | Florida
Florida | HURLBURT FIELD (AF) | -5 | 35 | 33 | Florida
Florida | JACKSONVILLE INTL ARPT | -5 | 36 | 34 | Florida
Florida | JACKSONVILLE NAS | -4 | 37 | 35 | Florida
Florida | JACKSONVILLE/CRAIG | -4 | 36 | 34 | Florida
Florida | KEY WEST INTL ARPT | 10 | 33 | 32 | Florida
Florida | KEY WEST NAS | 10 | 33 | 32 | Florida
Florida | MACDILL AFB/TAMPA | 1 | 35 | 34 | Florida
Florida | MARATHON AIRPORT | N/A | 34 | 33 | Florida
Florida | MAYPORT NS | -3 | 37 | 34 | Florida
Florida | MELBOURNE REGIONAL AP | 0 | 35 | 33 | Florida
Florida | MIAMI INTL AP | 5 | 34 | 33 | Florida
Florida | MIAMI/KENDALL-TAMIA | 4 | 34 | 33 | Florida
Florida | MOLASSES REEF | 9 | 31 | 30 | Florida
Florida | NAPLES MUNICIPAL | 3 | 34 | 32 | Florida
Florida | NASA SHUTTLE FCLTY | 0 | 34 | 33 | Florida
Florida | OCALA MUNI (AWOS) | -6 | 35 | 34 | Florida
Florida | ORLANDO EXECUTIVE AP | 1 | 35 | 34 | Florida
Florida | ORLANDO INTL ARPT | -1 | 35 | 34 | Florida
Florida | ORLANDO SANFORD AIRPORT | 1 | 36 | 34 | Florida
Florida | PANAMA CITY BAY CO | -4 | 36 | 33 | Florida
Florida | PENSACOLA FOREST SHERMAN NAS | -6 | 36 | 34 | Florida
Florida | PENSACOLA REGIONAL AP | -6 | 36 | 34 | Florida
Florida | SARASOTA BRADENTON | 0 | 35 | 33 | Florida
Florida | SOMBRERO KEY | 11 | 32 | 31 | Florida
Florida | SOUTHWEST FLORIDA I | 1 | 35 | 34 | Florida
Florida | ST AUGSUTINE ARPT | N/A | 35 | 33 | Florida
Florida | ST PETERSBURG CLEAR | 1 | 35 | 34 | Florida
Florida | ST. AUGUSTINE | 0 | 34 | 31 | Florida
Florida | TALLAHASSEE REGIONAL AP | -8 | 37 | 35 | Florida
Florida | TAMPA INTERNATIONAL AP | -1 | 34 | 33 | Florida
Florida | TYNDALL AFB | -5 | 35 | 32 | Florida
Florida | VENICE PIER | 1 | 32 | 30 | Florida
Florida | VERO BEACH MUNICIPAL ARPT | 0 | 35 | 33 | Florida
Florida | WEST PALM BEACH INTL ARPT | 3 | 34 | 33 | Florida
Florida | WHITING FIELD NAAS | -7 | 36 | 34 | Florida
Georgia | ALBANY DOUGHERTY COUNTY AP | -8 | 37 | 36 | Georgia
Georgia | ATHENS BEN EPPS AP | -11 | 37 | 35 | Georgia
Georgia | ATLANTA (NEXRAD) | -11 | 36 | 33 | Georgia
Georgia | ATLANTA HARTSFIELD INTL AP | -11 | 37 | 34 | Georgia
Georgia | AUGUSTA BUSH FIELD | -10 | 38 | 36 | Georgia
Georgia | AUGUSTA\DANIEL FLD | -6 | 37 | 35 | Georgia
Georgia | BRUNSWICK MALCOLM MCKINNON AP | -5 | 36 | 33 | Georgia
Georgia | COLUMBUS METROPOLITAN ARPT | -9 | 37 | 35 | Georgia
Georgia | DEKALB PEACHTREE | -9 | 36 | 34 | Georgia
Georgia | DOBBINS AFB/MARIETT | -12 | 36 | 34 | Georgia
Georgia | FORT BENNING | -10 | 38 | 36 | Georgia
Georgia | FULTON CO ARPT BROW | -11 | 36 | 34 | Georgia
Georgia | GAINESVILLE\LEE GIL | -8 | 35 | 33 | Georgia
Georgia | HUNTER AAF | -5 | 38 | 35 | Georgia
Georgia | MACON MIDDLE GA REGIONAL AP | -9 | 38 | 35 | Georgia
Georgia | MOODY AFB/VALDOSTA | -7 | 37 | 35 | Georgia
Georgia | ROME R B RUSSELL AP | -11 | 38 | 35 | Georgia
Georgia | SAVANNAH INTL AP | -7 | 37 | 35 | Georgia
Georgia | VALDOSTA WB AIRPORT | -7 | 37 | 35 | Georgia
Georgia | WARNER ROBINS AFB | -8 | 38 | 36 | Georgia
Georgia | WAYCROSS WARE CO AP | -6 | 38 | 35 | Georgia
Hawaii | BARBERS POINT NAS | 13 | 34 | 32 | Hawaii
Hawaii | HILO INTERNATIONAL AP | 15 | 30 | 29 | Hawaii
Hawaii | HONOLULU INTL ARPT | 14 | 32 | 32 | Hawaii
Hawaii | KAHULUI AIRPORT | 13 | 32 | 31 | Hawaii
Hawaii | KANEOHE BAY MCAS | 16 | 30 | 29 | Hawaii
Hawaii | KONA INTL AT KEAHOL | 14 | 31 | 30 | Hawaii
Hawaii | LIHUE AIRPORT | 14 | 30 | 29 | Hawaii
Hawaii | MOLOKAI (AMOS) | 13 | 31 | 30 | Hawaii
Idaho | BOISE AIR TERMINAL | -17 | 39 | 36 | Idaho
Idaho | BURLEY MUNICIPAL ARPT | -20 | 37 | 33 | Idaho
Idaho | CALDWELL (AWOS) | -13 | 39 | 35 | Idaho
Idaho | CHALLIS | -29 | 36 | 32 | Idaho
Idaho | COEUR D`ALENE(AWOS) | -18 | 36 | 32 | Idaho
Idaho | ELK CITY (RAMOS) | -15 | 38 | 34 | Idaho
Idaho | IDAHO FALLS FANNING FIELD | -26 | 36 | 33 | Idaho
Idaho | JOSLIN FLD MAGIC VA | -16 | 38 | 34 | Idaho
Idaho | LEWISTON NEZ PERCE CNTY AP | -14 | 40 | 35 | Idaho
Idaho | MCCALL ARPT | -26 | 33 | 29 | Idaho
Idaho | MOUNTAIN HOME AFB | -19 | 40 | 37 | Idaho
Idaho | MULLAN (AWRS) | -21 | 32 | 30 | Idaho
Idaho | POCATELLO REGIONAL AP | -24 | 37 | 34 | Idaho
Idaho | SALMON/LEMHI (AWOS) | -24 | 36 | 31 | Idaho
Illinois | AURORA MUNICIPAL | -25 | 35 | 32 | Illinois
Illinois | CAHOKIA/ST. LOUIS | -17 | 37 | 34 | Illinois
Illinois | CHICAGO MIDWAY AP | -22 | 36 | 33 | Illinois
Illinois | CHICAGO OHARE INTL AP | -24 | 36 | 33 | Illinois
Illinois | DECATUR | -22 | 36 | 33 | Illinois
Illinois | GLENVIEW NAS | -24 | 36 | 33 | Illinois
Illinois | LAWRENCEVILLE\VIN. | -18 | 36 | 33 | Illinois
Illinois | MARSEILLES ISLAND | -25 | 36 | 33 | Illinois
Illinois | MATTOON/CHARLESTON | -20 | 35 | 32 | Illinois
Illinois | MOLINE QUAD CITY INTL AP | -25 | 37 | 34 | Illinois
Illinois | MOUNT VERNON (AWOS) | -21 | 36 | 34 | Illinois
Illinois | PEORIA GREATER PEORIA AP | -23 | 36 | 33 | Illinois
Illinois | QUINCY MUNI BALDWIN FLD | -23 | 37 | 33 | Illinois
Illinois | ROCKFORD GREATER ROCKFORD AP | -26 | 35 | 33 | Illinois
Illinois | SCOTT AFB/BELLEVILL | -19 | 37 | 35 | Illinois
Illinois | SOUTHERN ILLINOIS | -17 | 36 | 34 | Illinois
Illinois | SPRINGFIELD CAPITAL AP | -23 | 36 | 33 | Illinois
Illinois | STERLING ROCKFALLS | -25 | 35 | 32 | Illinois
Illinois | UNIV OF ILLINOIS WI | -23 | 36 | 33 | Illinois
Illinois | W. CHICAGO/DU PAGE | -24 | 35 | 32 | Illinois
Indiana | EVANSVILLE REGIONAL AP | -19 | 36 | 34 | Indiana
Indiana | FORT WAYNE INTL AP | -23 | 35 | 32 | Indiana
Indiana | GRISSOM ARB | -23 | 36 | 33 | Indiana
Indiana | HUNTINGBURG | N/A | 35 | 33 | Indiana
Indiana | INDIANAPOLIS INTL AP | -22 | 35 | 32 | Indiana
Indiana | LAFAYETTE PURDUE UNIV AP | -23 | 36 | 33 | Indiana
Indiana | MONROE CO | -21 | 34 | 32 | Indiana
Indiana | SOUTH BEND MICHIANA RGNL AP | -22 | 36 | 32 | Indiana
Indiana | TERRE HAUTE/HULMAN | -23 | 36 | 33 | Indiana
Iowa | AMES MUNI ARPT | -26 | 34 | 32 | Iowa
Iowa | ANKENY REGIONAL ARP | -22 | 37 | 34 | Iowa
Iowa | ATLANTIC | N/A | 36 | 33 | Iowa
Iowa | BOONE MUNI | N/A | 35 | 33 | Iowa
Iowa | BURLINGTON MUNICIPAL AP | -23 | 37 | 33 | Iowa
Iowa | CARROLL | N/A | 35 | 33 | Iowa
Iowa | CEDAR RAPIDS MUNICIPAL AP | -26 | 36 | 33 | Iowa
Iowa | CHARITON | -23 | 37 | 33 | Iowa
Iowa | CHARLES CITY | N/A | 33 | 32 | Iowa
Iowa | CLARION | N/A | 35 | 32 | Iowa
Iowa | CLINTON MUNI (AWOS) | -25 | 35 | 32 | Iowa
Iowa | CRESTON | -23 | 36 | 33 | Iowa
Iowa | DAVENPORT NEXRAD | -25 | 34 | 32 | Iowa
Iowa | DES MOINES INTL AP | -25 | 37 | 33 | Iowa
Iowa | DUBUQUE REGIONAL AP | -26 | 34 | 31 | Iowa
Iowa | ESTHERVILLE MUNI | -26 | 34 | 31 | Iowa
Iowa | FAIR FIELD | N/A | 37 | 34 | Iowa
Iowa | FORT DODGE (AWOS) | -27 | 35 | 32 | Iowa
Iowa | KEOKUK MUNI | N/A | 38 | 34 | Iowa
Iowa | MARSHALL TOWN MUNI | -26 | 34 | 32 | Iowa
Iowa | MASON CITY MUNICIPAL ARPT | -28 | 35 | 32 | Iowa
Iowa | OTTUMWA INDUSTRIAL AP | -24 | 37 | 33 | Iowa
Iowa | SIOUX CITY SIOUX GATEWAY AP | -26 | 37 | 33 | Iowa
Iowa | SPENCER | -28 | 36 | 32 | Iowa
Iowa | STORM LAKE | N/A | 36 | 33 | Iowa
Iowa | WASHINGTON | N/A | 36 | 33 | Iowa
Iowa | WATERLOO MUNICIPAL AP | -28 | 36 | 33 | Iowa
Iowa | WEBSTER CITY | -25 | 35 | 33 | Iowa
Kansas | CHANUTE MARTIN JOHNSON AP | -19 | 38 | 35 | Kansas
Kansas | COFFEYVILLE MUNI | -17 | 38 | 36 | Kansas
Kansas | CONCORDIA BLOSSER MUNI AP | -21 | 40 | 37 | Kansas
Kansas | DODGE CITY REGIONAL AP | -20 | 40 | 37 | Kansas
Kansas | ELKHART (AWOS) | N/A | 39 | 37 | Kansas
Kansas | FT RILEY/MARSHALL A | -20 | 40 | 37 | Kansas
Kansas | GARDEN CITY MUNICIPAL AP | -22 | 39 | 37 | Kansas
Kansas | GOODLAND RENNER FIELD | -23 | 39 | 36 | Kansas
Kansas | GREAT BEND (AWOS) | -19 | 41 | 37 | Kansas
Kansas | HAYS MUNI (AWOS) | -20 | 41 | 38 | Kansas
Kansas | HILL CITY MUNICIPAL AP | -21 | 42 | 38 | Kansas
Kansas | LAWRENCE MUNI ARPT | -21 | 39 | 36 | Kansas
Kansas | LIBERAL MUNI | -18 | 39 | 37 | Kansas
Kansas | MANHATTAN RGNL | -22 | 40 | 37 | Kansas
Kansas | MCCONNELL AFB | -17 | 40 | 37 | Kansas
Kansas | MEDICINE LODGE ASOS | -17 | 41 | 38 | Kansas
Kansas | NEWTON (AWOS) | -17 | 40 | 36 | Kansas
Kansas | OLATHE/JOHNSON CO. | -20 | 37 | 35 | Kansas
Kansas | PARSONS\TRI CITY | -19 | 38 | 36 | Kansas
Kansas | RUSSELL MUNICIPAL AP | -21 | 41 | 37 | Kansas
Kansas | SALINA MUNICIPAL AP | -20 | 41 | 38 | Kansas
Kansas | TOPEKA FORBES FIELD | -20 | 38 | 35 | Kansas
Kansas | TOPEKA MUNICIPAL AP | -21 | 38 | 35 | Kansas
Kansas | WICHITA MID-CONTINENT AP | -18 | 41 | 37 | Kansas
Kansas | WICHITA/COL. JABARA | -17 | 41 | 36 | Kansas
Kansas | WINFIELD\ARK CITY | -17 | 40 | 37 | Kansas
Kentucky | BOWLING GREEN WARREN CO AP | -17 | 36 | 33 | Kentucky
Kentucky | CAPITAL CITY ARPT | -17 | 35 | 32 | Kentucky
Kentucky | CINCINNATI NORTHERN KY AP | -21 | 36 | 32 | Kentucky
Kentucky | FORT CAMPBELL (AAF) | -16 | 37 | 34 | Kentucky
Kentucky | FORT KNOX/GODMAN | -18 | 37 | 33 | Kentucky
Kentucky | HENDERSON CITY | -19 | 35 | 33 | Kentucky
Kentucky | JACKSON JULIAN CARROLL AP | -18 | 34 | 31 | Kentucky
Kentucky | LEXINGTON BLUEGRASS AP | -19 | 35 | 33 | Kentucky
Kentucky | LONDON-CORBIN AP | -18 | 34 | 32 | Kentucky
Kentucky | LOUISVILLE BOWMAN FIELD | -18 | 37 | 34 | Kentucky
Kentucky | LOUISVILLE STANDIFORD FIELD | -17 | 36 | 34 | Kentucky
Kentucky | PADUCAH BARKLEY REGIONAL AP | -17 | 36 | 34 | Kentucky
Kentucky | SOMERSET(AWOS) | -13 | 37 | 34 | Kentucky
Louisiana | ALEXANDRIA ESLER REGIONAL AP | -7 | 38 | 35 | Louisiana
Louisiana | ALEXANDRIA INTERNATIONAL | -7 | 37 | 35 | Louisiana
Louisiana | BARKSDALE AFB | -9 | 38 | 35 | Louisiana
Louisiana | BATON ROUGE RYAN ARPT | -6 | 35 | 34 | Louisiana
Louisiana | FORT POLK (ARMY) | -6 | 37 | 35 | Louisiana
Louisiana | GRAND ISLE | 0 | 32 | 31 | Louisiana
Louisiana | LAFAYETTE REGIONAL AP | -6 | 35 | 34 | Louisiana
Louisiana | LAKE CHARLES REGIONAL ARPT | -5 | 35 | 34 | Louisiana
Louisiana | MONROE REGIONAL AP | -8 | 37 | 36 | Louisiana
Louisiana | NEW ORLEANS ALVIN CALLENDER F | -5 | 35 | 33 | Louisiana
Louisiana | NEW ORLEANS INTL ARPT | -4 | 36 | 34 | Louisiana
Louisiana | NEW ORLEANS LAKEFRONT AP | -1 | 35 | 34 | Louisiana
Louisiana | PATTERSON MEMORIAL | -3 | 36 | 33 | Louisiana
Louisiana | SALT POINT (RAMOS) | N/A | 34 | 33 | Louisiana
Louisiana | SHREVEPORT DOWNTOWN | -6 | 39 | 37 | Louisiana
Louisiana | SHREVEPORT REGIONAL ARPT | -8 | 38 | 36 | Louisiana
Louisiana | SOUTHWEST PASS | 2 | 32 | 31 | Louisiana
Maine | AUBURN-LEWISTON | -27 | 33 | 30 | Maine
Maine | AUGUSTA AIRPORT | -23 | 33 | 30 | Maine
Maine | BANGOR INTERNATIONAL AP | -27 | 33 | 30 | Maine
Maine | BAR HARBOR (AWOS) | -22 | 30 | 27 | Maine
Maine | BRUNSWICK NAS | -24 | 33 | 30 | Maine
Maine | CARIBOU MUNICIPAL ARPT | -31 | 32 | 28 | Maine
Maine | GREENVILLE (AMOS) | -30 | 30 | 28 | Maine
Maine | HOULTON INTL ARPT | -32 | 32 | 29 | Maine
Maine | LORING AFB/LIMESTON | -29 | 32 | 28 | Maine
Maine | MATINICUS ROCK | -18 | 22 | 19 | Maine
Maine | MT DESERT ROCK | -18 | 21 | 18 | Maine
Maine | NORTHERN AROOSTOOK | -28 | 29 | 27 | Maine
Maine | PORTLAND INTL JETPORT | -23 | 33 | 30 | Maine
Maine | PRESQUE ISLE MUNICIP | -34 | 31 | 29 | Maine
Maine | ROCKLAND/KNOX(AWOS) | -21 | 31 | 27 | Maine
Maine | SANFORD MUNI (AWOS) | -27 | 34 | 31 | Maine
Maine | WATERVILLE (AWOS) | N/A | 32 | 29 | Maine
Maine | WISCASSET | -23 | 32 | 29 | Maine
Maryland | ANDREWS AFB | -15 | 37 | 34 | Maryland
Maryland | BALTIMORE BLT-WASHNGTN INT''L | -15 | 37 | 34 | Maryland
Maryland | PATUXENT RIVER NAS | -13 | 36 | 33 | Maryland
Maryland | SALISBURY WICOMICO CO AP | -14 | 36 | 33 | Maryland
Maryland | THOMAS POINT | -10 | 33 | 30 | Maryland
Massachusetts | BARNSTABLE MUNI BOA | -16 | 32 | 28 | Massachusetts
Massachusetts | BOSTON LOGAN INT''L ARPT | -17 | 35 | 32 | Massachusetts
Massachusetts | BUZZARDS BAY | -15 | 27 | 23 | Massachusetts
Massachusetts | CHATHAM MUNI ARPT | N/A | 31 | 27 | Massachusetts
Massachusetts | LAWRENCE MUNI | -18 | 34 | 32 | Massachusetts
Massachusetts | MARTHAS VINEYARD | -17 | 31 | 27 | Massachusetts
Massachusetts | NEW BEDFORD RGNL | -17 | 34 | 31 | Massachusetts
Massachusetts | NORWOOD MEMORIAL | N/A | 35 | 32 | Massachusetts
Massachusetts | OTIS ANGB | -16 | 32 | 29 | Massachusetts
Massachusetts | PLYMOUTH MUNICIPAL | -18 | 34 | 31 | Massachusetts
Massachusetts | PROVINCETOWN (AWOS) | -14 | 32 | 28 | Massachusetts
Massachusetts | SOUTH WEYMOUTH NAS | -19 | 35 | 32 | Massachusetts
Massachusetts | WORCESTER REGIONAL ARPT | -20 | 32 | 29 | Massachusetts
Michigan | ALPENA COUNTY REGIONAL AP | -26 | 34 | 30 | Michigan
Michigan | ANTRIM CO ARPT | -25 | 33 | 30 | Michigan
Michigan | BENTON HARBOR/ROSS | -19 | 34 | 31 | Michigan
Michigan | CADILLAC WEXFORD CO AP | -29 | 33 | 30 | Michigan
Michigan | CHIPPEWA CO INTL | -27 | 31 | 28 | Michigan
Michigan | COPPER HARBOR RAMOS | -22 | 31 | 26 | Michigan
Michigan | DETROIT CITY AIRPORT | -19 | 35 | 32 | Michigan
Michigan | DETROIT METROPOLITAN ARPT | -20 | 35 | 32 | Michigan
Michigan | DETROIT WILLOW RUN AP | -20 | 35 | 32 | Michigan
Michigan | ESCANABA (AWOS) | -26 | 31 | 27 | Michigan
Michigan | FLINT BISHOP INTL ARPT | -23 | 35 | 31 | Michigan
Michigan | GRAND RAPIDS KENT COUNTY INT'' | -22 | 34 | 31 | Michigan
Michigan | GROSSE ISLE ARPT | -16 | 34 | 31 | Michigan
Michigan | HANCOCK HOUGHTON CO AP | -24 | 33 | 28 | Michigan
Michigan | HARBOR BEACH(RAMOS) | -17 | 35 | 31 | Michigan
Michigan | HOLLAND/TULIP CITY | -19 | 33 | 30 | Michigan
Michigan | HOUGHTON LAKE ROSCOMMON CO AR | -26 | 33 | 30 | Michigan
Michigan | HOWELL | -20 | 34 | 32 | Michigan
Michigan | IRON MOUNTAIN/FORD | -29 | 34 | 30 | Michigan
Michigan | IRONWOOD (AWOS) | -30 | 33 | 29 | Michigan
Michigan | JACKSON REYNOLDS FIELD | -22 | 33 | 31 | Michigan
Michigan | KALAMAZOO BATTLE CR | -20 | 34 | 32 | Michigan
Michigan | LANSING CAPITAL CITY ARPT | -24 | 34 | 31 | Michigan
Michigan | MACKINACK ISLAND | -26 | 33 | 28 | Michigan
Michigan | MANISTEE (AWOS) | -21 | 32 | 29 | Michigan
Michigan | MANISTIQUE (AMOS) | -22 | 28 | 25 | Michigan
Michigan | MARQUETTE COUNTY ARPT | -30 | 33 | 29 | Michigan
Michigan | MENOMINEE (AWOS) | -26 | 33 | 29 | Michigan
Michigan | MUSKEGON COUNTY ARPT | -20 | 32 | 30 | Michigan
Michigan | NEWBERRY LUCE CO. | -26 | 32 | 28 | Michigan
Michigan | OAKLAND CO INTL | -20 | 34 | 31 | Michigan
Michigan | OSCODA WURTSMITH AFB | -22 | 35 | 31 | Michigan
Michigan | PASSAGE ISLAND | -24 | 22 | 19 | Michigan
Michigan | PELLSTON EMMET COUNTY AP | -29 | 33 | 30 | Michigan
Michigan | ROCK OF AGES | -26 | 25 | 21 | Michigan
Michigan | SAGINAW TRI CITY INTL AP | -21 | 35 | 32 | Michigan
Michigan | SAULT STE MARIE SANDERSON FIE | -29 | 32 | 28 | Michigan
Michigan | SELFRIDGE ANGB | -20 | 35 | 32 | Michigan
Michigan | ST.CLAIR COUNTY INT | -22 | 33 | 32 | Michigan
Michigan | STANNARD ROCK | -20 | 26 | 23 | Michigan
Michigan | STURGIS\KIRSH MUNI | -21 | 33 | 32 | Michigan
Michigan | TRAVERSE CITY CHERRY CAPITAL | -23 | 34 | 31 | Michigan
Minnesota | AITKIN NDB(AWOS) | -33 | 32 | 29 | Minnesota
Minnesota | ALBERT LEA (AWOS) | -28 | 34 | 31 | Minnesota
Minnesota | ALEXANDRIA MUNICIPAL AP | -31 | 35 | 31 | Minnesota
Minnesota | AUSTIN MUNI | -28 | 34 | 31 | Minnesota
Minnesota | BAUDETTE INTERNATIONAL AP | -35 | 32 | 29 | Minnesota
Minnesota | BEMIDJI MUNICIPAL | -34 | 33 | 30 | Minnesota
Minnesota | BENSON MUNI | -30 | 36 | 32 | Minnesota
Minnesota | BRAINERD/WIELAND | -33 | 34 | 30 | Minnesota
Minnesota | CAMBRIDGE MUNI | -31 | 37 | 32 | Minnesota
Minnesota | CLOQUET (AWOS) | -31 | 33 | 29 | Minnesota
Minnesota | CRANE LAKE (AWOS) | -34 | 33 | 29 | Minnesota
Minnesota | CROOKSTON MUNI FLD | -34 | 32 | 30 | Minnesota
Minnesota | DETROIT LAKES(AWOS) | -32 | 33 | 30 | Minnesota
Minnesota | DULUTH HARBOR (CGS) | -27 | 33 | 29 | Minnesota
Minnesota | DULUTH INTERNATIONAL ARPT | -32 | 32 | 28 | Minnesota
Minnesota | ELY MUNI | -37 | 32 | 29 | Minnesota
Minnesota | EVELETH MUNI (AWOS) | -35 | 33 | 29 | Minnesota
Minnesota | FAIRMONT MUNI(AWOS) | -26 | 33 | 31 | Minnesota
Minnesota | FARIBAULT MUNI AWOS | -29 | 34 | 31 | Minnesota
Minnesota | FERGUS FALLS(AWOS) | -31 | 35 | 31 | Minnesota
Minnesota | FLYING CLOUD | -27 | 35 | 32 | Minnesota
Minnesota | FOSSTON(AWOS) | -35 | 33 | 30 | Minnesota
Minnesota | GLENWOOD (ASOS) | -30 | 36 | 31 | Minnesota
Minnesota | GRAND MARAIS MUNI | -30 | 29 | 26 | Minnesota
Minnesota | GRAND RAPIDS(AWOS) | -32 | 32 | 28 | Minnesota
Minnesota | HALLOCK | -34 | 33 | 31 | Minnesota
Minnesota | HIBBING CHISHOLM-HIBBING AP | -36 | 32 | 29 | Minnesota
Minnesota | HUTCHINSON (AWOS) | -30 | 34 | 32 | Minnesota
Minnesota | INTERNATIONAL FALLS INTL AP | -37 | 32 | 29 | Minnesota
Minnesota | LITCHFIELD MUNI | -28 | 34 | 31 | Minnesota
Minnesota | LITTLE FALLS (AWOS) | -32 | 35 | 32 | Minnesota
Minnesota | MANKATO(AWOS) | -26 | 33 | 31 | Minnesota
Minnesota | MARSHALL/RYAN(AWOS) | -27 | 35 | 32 | Minnesota
Minnesota | MINNEAPOLIS/BLAINE | -26 | 35 | 32 | Minnesota
Minnesota | MINNEAPOLIS/CRYSTAL | -26 | 36 | 32 | Minnesota
Minnesota | MINNEAPOLIS-ST PAUL INT''L ARP | -28 | 36 | 32 | Minnesota
Minnesota | MONTEVIDEO (AWOS) | -28 | 34 | 32 | Minnesota
Minnesota | MORA MUNI (AWOS) | -31 | 33 | 31 | Minnesota
Minnesota | MORRIS MUNI (AWOS) | -30 | 33 | 31 | Minnesota
Minnesota | NEW ULM MUNI (AWOS) | -27 | 34 | 32 | Minnesota
Minnesota | ORR | -35 | 33 | 29 | Minnesota
Minnesota | OWATONNA (AWOS) | -28 | 33 | 31 | Minnesota
Minnesota | PARK RAPIDS MUNICIPAL AP | -34 | 33 | 30 | Minnesota
Minnesota | PEQUOT LAKE (AMOS) | -35 | 36 | 31 | Minnesota
Minnesota | PIPESTONE (AWOS) | -28 | 34 | 31 | Minnesota
Minnesota | PRINCETON MUNI | -29 | 35 | 31 | Minnesota
Minnesota | RED WING | -28 | 35 | 32 | Minnesota
Minnesota | REDWOOD FALLS MUNI | -29 | 36 | 33 | Minnesota
Minnesota | ROCHESTER INTERNATIONAL ARPT | -29 | 33 | 31 | Minnesota
Minnesota | ROSEAU MUNI (AWOS) | -35 | 33 | 29 | Minnesota
Minnesota | SILVER BAY | -34 | 32 | 28 | Minnesota
Minnesota | SOUTH ST PAUL MUNI | -26 | 35 | 32 | Minnesota
Minnesota | ST CLOUD REGIONAL ARPT | -32 | 35 | 31 | Minnesota
Minnesota | ST JAMES MUNI ARPT | -25 | 34 | 32 | Minnesota
Minnesota | ST PAUL DOWNTOWN AP | -28 | 36 | 31 | Minnesota
Minnesota | THIEF RIVER(AWOS) | -33 | 32 | 29 | Minnesota
Minnesota | TOFTE (RAMOS) | -29 | 29 | 25 | Minnesota
Minnesota | TWO HARBORS | -31 | 32 | 28 | Minnesota
Minnesota | WHEATON NDB (AWOS) | -30 | 33 | 31 | Minnesota
Minnesota | WILLMAR | -31 | 34 | 31 | Minnesota
Minnesota | WINONA MUNI (AWOS) | -28 | 36 | 32 | Minnesota
Minnesota | WORTHINGTON (AWOS) | -26 | 34 | 31 | Minnesota
Mississippi | COLUMBUS AFB | -11 | 37 | 35 | Mississippi
Mississippi | GOLDEN TRI(AWOS) | -10 | 37 | 35 | Mississippi
Mississippi | GREENWOOD LEFLORE ARPT | -10 | 37 | 35 | Mississippi
Mississippi | HATTIESBURG LAUREL | -8 | 38 | 35 | Mississippi
Mississippi | JACKSON INTERNATIONAL AP | -9 | 37 | 35 | Mississippi
Mississippi | KEESLER AFB/BILOXI | -6 | 36 | 34 | Mississippi
Mississippi | MCCOMB PIKE COUNTY AP | -8 | 36 | 34 | Mississippi
Mississippi | MERIDIAN KEY FIELD | -10 | 37 | 35 | Mississippi
Mississippi | MERIDIAN NAAS | -11 | 38 | 36 | Mississippi
Mississippi | NATCHEZ/HARDY(AWOS) | -7 | 36 | 34 | Mississippi
Mississippi | TUPELO C D LEMONS ARPT | -12 | 37 | 35 | Mississippi
Missouri | CAPE GIRARDEAU MUNICIPAL AP | -18 | 37 | 34 | Missouri
Missouri | COLUMBIA REGIONAL AIRPORT | -21 | 37 | 34 | Missouri
Missouri | JEFFERSON CITY MEM | -19 | 38 | 35 | Missouri
Missouri | JOPLIN MUNICIPAL AP | -18 | 37 | 35 | Missouri
Missouri | KAISER MEM (AWOS) | -18 | 38 | 35 | Missouri
Missouri | KANSAS CITY DOWNTOWN AP | -19 | 38 | 35 | Missouri
Missouri | KANSAS CITY INT''L ARPT | -21 | 38 | 35 | Missouri
Missouri | KIRKSVILLE REGIONAL AP | -22 | 37 | 34 | Missouri
Missouri | POPLAR BLUFF(AMOS) | -16 | 36 | 34 | Missouri
Missouri | SEDALIA MEMORIAL | -18 | 38 | 35 | Missouri
Missouri | SPICKARD (AMOS) | N/A | 38 | 35 | Missouri
Missouri | SPRINGFIELD REGIONAL ARPT | -19 | 37 | 34 | Missouri
Missouri | ST LOUIS LAMBERT INT''L ARPT | -19 | 37 | 35 | Missouri
Missouri | ST LOUIS SPIRIT OF ST LOUIS A | -20 | 37 | 34 | Missouri
Missouri | VICHY ROLLA NATL ARPT | -19 | 38 | 34 | Missouri
Missouri | WHITEMAN AFB | -20 | 38 | 35 | Missouri
Montana | BILLINGS LOGAN INT''L ARPT | -27 | 38 | 34 | Montana
Montana | BOZEMAN GALLATIN FIELD | -33 | 36 | 32 | Montana
Montana | BUTTE BERT MOONEY ARPT | -35 | 34 | 30 | Montana
Montana | CUT BANK MUNI AP | -33 | 34 | 30 | Montana
Montana | DILLON AIRPORT | -26 | 34 | 30 | Montana
Montana | GLASGOW INTL ARPT | -33 | 37 | 34 | Montana
Montana | GLENDIVE(AWOS) | -31 | 38 | 34 | Montana
Montana | GREAT FALLS | N/A | 36 | 31 | Montana
Montana | GREAT FALLS INTL ARPT | -31 | 36 | 32 | Montana
Montana | HAVRE CITY-COUNTY AP | -35 | 37 | 34 | Montana
Montana | HELENA REGIONAL AIRPORT | -30 | 37 | 33 | Montana
Montana | JORDAN (RAMOS) | -37 | 38 | 35 | Montana
Montana | KALISPELL GLACIER PK INT''L AR | -27 | 35 | 31 | Montana
Montana | LEWISTOWN MUNICIPAL ARPT | -31 | 35 | 31 | Montana
Montana | MALMSTROM AFB | -30 | 36 | 33 | Montana
Montana | MILES CITY MUNICIPAL ARPT | -31 | 39 | 36 | Montana
Montana | MISSOULA INTERNATIONAL AP | -25 | 37 | 33 | Montana
Montana | SIDNEY-RICHLAND | -32 | 37 | 33 | Montana
Nebraska | AINSWORTH MUNICIPAL | -26 | 40 | 34 | Nebraska
Nebraska | ALLIANCE MUNICIPAL | -30 | 39 | 35 | Nebraska
Nebraska | BEATRICE MUNICIPAL | -23 | 39 | 35 | Nebraska
Nebraska | BREWSTER FIELD ARPT | -22 | 38 | 35 | Nebraska
Nebraska | COLUMBUS MUNI | -25 | 37 | 33 | Nebraska
Nebraska | FREMONT MUNI ARPT | N/A | 37 | 33 | Nebraska
Nebraska | GRAND ISLAND CENTRAL NE REGIO | -25 | 39 | 35 | Nebraska
Nebraska | HASTINGS MUNICIPAL | -23 | 39 | 35 | Nebraska
Nebraska | KEARNEY MUNI (AWOS) | -23 | 38 | 34 | Nebraska
Nebraska | LINCOLN MUNICIPAL ARPT | -24 | 39 | 35 | Nebraska
Nebraska | MCCOOK MUNICIPAL | -22 | 42 | 38 | Nebraska
Nebraska | NORFOLK KARL STEFAN MEM ARPT | -26 | 37 | 34 | Nebraska
Nebraska | NORTH PLATTE REGIONAL AP | -26 | 39 | 35 | Nebraska
Nebraska | O`NEILL/BAKER FIELD | -25 | 39 | 34 | Nebraska
Nebraska | OFFUTT AFB/BELLEVUE | -22 | 38 | 34 | Nebraska
Nebraska | OMAHA EPPLEY AIRFIELD | -24 | 38 | 34 | Nebraska
Nebraska | OMAHA WSFO | -25 | 36 | 34 | Nebraska
Nebraska | SCOTTSBLUFF W B HEILIG FIELD | -28 | 39 | 35 | Nebraska
Nebraska | SIDNEY MUNICIPAL AP | -27 | 39 | 34 | Nebraska
Nebraska | TEKAMAH (ASOS) | -26 | 37 | 34 | Nebraska
Nebraska | VALENTINE MILLER FIELD | -29 | 40 | 36 | Nebraska
Nevada | CALIENTE (AMOS) | N/A | 39 | 37 | Nevada
Nevada | ELKO MUNICIPAL ARPT | -24 | 38 | 34 | Nevada
Nevada | ELY YELLAND FIELD | -25 | 35 | 32 | Nevada
Nevada | EUREKA (RAMOS) | -20 | 36 | 32 | Nevada
Nevada | FALLON NAAS | N/A | 39 | 37 | Nevada
Nevada | LAS VEGAS MCCARRAN INTL AP | -4 | 45 | 42 | Nevada
Nevada | LOVELOCK DERBY FIELD | -19 | 40 | 36 | Nevada
Nevada | MERCURY DESERT ROCK AP | -7 | 42 | 39 | Nevada
Nevada | NELLIS AFB | -6 | 46 | 43 | Nevada
Nevada | RENO TAHOE INTERNATIONAL AP | -15 | 38 | 35 | Nevada
Nevada | TONOPAH AIRPORT | -17 | 37 | 35 | Nevada
Nevada | WINNEMUCCA MUNICIPAL ARPT | -21 | 39 | 36 | Nevada
New Hampshire | BERLIN MUNICIPAL | -32 | 31 | 29 | New Hampshire
New Hampshire | CONCORD MUNICIPAL ARPT | -25 | 34 | 32 | New Hampshire
New Hampshire | DILLANT HOPKINS | -25 | 33 | 31 | New Hampshire
New Hampshire | ISLE OF SHOALS | -17 | 29 | 26 | New Hampshire
New Hampshire | JAFFREY MUNICIPAL | -23 | 32 | 30 | New Hampshire
New Hampshire | LACONIA MUNI (AWOS) | -24 | 33 | 31 | New Hampshire
New Hampshire | LEBANON MUNICIPAL | -27 | 34 | 31 | New Hampshire
New Hampshire | MANCHESTER AIRPORT | -21 | 36 | 33 | New Hampshire
New Hampshire | MOUNT WASHINGTON | -36 | 18 | 16 | New Hampshire
New Hampshire | PEASE INTL TRADEPOR | -19 | 34 | 31 | New Hampshire
New Jersey | ATLANTIC CITY INTL AP | -16 | 36 | 33 | New Jersey
New Jersey | BELMAR-FARMINGDALE | -14 | 36 | 32 | New Jersey
New Jersey | CAPE MAY CO | -13 | 34 | 31 | New Jersey
New Jersey | MCGUIRE AFB | -16 | 36 | 33 | New Jersey
New Jersey | MILLVILLE MUNICIPAL AP | -17 | 36 | 33 | New Jersey
New Jersey | NEWARK INTERNATIONAL ARPT | -15 | 37 | 34 | New Jersey
New Jersey | TETERBORO AIRPORT | -16 | 36 | 33 | New Jersey
New Jersey | TRENTON MERCER COUNTY AP | N/A | 37 | 33 | New Jersey
New Mexico | ALAMOGORDO WHITE SA | N/A | 39 | 38 | New Mexico
New Mexico | ALBUQUERQUE INTL ARPT | -12 | 37 | 35 | New Mexico
New Mexico | CANNON AFB/CLOVIS | -14 | 38 | 36 | New Mexico
New Mexico | CARLSBAD CAVERN CITY AIR TERM | -11 | 41 | 39 | New Mexico
New Mexico | CLAYTON MUNICIPAL AIRPARK | -19 | 36 | 34 | New Mexico
New Mexico | CLOVIS MUNI (AWOS) | -14 | 37 | 35 | New Mexico
New Mexico | FARMINGTON FOUR CORNERS REGL | -17 | 37 | 34 | New Mexico
New Mexico | GALLUP SEN CLARKE FLD | -23 | 35 | 32 | New Mexico
New Mexico | HOLLOMAN AFB | -11 | 39 | 37 | New Mexico
New Mexico | ROSWELL INDUSTRIAL AIR PARK | -13 | 39 | 37 | New Mexico
New Mexico | SIERRA BLANCA RGNL | -13 | 33 | 31 | New Mexico
New Mexico | TAOS MUNI APT(AWOS) | -23 | 33 | 31 | New Mexico
New Mexico | TRUTH OR CONSEQUENCES MUNI AP | -10 | 38 | 36 | New Mexico
New Mexico | TUCUMCARI | -17 | 40 | 37 | New Mexico
New Mexico | WHITE SANDS | -12 | 39 | 37 | New Mexico
New York | ALBANY COUNTY AP | -23 | 34 | 31 | New York
New York | AMBROSE LIGHT | -13 | 32 | 28 | New York
New York | BINGHAMTON EDWIN A LINK FIELD | -22 | 32 | 29 | New York
New York | BUFFALO NIAGARA INTL AP | -20 | 32 | 30 | New York
New York | DUNKIRK | -16 | 29 | 27 | New York
New York | ELMIRA CORNING REGIONAL AP | -23 | 35 | 32 | New York
New York | FORT DRUM/WHEELER-S | -28 | 32 | 29 | New York
New York | GALLOO ISLAND | -22 | 27 | 25 | New York
New York | GLENS FALLS AP | -29 | 33 | 31 | New York
New York | GRIFFISS AFB | -26 | 34 | 31 | New York
New York | ISLIP LONG ISL MACARTHUR AP | -15 | 34 | 31 | New York
New York | JAMESTOWN (AWOS) | -20 | 31 | 28 | New York
New York | MASSENA AP | -30 | 33 | 30 | New York
New York | MONTICELLO(AWOS) | N/A | 32 | 29 | New York
New York | NEW YORK J F KENNEDY INT''L AR | -14 | 35 | 31 | New York
New York | NEW YORK LAGUARDIA ARPT | -14 | 36 | 33 | New York
New York | NEWBURGH/STEWART | -20 | 35 | 31 | New York
New York | NIAGARA FALLS AF | -20 | 33 | 30 | New York
New York | PLATTSBURGH AFB | -28 | 32 | 30 | New York
New York | POUGHKEEPSIE DUTCHESS CO AP | -22 | 36 | 33 | New York
New York | REPUBLIC | -13 | 35 | 32 | New York
New York | ROCHESTER GREATER ROCHESTER I | -20 | 34 | 31 | New York
New York | SUPERIOR SHOALS | -23 | 29 | 27 | New York
New York | SYRACUSE HANCOCK INT''L ARPT | -24 | 33 | 31 | New York
New York | UTICA ONEIDA COUNTY AP | -24 | 33 | 30 | New York
New York | WATERTOWN AP | -32 | 31 | 29 | New York
New York | WHITE PLAINS WESTCHESTER CO A | -17 | 35 | 32 | New York
North Carolina | ASHEVILLE REGIONAL ARPT | -15 | 33 | 31 | North Carolina
North Carolina | CAPE HATTERAS | -4 | 32 | 30 | North Carolina
North Carolina | CAPE LOOKOUT | -6 | 31 | 29 | North Carolina
North Carolina | CHARLOTTE DOUGLAS INTL ARPT | -11 | 37 | 34 | North Carolina
North Carolina | CHERRY POINT MCAS | -9 | 36 | 33 | North Carolina
North Carolina | DIAMOND SHOALS (LS) | -3 | 30 | 28 | North Carolina
North Carolina | FAYETTEVILLE RGNL G | -10 | 38 | 35 | North Carolina
North Carolina | FORT BRAGG/SIMMONS | -10 | 38 | 35 | North Carolina
North Carolina | FRYING PAN SHOALS | -2 | 30 | 29 | North Carolina
North Carolina | GREENSBORO PIEDMONT TRIAD INT | -13 | 35 | 33 | North Carolina
North Carolina | HATTERAS BILLY MITCHELL AP | -6 | 33 | 31 | North Carolina
North Carolina | HICKORY REGIONAL AP | -13 | 36 | 33 | North Carolina
North Carolina | JACKSONVILLE (AWOS) | -11 | 37 | 34 | North Carolina
North Carolina | NEW BERN CRAVEN CO REGL AP | -9 | 36 | 34 | North Carolina
North Carolina | NEW RIVER MCAF | -9 | 36 | 34 | North Carolina
North Carolina | PITT GREENVILLE ARP | -10 | 37 | 35 | North Carolina
North Carolina | POPE AFB | -10 | 38 | 36 | North Carolina
North Carolina | RALEIGH DURHAM INTERNATIONAL | -12 | 36 | 34 | North Carolina
North Carolina | RICHMOND INTERNATIONAL AP | -13 | 37 | 34 | North Carolina
North Carolina | SEYMOUR-JOHNSON AFB | -10 | 38 | 35 | North Carolina
North Carolina | SOUTHERN PINES AWOS | -13 | 36 | 34 | North Carolina
North Carolina | WILMINGTON INTERNATIONAL ARPT | -9 | 36 | 34 | North Carolina
North Carolina | WINSTON-SALEM REYNOLDS AP | -13 | 36 | 33 | North Carolina
North Dakota | BISMARCK MUNICIPAL ARPT | -33 | 38 | 33 | North Dakota
North Dakota | DEVILS LAKE (AMOS) | -33 | 35 | 32 | North Dakota
North Dakota | DEVILS LAKE(AWOS) | -33 | 33 | 29 | North Dakota
North Dakota | DICKINSON MUNICIPAL AP | -31 | 38 | 33 | North Dakota
North Dakota | FARGO HECTOR INTERNATIONAL AP | -32 | 36 | 32 | North Dakota
North Dakota | GRAND FORKS AFB | -32 | 35 | 32 | North Dakota
North Dakota | GRAND FORKS INTERNATIONAL AP | -33 | 34 | 31 | North Dakota
North Dakota | JAMESTOWN MUNICIPAL ARPT | -31 | 36 | 32 | North Dakota
North Dakota | LIDGERWOOD (RAMOS) | -31 | 38 | 33 | North Dakota
North Dakota | MINOT AFB | -33 | 36 | 33 | North Dakota
North Dakota | MINOT FAA AP | -31 | 35 | 32 | North Dakota
North Dakota | WILLISTON SLOULIN INTL AP | -34 | 37 | 34 | North Dakota
Ohio | AKRON AKRON-CANTON REG AP | -21 | 34 | 31 | Ohio
Ohio | CINCINNATI MUNICIPAL AP LUNKI | -19 | 36 | 33 | Ohio
Ohio | CLEVELAND HOPKINS INTL AP | -20 | 34 | 31 | Ohio
Ohio | COLUMBUS PORT COLUMBUS INTL A | -20 | 35 | 32 | Ohio
Ohio | DAYTON INTERNATIONAL AIRPORT | -21 | 35 | 32 | Ohio
Ohio | FINDLAY AIRPORT | -22 | 35 | 32 | Ohio
Ohio | LANCASTER\FAIRFIEL | -21 | 34 | 32 | Ohio
Ohio | MANSFIELD LAHM MUNICIPAL ARPT | -22 | 33 | 31 | Ohio
Ohio | OHIO STATE UNIVERSI | -18 | 34 | 32 | Ohio
Ohio | RICKENBACKER ANGB | -19 | 36 | 33 | Ohio
Ohio | SOUTH BASS ISLAND | -17 | 31 | 29 | Ohio
Ohio | TOLEDO EXPRESS AIRPORT | -21 | 35 | 32 | Ohio
Ohio | WRIGHT-PATERSON AFB | -21 | 36 | 33 | Ohio
Ohio | YOUNGSTOWN REGIONAL AIRPORT | -21 | 34 | 31 | Ohio
Ohio | ZANESVILLE MUNICIPAL AP | -21 | 34 | 32 | Ohio
Oklahoma | ALTUS AFB | -13 | 41 | 39 | Oklahoma
Oklahoma | CLINTON-SHERMAN | -13 | 41 | 38 | Oklahoma
Oklahoma | FORT SILL | -13 | 41 | 37 | Oklahoma
Oklahoma | GAGE AIRPORT | -19 | 39 | 37 | Oklahoma
Oklahoma | HOBART MUNICIPAL AP | -14 | 41 | 38 | Oklahoma
Oklahoma | LAWTON MUNICIPAL | -12 | 41 | 38 | Oklahoma
Oklahoma | MCALESTER MUNICIPAL AP | -14 | 40 | 36 | Oklahoma
Oklahoma | OKLAHOMA CITY WILL ROGERS WOR | -14 | 40 | 36 | Oklahoma
Oklahoma | OKLAHOMA CITY/WILEY | -15 | 40 | 37 | Oklahoma
Oklahoma | PONCA CITY MUNICIPAL AP | -16 | 40 | 37 | Oklahoma
Oklahoma | STILLWATER RGNL | -15 | 41 | 37 | Oklahoma
Oklahoma | TINKER AFB | -14 | 39 | 36 | Oklahoma
Oklahoma | TULSA INTERNATIONAL AIRPORT | -15 | 39 | 36 | Oklahoma
Oklahoma | TULSA/LLOYD JONES | -14 | 39 | 37 | Oklahoma
Oklahoma | VANCE AFB | -16 | 40 | 37 | Oklahoma
Oregon | ASTORIA REGIONAL AIRPORT | -5 | 27 | 23 | Oregon
Oregon | AURORA STATE | -5 | 37 | 32 | Oregon
Oregon | BAKER MUNICIPAL AP | -23 | 36 | 33 | Oregon
Oregon | BURNS MUNICIPAL ARPT | -23 | 38 | 33 | Oregon
Oregon | CAPE ARAGO (LS) | 0 | 19 | 17 | Oregon
Oregon | CORVALLIS MUNI | -8 | 38 | 33 | Oregon
Oregon | EUGENE MAHLON SWEET ARPT | -8 | 37 | 32 | Oregon
Oregon | KLAMATH FALLS INTL AP | -18 | 35 | 32 | Oregon
Oregon | LA GRANDE MUNI AP | -17 | 37 | 32 | Oregon
Oregon | LAKEVIEW (AWOS) | -21 | 34 | 31 | Oregon
Oregon | MC MINNVILLE MUNI | -5 | 37 | 32 | Oregon
Oregon | MEACHAM | -28 | 33 | 30 | Oregon
Oregon | MEDFORD ROGUE VALLEY INTL AP | -8 | 40 | 36 | Oregon
Oregon | NEWPORT STATE BEACH | -2 | 18 | 17 | Oregon
Oregon | NORTH BEND MUNI AIRPORT | -4 | 22 | 20 | Oregon
Oregon | PENDLETON E OR REGIONAL AP | -16 | 39 | 35 | Oregon
Oregon | PORTLAND INTERNATIONAL AP | -6 | 36 | 32 | Oregon
Oregon | PORTLAND/HILLSBORO | -8 | 37 | 32 | Oregon
Oregon | REDMOND ROBERTS FIELD | -19 | 37 | 33 | Oregon
Oregon | SALEM MCNARY FIELD | -8 | 37 | 32 | Oregon
Oregon | SEXTON SUMMIT | -8 | 32 | 28 | Oregon
Pennsylvania | ALLENTOWN LEHIGH VALLEY INTL | -17 | 35 | 32 | Pennsylvania
Pennsylvania | ALTOONA BLAIR CO ARPT | -19 | 34 | 31 | Pennsylvania
Pennsylvania | BRADFORD REGIONAL AP | -25 | 31 | 28 | Pennsylvania
Pennsylvania | BUTLER CO. (AWOS) | -19 | 33 | 31 | Pennsylvania
Pennsylvania | DUBOIS FAA AP | -22 | 32 | 29 | Pennsylvania
Pennsylvania | ERIE INTERNATIONAL AP | -18 | 32 | 30 | Pennsylvania
Pennsylvania | FRANKLIN | -20 | 31 | 29 | Pennsylvania
Pennsylvania | HARRISBURG CAPITAL CITY ARPT | -17 | 37 | 33 | Pennsylvania
Pennsylvania | JOHNSTOWN CAMBRIA COUNTY AP | -20 | 32 | 29 | Pennsylvania
Pennsylvania | MIDDLETOWN HARRISBURG INTL AP | -15 | 37 | 33 | Pennsylvania
Pennsylvania | PHILADELPHIA INTERNATIONAL AP | -14 | 36 | 34 | Pennsylvania
Pennsylvania | PHILADELPHIA NE PHILADELPHIA | -15 | 37 | 33 | Pennsylvania
Pennsylvania | PITTSBURGH ALLEGHENY CO AP | -20 | 34 | 32 | Pennsylvania
Pennsylvania | PITTSBURGH INTERNATIONAL AP | -20 | 34 | 31 | Pennsylvania
Pennsylvania | READING SPAATZ FIELD | N/A | 37 | 33 | Pennsylvania
Pennsylvania | WASHINGTON (AWOS) | N/A | 33 | 31 | Pennsylvania
Pennsylvania | WILKES-BARRE SCRANTON INTL AP | -19 | 34 | 31 | Pennsylvania
Pennsylvania | WILLIAMSPORT REGIONAL AP | -19 | 36 | 32 | Pennsylvania
Pennsylvania | WILLOW GROVE NAS | -17 | 36 | 33 | Pennsylvania
Rhode Island | BLOCK ISLAND STATE ARPT | -14 | 31 | 27 | Rhode Island
Rhode Island | PAWTUCKET (AWOS) | N/A | 33 | 30 | Rhode Island
Rhode Island | PROVIDENCE T F GREEN STATE AR | -17 | 35 | 32 | Rhode Island
South Carolina | ANDERSON COUNTY AP | -10 | 37 | 34 | South Carolina
South Carolina | BEAUFORT MCAS | -6 | 37 | 34 | South Carolina
South Carolina | CHARLESTON INTL ARPT | -7 | 37 | 34 | South Carolina
South Carolina | COLUMBIA METRO ARPT | -10 | 38 | 36 | South Carolina
South Carolina | FLORENCE REGIONAL AP | -9 | 38 | 35 | South Carolina
South Carolina | FOLLY ISLAND | -3 | 33 | 30 | South Carolina
South Carolina | GREER GREENV''L-SPARTANBRG AP | -11 | 37 | 34 | South Carolina
South Carolina | MYRTLE BEACH AFB | -8 | 36 | 33 | South Carolina
South Carolina | SHAW AFB/SUMTER | -9 | 38 | 35 | South Carolina
South Dakota | ABERDEEN REGIONAL ARPT | -32 | 38 | 33 | South Dakota
South Dakota | BROOKINGS (AWOS) | -30 | 34 | 31 | South Dakota
South Dakota | BUFFALO (AMOS) | -29 | 40 | 34 | South Dakota
South Dakota | CHAMBERLAIN (AMOS) | -27 | 41 | 35 | South Dakota
South Dakota | CHAN GURNEY MUNI | -25 | 38 | 33 | South Dakota
South Dakota | CUSTER (RAMOS) | -28 | 34 | 30 | South Dakota
South Dakota | ELLSWORTH AFB | -26 | 39 | 35 | South Dakota
South Dakota | HURON REGIONAL ARPT | -30 | 38 | 34 | South Dakota
South Dakota | MITCHELL (AWOS) | -27 | 39 | 34 | South Dakota
South Dakota | MOBRIDGE | -30 | 39 | 34 | South Dakota
South Dakota | PIERRE MUNICIPAL AP | -28 | 41 | 36 | South Dakota
South Dakota | RAPID CITY REGIONAL ARPT | -27 | 40 | 35 | South Dakota
South Dakota | SIOUX FALLS FOSS FIELD | -29 | 37 | 33 | South Dakota
South Dakota | WATERTOWN MUNICIPAL AP | -29 | 36 | 32 | South Dakota
Tennessee | BRISTOL TRI CITY AIRPORT | -17 | 34 | 32 | Tennessee
Tennessee | CHATTANOOGA LOVELL FIELD AP | -12 | 37 | 34 | Tennessee
Tennessee | CROSSVILLE MEMORIAL AP | -18 | 33 | 31 | Tennessee
Tennessee | DYERSBURG MUNICIPAL AP | -12 | 36 | 34 | Tennessee
Tennessee | JACKSON MCKELLAR-SIPES REGL A | -15 | 36 | 34 | Tennessee
Tennessee | KNOXVILLE MCGHEE TYSON AP | -15 | 36 | 33 | Tennessee
Tennessee | MEMPHIS INTERNATIONAL AP | -12 | 37 | 35 | Tennessee
Tennessee | MILLINGTON MUNI ARP | -14 | 38 | 36 | Tennessee
Tennessee | NASHVILLE INTERNATIONAL AP | -15 | 37 | 34 | Tennessee
Texas | ABILENE DYESS AFB | -12 | 40 | 38 | Texas
Texas | ABILENE REGIONAL AP | -11 | 39 | 37 | Texas
Texas | ALICE INTL AP | -2 | 39 | 37 | Texas
Texas | AMARILLO INTERNATIONAL AP | -17 | 38 | 36 | Texas
Texas | AUSTIN/BERGSTROM | -7 | 39 | 37 | Texas
Texas | BEEVILLE CHASE NAAS | -5 | 39 | 37 | Texas
Texas | BROWNSVILLE S PADRE ISL INTL | 0 | 36 | 35 | Texas
Texas | BURNET MUNI. | -6 | 38 | 36 | Texas
Texas | CAMP MABRY | -5 | 39 | 37 | Texas
Texas | CHILDRESS MUNICIPAL AP | -12 | 40 | 38 | Texas
Texas | COLLEGE STATION EASTERWOOD FL | -6 | 38 | 37 | Texas
Texas | CORPUS CHRISTI INTL ARPT | -3 | 36 | 35 | Texas
Texas | CORPUS CHRISTI NAS | -1 | 34 | 34 | Texas
Texas | COTULLA FAA AP | -4 | 41 | 39 | Texas
Texas | COX FLD | -10 | 38 | 36 | Texas
Texas | DALHART MUNICIPAL AP | -17 | 38 | 36 | Texas
Texas | DALLAS HENSLEY FIELD NAS | -9 | 39 | 37 | Texas
Texas | DALLAS LOVE FIELD | -8 | 39 | 37 | Texas
Texas | DALLAS/REDBIRD ARPT | -8 | 40 | 37 | Texas
Texas | DALLAS-FORT WORTH INTL AP | -9 | 39 | 37 | Texas
Texas | DEL RIO INTERNATIONAL AP | -4 | 40 | 38 | Texas
Texas | DRAUGHON MILLER CEN | -7 | 39 | 37 | Texas
Texas | EL PASO INTERNATIONAL AP | -9 | 40 | 38 | Texas
Texas | FORT HOOD/GRAY AAF | -8 | 39 | 37 | Texas
Texas | FORT STOCKTON PECOS | -8 | 39 | 38 | Texas
Texas | FORT WORTH ALLIANCE | -9 | 40 | 38 | Texas
Texas | FORT WORTH MEACHAM | -10 | 40 | 37 | Texas
Texas | FORT WORTH NAS | -10 | 40 | 37 | Texas
Texas | GALVESTON/SCHOLES | -2 | 34 | 33 | Texas
Texas | GEORGETOWN (AWOS) | -7 | 38 | 36 | Texas
Texas | HARLINGEN RIO GRANDE VALLEY I | 0 | 38 | 37 | Texas
Texas | HONDO MUNICIPAL AP | -7 | 38 | 37 | Texas
Texas | HOUSTON BUSH INTERCONTINENTAL | -4 | 37 | 35 | Texas
Texas | HOUSTON WILLIAM P HOBBY AP | -3 | 36 | 35 | Texas
Texas | HOUSTON/D.W. HOOKS | -4 | 38 | 36 | Texas
Texas | HOUSTON/ELLINGTON | -3 | 37 | 35 | Texas
Texas | JUNCTION KIMBLE COUNTY AP | -10 | 39 | 37 | Texas
Texas | KELLY AFB | -6 | 39 | 37 | Texas
Texas | KILLEEN MUNI (AWOS) | -6 | 39 | 37 | Texas
Texas | KINGSVILLE | -3 | 37 | 36 | Texas
Texas | LAREDO INTL AIRPORT | -2 | 40 | 39 | Texas
Texas | LAUGHLIN AFB | -5 | 42 | 39 | Texas
Texas | LONGVIEW GREGG COUNTY AP | -8 | 39 | 36 | Texas
Texas | LUBBOCK INTERNATIONAL AP | -14 | 39 | 36 | Texas
Texas | LUFKIN ANGELINA CO | -7 | 38 | 36 | Texas
Texas | MARFA AP | -14 | 36 | 34 | Texas
Texas | MC GREGOR (AWOS) | -7 | 39 | 37 | Texas
Texas | MCALLEN MILLER INTL AP | 0 | 39 | 37 | Texas
Texas | MCKINNEY MUNI ARPT | -10 | 39 | 37 | Texas
Texas | MIDLAND INTERNATIONAL AP | -11 | 40 | 37 | Texas
Texas | NACOGDOCHES (AWOS) | -7 | 38 | 36 | Texas
Texas | PALACIOS MUNICIPAL AP | -3 | 34 | 33 | Texas
Texas | PINE SPRINGS GUADALUPE MOUNTA | -12 | 36 | 33 | Texas
Texas | PORT ARANSAS | 0 | 30 | 30 | Texas
Texas | PORT ARTHUR JEFFERSON COUNTY | -4 | 35 | 34 | Texas
Texas | RANDOLPH AFB | -6 | 39 | 37 | Texas
Texas | REESE AFB | -14 | 40 | 37 | Texas
Texas | ROCKPORT/ARANSAS CO | 0 | 34 | 33 | Texas
Texas | SABINE | -3 | 32 | 31 | Texas
Texas | SAN ANGELO MATHIS FIELD | -10 | 40 | 37 | Texas
Texas | SAN ANTONIO INTL AP | -6 | 38 | 36 | Texas
Texas | SAN ANTONIO/STINSON | -4 | 39 | 37 | Texas
Texas | SAN MARCOS MUNI | -5 | 38 | 37 | Texas
Texas | SANDERSON (RAMOS) | -8 | 39 | 36 | Texas
Texas | STEPHENVILLE CLARK FIELD | -10 | 38 | 36 | Texas
Texas | VICTORIA REGIONAL AP | -4 | 37 | 35 | Texas
Texas | WACO REGIONAL AP | -8 | 39 | 37 | Texas
Texas | WICHITA FALLS MUNICIPAL ARPT | -12 | 41 | 38 | Texas
Texas | WINK WINKLER COUNTY AP | -11 | 42 | 40 | Texas
Utah | CEDAR CITY MUNICIPAL AP | -21 | 37 | 34 | Utah
Utah | HILL AFB/OGDEN | -16 | 37 | 33 | Utah
Utah | LOGAN-CACHE AIRPORT | -24 | 38 | 34 | Utah
Utah | MILFORD MUNICIPAL AP | -22 | 39 | 35 | Utah
Utah | PRICE/CARBON COUNTY | -19 | 36 | 33 | Utah
Utah | PROVO MUNI (AWOS) | -15 | 38 | 34 | Utah
Utah | SAINT GEORGE (AWOS) | -6 | 44 | 41 | Utah
Utah | SALT LAKE CITY INT''L ARPT | -16 | 39 | 36 | Utah
Utah | VERNAL | -20 | 37 | 33 | Utah
Utah | WENDOVER USAF AUXILIARY FIELD | -16 | 38 | 35 | Utah
Vermont | BURLINGTON INTERNATIONAL AP | -26 | 34 | 31 | Vermont
Vermont | MONTPELIER AP | -28 | 32 | 29 | Vermont
Vermont | MORRISVILLE\STONE | -28 | 31 | 29 | Vermont
Vermont | RUTLAND STATE | -26 | 31 | 29 | Vermont
Vermont | SPRINGFIELD/HARTNES | -25 | 33 | 31 | Vermont
Virginia | ABINGTON | -16 | 32 | 31 | Virginia
Virginia | CHESAPEAKE | -8 | 31 | 28 | Virginia
Virginia | DANVILLE FAA AP | -12 | 36 | 34 | Virginia
Virginia | DINWIDDIE CO | -14 | 38 | 36 | Virginia
Virginia | FARMVILLE | -16 | 37 | 34 | Virginia
Virginia | FORT BELVOIR/DAVISO | -17 | 38 | 35 | Virginia
Virginia | HILLSVILLE | -15 | 31 | 29 | Virginia
Virginia | HOT SPRINGS/INGALLS | -19 | 31 | 28 | Virginia
Virginia | LANGLEY AFB/HAMPTON | -10 | 36 | 33 | Virginia
Virginia | LEESBURG/GODFREY | -14 | 37 | 34 | Virginia
Virginia | LYNCHBURG REGIONAL ARPT | -15 | 35 | 33 | Virginia
Virginia | MANASSAS MUNI(AWOS) | -16 | 36 | 33 | Virginia
Virginia | MARION / WYTHEVILLE | -17 | 33 | 32 | Virginia
Virginia | MARTINSVILLE | -15 | 36 | 34 | Virginia
Virginia | MECKLENBURG\BRUNS. | N/A | 37 | 34 | Virginia
Virginia | MELFA/ACCOMACK ARPT | N/A | 36 | 34 | Virginia
Virginia | NEWPORT NEWS | -11 | 37 | 34 | Virginia
Virginia | NORFOLK INTERNATIONAL AP | -9 | 36 | 34 | Virginia
Virginia | NORFOLK NAS | -9 | 37 | 34 | Virginia
Virginia | OCEANA NAS | -10 | 36 | 33 | Virginia
Virginia | QUANTICO MCAS | -13 | 36 | 33 | Virginia
Virginia | ROANOKE REGIONAL AP | -14 | 36 | 33 | Virginia
Virginia | SHANNON ARPT | -15 | 37 | 35 | Virginia
Virginia | STAUNTON/SHENANDOAH | -17 | 37 | 34 | Virginia
Virginia | VIRGINIA TECH ARPT | -15 | 33 | 31 | Virginia
Virginia | WALLOPS ISLAND UAU | -11 | 35 | 32 | Virginia
Virginia | WASHINGTON DC DULLES INT''L AR | -17 | 36 | 34 | Virginia
Virginia | WASHINGTON DC REAGAN AP | -12 | 37 | 34 | Virginia
Virginia | WINCHESTER RGNL | -15 | 37 | 34 | Virginia
Virginia | WISE/LONESOME PINE | N/A | 31 | 29 | Virginia
Washington | ARLINGTON MUNI | -9 | 32 | 27 | Washington
Washington | BELLINGHAM INTL AP | -10 | 29 | 26 | Washington
Washington | BREMERTON NATIONAL | -8 | 34 | 29 | Washington
Washington | DESTRUCTION ISLAND | -2 | 19 | 17 | Washington
Washington | FAIRCHILD AFB | -19 | 36 | 32 | Washington
Washington | FELTS FLD | -17 | 38 | 34 | Washington
Washington | FRIDAY HARBOR | -5 | 29 | 25 | Washington
Washington | GRAY AAF | -10 | 34 | 29 | Washington
Washington | HANFORD | -16 | 41 | 37 | Washington
Washington | HOQUIAM AP | -4 | 28 | 23 | Washington
Washington | KELSO WB AP | -8 | 35 | 29 | Washington
Washington | MC CHORD AFB/TACOMA | -10 | 34 | 29 | Washington
Washington | OLYMPIA AIRPORT | -11 | 35 | 30 | Washington
Washington | OMAK | -16 | 39 | 35 | Washington
Washington | PASCO | -17 | 41 | 36 | Washington
Washington | PEARSON FLD | -7 | 37 | 32 | Washington
Washington | PULLMAN/MOSCOW RGNL | -18 | 36 | 32 | Washington
Washington | QUILLAYUTE STATE AIRPORT | -7 | 29 | 25 | Washington
Washington | SEATTLE BOEING FIELD | -7 | 33 | 29 | Washington
Washington | SEATTLE SEATTLE-TACOMA INTL A | -6 | 33 | 29 | Washington
Washington | SHELTON/SANDERSON | -7 | 35 | 30 | Washington
Washington | SMITH ISLAND | -3 | 22 | 18 | Washington
Washington | SNOHOMISH CO | -5 | 30 | 26 | Washington
Washington | SPOKANE INTERNATIONAL AP | -20 | 37 | 33 | Washington
Washington | STAMPEDE PASS | -15 | 29 | 25 | Washington
Washington | TACOMA NARROWS | -4 | 33 | 28 | Washington
Washington | TATOOSH ISLAND | -2 | 19 | 17 | Washington
Washington | WALLA WALLA CITY COUNTY AP | -14 | 41 | 36 | Washington
Washington | WENATCHEE/PANGBORN | -16 | 38 | 34 | Washington
Washington | WEST POINT (LS) | -3 | 24 | 21 | Washington
Washington | WHIDBEY ISLAND NAS | -9 | 25 | 22 | Washington
Washington | WILLIAM R FAIRCHILD | -6 | 30 | 25 | Washington
Washington | YAKIMA AIR TERMINAL | -18 | 38 | 34 | Washington
West Virginia | BECKLEY RALEIGH CO MEM AP | -20 | 31 | 29 | West Virginia
West Virginia | BLUEFIELD/MERCER CO | -19 | 31 | 29 | West Virginia
West Virginia | CHARLESTON YEAGER ARPT | -18 | 35 | 32 | West Virginia
West Virginia | ELKINS ELKINS-RANDOLPH CO ARP | -24 | 32 | 30 | West Virginia
West Virginia | HARRISON MARION RGN | -17 | 33 | 32 | West Virginia
West Virginia | HUNTINGTON TRI-STATE ARPT | -18 | 35 | 33 | West Virginia
West Virginia | MARTINSBURG EASTERN WV REG AP | -18 | 37 | 33 | West Virginia
West Virginia | MORGANTOWN HART FIELD | -19 | 34 | 31 | West Virginia
West Virginia | PARKERSBURG WOOD COUNTY AP | -19 | 35 | 32 | West Virginia
Wisconsin | ANTIGO\LANG(AWOS) | N/A | 33 | 29 | Wisconsin
Wisconsin | APPLETON/OUTAGAMIE | -24 | 35 | 31 | Wisconsin
Wisconsin | DEVILS ISLAND | -24 | 30 | 25 | Wisconsin
Wisconsin | EAGLE RIVER UNION | -31 | 32 | 28 | Wisconsin
Wisconsin | EAU CLAIRE COUNTY AP | -30 | 36 | 32 | Wisconsin
Wisconsin | FOND DU LAC CO. | -24 | 34 | 31 | Wisconsin
Wisconsin | GREEN BAY AUSTIN STRAUBEL INT | -27 | 34 | 31 | Wisconsin
Wisconsin | HAYWARD MUNI ARPT | -32 | 36 | 30 | Wisconsin
Wisconsin | JUNEAU\DODGE CO | -23 | 33 | 30 | Wisconsin
Wisconsin | KENOSHA RGNL | -23 | 36 | 32 | Wisconsin
Wisconsin | LA CROSSE MUNICIPAL ARPT | -27 | 36 | 33 | Wisconsin
Wisconsin | MADISON DANE CO REGIONAL ARPT | -26 | 34 | 32 | Wisconsin
Wisconsin | MANITOWAC MUNI AWOS | -23 | 33 | 29 | Wisconsin
Wisconsin | MARSHFIELD MUNI | -27 | 35 | 30 | Wisconsin
Wisconsin | MILWAUKEE MITCHELL INTL AP | -24 | 35 | 32 | Wisconsin
Wisconsin | MOSINEE/CENTRAL WI | -28 | 34 | 30 | Wisconsin
Wisconsin | PARK FALLS MUNI | N/A | 31 | 29 | Wisconsin
Wisconsin | PHILLIPS/PRICE CO. | -32 | 33 | 29 | Wisconsin
Wisconsin | RHINELANDER ONEIDA | -30 | 33 | 29 | Wisconsin
Wisconsin | RICE LAKE MUNICIPAL | -29 | 34 | 30 | Wisconsin
Wisconsin | SHEBOYGAN | N/A | 34 | 30 | Wisconsin
Wisconsin | SHEBOYGAN | -22 | 32 | 28 | Wisconsin
Wisconsin | STURGEON BAY | -24 | 32 | 28 | Wisconsin
Wisconsin | WATERTOWN | -25 | 34 | 31 | Wisconsin
Wisconsin | WAUSAU MUNICIPAL ARPT | -29 | 34 | 31 | Wisconsin
Wisconsin | WISCONSIN RAPIDS | -27 | 34 | 31 | Wisconsin
Wisconsin | WITTMAN RGNL | -24 | 34 | 31 | Wisconsin
Wyoming | BIG PINEY (AMOS) | -33 | 32 | 29 | Wyoming
Wyoming | CASPER NATRONA CO INTL AP | -29 | 37 | 34 | Wyoming
Wyoming | CHEYENNE MUNICIPAL ARPT | -26 | 34 | 31 | Wyoming
Wyoming | CODY MUNI (AWOS) | -28 | 36 | 32 | Wyoming
Wyoming | GILLETTE/GILLETTE-C | -28 | 38 | 34 | Wyoming
Wyoming | JACKSON HOLE | -31 | 32 | 28 | Wyoming
Wyoming | LANDER HUNT FIELD | -27 | 36 | 33 | Wyoming
Wyoming | LARAMIE GENERAL BREES FIELD | -31 | 32 | 29 | Wyoming
Wyoming | ROCK SPRINGS ARPT | -26 | 34 | 30 | Wyoming
Wyoming | SHERIDAN COUNTY ARPT | -29 | 38 | 34 | Wyoming
Wyoming | WORLAND MUNICIPAL | -34 | 39 | 35 | Wyoming
Wyoming | YELLOWSTONE LAKE (RAMOS) | -33 | 27 | 24 | Wyoming
Alabama
Alaska
Arizona
Arkansas
California
Colorado
Connecticut
Delaware
Florida
Georgia
Hawaii
Idaho
Illinois
Indiana
Iowa
Kansas
Kentucky
Louisiana
Maine
Maryland
Massachusetts
Michigan
Minnesota
Mississippi
Missouri
Montana
Nebraska
Nevada
New_Hampshire
New_Jersey
New_Mexico
New_York
North_Carolina
North_Dakota
Ohio
Oklahoma
Oregon
Pennsylvania
Rhode_Island
South_Carolina
South_Dakota
Tennessee
Texas
Utah
Vermont
Virginia
Washington
West_Virginia
Wisconsin
Wyoming
|  | Delaware | Arkansas | Arizona | Alaska | Iowa | Idaho | Illinois | Indiana | Kansas | Kentucky | Louisiana | Massachusetts | Maryland | Maine | Michigan | Minnesota | Missouri | Mississippi | Montana | North_Carolina | North_Dakota | Nebraska | New_Hampshire | New_Jersey | New_Mexico | Nevada | New_York | Ohio | Oklahoma | Oregon | Pennsylvania | Rhode_Island | South_Carolina | South_Dakota | Tennessee | Texas | Utah | Virginia | Vermont | Washington | Wisconsin | West_Virginia | Wyoming